## README
AB | LEGEND
| AB-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| Distribution | Characteristics of existing distribution substations
| System | Miscellaneous provincial system characteristics
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review or being gathered
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to sources
See the accompanying calculations file and raw data files for additional supporting information
See the related Gitlab issue for a summary of inventory status

## AB-Sources
AB | PRIMARY SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| AESO | 2019 | Information Document Uniform Capacity Value Determination | https://www.aeso.ca/assets/Uploads/206.3-UCAP.pdf |  | Alberta
| AESO | 2019 | Current Supply Demand Report | http://ets.aeso.ca/ets_web/ip/Market/Reports/CSDReportServlet |  | Alberta
| Dispatcho | 2019 |  | https://www.dispatcho.app/assets |  | Alberta
| AESO | 2019 | AESO 2019 Annual Market Statistics | https://www.aeso.ca/market/market-and-system-reporting/annual-market-statistic-reports/ |  | Alberta
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" Column of the relevant tab
| Nova Scotia Power Inc. | 2020 | NS Power 2020 IRP Modeling Results Release | https://irp.nspower.ca/documents/modeling-results/ |  | Nova Scotia
| Alberta Utilities Commission | 2020 | Annual Electricity Data | https://www.auc.ab.ca/Pages/annual-electricity-data.aspx |  | Alberta
| AESO | 2021 | Alberta Electric System Operator System Co-ordination Plan Approved Outages | https://www.aeso.ca/grid/grid-operations/outages/ |  | Alberta | Reference includes archives dating back to 2014.
| CBC | 2020 | TC Energy joins hydroelectric power storage project at retired coal mine site | https://www.cbc.ca/news/canada/calgary/tc-energy-joins-pumped-hydro-power-storage-project-retired-coal-mine-site-1.5577377 |  | Ontario, Alberta
| WECC | 2019 | ADS 2028 Deliverables Datasets | https://www.wecc.org/SystemAdequacyPlanning/Pages/Datasets.aspx |  | Alberta, British Columbia | On the website, under Production Cost Model see 2024 Common Case sheet 150409_2024CC-V1.5_Resources
| WECC | 2019 | ADS 2028 Deliverables Anchor Data Set | https://www.wecc.org/SystemStabilityPlanning/Pages/AnchorDataSet.aspx |  | Alberta, British Columbia | On the website, under Production Cost Model see ADS_PCM_V0.3.2_GeneratorList.csv and supporting information
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | Canada
| Government of Alberta | 2019 | Alberta River Basins | https://rivers.alberta.ca |  | Alberta
| Government of Alberta | 2019 | Geodiscover Alberta | https://geodiscover.alberta.ca/geoportal/catalog/search/browse/browse.page |  | Alberta
| AESO | 2019 | AESO 2019 Long-term Outlook | https://www.aeso.ca/grid/forecasting/ |  | Alberta | See also the 2019 LTO Data File
| Transalta | 2019 | Facilities in Operation/Development | https://www.transaltarenewables.com/facilities/plants-operation/ |  | Alberta
| Hatch | 2010 | Update on Alberta's Hydroelectric Energy Resources. Final Report for Alberta Utilities Commission. |  |  | Alberta
| Transalta | 2017 | Brazeau Pumped Storage - Building Alberta's Future | https://www.brazeauhydro.com/details/ |  | Alberta
| AESO | 2020 | 2020 Long-term Transmission Plan (including SLDs) | https://www.aeso.ca/grid/long-term-transmission-plan/ |  | Alberta | See also the Single Line Diagrams
| AHP Development Corporation | 2019 | The Amisk Hydroelectric Project | http://www.amiskhydro.com |  | Alberta
| AESO | 2018 | Hourly Metered Volumes and Pool Price and AIL from 2008 to 2018 | https://www.aeso.ca/market/market-and-system-reporting/data-requests/hourly-metered-volumes-and-pool-price-and-ail-from-2008-to-2018/ |  | Alberta
| Turning Point Generation | 2017 | Alberta Utilities Commission Power Plant and Hydro Development Application for the Canyon Creek Pumped Storage Hydro Energy Storage Project | http://www.auc.ab.ca/Pages/default.aspx |  | Alberta
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
AB | EXISTING GENERATION | [13 empty] | DESIGN | [7 empty] | OPERATIONS | [13 empty] | OPERATING COSTS
| Project Name | Gen Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Unit | # of units | Inc Heat Rate @ Max | Minimum Capacity | Maximum Capacity | Minimum Up Time | Minimum Down Time | Spin Up Ramp Rate | Spin Down Ramp Rate | Start Up Ramp Limit | Shut Down Ramp Limit | Must Run | Operating Reserve Fraction | Outage Duration | Forced Outage Rate | Maintenance Outage Rate | Start Up Costs | Fuel Costs | Shut Down Costs | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | kV | kV |  |  |  |  | (MW) |  | (MW) | (%) | (GWh/year) |  | (MMBtu/MWh) | (MW) | (MW) | (hours) | (hours) | (%/min) | (%/min) | [MW/hr p MWcap] | [MW/hr p MWcap] | (T/F) | (%) | (hours) | (%) | (days/y) | (S/MWcap) | ($/MWh) | (S/MWcap) | ($/year) | ($/MWh)
| ALPAC | AB_ALP00_GEN | Alberta-Pacific Forest Industries | Boyle | 54.921 | -112.8622 | Alberta.a | Alberta | Boyle 56S | AB_56S_DSS | 138 | 138 | 2012 | 2100 | Biomass | biomass | 131 | 97% | 127.07 | 55% | 631.158 | 4 | 11.77 | 44.32 | 131.2 | 8 | 8 |  |  |  |  | TRUE |  | 38 | 3.09 | 11 | 5.3005 |  |  |  | 1.9082
| CANCARB | AB_CCB00_GEN | Tokai Carbon Co. | Medicine Hat | 50.0574 | -110.7262 | Alberta.a | Alberta | Medicine Hat 41S | AB_41S_GSS | 138 | 138 | 2000 | 2100 | Biomass | biomass | 36 | 97% | 34.92 | 55% | 173.448 | 1 | 10.7396 | 14.4 | 36 | 168 | 8 |  |  |  |  | TRUE |  | 38 | 3.09 | 11 | 5.3005 |  |  |  | 1.9082 |  | Waste heat recovery facility
| Daishowa | AB_DAI00_GEN | Daishowa-Marubeni | St. Isidore | 56.3711 | -117.1856 | Alberta.a | Alberta | Daishowa 839S | AB_839S_GSS | 144 | 144 | 2011 | 2100 | Biomass | biomass | 25.1 | 97% | 24.347 | 55% | 120.9318 | 1 | 11.77 | 21.335 | 25.1 | 8 | 8 |  |  |  |  | TRUE |  | 38 | 3.09 | 11 | 5.3005 |  |  |  | 1.9082
| Gold Creek | AB_GOC00_GEN | Maxim | Grovedale | 55.0256 | -118.8668 | Alberta.a | Alberta | Bridge Creek 798S | AB_798S_DSS | 144 | 144 | 1999 | 2100 | Biomass | biomass | 5 | 97% | 4.85 | 55% | 24.09 | 1 | 11.0823 | 3 | 5 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 2.49 | 15 | 109.1903 |  |  |  | 0.60426 |  | Waste heat recovery facility
| Grand Prairie | AB_GPR00_GEN | Canadian Forest Products Ltd. | Grande Prairie | 55.1602 | -118.8184 | Alberta.a | Alberta | CG&E 758S | AB_758S_DSS | 144 | 144 | 2004 | 2100 | Biomass | biomass | 27 | 97% | 26.19 | 55% | 130.086 | 1 | 11.77 | 8.1 | 27 | 8 | 8 |  |  |  |  | TRUE |  | 38 | 3.09 | 11 | 5.3005 |  |  |  | 1.9082
| Hinton_01 | AB_HNT01_GEN | West Fraser Timber Co. | Hinton | 53.4153 | -117.5717 | Alberta.a | Alberta | Dalehurst 975S | AB_975S_DSS | 144 | 144 | 1985 | 2100 | Biomass | biomass | 26 | 97% | 25.22 | 55% | 125.268 | 2
| Hinton_02 | AB_HNT02_GEN | West Fraser Timber Co. | Hinton | 53.4153 | -117.5717 | Alberta.a | Alberta | Dalehurst 975S | AB_975S_DSS | 144 | 144 | 1985 | 2100 | Biomass | biomass | 26 | 97% | 25.22 | 55% | 125.268 | 2
| NRGreen | AB_NRG00_GEN | NRGreen Power Limited Partnership | Swan Hills | 54.2075 | -115.1608 | Alberta.a | Alberta | Chickadee Creek 259S | AB_259S_DSS | 144 | 144 | 2013 | 2100 | Biomass | biomass | 16 | 97% | 15.52 | 55% | 77.088 | 1 | 11.0823 | 7.2 | 16 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Slave Lake Pulp | AB_SLP00_GEN | Slave Lake Pulp | Slave Lake | 55.2509 | -114.5181 | Alberta.a | Alberta | Otauwau 729S | AB_729S_DSS | 72 | 72 | 2015 | 2100 | Biomass | biomass | 9 | 97% | 8.73 | 55% | 43.362 | 1 | 11.77 | 7 | 9 | 168 | 8 |  |  |  |  | TRUE |  | 38
| Valley Power | AB_VLP00_GEN | Algonquin Power | Rocky Rapids | 53.2069 | -114.993 | Alberta.a | Alberta | Moon Lake 131S | AB_131S_DSS | 138 | 138 | 2000 | 2100 | Biomass | biomass | 12 | 97% | 11.64 | 55% | 57.816 | 1
| Vanderwell | AB_VNW00_GEN | Vanderwell Contractors (1971) | Slave Lake | 55.264 | -114.5893 | Alberta.a | Alberta | Otauwau 729S | AB_729S_DSS | 72 | 72 | 2000 | 2100 | Biomass | biomass | 4 | 97% | 3.88 | 55% | 19.272 | 1
| Vegreville Biodigester | AB_VGV00_GEN | Highmark Renewables | Vegreville | 53.6934 | -111.9786 | Alberta.a | Alberta | Vegreville 709S | AB_709S_DSS | 144 | 144 | 2000 | 2100 | Biomass | biomass | 1 | 97% | 0.97 | 55% | 4.818 | 1
| Weldwood | AB_WWD00_GEN | West Fraser Mills | Hinton | 53.5521 | -116.6165 | Alberta.a | Alberta | Cold Creek 602S | AB_602S_DSS | 138 | 138 | 1990 | 2100 | Biomass | biomass | 50 | 97% | 48.5 | 55% | 240.9 | 1 | 12.0145 | 12 | 50 | 8 | 8 |  |  |  |  | TRUE |  | 38 | 3.09 | 11 | 5.3005 |  |  |  | 1.9082
| Westlock | AB_WST00_GEN | Drayton Valley Power | Dapp | 54.4153 | -114.1769 | Alberta.a | Alberta | Westlock 438S | AB_438S_GSS | 138 | 138 | 1996 | 2100 | Biomass | biomass | 16.9 | 97% | 16.393 | 55% | 81.4242 | 1 | 13.8147 | 5.07 | 16.9 | 8 | 4 |  |  |  |  | TRUE |  | 38 | 3.09 | 11 | 5.3005 |  |  |  | 1.9082
| Weyerhaeuser | AB_WEY00_GEN | P&G Weyerhaeuser | Grande Prairie | 55.0711 | -118.6907 | Alberta.a | Alberta | P&G A808S | AB_A808S_DSS | 144 | 144 | 2011 | 2100 | Biomass | biomass | 15 | 97% | 14.55 | 55% | 72.27 | 1 | 13.5 | 4.5 | 15 | 5 | 8 |  |  |  |  | TRUE |  | 38 | 3.09 | 11 | 5.3005 |  |  |  | 1.9082
| Whitecourt | AB_WTC00_GEN | Whitecourt Power Ltd. | Whitecourt | 54.1624 | -115.7336 | Alberta.a | Alberta | Whitecourt 268S | AB_268S_DSS | 144 | 144 | 1994 | 2100 | Biomass | biomass | 23 | 97% | 22.31 | 55% | 110.814 | 1 | 10.0674 | 21.25 | 23 | 8 | 4 |  |  |  |  | TRUE |  | 38 | 3.09 | 11 | 5.3005 |  |  |  | 1.9082
| Battle River Coal_04 | AB_BRC04_GEN | Alberta Power (2000) Ltd. | Halkirk | 52.4685 | -112.1339 | Alberta.a | Alberta | Battle River 757S | AB_757S_GSS | 240 | 240 | 1975 | 2022 | Coal | coal | 148 | 90% | 133.2 | 55% | 713.064 | 2 | 10.3198 | 59.2 | 148 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 3.7 | 17 | 155.8347 |  |  |  | 2.9895 | Alberta Utilities Commission. 2020. Heartland Generation Ltd Battle River Power Plant Amendment.
| Battle River Coal_05 | AB_BRC05_GEN | Alberta Power (2000) Ltd. | Halkirk | 52.4685 | -112.1339 | Alberta.a | Alberta | Battle River 757S | AB_757S_GSS | 240 | 240 | 1981 | 2022 | Coal | coal | 407 | 90% | 366.3 | 55% | 1960.926 | 2 | 10.2331 | 162.8 | 407 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.21 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Utilities Commission. 2020. Heartland Generation Ltd Battle River Power Plant Amendment.
| Genesee Coal_01 | AB_GNC01_GEN | Capital Power (G3) Limited Partnership | Lake Wabamun | 53.3446 | -114.3049 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 138 | 138 | 1994 | 2022 | Coal | coal | 422 | 90% | 379.8 | 55% | 2033.196 | 3 | 8.9283 | 168.8 | 422 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.21 | 19 | 111.3105 |  |  |  | 2.8411 | https://www.capitalpower.com/operations/genesee-3/
| Genesee Coal_02 | AB_GNC02_GEN | Capital Power (G3) Limited Partnership | Lake Wabamun | 53.3446 | -114.3049 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 138 | 138 | 1989 | 2022 | Coal | coal | 422 | 90% | 379.8 | 55% | 2033.196 | 3 | 8.9283 | 168.8 | 422 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.21 | 19 | 111.3105 |  |  |  | 2.8411 | https://www.capitalpower.com/operations/genesee-3/
| Genesee Coal_03 | AB_GNC03_GEN | Capital Power (G3) Limited Partnership | Lake Wabamun | 53.3446 | -114.3049 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 138 | 138 | 2004 | 2022 | Coal | coal | 527 | 90% | 474.3 | 55% | 2539.086 | 3 | 8.5202 | 210.8 | 527 | 140 | 48 |  |  |  |  | FALSE |  | 48 | 5.79 | 20 | 110.2504 |  |  |  | 3.1379 | https://www.capitalpower.com/operations/genesee-3/
| Keephills Coal_01 | AB_KHC01_GEN | TransAlta Corporation | Lake Wabamun | 53.4487 | -114.4501 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 240 | 240 | 2012 | 2021 | Coal | coal | 434 | 90% | 390.6 | 55% | 2091.012 | 3 | 9.1841 | 173.6 | 434 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.19 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Utilities Commission. 2020. Transalta Corporation. Keephills Power Plant Repowering.
| Keephills Coal_02 | AB_KHC02_GEN | TransAlta Corporation | Lake Wabamun | 53.4487 | -114.4501 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 240 | 240 | 2012 | 2021 | Coal | coal | 434 | 90% | 390.6 | 55% | 2091.012 | 3 | 9.1841 | 173.6 | 434 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.19 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Utilities Commission. 2020. Transalta Corporation. Keephills Power Plant Repowering.
| Keephills Coal_03 | AB_KHC03_GEN | TransAlta Corporation | Lake Wabamun | 53.4487 | -114.4501 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 240 | 240 | 2011 | 2021 | Coal | coal | 498 | 90% | 448.2 | 55% | 2399.364 | 3 | 8.565 | 199.2 | 498 | 140 | 48 |  |  |  |  | FALSE |  | 48 | 5.79 | 20 | 110.2504 |  |  |  | 3.1379
| Sheerness Coal_01 | AB_SHC01_GEN | TransAlta Corporation | Sheerness | 51.4426 | -111.7919 | Alberta.a | Alberta | Sheerness 807S | AB_807S_GSS | 240 | 240 | 1986 | 2022 | Coal | coal | 408 | 90% | 367.2 | 55% | 1965.744 | 2 | 8.8679 | 163.2 | 408 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.21 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Power (2000) Ltd and TransAlta Cogeneration Ltd. 2020. Sheerness Power Plant Dual Fuel Conversion.
| Sheerness Coal_02 | AB_SHC02_GEN | TransAlta Corporation | Sheerness | 51.4426 | -111.7919 | Alberta.a | Alberta | Sheerness 807S | AB_807S_GSS | 240 | 240 | 1990 | 2022 | Coal | coal | 408 | 90% | 367.2 | 55% | 1965.744 | 2 | 8.8679 | 163.2 | 408 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.21 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Power (2000) Ltd and TransAlta Cogeneration Ltd. 2020. Sheerness Power Plant Dual Fuel Conversion.
| Sundance Coal_04 | AB_SDC04_GEN | TransAlta Corporation | Lake Wabamun | 53.5075 | -114.5569 | Alberta.a | Alberta | Sundance 310P | AB_310P_GSS | 240 | 240 | 2007 | 2021 | Coal | coal | 406 | 90% | 365.4 | 55% | 1956.108 | 2 | 9.1048 | 162.4 | 406 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.19 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Utilities Commission. 2020. Transalta Corporation Sundance Power Plant Repowering.
| Sundance Coal_06 | AB_SDC06_GEN | TransAlta Corporation | Lake Wabamun | 53.5075 | -114.5569 | Alberta.a | Alberta | Sundance 310P | AB_310P_GSS | 240 | 240 | 2001 | 2021 | Coal | coal | 401 | 90% | 360.9 | 55% | 1932.018 | 2 | 9.1532 | 160.4 | 401 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.19 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Utilities Commission. 2020. Transalta Corporation Sundance Power Plant Repowering.
| Bearspaw | AB_BSP00_GEN | TransAlta Corporation | Calgary | 51.1012 | -114.2823 | Alberta.a | Alberta | Bearspaw Plant 44S | AB_44S_GSS | 138 | 138 | 1954 | 2034 | Hydro_daily | hydro_daily | 17 | 100% | 17 | 24% | 35.7408 | 1 | n/a | 0 | 17 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Bighorn_01 | AB_BIG01_GEN | TransAlta Corporation | Nordegg | 52.3081 | -116.3245 | Alberta.a | Alberta | Bighorn Plant 250P | AB_250P_GSS | 144 | 144 | 1972 | 2034 | Hydro_daily | hydro_daily | 60 | 100% | 60 | 24% | 126.144 | 2 | n/a | 0 | 60 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Bighorn_02 | AB_BIG02_GEN | TransAlta Corporation | Nordegg | 52.3081 | -116.3245 | Alberta.a | Alberta | Bighorn Plant 250P | AB_250P_GSS | 144 | 144 | 1972 | 2034 | Hydro_daily | hydro_daily | 60 | 100% | 60 | 24% | 126.144 | 2 | n/a | 0 | 60 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Brazeau_01 | AB_BRA01_GEN | TransAlta Corporation | Drayton Valley | 52.9101 | -115.3754 | Alberta.a | Alberta | Brazeau 62S | AB_62S_GSS | 240 | 240 | 1966 | 2034 | Hydro_daily | hydro_daily | 162 | 100% | 162 | 24% | 340.5888 | 2 | n/a | 0 | 162 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Brazeau_02 | AB_BRA02_GEN | TransAlta Corporation | Drayton Valley | 52.9101 | -115.3754 | Alberta.a | Alberta | Brazeau 62S | AB_62S_GSS | 240 | 240 | 1966 | 2034 | Hydro_daily | hydro_daily | 200 | 100% | 200 | 24% | 420.48 | 2 | n/a | 0 | 200 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Cascade Hydro_01 | AB_CSC01_GEN | TransAlta Corporation | Banff | 51.2002 | -115.5021 | Alberta.a | Alberta | Cascade 29S | AB_29S_GSS | 138 | 138 | 1954 | 2034 | Hydro_daily | hydro_daily | 17 | 100% | 17 | 24% | 35.7408 | 2 | n/a | 0 | 17 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Cascade Hydro_02 | AB_CSC02_GEN | TransAlta Corporation | Banff | 51.2002 | -115.5021 | Alberta.a | Alberta | Cascade 29S | AB_29S_GSS | 138 | 138 | 1954 | 2034 | Hydro_daily | hydro_daily | 18 | 100% | 18 | 24% | 37.8432 | 2 | n/a | 0 | 18 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Ghost_01 | AB_GHT01_GEN | TransAlta Corporation | Cochrane | 51.2188 | -114.7078 | Alberta.a | Alberta | Ghost 20S | AB_20S_GSS | 138 | 138 | 1929 | 2034 | Hydro_daily | hydro_daily | 16 | 100% | 16 | 24% | 33.6384 | 4 | n/a | 0 | 1 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Ghost_02 | AB_GHT02_GEN | TransAlta Corporation | Cochrane | 51.2188 | -114.7078 | Alberta.a | Alberta | Ghost 20S | AB_20S_GSS | 138 | 138 | 1929 | 2034 | Hydro_daily | hydro_daily | 16 | 100% | 16 | 24% | 33.6384 | 4 | n/a | 0 | 16 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Ghost_03 | AB_GHT03_GEN | TransAlta Corporation | Cochrane | 51.2188 | -114.7078 | Alberta.a | Alberta | Ghost 20S | AB_20S_GSS | 138 | 138 | 1929 | 2034 | Hydro_daily | hydro_daily | 16 | 100% | 16 | 24% | 33.6384 | 4 | n/a | 0 | 16 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Ghost_04 | AB_GHT04_GEN | TransAlta Corporation | Cochrane | 51.2188 | -114.7078 | Alberta.a | Alberta | Ghost 20S | AB_20S_GSS | 138 | 138 | 1929 | 2034 | Hydro_daily | hydro_daily | 28 | 100% | 28 | 24% | 58.8672 | 4 | n/a | 0 | 28 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Oldman_01 | AB_OMH01_GEN | ATCO Power Canada Ltd. | Pincher Creek | 49.561 | -113.896 | Alberta.a | Alberta | Oldman River 806S | AB_806S_GSS | 144 | 144 | 2003 | 2034 | Hydro_daily | hydro_daily | 16 | 100% | 16 | 24% | 33.6384 | 2 | n/a | 0 | 16 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Oldman_02 | AB_OMH02_GEN | ATCO Power Canada Ltd. | Pincher Creek | 49.561 | -113.896 | Alberta.a | Alberta | Oldman River 806S | AB_806S_GSS | 144 | 144 | 2003 | 2034 | Hydro_daily | hydro_daily | 16 | 100% | 16 | 24% | 33.6384 | 2 | n/a | 0 | 16 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Rundle_01 | AB_RND01_GEN | TransAlta Corporation | Canmore | 51.0887 | -115.3736 | Alberta.a | Alberta | Rundle 35S | AB_35S_GSS | 138 | 138 | 1951 | 2034 | Hydro_daily | hydro_daily | 17 | 100% | 17 | 24% | 35.7408 | 2 | n/a | 0 | 17 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Rundle_02 | AB_RND02_GEN | TransAlta Corporation | Canmore | 51.0887 | -115.3736 | Alberta.a | Alberta | Rundle 35S | AB_35S_GSS | 138 | 138 | 1951 | 2034 | Hydro_daily | hydro_daily | 30 | 100% | 30 | 24% | 63.072 | 2 | n/a | 0 | 30 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Spray_01 | AB_SPR01_GEN | TransAlta Corporation | Canmore | 51.0745 | -115.4024 | Alberta.a | Alberta | Spray 33S | AB_33S_GSS | 138 | 138 | 1954 | 2034 | Hydro_daily | hydro_daily | 46 | 100% | 46 | 24% | 96.7104 | 2 | n/a | 0 | 46 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Spray_02 | AB_SPR02_GEN | TransAlta Corporation | Canmore | 51.0745 | -115.4024 | Alberta.a | Alberta | Spray 33S | AB_33S_GSS | 138 | 138 | 1954 | 2034 | Hydro_daily | hydro_daily | 46 | 100% | 46 | 24% | 96.7104 | 2 | n/a | 0 | 46 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Barrier | AB_BRR00_GEN | TransAlta Corporation | Seebe | 51.0342 | -115.0409 | Alberta.a | Alberta | Barrier 32S | AB_32S_GSS | 138 | 138 | 1954 | 2034 | Hydro_run | hydro_run | 11.2 | 30% | 3.36 | 24% | 23.5469 | 1 | n/a | 0 | 11.2 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Belly River | AB_BLR00_GEN | TransAlta Corporation | Glenwood | 49.315 | -113.5743 | Alberta.a | Alberta | Glenwood 229S | AB_229S_DSS | 138 | 138 | 1986 | 2034 | Hydro_run | hydro_run | 2.7 | 30% | 0.81 | 24% | 5.6765 | 1 | n/a | 0 | 2.7 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Chin Chute Hydro | AB_CHH00_GEN | Irrigation Canal Cooperative Ltd (Irrican) | Lethbridge County | 49.6756 | -112.3446 | Alberta.a | Alberta | Chin Chute 315S | AB_315S_GSS | 138 | 138 | 1994 | 2034 | Hydro_run | hydro_run | 12 | 30% | 3.6 | 24% | 25.2288 | 1 | n/a | 0 | 12 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Dickson Dam_01 | AB_DKSN01_GEN | Algonquin Power | Red Deer River | 52.0527 | -114.2229 | Alberta.a | Alberta | Red Deer 63S | AB_63S_DSS | 240 | 240 | 1992 | 2034 | Hydro_run | hydro_run | 5.6 | 30% | 1.68 | 24% | 11.7734 | 3 | n/a | 0 | 5.6 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Dickson Dam_02 | AB_DKSN02_GEN | Algonquin Power | Red Deer River | 52.0527 | -114.2229 | Alberta.a | Alberta | Red Deer 63S | AB_63S_DSS | 240 | 240 | 1992 | 2034 | Hydro_run | hydro_run | 5.6 | 30% | 1.68 | 24% | 11.7734 | 3 | n/a | 0 | 5.6 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Dickson Dam_03 | AB_DKSN03_GEN | Algonquin Power | Red Deer River | 52.0527 | -114.2229 | Alberta.a | Alberta | Red Deer 63S | AB_63S_DSS | 240 | 240 | 1992 | 2034 | Hydro_run | hydro_run | 5.6 | 30% | 1.68 | 24% | 11.7734 | 3 | n/a | 0 | 5.6 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Horseshoe_01 | AB_HSH01_GEN | TransAlta Corporation | Seebe | 51.118 | -115.0343 | Alberta.a | Alberta | Seebe 245S | AB_245S_DSS | 72 | 72 | 1911 | 2034 | Hydro_run | hydro_run | 5 | 30% | 1.5 | 24% | 10.512 | 4 | n/a | 0 | 5 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Horseshoe_02 | AB_HSH02_GEN | TransAlta Corporation | Seebe | 51.118 | -115.0343 | Alberta.a | Alberta | Seebe 245S | AB_245S_DSS | 72 | 72 | 1911 | 2034 | Hydro_run | hydro_run | 3 | 30% | 0.9 | 24% | 6.3072 | 4 | n/a | 0 | 3 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Horseshoe_03 | AB_HSH03_GEN | TransAlta Corporation | Seebe | 51.118 | -115.0343 | Alberta.a | Alberta | Seebe 245S | AB_245S_DSS | 72 | 72 | 1911 | 2034 | Hydro_run | hydro_run | 3 | 30% | 0.9 | 24% | 6.3072 | 4 | n/a | 0 | 3 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Horseshoe_04 | AB_HSH04_GEN | TransAlta Corporation | Seebe | 51.118 | -115.0343 | Alberta.a | Alberta | Seebe 245S | AB_245S_DSS | 72 | 72 | 1911 | 2034 | Hydro_run | hydro_run | 5 | 30% | 1.5 | 24% | 10.512 | 4 | n/a | 0 | 5 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Interlakes | AB_ILK00_GEN | TransAlta Corporation | Kananaskis | 50.6335 | -115.1392 | Alberta.a | Alberta | Interlakes 49S | AB_49S_GSS | 144 | 144 | 1954 | 2034 | Hydro_run | hydro_run | 5 | 30% | 1.5 | 24% | 10.512 | 1 | n/a | 0 | 5 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Kananaskis_01 | AB_KNK01_GEN | TransAlta Corporation | Seebe | 51.0969 | -115.0582 | Alberta.a | Alberta | Kananaskis 2S | AB_2S_GSS | 138 | 138 | 1954 | 2034 | Hydro_run | hydro_run | 4.5 | 30% | 1.35 | 24% | 9.4608 | 3 | n/a | 0 | 4.5 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Kananaskis_02 | AB_KNK02_GEN | TransAlta Corporation | Seebe | 51.0969 | -115.0582 | Alberta.a | Alberta | Kananaskis 2S | AB_2S_GSS | 138 | 138 | 1954 | 2034 | Hydro_run | hydro_run | 4.5 | 30% | 1.35 | 24% | 9.4608 | 3 | n/a | 0 | 4.5 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Kananaskis_03 | AB_KNK03_GEN | TransAlta Corporation | Seebe | 51.0969 | -115.0582 | Alberta.a | Alberta | Kananaskis 2S | AB_2S_GSS | 138 | 138 | 1954 | 2034 | Hydro_run | hydro_run | 10 | 30% | 3 | 24% | 21.024 | 3 | n/a | 0 | 10 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Pocaterra | AB_PCT00_GEN | TransAlta Corporation | Kananaskis | 50.6993 | -115.1194 | Alberta.a | Alberta | Pocaterra 48S | AB_48S_GSS | 144 | 144 | 1955 | 2034 | Hydro_run | hydro_run | 12 | 30% | 3.6 | 24% | 25.2288 | 1 | n/a | 0 | 12 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Raymond | AB_RMD00_GEN | Irrigation Canal Cooperative Ltd (Irrican) | Raymond | 49.4071 | -112.6924 | Alberta.a | Alberta | Raymond Reservoir 313S | AB_313S_GSS | 138 | 138 | 1994 | 2034 | Hydro_run | hydro_run | 20 | 30% | 6 | 24% | 42.048 | 1 | n/a | 0 | 20 | 1 | 1 |  |  |  |  | FALSE |  | 1
| St Mary River | AB_SMR00_GEN | Irrigation Canal Cooperative Ltd (Irrican) | Magrath | 49.4526 | -112.7165 | Alberta.a | Alberta | Irrican Power 314S | AB_314S_GSS | 138 | 138 | 2004 | 2034 | Hydro_run | hydro_run | 7 | 30% | 2.1 | 24% | 14.7168 | 1 | n/a | 0 | 7 | 1 | 1 |  |  |  |  | FALSE |  | 1
| St Mary Transalta | AB_SMT00_GEN | TransAlta Corporation | Magrath | 49.3665 | -113.1087 | Alberta.a | Alberta | Irrican Power 314S | AB_314S_GSS | 138 | 138 | 1992 | 2034 | Hydro_run | hydro_run | 2 | 30% | 0.6 | 93% | 16.2936 | 1 | n/a | 1 | 2 | 1 | 1 |  |  |  |  | FALSE |  | 1 | [7 empty] | https://www.transalta.com/facilities/plants-operation/st-mary/
| Taylor Coulee | AB_TAY00_GEN | TransAlta Corporation | Magrath | 49.3336 | -112.8871 | Alberta.a | Alberta | Magrath 225S | AB_225S_GSS | 138 | 138 | 2000 | 2034 | Hydro_run | hydro_run | 14 | 30% | 4.2 | 24% | 29.4336 | 1 | n/a | 0 | 14 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Three Sisters | AB_TSS00_GEN | TransAlta Corporation | Canmore | 50.9985 | -115.3746 | Alberta.a | Alberta | Three Sisters 36S | AB_36S_GSS | 144 | 144 | 1954 | 2034 | Hydro_run | hydro_run | 3 | 30% | 0.9 | 24% | 6.3072 | 1 | n/a | 0 | 3 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Waterton Hydro | AB_WTH00_GEN | TransAlta Corporation | Glenwood | 49.3291 | -113.6732 | Alberta.a | Alberta | Pincher Creek 396S | AB_396S_DSS | 138 | 138 | 1986 | 2034 | Hydro_run | hydro_run | 2.7 | 30% | 0.81 | 24% | 5.6765 | 1 | n/a | 0 | 2.7 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Battle River Gas_04 | AB_BRG04_GEN | Alberta Power (2000) Ltd. | Halkirk | 52.4685 | -112.1339 | Alberta.a | Alberta | Battle River 757S | AB_757S_GSS | 240 | 240 | 2023 | 2100 | NG_CC | gasCC | 148 | 94% | 139.12 | 60% | 777.888 | 2 | [19 empty] | Alberta Utilities Commission. 2020. Heartland Generation Ltd Battle River Power Plant Amendment.
| Battle River Gas_05 | AB_BRG05_GEN | Alberta Power (2000) Ltd. | Halkirk | 52.4685 | -112.1339 | Alberta.a | Alberta | Battle River 757S | AB_757S_GSS | 240 | 240 | 2023 | 2100 | NG_CC | gasCC | 407 | 94% | 382.58 | 60% | 2139.192 | 2 | [19 empty] | Alberta Utilities Commission. 2020. Heartland Generation Ltd Battle River Power Plant Amendment.
| Calgary Energy Centre | AB_CAL00_GEN | ENMAX Generation Portfolio Inc. | Calgary | 51.1805 | -113.9373 | Alberta.a | Alberta | Beddington 162S | AB_162S_DSS | 240 | 240 | 2003 | 2100 | NG_CC | gasCC | 300 | 94% | 282 | 60% | 1576.8 | 1 | 6.4604 | 138.662 | 300 | 8 | 4 |  |  |  |  | FALSE |  | 24 | 3.28 | 19 | 83.7479 |  |  |  | 1.0813
| Cascade Gas_01 | AB_CSG01_GEN | Kineticor | Edson | 53.5241 | -116.5992 | Alberta.a | Alberta | Bickerdike 39S | AB_39S_DSS | 240 | 240 | 2023 | 2100 | NG_CC | gasCC | 900 | 94% | 846 | 60% | 4730.4 | 2 | [19 empty] | https://cascadepower.ca
| Cascade Gas_02 | AB_CSG02_GEN | Kineticor | Edson | 53.5241 | -116.5992 | Alberta.a | Alberta | Bickerdike 39S | AB_39S_DSS | 240 | 240 | 2023 | 2100 | NG_CC | gasCC | 900 | 94% | 846 | 60% | 4730.4 | 2 | [19 empty] | https://cascadepower.ca
| Cavalier | AB_CAV00_GEN | ENMAX Cavalier LP | Strathmore | 51.0056 | -113.1716 | Alberta.a | Alberta | Cavalier | AB_XCAV_DSS | 144 | 144 | 2001 | 2100 | NG_CC | gasCC | 120 | 94% | 112.8 | 60% | 630.72 | 1 | 6.5993 | 66 | 120 | 8 | 4 |  |  |  |  | FALSE |  | 24 | 3 | 19 | 83.7479 |  |  |  | 1.0813
| Genesee Gas_01 | AB_GNG01_GEN | Capital Power (G3) Limited Partnership | Lake Wabamun | 53.3446 | -114.3049 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 138 | 138 | 2023 | 2100 | NG_CC | gasCC | 422 | 94% | 396.68 | 60% | 2218.032 | 3 | [19 empty] | https://www.capitalpower.com/operations/genesee-3/
| Genesee Gas_02 | AB_GNG02_GEN | Capital Power (G3) Limited Partnership | Lake Wabamun | 53.3446 | -114.3049 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 138 | 138 | 2023 | 2100 | NG_CC | gasCC | 422 | 94% | 396.68 | 60% | 2218.032 | 3 | [19 empty] | https://www.capitalpower.com/operations/genesee-3/
| Genesee Gas_03 | AB_GNG03_GEN | Capital Power (G3) Limited Partnership | Lake Wabamun | 53.3446 | -114.3049 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 138 | 138 | 2023 | 2100 | NG_CC | gasCC | 527 | 94% | 495.38 | 60% | 2769.912 | 3 | [19 empty] | https://www.capitalpower.com/operations/genesee-3/
| Keephills Gas_01 | AB_KHG01_GEN | TransAlta Corporation | Lake Wabamun | 53.4487 | -114.4501 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 240 | 240 | 2022 | 2100 | NG_CC | gasCC | 655 | 94% | 615.7 | 60% | 3442.68 | 3 | [19 empty] | Alberta Utilities Commission. 2020. Transalta Corporation. Keephills Power Plant Repowering.
| Keephills Gas_02 | AB_KHG02_GEN | TransAlta Corporation | Lake Wabamun | 53.4487 | -114.4501 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 240 | 240 | 2022 | 2100 | NG_CC | gasCC | 406 | 94% | 381.64 | 60% | 2133.936 | 3 | [19 empty] | Alberta Utilities Commission. 2020. Transalta Corporation. Keephills Power Plant Repowering.
| Keephills Gas_03 | AB_KHG03_GEN | TransAlta Corporation | Lake Wabamun | 53.4487 | -114.4501 | Alberta.a | Alberta | Keephills 320P | AB_320P_GSS | 240 | 240 | 2022 | 2100 | NG_CC | gasCC | 498 | 94% | 468.12 | 60% | 2617.488 | 3
| Medicine Hat | AB_MHT00_GEN | City of Medicine Hat | Medicine Hat | 50.094 | -110.7288 | Alberta.a | Alberta | Medicine Hat 41S | AB_41S_GSS | 138 | 138 | 2007 | 2100 | NG_CC | gasCC | 255 | 94% | 239.7 | 60% | 1340.28 | 1
| Nexen #1 | AB_NX100_GEN | ENMAX Balzac LP | Calgary | 51.1912 | -113.9424 | Alberta.a | Alberta | Turbo Balzac 391S | AB_391S_DSS | 144 | 144 | 2001 | 2100 | NG_CC | gasCC | 120 | 94% | 112.8 | 60% | 630.72 | 2 | 6.7044 | 66 | 120 | 8 | 4 |  |  |  |  | FALSE |  | 24 | 3 | 19 | 83.7479 |  |  |  | 1.0813
| Sheerness Gas_01 | AB_SHG01_GEN | TransAlta Corporation | Sheerness | 51.4426 | -111.7919 | Alberta.a | Alberta | Sheerness 807S | AB_807S_GSS | 240 | 240 | 2023 | 2100 | NG_CC | gasCC | 408 | 94% | 383.52 | 60% | 2144.448 | 2 | 8.8679 | 163.2 | 408 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.21 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Power (2000) Ltd and TransAlta Cogeneration Ltd. 2020. Sheerness Power Plant Dual Fuel Conversion.
| Sheerness Gas_02 | AB_SHG02_GEN | TransAlta Corporation | Sheerness | 51.4426 | -111.7919 | Alberta.a | Alberta | Sheerness 807S | AB_807S_GSS | 240 | 240 | 2023 | 2100 | NG_CC | gasCC | 408 | 94% | 383.52 | 60% | 2144.448 | 2 | 8.8679 | 163.2 | 408 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.21 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Power (2000) Ltd and TransAlta Cogeneration Ltd. 2020. Sheerness Power Plant Dual Fuel Conversion.
| Shepard | AB_SHP00_GEN | ENMAX Shepard Services Inc. | Calgary | 50.9713 | -113.8858 | Alberta.a | Alberta | Shepard SS-25 | AB_SS25_GSS | 240 | 240 | 2015 | 2100 | NG_CC | gasCC | 870 | 94% | 817.8 | 60% | 4572.72 | 1 | 6.3397 | 391.5 | 870 | 8 | 4 |  |  |  |  | FALSE |  | 24 | 3.28 | 19 | 83.7479 |  |  |  | 1.0813
| Sundance Gas_04 | AB_SDG04_GEN | TransAlta Corporation | Lake Wabamun | 53.5075 | -114.5569 | Alberta.a | Alberta | Sundance 310P | AB_310P_GSS | 240 | 240 | 2022 | 2100 | NG_CC | gasCC | 406 | 94% | 381.64 | 60% | 2133.936 | 2 | 9.1048 | 162.4 | 406 | 168 | 48 |  |  |  |  | FALSE |  | 48 | 4.19 | 19 | 111.3105 |  |  |  | 2.8411 | Alberta Utilities Commission. 2020. Transalta Corporation Sundance Power Plant Repowering.
| Sundance Gas_05 | AB_SDG05_GEN | TransAlta Corporation | Lake Wabamun | 53.5075 | -114.5569 | Alberta.a | Alberta | Sundance 310P | AB_310P_GSS | 240 | 240 | 2022 | 2100 | NG_CC | gasCC | 742 | 94% | 697.48 | 60% | 3899.952 | [20 empty] | Alberta Utilities Commission. 2020. Transalta Corporation Sundance Power Plant Repowering.
| Sundance Gas_06 | AB_SDG06_GEN | TransAlta Corporation | Lake Wabamun | 53.5075 | -114.5569 | Alberta.a | Alberta | Sundance 310P | AB_310P_GSS | 240 | 240 | 2022 | 2100 | NG_CC | gasCC | 401 | 94% | 376.94 | 60% | 2107.656 | 2 | [19 empty] | Alberta Utilities Commission. 2020. Transalta Corporation Sundance Power Plant Repowering.
| Air Liquide | AB_ALS00_GEN | Air Liquide | Fort Saskatchewan | 53.7987 | -113.0848 | Alberta.a | Alberta | Canada Liquid Air 337S | AB_337S_ISS | 144 | 144 | 2000 | 2100 | NG_CG | gasCC | 80 | 94% | 75.2 | 30% | 210.24 | 1 | 5.2679 | 48 | 80 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Base Plant | AB_BPT00_GEN | Suncor Energy Inc. | Fort McMurray | 57.2417 | -110.8547 | Alberta.a | Alberta | 29EDD-71 | AB_E71S_ISS | 144 | 144 | 2000 | 2100 | NG_CG | gasCC | 50 | 94% | 47 | 30% | 131.4 | 1
| Bear Creek_01 | AB_BCR01_GEN | TransCanada Energy Ltd. | Grande Prairie | 55.0715 | -118.6921 | Alberta.a | Alberta | Bear Creek 679S | AB_679S_DSS | 144 | 144 | 2002 | 2100 | NG_CG | gasCC | 64 | 94% | 60.16 | 30% | 168.192 | 2
| Bear Creek_02 | AB_BCR02_GEN | TransCanada Energy Ltd. | Grande Prairie | 55.0715 | -118.6921 | Alberta.a | Alberta | Bear Creek 679S | AB_679S_DSS | 138 | 138 | 2002 | 2100 | NG_CG | gasCC | 36 | 94% | 33.84 | 30% | 94.608 | 2
| Blackfalds | AB_BFD00_GEN | Horseshoe Power | Blackfalds | 52.3813 | -113.7967 | Alberta.a | Alberta | Blackfalds 198S | AB_198S_DSS | 144 | 144 | 2019 | 2100 | NG_CG | gasCC | 6 | 94% | 5.64 | 30% | 15.768 | 1
| Buck Lake | AB_BKL00_GEN | Keyera | Alder Flats | 52.9534 | -114.7955 | Alberta.a | Alberta | Buck Lake 454S | AB_454S_GSS | 144 | 144 | 2001 | 2100 | NG_CG | gasCC | 6 | 94% | 5.64 | 30% | 15.768 | 3 | 11.0823 | 2 | 6 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Camrose | AB_CMS00_GEN | Cargill | Camrose | 52.9831 | -112.7697 | Alberta.a | Alberta | East Camrose 285S | AB_285S_GSS | 138 | 138 | 2015 | 2100 | NG_CG | gasCC | 10 | 94% | 9.4 | 30% | 26.28 | 1 |  | 3.7 | 11.3 | 1 | 1 |  |  |  |  | TRUE |  | 50
| Carseland_01 | AB_CSL01_GEN | TransCanada Energy Ltd. | Strathmore | 50.8466 | -113.5816 | Alberta.a | Alberta | Carseland 525S | AB_525S_GSS | 138 | 138 | 2001 | 2100 | NG_CG | gasCC | 40 | 94% | 37.6 | 30% | 105.12 | 1 | 5.528 | 18 | 40 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Carseland_02 | AB_CSL02_GEN | TransCanada Energy Ltd. | Strathmore | 50.8466 | -113.5816 | Alberta.a | Alberta | Carseland 525S | AB_525S_GSS | 138 | 138 | 2001 | 2100 | NG_CG | gasCC | 40 | 94% | 37.6 | 30% | 105.12 | 1 | 5.528 | 18 | 40 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Christina Lake | AB_CLK00_GEN | Cenovus Energy | Christina Lake | 55.5628 | -110.9135 | Alberta.a | Alberta | Christina Lake 723S | AB_723S_GSS | 240 | 240 | 2000 | 2100 | NG_CG | gasCC | 100 | 94% | 94 | 30% | 262.8 | 1
| Coaldale | AB_COD00_GEN | Signalta | Lethbridge | 49.7362 | -112.5622 | Alberta.a | Alberta | Coaldale 254S | AB_254S_GSS | 138 | 138 | 2019 | 2100 | NG_CG | gasCC | 5 | 94% | 4.7 | 30% | 13.14 | 1
| Dow_01 | AB_DOW01_GEN | Dow Chemical Canada ULC | Fort Saskatchewan | 53.734 | -113.1714 | Alberta.a | Alberta | Dow Chemical Fort Sask. 166S | AB_166S_ISS | 144 | 144 | 1999 | 2100 | NG_CG | gasCC | 110 | 94% | 103.4 | 30% | 289.08 | 3 | 7.6979 | 60.5 | 110 | 8 | 4 |  |  |  |  | TRUE |  | 50 | 2.49 | 15 | 109.1903 |  |  |  | 0.60426
| Dow_02 | AB_DOW02_GEN | Dow Chemical Canada ULC | Fort Saskatchewan | 53.734 | -113.1714 | Alberta.a | Alberta | Dow Chemical Fort Sask. 166S | AB_166S_ISS | 144 | 144 | 1999 | 2100 | NG_CG | gasCC | 110 | 94% | 103.4 | 30% | 289.08 | 3 | 7.6979 | 60.5 | 110 | 8 | 4 |  |  |  |  | TRUE |  | 50 | 2.49 | 15 | 109.1903 |  |  |  | 0.60426
| Dow_03 | AB_DOW03_GEN | TransAlta Corporation | Fort Saskatchewan | 53.734 | -113.1714 | Alberta.a | Alberta | Dow Chemical Fort Sask. 166S | AB_166S_ISS | 144 | 144 | 1999 | 2100 | NG_CG | gasCC | 129.5 | 94% | 121.73 | 30% | 340.326 | 3 | 7.4116 | 71.225 | 129.5 | 8 | 4 |  |  |  |  | TRUE |  | 24 | 3.28 | 19 | 83.7479 |  |  |  | 1.0813
| Edson | AB_EDS00_GEN | Repsol Canada Energy | Edson | 53.5577 | -116.5474 | Alberta.a | Alberta | Edson 58S | AB_58S_GSS | 138 | 138 | 2004 | 2100 | NG_CG | gasCC | 18 | 94% | 16.92 | 30% | 47.304 | 1 |  | 6.646 | 18 | 1 | 1 |  |  |  |  | TRUE |  | 50
| Firebag 3_01 | AB_FB301_GEN | Suncor Energy Inc. | Fort McMurray | 57.2417 | -110.8547 | Alberta.a | Alberta | 29EDD-18 | AB_E18S_ISS | 144 | 144 | 2011 | 2100 | NG_CG | gasCC | 85 | 94% | 79.9 | 30% | 223.38 | 2 | 6.2433 | 38.25 | 85 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Firebag 3_02 | AB_FB302_GEN | Suncor Energy Inc. | Fort McMurray | 57.2417 | -110.8547 | Alberta.a | Alberta | 29EDD-18 | AB_E18S_ISS | 144 | 144 | 2012 | 2100 | NG_CG | gasCC | 85 | 94% | 79.9 | 30% | 223.38 | 2 | 6.2433 | 38.25 | 85 | 8 | 8 |  |  |  |  | FALSE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Firebag 4_01 | AB_FB401_GEN | Suncor Energy Inc. | Fort McMurray | 57.2417 | -110.8569 | Alberta.a | Alberta | 29EDD-18 | AB_E18S_ISS | 144 | 144 | 2012 | 2100 | NG_CG | gasCC | 90 | 94% | 84.6 | 30% | 236.52 | 2 | 6.2433 | 40.5 | 90 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Firebag 4_02 | AB_FB402_GEN | Suncor Energy Inc. | Fort McMurray | 57.2417 | -110.8569 | Alberta.a | Alberta | 29EDD-18 | AB_E18S_ISS | 144 | 144 | 2012 | 2100 | NG_CG | gasCC | 89 | 94% | 83.66 | 30% | 233.892 | 2 | 6.2433 | 40.05 | 89 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Firebag 7 | AB_FB700_GEN | Suncor Energy Inc. | Fort McMurray | 57.2356 | -110.85 | Alberta.a | Alberta | 29EDD-18 | AB_E18S_ISS | 144 | 144 | 2007 | 2100 | NG_CG | gasCC | 96 | 94% | 90.24 | 30% | 252.288 | 1 | 6.6693 | 43.2 | 96 | 1 | 1 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Fort Hills | AB_FHL00_GEN | Suncor Energy Inc. | Fort McMurray | 57.3954 | -111.5714 | Alberta.a | Alberta | Fort Hills 505S | AB_505S_GSS | 240 | 240 | 2000 | 2100 | NG_CG | gasCC | 199 | 94% | 187.06 | 30% | 522.972 | 1
| Foster Creek 1 | AB_FRK01_GEN | Cenovus Energy | Cold Lake | 55.0674 | -110.536 | Alberta.a | Alberta | Foster Creek 1200S | AB_1200S_GSS | 144 | 144 | 2003 | 2100 | NG_CG | gasCC | 47 | 94% | 44.18 | 30% | 123.516 | 2 | 5.4755 | 21.15 | 47 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Foster Creek 2 | AB_FRK02_GEN | Cenovus Energy | Cold Lake | 55.0674 | -110.536 | Alberta.a | Alberta | Foster Creek 1200S | AB_1200S_GSS | 144 | 144 | 2003 | 2100 | NG_CG | gasCC | 47 | 94% | 44.18 | 30% | 123.516 | 2 | 5.4755 | 21.15 | 47 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Harmattan | AB_HMT00_GEN | Altagas | Didsbury | 51.6584 | -114.1365 | Alberta.a | Alberta | Harmattan 256S | AB_256S_GSS | 144 | 144 | 1950 | 2100 | NG_CG | gasCC | 45 | 94% | 42.3 | 30% | 118.26 | 1 |  | 0 | 15 | 1 | 1 |  |  |  |  | TRUE |  | 1
| Horizon | AB_HRZ00_GEN | Canadian Natural Resources Ltd. | Fort McMurray | 57.3393 | -111.7578 | Alberta.a | Alberta | Horizon Upgrading 842S | AB_842S_GSS | 240 | 240 | 2007 | 2100 | NG_CG | gasCC | 103 | 94% | 96.82 | 30% | 270.684 | 1 | 6.6868 | 25.75 | 103 | 8 | 8 |  |  |  |  | TRUE |  | 24 | 3 | 19 | 83.7479 |  |  |  | 1.0813
| Joffre | AB_JOF00_GEN | NOVA Chemicals | Red Deer | 52.3078 | -113.5468 | Alberta.a | Alberta | Joffre 535S | AB_535S_GSS | 144 | 144 | 1999 | 2100 | NG_CG | gasCC | 504 | 94% | 473.76 | 30% | 1324.512 | 1 | 6.7 | 277.2 | 504 | 8 | 4 |  |  |  |  | TRUE |  | 24 | 3.28 | 19 | 83.7479 |  |  |  | 1.0813
| Kaybob | AB_KBB00_GEN | TransAlta Corporation | Fox Creek | 54.099 | -116.6138 | Alberta.a | Alberta | Kaybob 346S | AB_346S_GSS | 138 | 138 | 2022 | 2100 | NG_CG | gasCC | 40 | 94% | 37.6 | 30% | 105.12 | 1 | [19 empty] | https://majorprojects.alberta.ca/details/Kaybob-South-3-Cogeneration-Plant/3927
| Kearl | AB_KRL00_GEN | Imperial Oil Resources Ventures Limited | Fort McMurray | 57.421 | -110.9264 | Alberta.a | Alberta | Kearl 9900S | AB_9900S_GSS | 240 | 240 | 1950 | 2100 | NG_CG | gasCC | 81.1 | 94% | 76.234 | 30% | 213.1308 | 1 |  | 80.93 | 81.1 | 1 | 1 |  |  |  |  | TRUE |  | 1
| Lindbergh | AB_LBG00_GEN | Pengrowth Energy | Lindbergh | 53.8753 | -110.6737 | Alberta.a | Alberta | Lindbergh 969S | AB_969S_GSS | 144 | 144 | 2000 | 2100 | NG_CG | gasCC | 16 | 94% | 15.04 | 30% | 42.048 | 1
| MacKay | AB_MKY00_GEN | TransCanada Energy Ltd. | Fort McMurray | 57.0413 | -111.9055 | Alberta.a | Alberta | Mackay River 874S | AB_874S_GSS | 240 | 240 | 2004 | 2100 | NG_CG | gasCC | 207 | 94% | 194.58 | 30% | 543.996 | 1 | 5.5523 | 39.6 | 165 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 2.69 | 15 | 109.1903 |  |  |  | 0.60426
| Mahkeses_01 | AB_MHK01_GEN | Imperial Oil Resources Ventures Limited | Cold Lake | 54.5838 | -110.3934 | Alberta.a | Alberta | Mahkeses 889S | AB_889S_GSS | 144 | 144 | 2002 | 2100 | NG_CG | gasCC | 90 | 94% | 84.6 | 30% | 236.52 | 2 | 5.5098 | 21.6 | 90 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Mahkeses_02 | AB_MHK02_GEN | Imperial Oil Resources Ventures Limited | Cold Lake | 54.5838 | -110.3934 | Alberta.a | Alberta | Mahkeses 889S | AB_889S_GSS | 144 | 144 | 2002 | 2100 | NG_CG | gasCC | 90 | 94% | 84.6 | 30% | 236.52 | 2 | 5.5098 | 21.6 | 90 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| MEG Christina Lake | AB_MEG00_GEN | MEG Energy Corp. | Fort McMurray | 55.665 | -110.7185 | Alberta.a | Alberta | Conklin 762S | AB_762S_DSS | 240 | 240 | 2013 | 2100 | NG_CG | gasCC | 179 | 94% | 168.26 | 30% | 470.412 | 1 | 8.6145 | 77.2 | 179 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Mulligan | AB_MUL00_GEN | Tourmaline | Spirit River | 55.6693 | -118.9178 | Alberta.a | Alberta | Saddle Hills 865S | AB_865S_GSS | 144 | 144 | 2000 | 2100 | NG_CG | gasCC | 5 | 94% | 4.7 | 30% | 13.14 | 1
| Muskeg_01 | AB_MSK01_GEN | Shell Canada Energy | Fort McMurray | 57.2537 | -111.5064 | Alberta.a | Alberta | Muskeg River 847S | AB_847S_GSS | 240 | 240 | 2001 | 2100 | NG_CG | gasCC | 85 | 94% | 79.9 | 30% | 223.38 | 2 | 5.2251 | 51 | 85 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Muskeg_02 | AB_MSK02_GEN | Shell Canada Energy | Fort McMurray | 57.2537 | -111.5064 | Alberta.a | Alberta | Muskeg River 847S | AB_847S_GSS | 240 | 240 | 2001 | 2100 | NG_CG | gasCC | 85 | 94% | 79.9 | 30% | 223.38 | 2 | 5.2251 | 51 | 85 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Nabiye_01 | AB_NBY01_GEN | Imperial Oil Resources Ventures Limited | Cold Lake | 54.7265 | -110.3441 | Alberta.a | Alberta | Nabiye 942S | AB_942S_GSS | 144 | 144 | 2014 | 2100 | NG_CG | gasCC | 85 | 94% | 79.9 | 30% | 223.38 | 2 | 6.3095 | 20.4 | 85 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Nabiye_02 | AB_NBY02_GEN | Imperial Oil Resources Ventures Limited | Cold Lake | 54.7265 | -110.3441 | Alberta.a | Alberta | Nabiye 942S | AB_942S_GSS | 144 | 144 | 2014 | 2100 | NG_CG | gasCC | 85 | 94% | 79.9 | 30% | 223.38 | 2 | 6.3095 | 20.4 | 85 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Nexen #2_01 | AB_NX201_GEN | Nexen | Anzac | 56.4521 | -111.0222 | Alberta.a | Alberta | Long Lake Cogen 864S | AB_864S_GSS | 138 | 138 | 2008 | 2100 | NG_CG | gasCC | 80 | 94% | 75.2 | 30% | 210.24 | 4 | 6.2703 | 48 | 80 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Nexen #2_02 | AB_NX202_GEN | Nexen | Anzac | 56.4521 | -111.0222 | Alberta.a | Alberta | Long Lake Cogen 864S | AB_864S_GSS | 138 | 138 | 2008 | 2100 | NG_CG | gasCC | 80 | 94% | 75.2 | 30% | 210.24 | 4 | 6.2703 | 48 | 80 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 2.29 | 15 | 109.1903 |  |  |  | 0.60426
| Nexen #2_03 | AB_NX203_GEN | Nexen | Anzac | 56.4521 | -111.0222 | Alberta.a | Alberta | Long Lake Cogen 864S | AB_864S_GSS | 138 | 138 | 2008 | 2100 | NG_CG | gasCC | 11.5 | 94% | 10.81 | 30% | 30.222 | 4 | 4.788 | 6.9 | 11.5 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Nexen #2_04 | AB_NX204_GEN | Nexen | Anzac | 56.4521 | -111.0222 | Alberta.a | Alberta | Long Lake Cogen 864S | AB_864S_GSS | 138 | 138 | 2008 | 2100 | NG_CG | gasCC | 11.5 | 94% | 10.81 | 30% | 30.222 | 4 | 4.788 | 6.9 | 11.5 | 8 | 8 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Poplar Creek | AB_PPC00_GEN | Suncor Energy Inc. | Fort McMurray | 56.7706 | -111.418 | Alberta.a | Alberta | 29EDD-0063 | AB_E63S_ISS | 144 | 144 | 1986 | 2100 | NG_CG | gasCC | 376 | 94% | 353.44 | 30% | 988.128 | 1
| Primrose | AB_PRM00_GEN | ATCO Power Canada Ltd. | Cold Lake | 54.6963 | -110.7238 | Alberta.a | Alberta | Primrose 859S | AB_859S_GSS | 144 | 144 | 1998 | 2100 | NG_CG | gasCC | 75 | 94% | 70.5 | 30% | 197.1 | 1 | 5.5825 | 18 | 75 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 2.09 | 15 | 109.1903 |  |  |  | 0.60426
| Rainbow_01 | AB_RBL01_GEN | ATCO Power Canada Ltd. | Rainbow Lake | 58.4471 | -119.2383 | Alberta.a | Alberta | Rainbow Lake 791S | AB_791S_GSS | 144 | 144 | 2000 | 2100 | NG_CG | gasCC | 47 | 94% | 44.18 | 30% | 123.516 | 1
| Redwater | AB_RWR00_GEN | TransCanada Energy Ltd. | Fort Saskatchewan | 53.8162 | -113.1263 | Alberta.a | Alberta | Riverside 388S | AB_388S_DSS | 144 | 144 | 2001 | 2100 | NG_CG | gasCC | 46 | 94% | 43.24 | 30% | 120.888 | 1 | 5.528 | 18.36 | 46 | 2 | 2 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Saddle Hills | AB_SDH00_GEN | Tourmaline | Spirit River | 55.6693 | -118.9178 | Alberta.a | Alberta | Saddle Hills 865S | AB_865S_GSS | 144 | 144 | 2000 | 2100 | NG_CG | gasCC | 10 | 94% | 9.4 | 30% | 26.28 | 1
| Scotford | AB_SCF00_GEN | ATCO Power Canada Ltd. | Fort Saskatchewan | 53.7985 | -113.0943 | Alberta.a | Alberta | Scotford 409S | AB_409S_GSS | 138 | 138 | 2003 | 2100 | NG_CG | gasCC | 195 | 94% | 183.3 | 30% | 512.46 | 1 | 6.6493 | 107.25 | 195 | 8 | 4 |  |  |  |  | TRUE |  | 24 | 3.28 | 19 | 83.7479 |  |  |  | 1.0813
| Shell Caroline | AB_SHC00_GEN | Shell Canada Limited | Caroline | 52.1039 | -114.0392 | Alberta.a | Alberta | Caroline 378S | AB_378S_GSS | 144 | 144 | 2009 | 2100 | NG_CG | gasCC | 23 | 94% | 21.62 | 30% | 60.444 | 1 | 11.0823 | 8.05 | 23 | 1 | 1 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Strathcona | AB_STC00_GEN | Imperial Oil | Edmonton | 53.5434 | -113.391 | Alberta.a | Alberta | Strathcona | AB_XSTR_GSS | 72 | 72 | 2020 | 2100 | NG_CG | gasCC | 43 | 94% | 40.42 | 30% | 113.004 | 1
| Syncrude | AB_SCD00_GEN | Syncrude Canada Ltd. | Fort McMurray | 57.0485 | -111.5802 | Alberta.a | Alberta | Ruth Lake 848S | AB_848S_DSS | 240 | 240 | 1978 | 2100 | NG_CG | gasCC | 528.2 | 94% | 496.508 | 30% | 1388.1096 | 1 | 5.528 | 68.666 | 528.2 | 8 | 8 |  |  |  |  | TRUE |  | 24 | 3.28 | 19 | 83.7479 |  |  |  | 1.0813
| UofA_01 | AB_UOA01_GEN | University of Alberta | Edmonton | 53.5237 | -113.5262 | Alberta.a | Alberta | Jasper 805S | AB_805S_DSS | 240 | 240 | 2000 | 2100 | NG_CG | gasCC | 16 | 94% | 15.04 | 30% | 42.048 | 2 | 11.0823 | 7.2 | 16 | 1 | 1 |  |  |  |  | TRUE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| UofA_02 | AB_UOA02_GEN | University of Alberta | Edmonton | 53.5237 | -113.5262 | Alberta.a | Alberta | Jasper 805S | AB_805S_DSS | 240 | 240 | 1994 | 2100 | NG_CG | gasCC | 26 | 94% | 24.44 | 30% | 68.328 | 2 | 11.0823 | 11.7 | 26 | 1 | 1 |  |  |  |  | TRUE |  | 50 | 3.59 | 15 | 109.1903 |  |  |  | 0.60426
| UofC | AB_UOC00_GEN | University of Calgary | Calgary | 51.0775 | -114.1335 | Alberta.a | Alberta | SS-36 | AB_SS36_DSS | 138 | 138 | 2011 | 2100 | NG_CG | gasCC | 15 | 94% | 14.1 | 30% | 39.42 | 1 | 7.5277 | 5.25 | 15 | 8 | 8 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| AB Newsprint | AB_ANC00_GEN | Alberta Newsprint Co. | Whitecourt | 54.1279 | -115.6659 | Alberta.a | Alberta | Alberta Newsprint 122S | AB_122S_GSS | 240 | 240 | 2014 | 2100 | NG_CT | gasSC | 63 | 94% | 59.22 | 30% | 165.564 | 9 |  | 9 | 63 | 5 | 3 |  |  |  |  | FALSE |  | 37
| Bantry | AB_BTY00_GEN | AltaGas | Brooks | 50.4847 | -111.7454 | Alberta.a | Alberta | Tilley 498S | AB_498S_DSS | 138 | 138 | 2012 | 2100 | NG_CT | gasSC | 10 | 94% | 9.4 | 30% | 26.28 | 1 | 11.0823 | 3.2 | 10 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Bellshill | AB_BHL00_GEN | Genalta Power | Sedgewick | 52.7751 | -111.6923 | Alberta.a | Alberta | Sedgewick 137S | AB_137S_DSS | 144 | 144 | 2012 | 2100 | NG_CT | gasSC | 5 | 94% | 4.7 | 30% | 13.14 | 1
| Carson Creek | AB_CCK00_GEN | Genalta Power | Whitecourt | 54.1282 | -115.6651 | Alberta.a | Alberta | Whitecourt 268S | AB_268S_DSS | 144 | 144 | 2014 | 2100 | NG_CT | gasSC | 15 | 94% | 14.1 | 30% | 39.42 | 1 |  | 6.75 | 15 | 1 | 1 |  |  |  |  | FALSE |  | 50
| Cloverbar_01 | AB_ENC01_GEN | Capital Power | Edmonton | 53.5956 | -113.3322 | Alberta.a | Alberta | Clover Bar 987S | AB_987S_GSS | 240 | 240 | 2008 | 2100 | NG_CT | gasSC | 48 | 94% | 45.12 | 30% | 126.144 | 1 | 5.5454 | 14.4 | 48 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Cloverbar_02 | AB_ENC02_GEN | Capital Power | Edmonton | 53.5956 | -113.3322 | Alberta.a | Alberta | Clover Bar 987S | AB_987S_GSS | 240 | 240 | 2008 | 2100 | NG_CT | gasSC | 101 | 94% | 94.94 | 30% | 265.428 | 1 | 6.6906 | 45.45 | 101 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 2.69 | 15 | 109.1903 |  |  |  | 0.60426
| Cloverbar_03 | AB_ENC03_GEN | Capital Power | Edmonton | 53.5956 | -113.3322 | Alberta.a | Alberta | Clover Bar 987S | AB_987S_GSS | 240 | 240 | 2010 | 2100 | NG_CT | gasSC | 101 | 94% | 94.94 | 30% | 265.428 | 1 | 6.6906 | 45.45 | 101 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 2.69 | 15 | 109.1903 |  |  |  | 0.60426
| Crossfield Energy Centre_01 | AB_CRS01_GEN | ENMAX Generation Portfolio Inc. | Airdrie | 51.3972 | -114.0147 | Alberta.a | Alberta | Summit 653S | AB_653S_DSS | 138 | 138 | 2010 | 2100 | NG_CT | gasSC | 48 | 94% | 45.12 | 30% | 126.144 | 1 | 5.3912 | 21.6 | 48 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Crossfield Energy Centre_02 | AB_CRS02_GEN | ENMAX Generation Portfolio Inc. | Airdrie | 51.3972 | -114.0147 | Alberta.a | Alberta | Summit 653S | AB_653S_DSS | 138 | 138 | 2010 | 2100 | NG_CT | gasSC | 48 | 94% | 45.12 | 30% | 126.144 | 1 | 5.3912 | 21.6 | 48 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Crossfield Energy Centre_03 | AB_CRS03_GEN | ENMAX Generation Portfolio Inc. | Airdrie | 51.3972 | -114.0147 | Alberta.a | Alberta | Summit 653S | AB_653S_DSS | 138 | 138 | 2010 | 2100 | NG_CT | gasSC | 48 | 94% | 45.12 | 30% | 126.144 | 1 | 5.3912 | 21.6 | 48 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Denis St. Pierre | AB_DSP00_GEN | Northstone Power Corp. | Elmworth | 55.0502 | -119.617 | Alberta.a | Alberta | Elmworth 731S | AB_731S_DSS | 144 | 144 | 2000 | 2100 | NG_CT | gasSC | 11 | 94% | 10.34 | 30% | 28.908 | 1
| Drywood | AB_DRW00_GEN | BowArk Energy Ltd. | Glenwood | 49.3683 | -113.5205 | Alberta.a | Alberta | Goose Lake 103S | AB_103S_DSS | 240 | 240 | 1999 | 2100 | NG_CT | gasSC | 6 | 94% | 5.64 | 30% | 15.768 | 1 | 11.0823 | 3.6 | 6 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 3.59 | 15 | 109.1903 |  |  |  | 0.60426
| House Mountain | AB_HSM00_GEN | ATCO Power Canada Ltd. | Swan Hills | 54.7093 | -115.3883 | Alberta.a | Alberta | Edith Lake 739S | AB_739S_DSS | 138 | 138 | 2000 | 2100 | NG_CT | gasSC | 6 | 94% | 5.64 | 30% | 15.768 | 1
| HR Milner | AB_HRM00_GEN | Milner Power Limited Partnership | Grande Cache | 54.0082 | -119.1022 | Alberta.a | Alberta | H.R. Milner 740S | AB_740S_GSS | 144 | 144 | 2019 | 2100 | NG_CT | gasSC | 204 | 94% | 191.76 | 30% | 536.112 | 1 | [19 empty] | https://maximpowercorp.com/hr-milner-generating-station/
| JL Landry | AB_JLL00_GEN | Northstone Power Corp. | Elmworth | 55.0501 | -119.616 | Alberta.a | Alberta | Elmworth 731S | AB_731S_DSS | 144 | 144 | 2000 | 2100 | NG_CT | gasSC | 9 | 94% | 8.46 | 30% | 23.652 | 1
| Judy Creek | AB_JDK00_GEN | Genalta Power | Swan Lake | 54.5753 | -115.5055 | Alberta.a | Alberta | Judy Creek Gas Plant 785S | AB_785S_ISS | 144 | 144 | 2014 | 2100 | NG_CT | gasSC | 15 | 94% | 14.1 | 30% | 39.42 | 1 |  | 6.75 | 15 | 1 | 1 |  |  |  |  | FALSE |  | 50
| Lethbridge Burdett | AB_LTB00_GEN | Signalta | Burdett | 49.8331 | -111.5216 | Alberta.a | Alberta | Burdett 368S | AB_368S_GSS | 138 | 138 | 2001 | 2100 | NG_CT | gasSC | 8 | 94% | 7.52 | 30% | 21.024 | 1 | 11.0823 | 3.6 | 8 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Lethbridge Coaldale | AB_LTC00_GEN | Signalta | Coaldale | 49.7284 | -112.6235 | Alberta.a | Alberta | Coaldale 254S | AB_254S_GSS | 138 | 138 | 2001 | 2100 | NG_CT | gasSC | 7 | 94% | 6.58 | 30% | 18.396 | 1 | 11.0823 | 3.15 | 7 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Lethbridge Fort McLeod | AB_LTF00_GEN | Signalta | Fort Macleod | 49.7229 | -113.4044 | Alberta.a | Alberta | Fort Macleod 15S | AB_15S_GSS | 138 | 138 | 2001 | 2100 | NG_CT | gasSC | 4.1 | 94% | 3.854 | 30% | 10.7748 | 1 | 11.0823 | 1.845 | 4.1 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Lethbridge Taber | AB_LTT00_GEN | Signalta | Taber | 49.7822 | -112.1501 | Alberta.a | Alberta | Taber Wind Farm 134S | AB_134S_GSS | 138 | 138 | 2001 | 2100 | NG_CT | gasSC | 6 | 94% | 5.64 | 30% | 15.768 | 1 | 11.0823 | 2.7 | 6 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Northern Prairie | AB_NPR00_GEN | Grande Prairie Generation Inc. | Grande Prairie | 57.0335 | -111.6019 | Alberta.a | Alberta | Lowe Lake 944S | AB_944S_DSS | 138 | 138 | 2008 | 2100 | NG_CT | gasSC | 105 | 94% | 98.7 | 30% | 275.94 | 1
| Parkland | AB_PKL00_GEN | Altagas | Parkland | 50.3494 | -113.7745 | Alberta.a | Alberta | Stavely 349S | AB_349S_DSS | 144 | 144 | 2000 | 2100 | NG_CT | gasSC | 10 | 94% | 9.4 | 30% | 26.28 | 1
| Poplar Hill | AB_PPH00_GEN | ATCO Power Canada Ltd. | Grande Prairie | 57.008 | -111.4868 | Alberta.a | Alberta | Poplar Hill 790S | AB_790S_GSS | 144 | 144 | 1998 | 2100 | NG_CT | gasSC | 48 | 94% | 45.12 | 30% | 126.144 | 1 | 11.0823 | 21.6 | 48 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 3.59 | 15 | 109.1903 |  |  |  | 0.60426
| Rainbow_05 | AB_RBL05_GEN | ATCO Power Canada Ltd. | Rainbow Lake | 58.4471 | -119.2383 | Alberta.a | Alberta | Rainbow Cogen 850S | AB_850S_GSS | 144 | 144 | 2001 | 2100 | NG_CT | gasSC | 45 | 94% | 42.3 | 30% | 118.26 | 1 | 5.528 | 20.25 | 45 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Ralston | AB_RLT00_GEN | NAT-1 Limited Partnership | Ralston | 50.2194 | -111.1597 | Alberta.a | Alberta | Suffield 895S | AB_895S_GSS | 138 | 138 | 2015 | 2100 | NG_CT | gasSC | 20 | 94% | 18.8 | 30% | 52.56 | 1 |  | 8.75 | 20 | 1 | 1 |  |  |  |  | FALSE |  | 50
| Sherrit | AB_SHR00_GEN | Sherritt Gordon | Fort Saskatchewan | 53.7198 | -113.1905 | Alberta.a | Alberta | Sherritt Gordon 172S | AB_172S_GSS | 144 | 144 | 1986 | 2100 | NG_CT | gasSC | 10 | 94% | 9.4 | 30% | 26.28 | 1 | 11.0823 | 5 | 10 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 2.49 | 15 | 109.1903 |  |  |  | 0.60426
| Valleyview_01 | AB_VVW01_GEN | ATCO Power Canada Ltd. | Valleyview | 54.94 | -117.237 | Alberta.a | Alberta | Little Smoky 813S | AB_813S_DSS | 240 | 240 | 2001 | 2100 | NG_CT | gasSC | 45 | 94% | 42.3 | 30% | 118.26 | 2 | 10.3089 | 13.5 | 45 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Valleyview_02 | AB_VVW02_GEN | ATCO Power Canada Ltd. | Valleyview | 54.94 | -117.237 | Alberta.a | Alberta | Little Smoky 813S | AB_813S_DSS | 240 | 240 | 2008 | 2100 | NG_CT | gasSC | 45 | 94% | 42.3 | 30% | 118.26 | 2 | 7.9366 | 20.25 | 45 | 2 | 2 |  |  |  |  | FALSE |  | 50 | 4.19 | 15 | 109.1903 |  |  |  | 0.60426
| Waterton CT_01 | AB_WTT01_GEN | Pieridae | Waterton | 49.3833 | -113.6104 | Alberta.a | Alberta | Pincher Creek 396S | AB_396S_DSS | 138 | 138 | 1986 | 2100 | NG_CT | gasSC | 5.4 | 94% | 5.076 | 30% | 14.1912 | 2 | 11.0823 | 3.24 | 5.4 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 2.49 | 15 | 109.1903 |  |  |  | 0.60426
| Waterton CT_02 | AB_WTT02_GEN | Pieridae | Waterton | 49.3833 | -113.6104 | Alberta.a | Alberta | Pincher Creek 396S | AB_396S_DSS | 138 | 138 | 1986 | 2100 | NG_CT | gasSC | 4.9 | 94% | 4.606 | 30% | 12.8772 | 2 | 11.0823 | 2.94 | 4.9 | 1 | 1 |  |  |  |  | FALSE |  | 50 | 2.49 | 15 | 109.1903 |  |  |  | 0.60426
| West Cadotte | AB_WCD00_GEN | Genalta Power | Peace River | 56.4715 | -116.3856 | Alberta.a | Alberta | Carmon 830S | AB_830S_DSS | 144 | 144 | 2015 | 2100 | NG_CT | gasSC | 20 | 94% | 18.8 | 30% | 52.56 | 1 |  | 1.6 | 20 | 1 | 1 |  |  |  |  | FALSE |  | 50
| West Pembina | AB_WPM00_GEN | Keyera | Violet Grove | 53.0979 | -115.3157 | Alberta.a | Alberta | West Pembina 477S | AB_477S_GSS | 144 | 144 | 2020 | 2100 | NG_CT | gasSC | 13 | 94% | 12.22 | 30% | 34.164 | 1 | [19 empty] | https://www.keyera.com/titanweb/keyera/webcms.nsf/AllDoc/A9EC018EADDB389B87257F7D00621F79/$File/West%20Pembina%20Fact%20Sheet.pdf
| Alberta One | AB_AOS00_GEN | Enbridge | Burdett | 49.8434 | -111.5631 | Alberta.a | Alberta | Burdett 368S | AB_368S_GSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 11 | 0% | 0 | 18% | 17.3448 | [20 empty] | https://www.enbridge.com/projects-and-infrastructure/projects/alberta-solar-one-project
| Barlow | AB_BRL00_GEN | DP Energy | Calgary | 50.9533 | -113.9854 | Alberta.a | Alberta | SS-24 | AB_SS24_DSS | 144 | 144 | 2022 | 2042 | Solar_PV | solar | 27 | 0% | 0 | 18% | 42.5736 | [20 empty] | https://www.dpenergy.com/projects/canada-barlow-solar-park-alberta/
| Brooks | AB_BKS00_GEN | Elemental Energy | Brooks | 50.5833 | -111.8808 | Alberta.a | Alberta | Brooks 121S | AB_121S_GSS | 138 | 138 | 2017 | 2037 | Solar_PV | solar | 17 | 0% | 0 | 18% | 26.8056
| Burdett | AB_BRD00_GEN | BluEarth Renewables | Burdett | 49.8274 | -111.5382 | Alberta.a | Alberta | Burdett 368S | AB_368S_GSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 20 | 0% | 0 | 18% | 31.536 | [20 empty] | https://bluearthrenewables.com/projects/burdett-solar-project/
| Chappice Lake | AB_CPL00_GEN | Elemental Energy | Chappice Lake | 50.2211 | -110.4461 | Alberta.a | Alberta | Chappice Lake 649S | AB_649S_DSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 15 | 0% | 0 | 18% | 23.652 | [20 empty] | http://elementalenergy.ca/portfolio/chappice-lake-solar/
| Claresholm | AB_CLS00_GEN | Capstone Infractructure | Champion | 50.2557 | -113.2424 | Alberta.a | Alberta | East Stavely 928S | AB_928S_DSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 132 | 0% | 0 | 18% | 208.1376 | [20 empty] | https://www.capstoneinfrastructure.com/our-businesses/in-development/claresholm
| Deerfoot | AB_DFT00_GEN | DP Energy | Calgary | 50.9487 | -113.9611 | Alberta.a | Alberta | SS-24 | AB_SS24_DSS | 144 | 144 | 2022 | 2042 | Solar_PV | solar | 35 | 0% | 0 | 18% | 55.188 | [20 empty] | https://www.dpenergy.com/projects/canada-deerfoot-solar-park-alberta/
| Drumheller | AB_DRM00_GEN | Longspur Developments | Drumheller | 51.4439 | -112.6674 | Alberta.a | Alberta | Michichi Creek 802S | AB_802S_DSS | 144 | 144 | 2022 | 2042 | Solar_PV | solar | 14 | 0% | 0 | 18% | 22.0752
| East Strathmore | AB_EST00_GEN | Elemental Energy | Strathmore | 51.0241 | -113.1491 | Alberta.a | Alberta | Namaka 428S | AB_428S_DSS | 144 | 144 | 2022 | 2042 | Solar_PV | solar | 26 | 0% | 0 | 18% | 40.9968 | [20 empty] | http://elementalenergy.ca/portfolio/east-strathmore-solar/
| Green Acres | AB_GAC00_GEN | Skyfire Energy | Bassano | 50.9061 | -112.708 | Alberta.a | Alberta | Bassano 435S | AB_435S_DSS | 144 | 144 | 2017 | 2037 | Solar_PV | solar | 2 | 0% | 0 | 18% | 3.1536
| Hays | AB_HYS00_GEN | C&B Alberta Solar Development | Hays | 50.0774 | -111.7592 | Alberta.a | Alberta | Hays 421S | AB_421S_GSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 23 | 0% | 0 | 18% | 36.2664 | [20 empty] | http://www.hayssolar.com/CBA.html
| Innisfail | AB_INN00_GEN | Elemental Energy | Innisfail | 52.0481 | -113.9768 | Alberta.a | Alberta | Innisfail 214S | AB_214S_GSS | 144 | 144 | 2017 | 2037 | Solar_PV | solar | 17 | 0% | 0 | 18% | 26.8056 | [20 empty] | http://elementalenergy.ca/portfolio/innisfail-solar/
| Jenner Solar | AB_JNS00_GEN | C&B Alberta Solar Development | Jenner | 50.7509 | -111.1385 | Alberta.a | Alberta | Jenner 275S | AB_275S_GSS | 144 | 144 | 2022 | 2042 | Solar_PV | solar | 23 | 0% | 0 | 18% | 36.2664 | [20 empty] | http://www.jennersolar.com
| Prairie Sunlight I | AB_PSN01_GEN | Solar Krafte Utilities | Enchant | 50.3028 | -112.4409 | Alberta.a | Alberta | Enchant 447S | AB_447S_DSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 74 | 0% | 0 | 18% | 116.6832 | [20 empty] | https://www.prairiesunlight.com/prairiesunlightone
| Prairie Sunlight II | AB_PSN02_GEN | Solar Krafte Utilities | Taber | 49.9908 | -112.0624 | Alberta.a | Alberta | Hull 257S | AB_257S_DSS | 138 | 138 | 2020 | 2040 | Solar_PV | solar | 25 | 0% | 0 | 18% | 39.42 | [20 empty] | https://www.prairiesunlight.com/prairiesunlighttwo
| Prairie Sunlight III | AB_PSN03_GEN | Solar Krafte Utilities | Vauxhall | 50.099 | -112.1078 | Alberta.a | Alberta | Vauxhall 158S | AB_158S_DSS | 138 | 138 | 2020 | 2040 | Solar_PV | solar | 22 | 0% | 0 | 18% | 34.6896 | [20 empty] | https://www.prairiesunlight.com/prairiesunlightthree
| Spring Coulee | AB_SPC00_GEN | Solar Krafte Utilities | Spring Coulee | 49.2871 | -113.1577 | Alberta.a | Alberta | Spring Coulee 385S | AB_385S_GSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 30 | 0% | 0 | 18% | 47.304 | [20 empty] | https://www.prairiesunlight.com/springcoulee
| Strathmore | AB_STM00_GEN | Solar Krafte Utilities | Strathmore | 51.0327 | -113.3767 | Alberta.a | Alberta | Strathmore 151S | AB_151S_GSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 41 | 0% | 0 | 18% | 64.6488 | [20 empty] | https://www.prairiesunlight.com/strathmore
| Suffield | AB_SFF00_GEN | BluEarth Renewables | Suffield | 50.2776 | -111.2812 | Alberta.a | Alberta | Suffield 895S | AB_895S_GSS | 138 | 138 | 2021 | 2041 | Solar_PV | solar | 23 | 0% | 0 | 18% | 36.2664 | [20 empty] | https://bluearthrenewables.com/projects/suffield-solar-project/
| Tilley | AB_TLL00_GEN | C&B Alberta Solar Development | Tilley | 50.5339 | -111.6702 | Alberta.a | Alberta | Tilley 498S | AB_498S_DSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 21 | 0% | 0 | 18% | 33.1128 | [20 empty] | http://www.tilleysolar.com
| Travers | AB_TRV00_GEN | Travers Solar GP | Enchant | 50.2789 | -112.7322 | Alberta.a | Alberta | Enchant 477S | AB_447S_DSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 465 | 0% | 0 | 18% | 733.212 | [20 empty] | https://www.traverssolar.com
| Vauxhall | AB_VXH00_GEN | Solar Krafte Utilities | Vauxhall | 50.1091 | -112.1421 | Alberta.a | Alberta | Vauxhall 158S | AB_158S_DSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 150 | 0% | 0 | 18% | 236.52 | [20 empty] | https://www.prairiesunlight.com/vauxhall
| Wheatcrest | AB_WHC00_GEN | BluEarth Renewables | Enchant | 50.2659 | -112.3882 | Alberta.a | Alberta | Enchant 477S | AB_447S_DSS | 138 | 138 | 2023 | 2043 | Solar_PV | solar | 60 | 0% | 0 | 18% | 94.608 | [20 empty] | https://bluearthrenewables.com/projects/wheatcrest-solar-project/
| Wrentham | AB_WRN00_GEN | Solar Krafte Utilities | Wrentham | 49.5204 | -112.0366 | Alberta.a | Alberta | Conrad 135S | AB_135S_DSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 41 | 0% | 0 | 18% | 64.6488 | [20 empty] | https://www.prairiesunlight.com/wrentham
| Yellow Lake | AB_YLK00_GEN | BluEarth Renewables | Burdett | 49.6654 | -111.5113 | Alberta.a | Alberta | Burdett 368S | AB_368S_GSS | 138 | 138 | 2022 | 2042 | Solar_PV | solar | 19 | 0% | 0 | 18% | 29.9592 | [20 empty] | https://bluearthrenewables.com/projects/yellow-lake-solar-project/
| Ardenville | AB_ARD00_GEN | TransAlta Corporation | Fort Macleod | 49.583 | -113.4351 | Alberta.a | Alberta | Ardenville Wind Farm 418S | AB_418S_GSS | 138 | 138 | 2010 | 2030 | Wind_Onshore | wind | 68 | 9% | 6.12 | 33% | 196.5744 |  | n/a | 0 | 68 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Blackspring Ridge | AB_BSR00_GEN | EDF/Enbridge | Carmangay | 50.1525 | -112.8226 | Alberta.a | Alberta | Blackspring Ridge 485S | AB_485S_DSS | 240 | 240 | 2014 | 2034 | Wind_Onshore | wind | 300 | 9% | 27 | 33% | 867.24 |  | n/a | 0 | 300 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Blue Trail | AB_BTR00_GEN | TransAlta Corporation | Fort Macleod | 49.6687 | -113.4522 | Alberta.a | Alberta | Blue Trail 528S | AB_528S_DSS | 144 | 144 | 2009 | 2029 | Wind_Onshore | wind | 66 | 9% | 5.94 | 33% | 190.7928
| Box Springs | AB_BXS00_GEN | City of Medicine Hat | Medicine Hat | 50.1004 | -110.7276 | Alberta.a | Alberta | Medicine Hat 41S | AB_41S_GSS | 138 | 138 | 2014 | 2034 | Wind_Onshore | wind | 6 | 9% | 0.54 | 33% | 17.3448
| Buffalo Atlee | AB_BFA00_GEN | Capstone Infractructure | Jenner | 50.7486 | -111.0489 | Alberta.a | Alberta | Jenner 275S | AB_275S_GSS | 144 | 144 | 2022 | 2042 | Wind_Onshore | wind | 48 | 9% | 4.32 | 33% | 138.7584 | [20 empty] | https://buffaloatlee.com
| Bull Creek | AB_BUL00_GEN | Bull Creek Wind Power Ltd. | Chauvin | 52.5091 | -110.0831 | Alberta.a | Alberta | Hayter 277S | AB_277S_DSS | 138 | 138 | 2014 | 2034 | Wind_Onshore | wind | 57.5 | 9% | 5.175 | 33% | 166.221 |  | n/a | 0 | 57.5 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Bull Trail | AB_BLT00_GEN | EDF Renewables | Irvine | 49.8138 | -110.2057 | Alberta.a | Alberta | Peace Butte 404S | AB_404S_DSS | 144 | 144 | 2024 | 2044 | Wind_Onshore | wind | 202 | 9% | 18.18 | 33% | 583.9416 | [20 empty] | https://www.edf-re.com/project/bull-trail-wind/about/
| Castle River | AB_CRV00_GEN | TransAlta Corporation | Pincher Creek | 49.516 | -114.0276 | Alberta.a | Alberta | Castle River 239S | AB_239S_GSS | 138 | 138 | 2001 | 2021 | Wind_Onshore | wind | 39.6 | 9% | 3.564 | 33% | 114.4757 |  | n/a | 0 | 39.6 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Castlerock Ridge I | AB_CRR01_GEN | Enel | Pincher Creek | 49.5561 | -113.963 | Alberta.a | Alberta | Castle Rock Ridge 205S | AB_205S_GSS | 240 | 240 | 2012 | 2032 | Wind_Onshore | wind | 77 | 9% | 6.93 | 33% | 222.5916 | [20 empty] | https://www.enelgreenpower.com/our-projects/highlights/castle-rock-ridge-wind-farms
| Castlerock Ridge II | AB_CRR02_GEN | Enel | Pincher Creek | 49.5561 | -113.963 | Alberta.a | Alberta | Castle Rock Ridge 205S | AB_205S_GSS | 240 | 240 | 2019 | 2039 | Wind_Onshore | wind | 29 | 9% | 2.61 | 33% | 83.8332 | [20 empty] | https://www.enelgreenpower.com/our-projects/highlights/castle-rock-ridge-wind-farms
| Chin Chute Wind | AB_CCW00_GEN | Suncor/EHN/Enbridge | Taber | 49.6933 | -112.3292 | Alberta.a | Alberta | Hillridge 139S | AB_139S_DSS | 138 | 138 | 2004 | 2024 | Wind_Onshore | wind | 30 | 9% | 2.7 | 33% | 86.724 |  | n/a | 0 | 30 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Cowley North | AB_CLN00_GEN | TransAlta Corporation | Pincher Creek | 49.5619 | -114.1075 | Alberta.a | Alberta | Pincher Creek 396S | AB_396S_DSS | 138 | 138 | 2001 | 2021 | Wind_Onshore | wind | 21.4 | 9% | 1.926 | 33% | 61.8631 |  | n/a | 0 | 21.4 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Forty Mile | AB_FML00_GEN | Suncor Energy Inc. | Maleb | 49.6936 | -111.1328 | Alberta.a | Alberta | Whitla 251S | AB_251S_DSS | 240 | 240 | 2023 | 2043 | Wind_Onshore | wind | 203 | 9% | 18.27 | 33% | 586.8324 | [20 empty] | https://www.suncor.com/en-ca/about-us/wind-power/suncor-energy-forty-mile-wind-power-project
| Ghost Pine | AB_GHP00_GEN | Finavera | Three Hills | 51.8723 | -113.3181 | Alberta.a | Alberta | Ghost Pine 114S | AB_114S_DSS | 138 | 138 | 2010 | 2030 | Wind_Onshore | wind | 81.6 | 9% | 7.344 | 33% | 235.8893 |  | n/a | 0 | 81.6 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Halkirk | AB_HAL00_GEN | Halkirk I Wind Project LP | Halkirk | 52.2609 | -112.0271 | Alberta.a | Alberta | Halkirk 615S | AB_615S_GSS | 240 | 240 | 2012 | 2032 | Wind_Onshore | wind | 150 | 9% | 13.5 | 33% | 433.62 |  | n/a | 0 | 149.4 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Jenner Wind 1 | AB_JNW01_GEN | Potentia Renewables | Jenner | 50.8088 | -111.0751 | Alberta.a | Alberta | Jenner 275S | AB_275S_GSS | 144 | 144 | 2024 | 2044 | Wind_Onshore | wind | 122 | 9% | 10.98 | 33% | 352.6776 | [20 empty] | https://jennerwind.com
| Jenner Wind 2 | AB_JNW02_GEN | Potentia Renewables | Jenner | 50.8088 | -111.0751 | Alberta.a | Alberta | Jenner 275S | AB_275S_GSS | 144 | 144 | 2024 | 2044 | Wind_Onshore | wind | 71 | 9% | 6.39 | 33% | 205.2468 | [20 empty] | https://jennerwind.com
| Kettles Hill | AB_KHL00_GEN | Kettles Hill Wind Energy | Pincher Creek | 49.5159 | -113.8218 | Alberta.a | Alberta | Kettle's Hill 383S | AB_383S_GSS | 144 | 144 | 2007 | 2027 | Wind_Onshore | wind | 63 | 9% | 5.67 | 33% | 182.1204 |  | n/a | 0 | 63 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Macleod Flats | AB_MCF00_GEN | TransAlta Corporation | Fort Macleod | 49.6868 | -113.4752 | Alberta.a | Alberta | Fort Macleod 15S | AB_15S_GSS | 138 | 138 | 2004 | 2024 | Wind_Onshore | wind | 3 | 9% | 0.27 | 33% | 8.6724 |  | n/a | 0 | 33 | 1 | 1 |  |  |  |  | FALSE |  | 1 | [7 empty] | https://www.transalta.com/facilities/plants-operation/
| Magrath | AB_MGH00_GEN | Suncor/EHN/Enbridge | Magrath | 49.3859 | -112.9488 | Alberta.a | Alberta | Magrath 225S | AB_225S_GSS | 138 | 138 | 2004 | 2024 | Wind_Onshore | wind | 30 | 9% | 2.7 | 33% | 86.724 |  | n/a | 0 | 30 | 1 | 1 |  |  |  |  | FALSE |  | 1
| McBride Lake | AB_MCB00_GEN | ENMAX / Transalta | Fort Macleod | 49.6123 | -113.4815 | Alberta.a | Alberta | Mcbride Lake 240S | AB_240S_GSS | 144 | 144 | 2002 | 2022 | Wind_Onshore | wind | 73 | 9% | 6.57 | 33% | 211.0284 |  | n/a | 0 | 73 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Oldman Wind | AB_OMW00_GEN | Oldman 2 Wind Farm Limited | Pincher Creek | 49.5708 | -113.8534 | Alberta.a | Alberta | Windy Point 112S | AB_112S_DSS | 144 | 144 | 2013 | 2033 | Wind_Onshore | wind | 46.8 | 9% | 4.212 | 33% | 135.2894 |  | n/a | 0 | 46.8 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Rattlesnake Ridge | AB_RSR00_GEN | BHE Canada | Whitla | 49.8439 | -111.0428 | Alberta.a | Alberta | Burdett 368S | AB_368S_GSS | 138 | 138 | 2022 | 2042 | Wind_Onshore | wind | 118 | 9% | 10.62 | 33% | 341.1144 | [20 empty] | http://www.rattlesnakeridgewind.com/about-the-project/project-details/
| Riverview | AB_RIV00_GEN | Enel | Pincher Creek | 49.5561 | -113.963 | Alberta.a | Alberta | Castle Rock Ridge 205S | AB_205S_GSS | 240 | 240 | 2019 | 2039 | Wind_Onshore | wind | 105 | 9% | 9.45 | 33% | 303.534 |  | n/a | 0 | 105 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Sharp Hills | AB_SPH00_GEN | EDP Renewables | Oyen | 51.6886 | -110.581 | Alberta.a | Alberta | Oyen 767S | AB_767S_DSS | 144 | 144 | 2023 | 2043 | Wind_Onshore | wind | 298 | 9% | 26.82 | 33% | 861.4584 | [20 empty] | https://sharphillswindfarm.com
| Sinnott | AB_SNT00_GEN | TransAlta Corporation | Pincher Creek | 49.5325 | -113.9773 | Alberta.a | Alberta | Pincher Creek 396S | AB_396S_DSS | 138 | 138 | 2014 | 2034 | Wind_Onshore | wind | 6 | 9% | 0.54 | 33% | 17.3448
| Soderglen | AB_SDG00_GEN | TransAlta Corporation | Fort Macleod | 49.5385 | -113.5231 | Alberta.a | Alberta | Soderglen 243S | AB_243S_GSS | 144 | 144 | 2006 | 2026 | Wind_Onshore | wind | 70 | 9% | 6.3 | 33% | 202.356 |  | n/a | 0 | 70 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Stirling | AB_STL00_GEN | Potentia Renewables | Stirling | 49.5655 | -112.3642 | Alberta.a | Alberta | Stirling 67S | AB_67S_GSS | 144 | 144 | 2024 | 2044 | Wind_Onshore | wind | 113 | 9% | 10.17 | 33% | 326.6604 | [20 empty] | https://stirlingwind.com
| Summerview 1 | AB_SVW01_GEN | TransAlta Corporation | Pincher Creek | 49.5829 | -113.7931 | Alberta.a | Alberta | Summerview 354S | AB_354S_GSS | 144 | 144 | 2004 | 2024 | Wind_Onshore | wind | 66 | 9% | 5.94 | 33% | 190.7928 |  | n/a | 0 | 66 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Summerview 2 | AB_SVW02_GEN | TransAlta Corporation | Pincher Creek | 49.5829 | -113.7931 | Alberta.a | Alberta | Summerview 354S | AB_354S_GSS | 144 | 144 | 2004 | 2024 | Wind_Onshore | wind | 66 | 9% | 5.94 | 33% | 190.7928 |  | n/a | 0 | 66 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Taber | AB_TAB00_GEN | Enmax Green Power Inc | Taber | 49.7184 | -111.9266 | Alberta.a | Alberta | Taber Wind Farm 134S | AB_134S_GSS | 144 | 144 | 2006 | 2026 | Wind_Onshore | wind | 80 | 9% | 7.2 | 33% | 231.264 |  | n/a | 0 | 80 | 1 | 1 |  |  |  |  | FALSE |  | 1
| Waterton Wind | AB_WTW00_GEN | TransAlta Corporation | Cardston County | 49.1897 | -113.6806 | Alberta.a | Alberta | Pincher Creek 396S | AB_396S_DSS | 138 | 138 | 2014 | 2034 | Wind_Onshore | wind | 3.9 | 9% | 0.351 | 33% | 11.2741
| Wheatland | AB_WHL00_GEN | Potentia Renewables / Greengate | Dorothy | 51.2314 | -112.4079 | Alberta.a | Alberta | Wheatland 609S | AB_609S_GSS | 138 | 138 | 2023 | 2043 | Wind_Onshore | wind | 120 | 9% | 10.8 | 33% | 346.896 | [20 empty] | https://wheatlandwind.com
| Whitla 1 | AB_WLA01_GEN | Capital Power | Etzikom | 49.5519 | -111.077 | Alberta.a | Alberta | Shamrock 1018S | AB_1018S_DSS | 240 | 240 | 2019 | 2039 | Wind_Onshore | wind | 202 | 9% | 18.18 | 33% | 583.9416
| Whitla 2 | AB_WLA02_GEN | Capital Power | Etzikom | 49.5519 | -111.077 | Alberta.a | Alberta | Shamrock 1018S | AB_1018S_DSS | 240 | 240 | 2022 | 2042 | Wind_Onshore | wind | 97 | 9% | 8.73 | 33% | 280.4076 | [20 empty] | https://www.capitalpower.com/operations/whitla-wind-2/
| Whitla 3 | AB_WLA03_GEN | Capital Power | Etzikom | 49.5519 | -111.077 | Alberta.a | Alberta | Shamrock 1018S | AB_1018S_DSS | 240 | 240 | 2023 | 2043 | Wind_Onshore | wind | 54 | 9% | 4.86 | 33% | 156.1032 | [20 empty] | https://www.capitalpower.com/operations/whitla-wind-3/
| Wild Rose 1 | AB_WRS01_GEN | NaturEner | Irvine | 49.9979 | -110.4239 | Alberta.a | Alberta | Whitla 251S | AB_251S_DSS | 240 | 240 | 2023 | 2043 | Wind_Onshore | wind | 218 | 9% | 19.62 | 33% | 630.1944 | [20 empty] | https://majorprojects.alberta.ca/details/Wild-Rose-1-Wind-Farm/2005
| Wild Rose 2 | AB_WRS02_GEN | NaturEner | Irvine | 49.9979 | -110.4239 | Alberta.a | Alberta | Whitla 251S | AB_251S_DSS | 241 | 241 | 2023 | 2043 | Wind_Onshore | wind | 192 | 9% | 17.28 | 33% | 555.0336 | [20 empty] | https://www.auc.ab.ca/regulatory_documents/ProceedingDocuments/2019/24912-D01-2019.pdf
| Windrise | AB_WND00_GEN | TransAlta Corporation | Pincher Creek | 49.4859 | -113.4542 | Alberta.a | Alberta | Windy Flats 138S | AB_138S_DSS | 240 | 240 | 2023 | 2043 | Wind_Onshore | wind | 206 | 9% | 18.54 | 33% | 595.5048 | [20 empty] | https://www.transalta.com/facilities/plants-operation/windrise/
| Wintering Hills | AB_WGL00_GEN | Suncor Energy Products Inc. | Wheatland County | 51.2214 | -112.5779 | Alberta.a | Alberta | Wheatland 609S | AB_609S_GSS | 138 | 138 | 2011 | 2031 | Wind_Onshore | wind | 88 | 9% | 7.92 | 33% | 254.3904 |  | n/a | 0 | 88 | 1 | 1 |  |  |  |  | FALSE |  | 1
Specific Notes:
AESO IPP contract durations presumed to be: hydroelectric - all terminating in 2034; wind - 20 years; solar - 20 years; biomass - 15 years; biogas automatically renewed
Missing values for "outage duration", "minimum capacity", maximum capacity", "must run", "minimum up time", "minimum down time" filled in using values for similar types of projects where values are known.
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Unless noted otherwise, the wind generating stations are presumed to be connected to the nearest 69 kV substation
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit Hydro_run facilities treated as single-unit facilities

## Storage
AB | EXISTING STORAGE | [12 empty] | DESIGN | [7 empty] | OPERATIONS
| Project Name | Storage Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Technology | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Days | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | kV | [5 empty] | (MW) | (MWh) | (Hours) |  | ($M) | (hours) | (hours) | (%) | (days/y) | ($/year) | ($/MWh)
| WindCharger | AB_WND00_STO | TransAlta Corporation | Pincher Creek | 49.5829 | -113.7931 | alberta.a | Alberta | SUMMERVIEW 354S | AB_354S_SUB | 144 | 2020 | 2040 | Storage | storage | Lithium Ion | 10 | 20 | 2 | Summerview 2 | 22.7 | 2 | 2 |  |  |  |  | https://www.newswire.ca/news-releases/transalta-renewables-announces-commercial-operation-of-windcharger-alberta-s-first-utility-scale-battery-storage-project-860743949.html https://www.energy-storage.news/news/first-grid-scale-battery-storage-project-in-alberta-canada-comes-online-thi
| eReserve 1 | AB_ERS01_STO | Teric Power Ltd. | Rycroft | 55.7396 | -118.7007 | alberta.a | Alberta | RYCROFT 730S | AB_730S_SUB | 144 | 2020 | 2040 | Storage | storage | Lithium Ion | 20 | 20 | 1 | Grid |  | 1 | 1 |  |  |  |  | https://ereserve-project.com
| eReserve 2 | AB_ERS02_STO | Teric Power Ltd. | Jarrow | 53.1185 | -111.2008 | alberta.a | Alberta | BUFFALO CREEK 526S | AB_526S_SUB | 144 | 2020 | 2040 | Storage | storage | Lithium Ion | 20 | 20 | 1 | Grid |  | 1 | 1 |  |  |  |  | https://ereserve-project.com
| eReserve 3 | AB_ERS03_STO | Teric Power Ltd. | Clairmont Lake | 55.2879 | -118.6433 | alberta.a | Alberta | CLAIRMONT LAKE 811S | AB_811S_SUB | 144 | 2020 | 2040 | Storage | storage | Lithium Ion | 20 | 35 | 1.75 | Grid |  | 1.75 | 1.75 |  |  |  |  | https://ereserve-project.com
Specific Notes:
AESO IPP contract durations presumed to be: storage - 20 years

## HydroExisting
AB | EXISTING HYDROELECTRIC | [24 empty] | RESERVOIR
| Project Name | Type | Installed Capacity Plant | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Renewal Year | Dam Type | Penstock | Rated Head | Maximum Head | Minimum Head | Average Flow (Facility) | Rated Discharge (Unit) | Rated Discharge (Facility) | Upstream Reservoir Area | Upstream Reservoir Storage | Turbine Type | Station Flow | Upper Storage | Upper Storage Level | Lower Storage | Lower Storage Level | Upper Storage Name | Minimum Level | Maximum Level | Initial Level | Low Reference Level | High Reference Level | Low Volume | High Volume | Live Storage | M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10 | M11 | M12 | Notes
|  |  | (MW) |  | (MW) | [5 empty] | (m) | (m) | (m) | (m) | (m3/s) | (m3/s) | (m3/s) | (km2) | (hours) |  | (WSC#) |  | (WSC#) |  | (WSC#) |  | (m) | (m) | (m) | (m) | (m) | (m3) | (m3) | (m3) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s)
| Bearspaw | Hydro_hourly | 17 | 100% | 17 | 24% | 35.7408 | 1 |  |  |  | 15 | [8 empty] | 05BH008 | Bearspaw |  |  |  | Bearspaw
| Bighorn | Hydro_daily | 120 | 100% | 120 | 24% | 252.288 | 2 |  |  |  | 95 |  |  | 60 | [5 empty] | 05DC010 | Bighorn Reservoir | 05DC009 |  |  | Bighorn Reservoir
| Brazeau | Hydro_daily | 362 | 100% | 362 | 24% | 761.0688 | 2 |  |  |  | 126 |  |  | 56 | [5 empty] | 05DD005 | Brazeau Reservoir | 05DD006 |  |  | Brazeau Reservoir
| Cascade | Hydro_hourly | 35 | 100% | 35 | 24% | 73.584 | 2 |  |  |  | 105 |  |  | 14 | [5 empty] | 05BD004 | Lake Minnewanka | 05BD003 |  |  | Lake Minnewanka
| Ghost | Hydro_hourly | 61 | 100% | 61 | 24% | 128.2464 | 4 |  |  |  | 34 | [8 empty] | 05BE999 | Ghost Lake | 05BE005 |  |  | Ghost Lake
| Oldman | Hydro_hourly | 32 | 100% | 32 | 24% | 67.2768 | 2 |  |  |  | 65 |  |  | 38 | [5 empty] | 05AA024 | Oldman Reservoir | 05AA032 |  |  | Oldman Reservoir
| Rundle | Hydro_hourly | 47 | 100% | 47 | 24% | 98.8128 | 2 |  |  |  | 98 | [8 empty] | TAU-009 | Rundle | TAU-009 |  |  | Rundle
| Spray | Hydro_hourly | 92 | 100% | 92 | 24% | 193.4208 | 2 |  |  |  | 274 | [8 empty] | 05BE007 | Spray Lakes Reservoir | 05BC006 | Rundle |  | Spray Lakes Reservoir
Specific Notes:
Hydroelectric generation type has been estimated based on available information concerning operations, reservoir size and operations, facility location and design flows.
The WSC# refers to the Water Survey of Canada Hydrometric station

## HydroRenewals
AB | HYDROELECTRIC RENEWAL |  | Existing Design | [7 empty] | Renewal Design | [14 empty] | Costs | 1.77% | 1.06 |  |  | 7% | 70
| Existing Project Name | Owner | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Renewal Project Name | Renewal Project Code | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Additional Annual Energy | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed Cost Existing Project | Fixed Cost Renewed Project | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
|  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) | [11 empty] | (km) |  |  | (MW) | (MW) | (GWh/year) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/year) | ($/year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
| Brazeau | Transalta | Hydro_daily | 362 | 24% | 362 | 24% | 761.0688 | 2 | 1966 | Brazeau Capacity Addition | RN_BRA | Drayton Valley | 52.9101 | -115.3754 | Alberta.a | BRAZEAU 62S | AB_62S_SUB | 13.8 | 50 | Hydro_monthly | hydro_daily | 170 | 170 | 0 | 500 | 8.85 | 99.2582 | 608.1082 | 14.7634 | 622.8715 | 43.9869 | 258.7464 | 6929873.0336 | 8266168.9983 | 7860.5645 | 1.968 | 0 | 1.968 |  |  | 5 | 8 | Requires new 240 kV kV transmission
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroGreenfield
AB | HYDROELECTRIC GREENFIELD | [10 empty] | DESIGN | [5 empty] | COSTS |  | 1.77% | 1.06 |  | 5% | 7% | 70
| Project Name | Project Short Name | Owner | Location | Latitude | Longitude | Balancing Area | Distance to Market Grid | Connecting Node Name | Connecting Node Code | Substation Voltage | Generation Type | Generation Type - CREST EMI | Installed Capacity | Dependable Capacity | Average Annual Energy | # of units | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
[11 empty] | (kV) |  |  | (MW) | (MW) | (GWh/year) |  | ($2008M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
| Slave River Hydro Development | GF_SRD | Atco Power | Slave River | 59.9821 | -111.7869 | Alberta.a | 350 | THICKWOOD HILLS 951S | AB_951S_SUB | 500 | hydro_daily | hydro_daily | 1100 | 1100 | 6500 | 6 | n/a | 7000 | 123.9 | 799.184 | 7923.084 | 421.2236 | 8344.3076 | 589.2711 | 535.701 | 10480.9806 | 0.96259 | 0 | 0.96259 |  |  | 8 | 15
| Amisk Hydro Development | GF_AMK | AHP Development Corporation | Peace River | 55.9682 | -118.807 | Alberta.a | 100 | WESLEY CREEK 834S | AB_834S_SUB | 240 | hydro_daily | hydro_daily | 370 | 370 | 2588 | 22 | n/a | 1700 | 30.09 | 468.97 | 2199.06 | 176.5536 | 2375.6136 | 167.7647 | 453.4181 | 18917.8343 | 1.4611 | 0 | 1.4611 |  |  | 7 | 13
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroPS
AB | HYDROELECTRIC PUMPED STORAGE | [16 empty] | Existing Facility | [8 empty] | Reservoir Design | [14 empty] | Costs |  | 2% | 4% |  |  | 5% | 70
| Pumped Storage Project | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Installed Capacity | Dependable Capacity | Annual Generation | Annual Pumping | Existing Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Start Year | Water Type | Cycle Type | Storage Type | Reservoir Storage | Storage Requirement | Gross Head | Penstock | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping) | Turbine Type | Pump Type | Generation Duration to Empty Reservoir | Pumping Duration to Fill Reservoir | Total Footprint | Overnight Capital Cost | Overnight Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Annual Fixed O&M | Variable Cost | Water Rentals | Annualized Variable O&M | Levelized Cost of Capacity | Construction Time | Development Time | Notes
[5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) | (GWh/y) | (GWh/y) |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) | [5 empty] | (m3) | (MWh) | (m) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($M) | ($2021M) | ($2021M) | ($2021M) | ($2021M) | ($2021M) | ($2021M) | ($2021M/year) | ($/kW-year) | ($/kW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2021/kW-year) | (years) | (years)
| Brazeau Pumped Storage | AB_BRA00_STO | Transalta | Drayton Valley | 52.9101 | -115.3754 | Alberta.a | Brazeau 62S | AB_62S_DSS | 240 | 150 | hydro_pump | hydro_pump | 900 | 900 | 2628 | 3285 | Brazeau | Hydro_daily | 362 |  | 362 |  |  | 2 | 1966 | Fresh | Open | Reservoir to Reservoir | [12 empty] | 2510 | 2737.2931 | 54.7459 | 346.5279 | 3138.5668 | 112.3713 | 3250.9381 | 168.0707 | 186.7453 | 12.6291 | 1.0395 | 0 | 3.0353 | 202.4096 | 5 | 8 | Requires 500 kV transmission to Benalto
| Canyon Creek | AB_CYC00_STO | Turning Point Generation | Hinton | 53.5094 | -117.4225 | Alberta.a | Excel 910S | AB_910S_DSS | 138 | 10.2 | hydro_pump | hydro_pump | 75 | 75 | 219 | 273.75 | No Existing Project | [8 empty] | Fresh | Closed | Reservoir to Reservoir | 2543000 | 2775 | 480 | 7000 | 6.857% |  |  | Pelton | Staged | 37 | 77 | 55 | 200 | 209.9213 | 4.1984 | 17.246 | 231.3657 | 19.1608 | 250.5265 | 12.952 | 172.6934 | 41.3181 | 2.6924 | 0 | 7.8619 | 221.8735 | 3 | 5
General Notes:
All projects assumed to be connected to the provincial or territorial transmission system
Assume installed capacity is all dependable capacity, though this should be verified with new studies.
Annual generation based on 8 hours per day generation, unless otherwise provided
Annual pumping estimated at 125% of annual generation, unless otherwise provided
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 2% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate of 1.77%
Assume IDC rate of 4% real
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume pumped storage facilities have an economic life of 70 years
Assume a discount rate of 5% real
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset
Water Rental assumed to be $0/MWh (i.e., not applied to pumped storage)

## Transmission
| Circuit ID | Owner | Operating Region | Number of Circuits | Current | Length | Length | Voltage | Reactance | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | Power Factor | Smax | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes | Count
[6 empty] | (km) | (miles) | (kV) | (ohm) | (A) | (A) | (MVA) | (MVA) |  |  | (MW) | (MW)
| 854L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 138 | 10.8393 |  |  | 283 | 287 | 0.9 | n/a | 254.7 | 258.3 | Marlboro 348S JCT | AB_348S_JCT | Deer Hill 1012S | AB_1012S_DSS | AESO. 2020. Cascade Connection Assessment |  | 877
| 685L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 138 | 13.0071 |  |  | 167 | 201 | 0.9 | n/a | 150.3 | 180.9 | Benbow 397S | AB_397S_DSS | Deer Hill 1012S | AB_1012S_DSS | AESO. 2018. Vista Connection Assessment |  | 363
| 762L | Altalink Management Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 144 | 17.5143 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Coal Valley 527S JCT | AB_527S_JCT | Cheviot 101S | AB_101S_DSS |  |  | 550
| 847L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Fickle Lake 406S | AB_406S_DSS | Vista 1029S | AB_1029S_DSS | AESO. 2018. Vista Connection Assessment |  | 865
| 924L | Altalink Management Ltd. | Alberta | 1 | ac | 105 | 64.8148 | 240 | 50.0694 |  |  | 547 | 676 | 0.9 | n/a | 492.3 | 608.4 | Milo 356S | AB_356S_DSS | Langdon 102S | AB_102S_DSS | AESO. 2019. Travers Connection Assessment |  | 959
| 927L | Altalink Management Ltd. | Alberta | 1 | ac | 105 | 64.8148 | 240 | 50.0694 |  |  | 576 | 711 | 0.9 | n/a | 518.4 | 639.9 | Milo 356S | AB_356S_DSS | Langdon 102S | AB_102S_DSS | AESO. 2019. Travers Connection Assessment |  | 962
| 936L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 481 | 581 | 0.9 | n/a | 432.9 | 522.9 | East Calgary 5S | AB_5S_DSS | Langdon 102S | AB_102S_DSS | AESO. 2017. SS 7 Connection Assessment |  | 971
| 937L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 481 | 581 | 0.9 | n/a | 432.9 | 522.9 | East Calgary 5S | AB_5S_DSS | Langdon 102S | AB_102S_DSS | AESO. 2017. SS 7 Connection Assessment |  | 972
| 1064L | Altalink Management Ltd. | Alberta | 1 | ac | 17 | 10.4938 | 240 | 8.1065 |  |  | 974 | 1208 | 0.9 | n/a | 876.6 | 1087.2 | Janet 74S | AB_74S_DSS | Langdon 102S | AB_102S_DSS | AESO. 2017. SS 7 Connection Assessment |  | 41
| 1065L | Altalink Management Ltd. | Alberta | 1 | ac | 17 | 10.4938 | 240 | 8.1065 |  |  | 974 | 1208 | 0.9 | n/a | 876.6 | 1087.2 | Janet 74S | AB_74S_DSS | Langdon 102S | AB_102S_DSS | AESO. 2017. SS 7 Connection Assessment |  | 42
| 1114L | Altalink Management Ltd. | Alberta | 1 | ac | 0.85 | 0.52469 | 500 | 0.33575 |  |  |  |  | 0.9 | 3 | 2550 | 3225 | Bennett 520S | AB_520S_DSS | Langdon 102S | AB_102S_DSS |  |  | 64
| 1325L | Altalink Management Ltd. | Alberta | 1 | ac | 0.85 | 0.52469 | 500 | 0.33575 |  |  |  |  | 0.9 | 3 | 2550 | 3225 | Crossings 511S | AB_511S_DSS | Langdon 102S | AB_102S_DSS |  |  | 92
| 613L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 119 | 147 | 0.9 | n/a | 107.1 | 132.3 | Pincher Creek 396S | AB_396S_DSS | Goose Lake 103S | AB_103S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 333
| 893L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 144 | 15.325 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Windy Point 112S JCT | AB_112S_JCT | Goose Lake 103S | AB_103S_DSS |  |  | 916
| 615L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 120 | 145 | 0.9 | n/a | 108 | 130.5 | Cold Creek 602S | AB_602S_DSS | Watson Creek 104S | AB_104S_DSS | AESO. 2016. Hornbeck Connection Assessment |  | 334
| 790AL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 138 | 2.6014 |  |  | 123 | 151 | 0.9 | n/a | 110.7 | 135.9 | Bilby 105S JCT | AB_105S_JCT | Bilby 105S | AB_105S_DSS | AESO. 2016. Gainford Connection Assessment |  | 588
| 790L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 120 | 143 | 0.9 | n/a | 108 | 128.7 | Stony Plain 434S | AB_434S_DSS | Bilby 105S JCT | AB_105S_JCT | AESO. 2016. Gainford Connection Assessment |  | 586
| 744AL | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 138 | 4.3357 |  |  | 120 | 145 | 0.9 | n/a | 108 | 130.5 | Paddle River 106S JCT | AB_106S_JCT | Paddle River 106S | AB_106S_DSS | AESO. 2016. Gainford Connection Assessment |  | 512
| 744L | Altalink Management Ltd. | Alberta | 1 | ac | 8 | 4.9383 | 138 | 3.4686 |  |  | 75 | 79 | 0.9 | n/a | 67.5 | 71.1 | Entwistle 235S | AB_235S_DSS | Paddle River 106S JCT | AB_106S_JCT | AESO. 2016. Gainford Connection Assessment |  | 509
| 722L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 144 | 10.7275 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Burdett 368S | AB_368S_GSS | Westfield 107S | AB_107S_DSS |  |  | 439
| 943L | Altalink Management Ltd. | Alberta | 1 | ac | 13 | 8.0247 | 240 | 6.1991 |  |  | 457 | 457 | 0.9 | n/a | 411.3 | 411.3 | Deerland 13S | AB_13S_DSS | Amelia 108S | AB_108S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 975
| 207L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | North Lethbridge 370S | AB_370S_DSS | Coalbanks 111S | AB_111S_DSS | AESO. 2019. Travers Connection Assessment |  | 149
| 725L | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 138 | 3.035 |  |  | 116 | 146 | 0.9 | n/a | 104.4 | 131.4 | Riverbend 618S JCT | AB_618S_JCT | Coalbanks 111S | AB_111S_DSS | AESO. 2019. Travers Connection Assessment |  | 448
| 893AL | Altalink Management Ltd. | Alberta | 1 | ac | 5.6 | 3.4568 | 144 | 2.452 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Windy Point 112S JCT | AB_112S_JCT | Windy Point 112S | AB_112S_DSS |  |  | 917
| 893L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 144 | 7.6625 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Fidler 312S | AB_312S_DSS | Windy Point 112S JCT | AB_112S_JCT |  |  | 915
| 7LA159 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Ghost Pine 114S JCT | AB_114S_JCT | Ghost Pine 114S | AB_114S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 669
| 7L159 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 109.3 | 126.5 | 0.9 | n/a | 98.37 | 113.85 | Heatburg 948S | AB_948S_DSS | Ghost Pine 114S JCT | AB_114S_JCT | AESO. 2018. Wheatland Connection Assessment |  | 667
| 754L | Altalink Management Ltd. | Alberta | 1 | ac | 8.4 | 5.1852 | 138 | 3.642 |  |  | 94 | 135 | 0.9 | n/a | 84.6 | 121.5 | Baymag 437S | AB_437S_DSS | Canmore 118S | AB_118S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 537
| 7L86 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 139 | 143 | 0.9 | n/a | 125.1 | 128.7 | Wolf Lake 822S | AB_822S_DSS | Foster Creek 1200S | AB_1200S_GSS | AESO. 2016. Bauer 918S Connection Assessment |  | 796
| 814L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | West Brooks 28S | AB_28S_DSS | Brooks 121S | AB_121S_GSS |  |  | 833
| 827L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | West Brooks 28S | AB_28S_DSS | Brooks 121S | AB_121S_GSS |  |  | 844
| 54L | Altalink Management Ltd. | Alberta | 1 | ac | 5.6 | 3.4568 | 138 | 2.428 |  |  | 143 | 172 | 0.9 | n/a | 128.7 | 154.8 | West Cascade 177S | AB_177S_DSS | Banff 123S | AB_123S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 307
| 773L | Altalink Management Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 138 | 10.926 |  |  | 121 | 127 | 0.9 | n/a | 108.9 | 114.3 | ALBChem Beaverhill Creek 308S | AB_308S_ISS | Bruderheim 127S | AB_127S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 567
| 846L | Altalink Management Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 138 | 7.284 |  |  | 167 | 191 | 0.9 | n/a | 150.3 | 171.9 | Canadian Oxy Astotin Creek 365S | AB_365S_ISS | Bruderheim 127S | AB_127S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 863
| 815L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 141 | 163 | 0.9 | n/a | 126.9 | 146.7 | Deerland 13S | AB_13S_DSS | Bruderheim 127S | AB_127S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 834
| 1054L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  | 594 | 624 | 0.9 | n/a | 534.6 | 561.6 | Deerland 13S | AB_13S_DSS | Heartland 12S | AB_12S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 32
| 1206L | Altalink Management Ltd. | Alberta | 1 | ac | 138 | 85.1852 | 500 | 54.51 |  |  | 2598 | 2598 | 0.9 | n/a | 2338.2 | 2338.2 | Ellerslie 89S | AB_89S_DSS | Heartland 12S | AB_12S_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 78
| 1212L | Altalink Management Ltd. | Alberta | 1 | ac | 138 | 85.1852 | 500 | 54.51 |  |  | 2598 | 2598 | 0.9 | n/a | 2338.2 | 2338.2 | Ellerslie 89S | AB_89S_DSS | Heartland 12S | AB_12S_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 80
| 672L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 167 | 201 | 0.9 | n/a | 150.3 | 180.9 | Entwistle 235S | AB_235S_DSS | Moon Lake 131S | AB_131S_DSS | AESO. 2016. Gainford Connection Assessment |  | 354
| 673L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Violet Grove 283S | AB_283S_DSS | Moon Lake 131S | AB_131S_DSS |  |  | 355
| 944L | Altalink Management Ltd. | Alberta | 1 | ac | 73.5 | 45.3704 | 240 | 35.0486 |  |  | 550 | 679 | 0.9 | n/a | 495 | 611.1 | Jenner 275S | AB_275S_GSS | Ware Junction 132S | AB_132S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 976
| 951L | Altalink Management Ltd. | Alberta | 1 | ac | 73.5 | 45.3704 | 240 | 35.0486 |  |  | 550 | 679 | 0.9 | n/a | 495 | 611.1 | Jenner 275S | AB_275S_GSS | Ware Junction 132S | AB_132S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 981
| 931L | Altalink Management Ltd. | Alberta | 1 | ac | 31.5 | 19.4444 | 240 | 15.0208 |  |  | 592 | 665 | 0.9 | n/a | 532.8 | 598.5 | West Brooks 28S | AB_28S_DSS | Ware Junction 132S | AB_132S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 966
| 1053L | Altalink Management Ltd. | Alberta | 1 | ac | 45.5 | 28.0864 | 240 | 21.6968 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Cassils 324S | AB_324S_DSS | Ware Junction 132S | AB_132S_DSS |  |  | 31
| 1075L | Altalink Management Ltd. | Alberta | 1 | ac | 31.5 | 19.4444 | 240 | 15.0208 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | West Brooks 28S | AB_28S_DSS | Ware Junction 132S | AB_132S_DSS |  |  | 45
| 822L | Altalink Management Ltd. | Alberta | 1 | ac | 4.6 | 2.8395 | 138 | 1.9944 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | East Edmonton 38S | AB_38S_DSS | Stelco Edmonton East 133S | AB_133S_DSS | AESO. 2016. Henday Connection Assessment |  | 839
| 607AL | Altalink Management Ltd. | Alberta | 1 | ac | 8.4 | 5.1852 | 144 | 3.678 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Taber Wind Farm 134S JCT | AB_134S_JCT | Taber Wind Farm 134S | AB_134S_GSS |  |  | 326
| 607L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 119 | 119 | 0.9 | n/a | 107.1 | 107.1 | Fincastle 336S | AB_336S_DSS | Taber Wind Farm 134S JCT | AB_134S_JCT | AESO. 2018. Fincastle Connection Assessment |  | 324
| 607L | Altalink Management Ltd. | Alberta | 1 | ac | 15.4 | 9.5062 | 138 | 6.677 |  |  | 119 | 119 | 0.9 | n/a | 107.1 | 107.1 | Taber Wind Farm 134S JCT | AB_134S_JCT | Conrad 135S | AB_135S_DSS | AESO. 2018. Fincastle Connection Assessment |  | 325
| 702AL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sedgewick 137S JCT | AB_137S_JCT | Sedgewick 137S | AB_137S_DSS |  |  | 407
| 702L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 87 | 135 | 0.9 | n/a | 78.3 | 121.5 | Hardisty 377S | AB_377S_DSS | Sedgewick 137S JCT | AB_137S_JCT | AESO. 2016. Bauer 918S Connection Assessment |  | 405
| 172EL | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Hillridge 139S JCT | AB_139S_JCT | Hillridge 139S | AB_139S_DSS | AESO. 2018. Fincastle Connection Assessment |  | 122
| 172L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Coaldale 254S | AB_254S_GSS | Hillridge 139S JCT | AB_139S_JCT | AESO. 2018. Fincastle Connection Assessment |  | 120
| 808L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 138 | 15.175 |  |  | 98 | 114 | 0.9 | n/a | 88.2 | 102.6 | Weasel Creek 947S JCT | AB_947S_JCT | Deerland 13S | AB_13S_DSS | AESO. 2018. Strathcona CG Connection Assessment |  | 826
| 788AL | Altalink Management Ltd. | Alberta | 1 | ac | 8.4 | 5.1852 | 144 | 3.678 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Thompson 140S JCT | AB_140S_JCT | Thompson 140S | AB_140S_DSS |  |  | 584
| 788L | Altalink Management Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 138 | 10.926 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Heart Lake 898S | AB_898S_DSS | Thompson 140S JCT | AB_140S_JCT | AESO. 2018. Kirby Connection Assessment |  | 582
| 727L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Magcan 142S JCT | AB_142S_JCT | Magcan 142S | AB_142S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 453
| 727L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 119 | 143 | 0.9 | n/a | 107.1 | 128.7 | High River 65S | AB_65S_DSS | Magcan 142S JCT | AB_142S_JCT | AESO. 2016. Okotoks Connection Assessment |  | 452
| 604L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Blackmud 155S | AB_155S_DSS | Nisku 149S | AB_149S_DSS | AESO. 2017. Heartland Connection Assessment |  | 321
| 454L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Saunders Lake 289S | AB_289S_DSS | Nisku 149S | AB_149S_DSS |  |  | 267
| 455L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Saunders Lake 289S | AB_289S_DSS | Nisku 149S | AB_149S_DSS |  |  | 268
| 739L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 138 | 10.8393 |  |  | 143 | 162 | 0.9 | n/a | 128.7 | 145.8 | Acheson 305S | AB_305S_DSS | Devon 14S | AB_14S_DSS | AESO. 2017. Heartland Connection Assessment |  | 499
| 223L | Altalink Management Ltd. | Alberta | 1 | ac | 37.8 | 23.3333 | 144 | 16.551 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Colinton 159S | AB_159S_DSS | Clyde 150S | AB_150S_DSS | AESO. 2016. Plamondon Connection Assessment |  | 154
| 723L | Altalink Management Ltd. | Alberta | 1 | ac | 15.12 | 9.3333 | 138 | 6.5556 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | Westlock 438S | AB_438S_GSS | Clyde 150S | AB_150S_DSS | AESO. 2016. Plamondon Connection Assessment |  | 442
| 971L | Altalink Management Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 240 | 12.0167 |  |  | 549 | 701 | 0.9 | n/a | 494.1 | 630.9 | Conklin 762S | AB_762S_DSS | Black Spruce 154S | AB_154S_DSS | AESO. 2019. Boreal 193S Connection Assessment |  | 991
| 1115L | Altalink Management Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 240 | 12.0167 |  |  | 874 | 1103 | 0.9 | n/a | 786.6 | 992.7 | Pike 170S | AB_170S_DSS | Black Spruce 154S | AB_154S_DSS | AESO. 2019. Boreal 193S Connection Assessment |  | 65
| 1118L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  | 647 | 802 | 0.9 | n/a | 582.3 | 721.8 | Sunday Creek 539S | AB_539S_DSS | Black Spruce 154S | AB_154S_DSS | AESO. 2018. Kirby Connection Assessment |  | 68
| 739L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Devon 14S | AB_14S_DSS | Blackmud 155S | AB_155S_DSS |  |  | 500
| 788L | Altalink Management Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 138 | 7.284 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Thompson 140S JCT | AB_140S_JCT | Lac La Biche 157S | AB_157S_DSS | AESO. 2018. Kirby Connection Assessment |  | 583
| 763L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Hull 257S | AB_257S_DSS | Vauxhall 158S | AB_158S_DSS | AESO. 2018. Fincastle Connection Assessment |  | 551
| 932L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Janet 74S | AB_74S_DSS | Beddington 162S | AB_162S_DSS |  |  | 967
| 918L | Altalink Management Ltd. | Alberta | 1 | ac | 120 | 74.0741 | 240 | 57.2222 |  |  |  |  | 0.9 | 2.4793 | 362.4493 | 393.4022 | Johnson 281S | AB_281S_DSS | Beddington 162S | AB_162S_DSS |  |  | 951
| 669L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 138 | 15.175 |  |  | 177 | 195 | 0.9 | n/a | 159.3 | 175.5 | Cypress 562S | AB_562S_DSS | AMOCO Empress 163S | AB_163S_ISS | AESO. 2018. Whitla Connection Assessment |  | 352
| 760L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Empress 394S | AB_394S_DSS | AMOCO Empress 163S | AB_163S_ISS | AESO. 2016. Jenner Connection Assessment |  | 545
| 760AL | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 144 | 7.6625 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Empress Liquids 164S JCT | AB_164S_JCT | Empress Liquids 164S | AB_164S_ISS |  |  | 548
| 760L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 144 | 7.6625 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | AMOCO Empress 163S | AB_163S_ISS | Empress Liquids 164S JCT | AB_164S_JCT |  |  | 546
| 156BL | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 138 | 4.3357 |  |  | 121 | 149 | 0.9 | n/a | 108.9 | 134.1 | T.M.P.L. Gainford 165S JCT | AB_165S_JCT | T.M.P.L. Gainford 165S | AB_165S_ISS | AESO. 2016. Gainford Connection Assessment |  | 104
| 156L | Altalink Management Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 138 | 23.8464 |  |  | 126 | 169 | 0.9 | n/a | 113.4 | 152.1 | Wabamun 19S | AB_19S_DSS | T.M.P.L. Gainford 165S JCT | AB_165S_JCT | AESO. 2016. Gainford Connection Assessment |  | 102
| 707L | Altalink Management Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 138 | 5.463 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Fort Sask. 54S | AB_54S_DSS | Dow Chemical Fort Sask. 166S | AB_166S_ISS | AESO. 2017. Heartland Connection Assessment |  | 416
| 899L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Fort Sask. Cogen 218S | AB_218S_GSS | Dow Chemical Fort Sask. 166S | AB_166S_ISS |  |  | 922
| 787L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Ross Creek 906S JCT | AB_906S_JCT | Dow Chemical Fort Sask. 166S | AB_166S_ISS |  |  | 580
| 1117L | Altalink Management Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 240 | 21.4583 |  |  | 874 | 1103 | 0.9 | n/a | 786.6 | 992.7 | Heart Lake 898S | AB_898S_DSS | Ipiatik 167S | AB_167S_DSS | AESO. 2019. Boreal 193S Connection Assessment |  | 67
| 1116L | Altalink Management Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 240 | 14.0194 |  |  | 874 | 1103 | 0.9 | n/a | 786.6 | 992.7 | Pike 170S | AB_170S_DSS | Ipiatik 167S | AB_167S_DSS | AESO. 2019. Boreal 193S Connection Assessment |  | 66
| 781L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 138 | 4.3357 |  |  | 143 | 172 | 0.9 | n/a | 128.7 | 154.8 | Lamoureux 71S | AB_71S_DSS | Sherritt Gordon 172S | AB_172S_GSS | AESO. 2017. Heartland Connection Assessment |  | 574
| 709L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Fort Sask. 54S | AB_54S_DSS | Sherritt Gordon 172S | AB_172S_GSS |  |  | 423
| 54L | Altalink Management Ltd. | Alberta | 1 | ac | 5.6 | 3.4568 | 138 | 2.428 |  |  | 143 | 172 | 0.9 | n/a | 128.7 | 154.8 | Cascade 29S JCT | AB_29S_JCT | West Cascade 177S | AB_177S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 306
| 202L | Altalink Management Ltd. | Alberta | 1 | ac | 85 | 52.4691 | 138 | 36.8536 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Edson 58S | AB_58S_GSS | Cynthia 178S | AB_178S_DSS | AESO. 2020. Cascade Connection Assessment |  | 144
| 828L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Petro Canada Brazeau River 489S | AB_489S_ISS | Cynthia 178S | AB_178S_DSS |  |  | 845
| 733L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Namaka 428S | AB_428S_DSS | Gleichen 179S | AB_179S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 490
| 995L | Altalink Management Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 240 | 20.0278 |  |  | 333 | 333 | 0.9 | n/a | 299.7 | 299.7 | Willesdengreen 68S JCT | AB_68S_JCT | Benalto 17S | AB_17S_DSS | AESO. 2020. Cascade Connection Assessment |  | 999
| 190L | Altalink Management Ltd. | Alberta | 1 | ac | 140 | 86.4198 | 240 | 66.7593 |  |  | 466 | 499 | 0.9 | n/a | 419.4 | 449.1 | Keephills 320P | AB_320P_GSS | Benalto 17S | AB_17S_DSS | AESO. 2016. Gainford Connection Assessment |  | 132
| 903L | Altalink Management Ltd. | Alberta | 1 | ac | 140 | 86.4198 | 240 | 66.7593 |  |  | 448 | 499 | 0.9 | n/a | 403.2 | 449.1 | Keephills 320P | AB_320P_GSS | Benalto 17S | AB_17S_DSS | AESO. 2016. Gainford Connection Assessment |  | 930
| 922L | Altalink Management Ltd. | Alberta | 1 | ac | 145 | 89.5062 | 240 | 69.1435 |  |  | 466 | 499 | 0.9 | n/a | 419.4 | 449.1 | Sundance 310P | AB_310P_GSS | Benalto 17S | AB_17S_DSS | AESO. 2016. Gainford Connection Assessment |  | 957
| 926L | Altalink Management Ltd. | Alberta | 1 | ac | 145 | 89.5062 | 240 | 69.1435 |  |  | 481 | 499 | 0.9 | n/a | 432.9 | 449.1 | Sundance 310P | AB_310P_GSS | Benalto 17S | AB_17S_DSS | AESO. 2016. Gainford Connection Assessment |  | 961
| 757L | Altalink Management Ltd. | Alberta | 1 | ac | 22.5 | 13.8889 | 144 | 9.8518 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Eckville 534S JCT | AB_534S_JCT | Benalto 17S | AB_17S_DSS |  |  | 542
| 463L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Monarch 492S JCT | AB_492S_JCT | Chinook 181S | AB_181S_DSS | AESO. 2018. Vulcan and Stavely Connection Assessment |  | 272
| 445L | Altalink Management Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 144 | 7.356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Pike 170S | AB_170S_DSS | Underwood 183S | AB_183S_DSS |  |  | 263
| 705L | Altalink Management Ltd. | Alberta | 1 | ac | 4.025 | 2.4846 | 138 | 1.7451 |  |  | 119 | 113 | 0.9 | n/a | 107.1 | 101.7 | Knightsbridge 216S | AB_216S_DSS | Petro Canada Edmonton 184S | AB_184S_DSS | AESO. 2016. Henday Connection Assessment |  | 412
| 606L | Altalink Management Ltd. | Alberta | 1 | ac | 10.8 | 6.6667 | 138 | 4.6826 |  |  | 120 | 146 | 0.9 | n/a | 108 | 131.4 | Petro Canada Edmonton 184S | AB_184S_DSS | Bretville 185S | AB_185S_DSS | AESO. 2016. Henday Connection Assessment |  | 323
| 792L | Altalink Management Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 138 | 17.3429 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Clyde 150S | AB_150S_DSS | N.W. Cardiff 191S | AB_191S_DSS | AESO. 2016. Plamondon Connection Assessment |  | 589
| 425L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | North Red Deer 217S | AB_217S_DSS | South Red Deer 194S | AB_194S_DSS |  |  | 252
| 174L | Altalink Management Ltd. | Alberta | 1 | ac | 27 | 16.6667 | 138 | 11.7064 |  |  | 85.1 | 90.1 | 0.9 | n/a | 76.59 | 81.09 | Cooking Lake 522S | AB_522S_DSS | Bardo 197S | AB_197S_DSS | AESO. 2020. Summerside Connection Assessment |  | 124
| 461L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 144 | 7.6625 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | N.E. Lacombe 212S | AB_212S_DSS | Blackfalds 198S | AB_198S_DSS |  |  | 270
| 444L | Altalink Management Ltd. | Alberta | 1 | ac | 7.5 | 4.6296 | 144 | 3.2839 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | North Red Deer 217S | AB_217S_DSS | Blackfalds 198S | AB_198S_DSS |  |  | 261
| 631L | Altalink Management Ltd. | Alberta | 1 | ac | 8.5 | 5.2469 | 138 | 3.6854 |  |  | 106 | 117 | 0.9 | n/a | 95.4 | 105.3 | Dry Creek 186S | AB_186S_DSS | East Airdrie 199S | AB_199S_DSS | AESO. 2018. East Crossfield Connection Assessment |  | 339
| 688L | Altalink Management Ltd. | Alberta | 1 | ac | 2.55 | 1.5741 | 138 | 1.1056 |  |  | 121 | 142 | 0.9 | n/a | 108.9 | 127.8 | Summit 653S JCT | AB_653S_JCT | East Airdrie 199S | AB_199S_DSS | AESO. 2018. East Crossfield Connection Assessment |  | 364
| 905L | Altalink Management Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 240 | 33.3796 |  |  | 299 | 437 | 0.9 | n/a | 269.1 | 393.3 | North Calder 37S | AB_37S_DSS | Wabamun 19S | AB_19S_DSS | AESO. 2017. Heartland Connection Assessment |  | 931
| 902L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 240 | 11.9213 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Sundance 310P | AB_310P_GSS | Wabamun 19S | AB_19S_DSS | AESO. 2016. Gainford Connection Assessment |  | 929
| WAP-7L1 | Dapp Power Corporation | Alberta | 1 | ac | 16.8 | 10.3704 | 144 | 7.356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Wap 1S JCT | AB_1S_JCT | Wap 1S | AB_1S_DSS |  |  | 1078
| 724L | Altalink Management Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 144 | 5.517 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Flatbush 500S JCT | AB_500S_JCT | Wap 1S JCT | AB_1S_JCT |  |  | 443
| 9L32 | ATCO Electric Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 240 | 20.0278 |  |  | 761 | 831 | 0.9 | n/a | 684.9 | 747.9 | Bitumount 941S | AB_941S_ISS | Secord 2005S | AB_2005S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1026
| 9L101 | ATCO Electric Ltd. | Alberta | 1 | ac | 33.6 | 20.7407 | 240 | 16.0222 |  |  | 759 | 831 | 0.9 | n/a | 683.1 | 747.9 | Mcclelland 957S | AB_957S_DSS | Secord 2005S | AB_2005S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1010
| 635PL9-1000 | Suncor | Alberta | 1 | ac | 8.4 | 5.1852 | 240 | 4.0056 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Fort Hills 505S | AB_505S_GSS | Secord 2005S | AB_2005S_DSS |  |  | 342
| 635PL9-1001 | Suncor | Alberta | 1 | ac | 8.4 | 5.1852 | 240 | 4.0056 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Fort Hills 505S | AB_505S_GSS | Secord 2005S | AB_2005S_DSS |  |  | 343
| 7L126 | ATCO Electric Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 144 | 7.356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | AHS 01 279S | AB_279S_ISS | Willow Lake 2009S | AB_2009S_DSS |  |  | 636
| 7L182 | ATCO Electric Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 144 | 7.356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | AHS 01 279S | AB_279S_ISS | Willow Lake 2009S | AB_2009S_DSS |  |  | 679
| 7L194 | ATCO Electric Ltd. | Alberta | 1 | ac | 60 | 37.037 | 144 | 26.2714 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Dawes 2011S | AB_2011S_DSS | Willow Lake 2009S | AB_2009S_DSS |  |  | 684
| 7L155 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Gregoire 883S | AB_883S_DSS | Willow Lake 2009S | AB_2009S_DSS |  |  | 665
| 7L36 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Hangingstone 820S | AB_820S_DSS | Willow Lake 2009S | AB_2009S_DSS |  |  | 711
| 9L89 | ATCO Electric Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 240 | 26.2269 |  |  | 499 | 609 | 0.9 | n/a | 449.1 | 548.1 | Mcmillan 885S | AB_885S_DSS | Dawes 2011S | AB_2011S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1051
| 7LA97 | ATCO Electric Ltd. | Alberta | 1 | ac | 15.12 | 9.3333 | 144 | 6.6204 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Halfway 2014S JCT | AB_2014S_JCT | Halfway 2014S | AB_2014S_DSS |  |  | 813
| 7L97 | ATCO Electric Ltd. | Alberta | 1 | ac | 33.6 | 20.7407 | 144 | 14.712 |  |  | 117 | 155 | 0.9 | n/a | 105.3 | 139.5 | Tower Road 933S | AB_933S_DSS | Halfway 2014S JCT | AB_2014S_JCT | AESO. 2020. Suncor Base Plant Connection Assessment |  | 811
| 9L144 | ATCO Electric Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  | 433 | 524 | 0.9 | n/a | 389.7 | 471.6 | Birchwood Creek 960S | AB_960S_DSS | Yeo 2015S | AB_2015S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1013
| 7LA90 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Muir 2018S JCT | AB_2018S_JCT | Muir 2018S | AB_2018S_DSS |  |  | 802
| 7L90 | ATCO Electric Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 144 | 19.7036 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Little Smoky 813S | AB_813S_DSS | Muir 2018S JCT | AB_2018S_JCT | AESO. 2016. Fox Creek Connection Assessment |  | 800
| 12L70 | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 500 | 8.295 |  |  |  |  | 0.9 | 3 | 2550 | 3225 | Heartland 12S | AB_12S_DSS | Heathfield 2029S | AB_2029S_DSS |  |  | 87
| 12L85 | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 500 | 8.295 |  |  |  |  | 0.9 | 3 | 2550 | 3225 | Heartland 12S | AB_12S_DSS | Heathfield 2029S | AB_2029S_DSS |  |  | 88
| 7L147 | ATCO Electric Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 144 | 35.0286 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Dawes 2011S | AB_2011S_DSS | Sweetheart Lake 2032S | AB_2032S_DSS |  |  | 660
| 7LA10 | ATCO Electric Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  | 49 | 49 | 0.9 | n/a | 44.1 | 44.1 | Mowat 2033S JCT | AB_2033S_JCT | Mowat 2033S | AB_2033S_DSS | AESO. 2015. Eureka Connection Assessment |  | 614
| 7L10 | ATCO Electric Ltd. | Alberta | 1 | ac | 8 | 4.9383 | 144 | 3.5029 |  |  | 85 | 134 | 0.9 | n/a | 76.5 | 120.6 | Rycroft 730S | AB_730S_DSS | Mowat 2033S JCT | AB_2033S_JCT | AESO. 2018. Ksituan Connection Assessment |  | 612
| 869L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 144 | 7.6625 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | AMOCO Empress 163S | AB_163S_ISS | Sandy Point 204S | AB_204S_DSS |  |  | 897
| 1072L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  | 967 | 1203 | 0.9 | n/a | 870.3 | 1082.7 | Goose Lake 103S | AB_103S_DSS | Castle Rock Ridge 205S | AB_205S_GSS | AESO. 2019. Windrise Connection Assessment |  | 44
| 7L183 | ATCO Electric Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 144 | 5.517 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Meadow Creek 2081S JCT | AB_2081S_JCT | Engstrom 2060S | AB_2060S_DSS |  |  | 681
| 1087L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  | 547 | 711.1 | 0.9 | n/a | 492.3 | 639.99 | Cassils 324S | AB_324S_DSS | Newell 2075S | AB_2075S_DSS | AESO. 2020. Cypress Connection Assessment |  | 52
| 1088L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 240 | 8.3449 |  |  | 931 | 1210.3 | 0.9 | n/a | 837.9 | 1089.27 | Cassils 324S | AB_324S_DSS | Newell 2075S | AB_2075S_DSS | AESO. 2020. Cypress Connection Assessment |  | 53
| 923L | Altalink Management Ltd. | Alberta | 1 | ac | 50 | 30.8642 | 240 | 23.8426 |  |  | 547 | 676 | 0.9 | n/a | 492.3 | 608.4 | Milo 356S | AB_356S_DSS | Newell 2075S | AB_2075S_DSS | AESO. 2019. Travers Connection Assessment |  | 958
| 1035L | Altalink Management Ltd. | Alberta | 1 | ac | 125 | 77.1605 | 240 | 59.6065 |  |  | 952 | 1047 | 0.9 | n/a | 856.8 | 942.3 | Bowmanton 244S | AB_244S_DSS | Newell 2075S | AB_2075S_DSS | AESO. 2018. Whitla Connection Assessment |  | 14
| 13L50 | ATCO Electric Ltd. | Alberta | 1 | ac | 360 | 222.2222 | 500 | 142.2 |  |  |  |  | 0.9 | 1.2013 | 1021.1239 | 1291.4214 | Heathfield 2029S | AB_2029S_DSS | Newell 2075S | AB_2075S_DSS |  |  | 95
| 744L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 75 | 79 | 0.9 | n/a | 67.5 | 71.1 | TMPL Niton 228S | AB_228S_ISS | Pinedale 207S | AB_207S_DSS | AESO. 2020. Cascade Connection Assessment |  | 511
| 7LA183 | ATCO Electric Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 144 | 5.517 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Meadow Creek 2081S JCT | AB_2081S_JCT | Meadow Creek 2081S | AB_2081S_DSS |  |  | 682
| 7L183 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Kinosis 856S | AB_856S_DSS | Meadow Creek 2081S JCT | AB_2081S_JCT |  |  | 680
| 7L71 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 117 | 125 | 0.9 | n/a | 105.3 | 112.5 | Ruth Lake 848S | AB_848S_DSS | Dog Rib 2082S | AB_2082S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 772
| 7L228 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 150 | 150 | 0.9 | n/a | 135 | 135 | Big Mountain 845S | AB_845S_DSS | Thornton 2091S | AB_2091S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 691
| 150L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 143 | 172 | 0.9 | n/a | 128.7 | 154.8 | Jumping Pound 271S JCT | AB_271S_JCT | Ghost 20S | AB_20S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 100
| 418L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Madden 373S JCT | AB_373S_JCT | Ghost 20S | AB_20S_GSS |  |  | 245
| 703L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 121 | 145 | 0.9 | n/a | 108.9 | 130.5 | HRT Express 329S JCT | AB_329S_JCT | Hughenden 213S | AB_213S_DSS | AESO. 2016. Hughenden Connection Assessment |  | 409
| 419L | Altalink Management Ltd. | Alberta | 1 | ac | 4.8 | 2.963 | 144 | 2.1017 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Hazelwood 287S | AB_287S_DSS | Innisfail 214S | AB_214S_GSS |  |  | 246
| 420L | Altalink Management Ltd. | Alberta | 1 | ac | 4.8 | 2.963 | 144 | 2.1017 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Hazelwood 287S | AB_287S_DSS | Innisfail 214S | AB_214S_GSS |  |  | 247
| 443L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Olds 55S | AB_55S_DSS | Innisfail 214S | AB_214S_GSS |  |  | 260
| 865L | Altalink Management Ltd. | Alberta | 1 | ac | 4.6 | 2.8395 | 138 | 1.9944 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | East Edmonton 38S | AB_38S_DSS | Knightsbridge 216S | AB_216S_DSS | AESO. 2016. Henday Connection Assessment |  | 896
| 425L | Altalink Management Ltd. | Alberta | 1 | ac | 1 | 0.61728 | 144 | 0.43786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Red Deer North RD14S | AB_RD14S_DSS | North Red Deer 217S | AB_217S_DSS |  |  | 251
| 767AL | Altalink Management Ltd. | Alberta | 1 | ac | 10.8 | 6.6667 | 138 | 4.6826 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Marion 21S JCT | AB_21S_JCT | Marion 21S | AB_21S_DSS | AESO. 2016. Gainford Connection Assessment |  | 560
| 767L | Altalink Management Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 138 | 10.4057 |  |  | 121 | 143 | 0.9 | n/a | 108.9 | 128.7 | Sundance 310P | AB_310P_GSS | Marion 21S JCT | AB_21S_JCT | AESO. 2016. Gainford Connection Assessment |  | 557
| 472AL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sunken Lake 221S JCT | AB_221S_JCT | Sunken Lake 221S | AB_221S_DSS |  |  | 276
| 472L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 121 | 150 | 0.9 | n/a | 108.9 | 135 | Hughenden 213S | AB_213S_DSS | Sunken Lake 221S JCT | AB_221S_JCT | AESO. 2018. Provost Connection Assessment |  | 274
| 701L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | North Holden 395S | AB_395S_DSS | Strome 223S | AB_223S_DSS | AESO. 2016. Cooking Lake Connection Assessment |  | 404
| 225L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 69 | 9.415 |  |  | 24 | 31.2 | 0.9 | n/a | 21.6 | 28.08 | Spring Coulee 385S | AB_385S_GSS | Magrath 225S | AB_225S_GSS | AESO. 2019. Mclaughlin Connection Assessment |  | 156
| 891L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 120 | 145 | 0.9 | n/a | 108 | 130.5 | Garden City 226S JCT | AB_226S_JCT | Garden City 226S | AB_226S_DSS | AESO. 2018. Fincastle Connection Assessment |  | 913
| 863L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Magrath 225S | AB_225S_GSS | Garden City 226S JCT | AB_226S_JCT | AESO. 2019. Claresholm Connection Assessment |  | 889
| 831AL | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 144 | 3.065 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Cutting Lake 227S JCT | AB_227S_JCT | Cutting Lake 227S | AB_227S_DSS |  |  | 850
| 831L | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 144 | 3.065 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Brooks 121S | AB_121S_GSS | Cutting Lake 227S JCT | AB_227S_JCT |  |  | 848
| 744L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 75 | 79 | 0.9 | n/a | 67.5 | 71.1 | Paddle River 106S JCT | AB_106S_JCT | TMPL Niton 228S | AB_228S_ISS | AESO. 2016. Gainford Connection Assessment |  | 510
| 162L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 69 | 14.795 |  |  | 40 | 52 | 0.9 | n/a | 36 | 46.8 | Drywood 415S | AB_415S_DSS | Glenwood 229S | AB_229S_DSS | AESO. 2019. Drywood Connection Assessment |  | 111
| 601L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 144 | 10.7275 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Jenner 275S | AB_275S_GSS | Wardlow 230S | AB_230S_DSS |  |  | 319
| 735L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 96 | 94 | 0.9 | n/a | 86.4 | 84.6 | Redwater 171S | AB_171S_DSS | Beamer 233S | AB_233S_DSS | AESO. 2018. Strathcona CG Connection Assessment |  | 492
| 708L | Altalink Management Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 138 | 12.747 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Riverside 388S JCT | AB_388S_JCT | Beamer 233S | AB_233S_DSS | AESO. 2017. Heartland Connection Assessment |  | 418
| 807L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Shell AOSP 402S JCT | AB_402S_JCT | Beamer 233S | AB_233S_DSS | AESO. 2017. Heartland Connection Assessment |  | 823
| 888AL | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 123 | 150 | 0.9 | n/a | 110.7 | 135 | Fort Assiniboine 234S JCT | AB_234S_JCT | Fort Assiniboine 234S | AB_234S_DSS | AESO. 2016. Gainford Connection Assessment |  | 910
| 7L230 | ATCO Electric Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 144 | 19.7036 |  |  | 86 | 91 | 0.9 | n/a | 77.4 | 81.9 | Sarah Lake 743S | AB_743S_DSS | Fort Assiniboine 234S JCT | AB_234S_JCT | AESO. 2016. Gainford Connection Assessment |  | 694
| 156L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 138 | 4.3357 |  |  | 126 | 169 | 0.9 | n/a | 113.4 | 152.1 | T.M.P.L. Gainford 165S JCT | AB_165S_JCT | Entwistle 235S | AB_235S_DSS | AESO. 2016. Gainford Connection Assessment |  | 103
| 166AL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Shell Harmattan 238S JCT | AB_238S_JCT | Shell Harmattan 238S | AB_238S_GSS |  |  | 115
| 166L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Johnson 281S | AB_281S_DSS | Shell Harmattan 238S JCT | AB_238S_JCT |  |  | 113
| 170AL | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Russell 632S | AB_632S_DSS | Castle River 239S | AB_239S_GSS | AESO. 2015. McLaughlin Aggregated Connection Assessment | Line is also referred to as 413L | 117
| 725BL | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mcbride Lake 240S JCT | AB_240S_JCT | Mcbride Lake 240S | AB_240S_GSS |  |  | 450
| 725L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Fort Macleod 15S | AB_15S_GSS | Mcbride Lake 240S JCT | AB_240S_JCT | AESO. 2019. Travers Connection Assessment |  | 445
| 734L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 138 | 4.3357 |  |  | 167 | 201 | 0.9 | n/a | 150.3 | 180.9 | North Lethbridge 370S | AB_370S_DSS | Uplands 241S | AB_241S_DSS | AESO. 2019. Travers Connection Assessment |  | 491
| 813L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 144 | 6.13 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Macdonald 146S | AB_146S_DSS | Uplands 241S | AB_241S_DSS |  |  | 832
| 796AL | Altalink Management Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 144 | 5.517 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Flat Lake 242S JCT | AB_242S_JCT | Flat Lake 242S | AB_242S_DSS |  |  | 596
| 796L | Altalink Management Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 144 | 11.034 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Waupisoo 405S | AB_405S_DSS | Flat Lake 242S JCT | AB_242S_JCT |  |  | 594
| 603L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 144 | 10.7275 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Windy Flats 138S | AB_138S_DSS | Soderglen 243S | AB_243S_GSS |  |  | 320
| 675L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 287 | 373.1 | 0.9 | n/a | 258.3 | 335.79 | Al Rothbauer 321S | AB_321S_DSS | Bowmanton 244S | AB_244S_DSS | AESO. 2020. Rattlesnake Connection Assessment |  | 357
| 879L | Altalink Management Ltd. | Alberta | 1 | ac | 112 | 69.1358 | 138 | 48.56 |  |  | 85 | 94 | 0.9 | n/a | 76.5 | 84.6 | Burdett 368S | AB_368S_GSS | Bowmanton 244S | AB_244S_DSS | AESO. 2018. Whitla Connection Assessment |  | 902
| 674L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 121 | 133 | 0.9 | n/a | 108.9 | 119.7 | Chappice Lake 649S | AB_649S_DSS | Bowmanton 244S | AB_244S_DSS | AESO. 2018. Whitla Connection Assessment |  | 356
| 892L | Altalink Management Ltd. | Alberta | 1 | ac | 50 | 30.8642 | 138 | 21.6786 |  |  | 67 | 74 | 0.9 | n/a | 60.3 | 66.6 | Suffield 895S | AB_895S_GSS | Bowmanton 244S | AB_244S_DSS | AESO. 2018. Whitla Connection Assessment |  | 914
| 676L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 138 | 16.6925 |  |  | 365 | 474.5 | 0.9 | n/a | 328.5 | 427.05 | Bullshead 523S | AB_523S_DSS | Bowmanton 244S | AB_244S_DSS | AESO. 2016. Bullshead Connection Assessment |  | 358
| 56L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 108 | 114 | 0.9 | n/a | 97.2 | 102.6 | Ghost 20S | AB_20S_GSS | Seebe 245S | AB_245S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 312
| 3L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 118 | 146 | 0.9 | n/a | 106.2 | 131.4 | Jumping Pound Junction 43S JCT | AB_43S_JCT | Seebe 245S | AB_245S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 236
| 755L | Altalink Management Ltd. | Alberta | 1 | ac | 27.5 | 16.9753 | 144 | 12.0411 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Joffre 535S | AB_535S_GSS | Piper Creek 247S | AB_247S_DSS |  |  | 538
| 718L | Altalink Management Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 144 | 39.4071 |  |  |  |  | 0.9 | 2.9972 | 153.4575 | 169.8095 | Strachan 263S | AB_263S_DSS | Bighorn Plant 250P | AB_250P_GSS |  |  | 429
| 964L | Altalink Management Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 240 | 38.1481 |  |  | 952 | 1047 | 0.9 | n/a | 856.8 | 942.3 | Bowmanton 244S | AB_244S_DSS | Whitla 251S | AB_251S_DSS | AESO. 2018. Whitla Connection Assessment |  | 987
| 983L | Altalink Management Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 240 | 38.1481 |  |  | 952 | 1047 | 0.9 | n/a | 856.8 | 942.3 | Bowmanton 244S | AB_244S_DSS | Whitla 251S | AB_251S_DSS | AESO. 2018. Whitla Connection Assessment |  | 994
| 1148L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 240 | 5.0069 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Shamrock 1018S | AB_1018S_DSS | Whitla 251S | AB_251S_DSS |  |  | 73
| 408L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 75 | 79 | 0.9 | n/a | 67.5 | 71.1 | Wainright 51S | AB_51S_DSS | Jarrow 252S | AB_252S_DSS | AESO. 2017. Paintearth Connection Assessment |  | 240
| 491L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Jarrow 252S JCT | AB_252S_JCT | Jarrow 252S | AB_252S_DSS |  |  | 277
| 7L50 | ATCO Electric Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 144 | 18.39 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Battle River 757S | AB_757S_GSS | Jarrow 252S JCT | AB_252S_JCT | AESO. 2016. Bauer 918S Connection Assessment |  | 730
| 851L | Altalink Management Ltd. | Alberta | 1 | ac | 31.5 | 19.4444 | 138 | 13.6575 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Carseland 525S | AB_525S_GSS | Blackie 253S | AB_253S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 872
| 876L | Altalink Management Ltd. | Alberta | 1 | ac | 49 | 30.2469 | 138 | 21.245 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Gleichen 179S | AB_179S_DSS | Blackie 253S | AB_253S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 901
| 820L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Chin Chute 315S JCT | AB_315S_JCT | Coaldale 254S | AB_254S_GSS | AESO. 2019. Travers Connection Assessment |  | 836
| 770L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | North Lethbridge 370S | AB_370S_DSS | Coaldale 254S | AB_254S_GSS | AESO. 2019. Travers Connection Assessment |  | 565
| 172L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | North Lethbridge 370S | AB_370S_DSS | Coaldale 254S | AB_254S_GSS | AESO. 2019. Claresholm Connection Assessment |  | 119
| 180L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 112 | 120 | 0.9 | n/a | 100.8 | 108 | East Stavely 928S | AB_928S_DSS | Vulcan 255S | AB_255S_DSS | AESO. 2019. Travers Connection Assessment |  | 127
| 166L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Shell Harmattan 238S JCT | AB_238S_JCT | Harmattan 256S | AB_256S_GSS |  |  | 114
| 507L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Taber 83S | AB_83S_DSS | Hull 257S | AB_257S_DSS | AESO. 2018. Fincastle Connection Assessment |  | 283
| 862L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Dow Chemical Fort Sask. 166S | AB_166S_ISS | Dow Hydro Carbons 258S | AB_258S_ISS |  |  | 888
| 861L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Lamoureux 71S | AB_71S_DSS | Dow Hydro Carbons 258S | AB_258S_ISS |  |  | 886
| 199AL | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Chickadee Creek 259S JCT | AB_259S_JCT | Chickadee Creek 259S | AB_259S_DSS |  |  | 136
| 199L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Fox Creek Altalink 347S | AB_347S_DSS | Chickadee Creek 259S JCT | AB_259S_JCT | AESO. 2020. Cascade Connection Assessment |  | 134
| 717L | Altalink Management Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 144 | 24.0821 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Benalto 17S | AB_17S_DSS | Rocky Mountain House 262S | AB_262S_DSS |  |  | 428
| 719L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Ricinus 581S JCT | AB_581S_JCT | Strachan 263S | AB_263S_DSS |  |  | 434
| 870L | Altalink Management Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 144 | 10.5086 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Rocky Mountain House 262S | AB_262S_DSS | Strachan 263S | AB_263S_DSS |  |  | 898
| 1037L | Altalink Management Ltd. | Alberta | 1 | ac | 49 | 30.2469 | 240 | 23.3657 |  |  | 973 | 1208 | 0.9 | n/a | 875.7 | 1087.2 | Foothills 237S | AB_237S_DSS | SC1 266S | AB_266S_DSS | AESO. 2019. Travers Connection Assessment |  | 16
| 1038L | Altalink Management Ltd. | Alberta | 1 | ac | 49 | 30.2469 | 240 | 23.3657 |  |  | 973 | 1208 | 0.9 | n/a | 875.7 | 1087.2 | Foothills 237S | AB_237S_DSS | SC1 266S | AB_266S_DSS | AESO. 2019. Travers Connection Assessment |  | 18
| 1037L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 240 | 18.3588 |  |  | 973 | 1208 | 0.9 | n/a | 875.7 | 1087.2 | Windy Flats 138S | AB_138S_DSS | SC1 266S | AB_266S_DSS | AESO. 2019. Travers Connection Assessment |  | 17
| 1038L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 240 | 18.3588 |  |  | 973 | 1208 | 0.9 | n/a | 875.7 | 1087.2 | Windy Flats 138S | AB_138S_DSS | SC1 266S | AB_266S_DSS | AESO. 2019. Travers Connection Assessment |  | 19
| 749AL | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Killarney Lake 267S JCT | AB_267S_JCT | Killarney Lake 267S | AB_267S_DSS | AESO. 2017. Irma Connection Assessment |  | 526
| 749L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 138 | 2.6014 |  |  | 121 | 149 | 0.9 | n/a | 108.9 | 134.1 | Metiskow 648S | AB_648S_DSS | Killarney Lake 267S JCT | AB_267S_JCT | AESO. 2016. Bauer 918S Connection Assessment |  | 524
| 199L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 144 | 15.325 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Chickadee Creek 259S JCT | AB_259S_JCT | Whitecourt 268S | AB_268S_DSS |  |  | 135
| 526L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 72 | 6.9557 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Mobil Oil Carson Creek 887S JCT | AB_887S_JCT | Whitecourt 268S | AB_268S_DSS |  |  | 300
| 150AL | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 138 | 3.035 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | Jumping Pound 271S JCT | AB_271S_JCT | Jumping Pound 271S | AB_271S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 101
| 150L | Altalink Management Ltd. | Alberta | 1 | ac | 28 | 17.284 | 138 | 12.14 |  |  | 173 | 250 | 0.9 | n/a | 155.7 | 225 | Sarcee 42S | AB_42S_DSS | Jumping Pound 271S JCT | AB_271S_JCT | AESO. 2018. Mount Allan Connection Assessment |  | 99
| 3L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 97 | 111 | 0.9 | n/a | 87.3 | 99.9 | Sarcee 42S | AB_42S_DSS | Springbank 272S | AB_272S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 234
| 124L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 69 | 8.07 |  |  | 29 | 36 | 0.9 | n/a | 26.1 | 32.4 | Wabamun 19S | AB_19S_DSS | Wabamun 2739S | AB_2739S_DSS | AESO. 2016. Gainford Connection Assessment |  | 84
| 1002L | Altalink Management Ltd. | Alberta | 1 | ac | 85 | 52.4691 | 240 | 40.5324 |  |  | 550 | 679 | 0.9 | n/a | 495 | 611.1 | AMOCO Empress 163S | AB_163S_ISS | Jenner 275S | AB_275S_GSS | AESO. 2016. Jenner Connection Assessment |  | 7
| 775L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Joffre 535S | AB_535S_GSS | Union Carbide Prentiss 276S | AB_276S_ISS |  |  | 569
| 423L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 144 | 15.325 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | N.E. Lacombe 212S | AB_212S_DSS | Union Carbide Prentiss 276S | AB_276S_ISS |  |  | 250
| 759L | Altalink Management Ltd. | Alberta | 1 | ac | 27.5 | 16.9753 | 144 | 12.0411 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Red Deer 63S | AB_63S_DSS | Union Carbide Prentiss 276S | AB_276S_ISS |  |  | 544
| 748L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Killarney Lake 267S | AB_267S_DSS | Hayter 277S | AB_277S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 523
| 1081L | Altalink Management Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  |  |  | 0.9 | 2.9972 | 438.1717 | 475.5913 | Benalto 17S | AB_17S_DSS | Johnson 281S | AB_281S_DSS |  |  | 47
| 417L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Olds 55S | AB_55S_DSS | Johnson 281S | AB_281S_DSS |  |  | 243
| 796L | Altalink Management Ltd. | Alberta | 1 | ac | 37.8 | 23.3333 | 144 | 16.551 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Flat Lake 242S JCT | AB_242S_JCT | Grassland 282S | AB_282S_DSS |  |  | 595
| 835L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Buck Lake 454S JCT | AB_454S_JCT | Violet Grove 283S | AB_283S_DSS |  |  | 856
| 730L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 85.1 | 90.1 | 0.9 | n/a | 76.59 | 81.09 | Kingman 299S JCT | AB_299S_JCT | East Camrose 285S | AB_285S_GSS | AESO. 2016. Cooking Lake Connection Assessment |  | 483
| 605L | Altalink Management Ltd. | Alberta | 1 | ac | 5.175 | 3.1944 | 138 | 2.2437 |  |  | 120 | 146 | 0.9 | n/a | 108 | 131.4 | Bretville 185S | AB_185S_DSS | Yasa 286S | AB_286S_DSS | AESO. 2016. Henday Connection Assessment |  | 322
| 215L | Altalink Management Ltd. | Alberta | 1 | ac | 4.6 | 2.8395 | 138 | 1.9944 |  |  | 120 | 146 | 0.9 | n/a | 108 | 131.4 | East Edmonton 38S | AB_38S_DSS | Yasa 286S | AB_286S_DSS | AESO. 2015. Broadmoor Connection Assessment |  | 152
| 929L | Altalink Management Ltd. | Alberta | 1 | ac | 125 | 77.1605 | 240 | 59.6065 |  |  |  |  | 0.9 | 2.4134 | 352.8216 | 382.9523 | Janet 74S | AB_74S_DSS | Hazelwood 287S | AB_287S_DSS |  |  | 964
| 1082L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 240 | 5.7222 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Red Deer 63S | AB_63S_DSS | Hazelwood 287S | AB_287S_DSS |  |  | 48
| 910L | Altalink Management Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 240 | 33.3796 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Saunders Lake 289S | AB_289S_DSS | Wolf Creek 288S | AB_288S_DSS |  |  | 942
| 853L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Bassano 435S JCT | AB_435S_JCT | West Brooks 28S | AB_28S_DSS | AESO. 2019. Travers Connection Assessment |  | 874
| 763L | Altalink Management Ltd. | Alberta | 1 | ac | 28 | 17.284 | 138 | 12.14 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Enchant 447S JCT | AB_447S_JCT | West Brooks 28S | AB_28S_DSS | AESO. 2018. Fincastle Connection Assessment |  | 553
| 433L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Horse Creek T793S | AB_T793S_DSS | Cochrane 291S | AB_291S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 258
| 736L | Altalink Management Ltd. | Alberta | 1 | ac | 4.6 | 2.8395 | 138 | 1.9944 |  |  | 121 | 149 | 0.9 | n/a | 108.9 | 134.1 | East Edmonton 38S | AB_38S_DSS | Bernese 293S | AB_293S_DSS | AESO. 2016. Henday Connection Assessment |  | 493
| 801L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Brazeau 62S | AB_62S_GSS | Brazeau Outlet Works 294S | AB_294S_DSS |  |  | 814
| 769L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 86 | 115 | 0.9 | n/a | 77.4 | 103.5 | Hardisty 377S | AB_377S_DSS | Rosyth 296S | AB_296S_DSS | AESO. 2016. Wainright Connection Assessment |  | 562
| 732L | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 144 | 3.1526 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Queensland 301S JCT | AB_301S_JCT | Kingman 299S | AB_299S_DSS |  |  | 487
| 730L | Altalink Management Ltd. | Alberta | 1 | ac | 10.8 | 6.6667 | 138 | 4.6826 |  |  | 86 | 91.1 | 0.9 | n/a | 77.4 | 81.99 | Bardo 197S | AB_197S_DSS | Kingman 299S JCT | AB_299S_JCT | AESO. 2016. Cooking Lake Connection Assessment |  | 482
| 54AL | Altalink Management Ltd. | Alberta | 1 | ac | 5.6 | 3.4568 | 138 | 2.428 |  |  | 130 | 160 | 0.9 | n/a | 117 | 144 | Cascade 29S JCT | AB_29S_JCT | Cascade 29S | AB_29S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 308
| 54L | Altalink Management Ltd. | Alberta | 1 | ac | 3.5 | 2.1605 | 138 | 1.5175 |  |  | 129 | 158 | 0.9 | n/a | 116.1 | 142.2 | Rundle 35S JCT | AB_35S_JCT | Cascade 29S JCT | AB_29S_JCT | AESO. 2018. Mount Allan Connection Assessment |  | 305
| 87L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | Seebe 245S | AB_245S_DSS | Kananaskis 2S | AB_2S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 903
| 732AL | Altalink Management Ltd. | Alberta | 1 | ac | 4.8 | 2.963 | 144 | 2.1017 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Queensland 301S JCT | AB_301S_JCT | Queensland 301S | AB_301S_DSS |  |  | 488
| 732L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Kingman 299S JCT | AB_299S_JCT | Queensland 301S JCT | AB_301S_JCT |  |  | 486
| 501L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 72 | 2.3186 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Cheviot 101S | AB_101S_DSS | Cardinal River 302S | AB_302S_DSS |  |  | 278
| 909L | Altalink Management Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 240 | 26.2269 |  |  | 481 | 499 | 0.9 | n/a | 432.9 | 449.1 | Dome 665S | AB_665S_DSS | Sundance 310P | AB_310P_GSS | AESO. 2020. Summerside Connection Assessment |  | 939
| 1045L | Altalink Management Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  | 481 | 581 | 0.9 | n/a | 432.9 | 522.9 | Jasper 805S | AB_805S_DSS | Sundance 310P | AB_310P_GSS | AESO. 2017. Clover Bar Connection Assessment |  | 24
| 234L | Altalink Management Ltd. | Alberta | 1 | ac | 36 | 22.2222 | 72 | 13.9114 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Sundance 310P JCT | AB_310P_JCT | Sundance 310P | AB_310P_GSS |  |  | 161
| 133L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 69 | 5.7643 |  |  | 29 | 36 | 0.9 | n/a | 26.1 | 32.4 | Wabamun 19S | AB_19S_DSS | Sundance 310P JCT | AB_310P_JCT | AESO. 2016. Gainford Connection Assessment |  | 93
| 1071L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 240 | 11.6829 |  |  | 952 | 1203 | 0.9 | n/a | 856.8 | 1082.7 | Castle Rock Ridge 205S | AB_205S_GSS | Fidler 312S | AB_312S_DSS | AESO. 2019. Windrise Connection Assessment |  | 43
| 994L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 240 | 11.9213 |  |  | 831 | 1080.3 | 0.9 | n/a | 747.9 | 972.27 | Goose Lake 103S | AB_103S_DSS | Fidler 312S | AB_312S_DSS | AESO. 2019. Mclaughlin Connection Assessment |  | 997
| 225AL | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 72 | 2.705 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Raymond Reservoir 313S JCT | AB_313S_JCT | Raymond Reservoir 313S | AB_313S_GSS |  |  | 159
| 225L | Altalink Management Ltd. | Alberta | 1 | ac | 16.1 | 9.9383 | 69 | 6.187 |  |  | 25 | 32.5 | 0.9 | n/a | 22.5 | 29.25 | Magrath 225S | AB_225S_GSS | Raymond Reservoir 313S JCT | AB_313S_JCT | AESO. 2019. Mclaughlin Connection Assessment |  | 157
| 820AL | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Chin Chute 315S JCT | AB_315S_JCT | Chin Chute 315S | AB_315S_GSS | AESO. 2019. Claresholm Connection Assessment |  | 837
| 820L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Stirling 67S | AB_67S_GSS | Chin Chute 315S JCT | AB_315S_JCT | AESO. 2019. Travers Connection Assessment |  | 835
| 752AL | Altalink Management Ltd. | Alberta | 1 | ac | 3.4 | 2.0988 | 138 | 1.4741 |  |  | 118 | 145 | 0.9 | n/a | 106.2 | 130.5 | Summit 653S JCT | AB_653S_JCT | West Crossfield 316S | AB_316S_DSS | AESO. 2018. East Crossfield Connection Assessment |  | 533
| 741L | Altalink Management Ltd. | Alberta | 1 | ac | 2.875 | 1.7747 | 138 | 1.2465 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | Knightsbridge 216S | AB_216S_DSS | Baseline 317S | AB_317S_DSS | AESO. 2016. Henday Connection Assessment |  | 506
| 708AL | Altalink Management Ltd. | Alberta | 1 | ac | 1.68 | 1.037 | 144 | 0.7356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Granite 342S | AB_342S_DSS | Scoria 318S | AB_318S_DSS |  |  | 421
| 1202L | Altalink Management Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 500 | 27.65 |  |  | 2598 | 2598 | 0.9 | n/a | 2338.2 | 2338.2 | Ellerslie 89S | AB_89S_DSS | Keephills 320P | AB_320P_GSS | AESO. 2017. Clover Bar Connection Assessment |  | 76
| 1203L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 500 | 8.295 |  |  | 2500 | 2500 | 0.9 | n/a | 2250 | 2250 | Sunnybrook 510S | AB_510S_DSS | Keephills 320P | AB_320P_GSS | AESO. 2017. Clover Bar Connection Assessment |  | 77
| 767L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | New Rose Valley 635S JCT | AB_635S_JCT | Keephills 320P | AB_320P_GSS | AESO. 2016. Gainford Connection Assessment |  | 559
| 133L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 72 | 11.5929 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Sundance 310P JCT | AB_310P_JCT | Keephills 320P | AB_320P_GSS |  |  | 94
| 809L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sunnybrook 510S | AB_510S_DSS | Keephills 320P | AB_320P_GSS |  |  | 828
| 880L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 123 | 135 | 0.9 | n/a | 110.7 | 121.5 | Bullshead 523S | AB_523S_DSS | Al Rothbauer 321S | AB_321S_DSS | AESO. 2018. Whitla Connection Assessment |  | 904
| 514BL | Altalink Management Ltd. | Alberta | 1 | ac | 5.6 | 3.4568 | 72 | 2.164 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Cowley Ridge 322S JCT | AB_322S_JCT | Cowley Ridge 322S | AB_322S_DSS |  |  | 289
| 514L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Pincher Creek 396S | AB_396S_DSS | Cowley Ridge 322S JCT | AB_322S_JCT |  |  | 287
| 503L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Whitecourt 268S | AB_268S_DSS | Whitecourt Power 323S | AB_323S_GSS |  |  | 282
| 1034L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 240 | 16.6898 |  |  | 931 | 1024 | 0.9 | n/a | 837.9 | 921.6 | Tilley 498S | AB_498S_DSS | Cassils 324S | AB_324S_DSS | AESO. 2018. Whitla Connection Assessment |  | 13
| 1051L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | West Brooks 28S | AB_28S_DSS | Cassils 324S | AB_324S_DSS |  |  | 29
| 1052L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | West Brooks 28S | AB_28S_DSS | Cassils 324S | AB_324S_DSS |  |  | 30
| 632L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Buford 538S | AB_538S_DSS | Leduc 325S | AB_325S_DSS |  |  | 340
| 838L | Altalink Management Ltd. | Alberta | 1 | ac | 17 | 10.4938 | 144 | 7.4436 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Devon 14S | AB_14S_DSS | Leduc 325S | AB_325S_DSS |  |  | 860
| 703BL | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 123 | 150 | 0.9 | n/a | 110.7 | 135 | HRT Express 329S JCT | AB_329S_JCT | HRT Express 329S | AB_329S_DSS | AESO. 2016. Hughenden Connection Assessment |  | 410
| 703L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 83 | 83 | 0.9 | n/a | 74.7 | 74.7 | Hardisty 377S | AB_377S_DSS | HRT Express 329S JCT | AB_329S_JCT | AESO. 2016. Hughenden Connection Assessment |  | 408
| 90L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 81 | 111 | 0.9 | n/a | 72.9 | 99.9 | Mt. Allan 115S | AB_115S_DSS | Barrier 32S | AB_32S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 940
| 58L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 105 | 120 | 0.9 | n/a | 94.5 | 108 | Seebe 245S | AB_245S_DSS | Barrier 32S | AB_32S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 314
| 1209L | Altalink Management Ltd. | Alberta | 1 | ac | 65 | 40.1235 | 500 | 25.675 |  |  | 2500 | 2500 | 0.9 | n/a | 2250 | 2250 | Ellerslie 89S | AB_89S_DSS | Genesee 330P | AB_330P_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 79
| 1238L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 500 | 4.74 |  |  | 3464 | 3464 | 0.9 | n/a | 3117.6 | 3117.6 | Sunnybrook 510S | AB_510S_DSS | Genesee 330P | AB_330P_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 81
| 1239L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 500 | 4.74 |  |  | 3464 | 3464 | 0.9 | n/a | 3117.6 | 3117.6 | Sunnybrook 510S | AB_510S_DSS | Genesee 330P | AB_330P_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 82
| 430L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sunnybrook 510S | AB_510S_DSS | Genesee 330P | AB_330P_DSS |  |  | 257
| 421L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Wolf Creek 288S | AB_288S_DSS | Ponoka 331S | AB_331S_DSS |  |  | 248
| 422L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Wolf Creek 288S | AB_288S_DSS | Ponoka 331S | AB_331S_DSS |  |  | 249
| 774L | Altalink Management Ltd. | Alberta | 1 | ac | 7.5 | 4.6296 | 144 | 3.2839 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Union Carbide Prentiss 276S | AB_276S_ISS | Ellis 332S | AB_332S_DSS |  |  | 568
| 610L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 85 | 94 | 0.9 | n/a | 76.5 | 84.6 | Taber 83S | AB_83S_DSS | Fincastle 336S | AB_336S_DSS | AESO. 2018. Whitla Connection Assessment |  | 330
| 746BL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Canada Liquid Air 337S JCT | AB_337S_JCT | Canada Liquid Air 337S | AB_337S_ISS |  |  | 520
| 746L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Fiberglass 524S JCT | AB_524S_JCT | Canada Liquid Air 337S JCT | AB_337S_JCT |  |  | 518
| 1046L | Altalink Management Ltd. | Alberta | 1 | ac | 65 | 40.1235 | 240 | 30.9954 |  |  | 337 | 404 | 0.9 | n/a | 303.3 | 363.6 | Sundance 310P | AB_310P_GSS | Cherhill 338S | AB_338S_DSS | AESO. 2017. Heartland Connection Assessment |  | 25
| 831L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 144 | 4.5975 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Cutting Lake 227S JCT | AB_227S_JCT | Duchess 339S | AB_339S_DSS |  |  | 849
| 113L | Altalink Management Ltd. | Alberta | 1 | ac | 52.5 | 32.4074 | 138 | 22.7625 |  |  | 120 | 120 | 0.9 | n/a | 108 | 108 | Ghost 20S | AB_20S_GSS | Spray 33S | AB_33S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 71
| 76L | Altalink Management Ltd. | Alberta | 1 | ac | 28 | 17.284 | 138 | 12.14 |  |  | 113 | 120 | 0.9 | n/a | 101.7 | 108 | Mt. Allan 115S | AB_115S_DSS | Spray 33S | AB_33S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 564
| 84L | Altalink Management Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 138 | 5.463 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | Rundle 35S | AB_35S_GSS | Spray 33S | AB_33S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 870
| 871L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 144 | 7.6625 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | AMOCO Empress 163S | AB_163S_ISS | Sand Hills Sub 341S | AB_341S_DSS |  |  | 899
| 708AL | Altalink Management Ltd. | Alberta | 1 | ac | 1.68 | 1.037 | 144 | 0.7356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Riverside 388S | AB_388S_DSS | Granite 342S | AB_342S_DSS |  |  | 420
| 508L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 72 | 13.525 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Stirling 67S | AB_67S_GSS | Warner 344S | AB_344S_DSS |  |  | 284
| 864AL | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 99 | 133 | 0.9 | n/a | 89.1 | 119.7 | Kaybob 346S JCT | AB_346S_JCT | Kaybob 346S | AB_346S_GSS | AESO. 2016. Fox Creek Connection Assessment |  | 894
| 864L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  | 86 | 91 | 0.9 | n/a | 77.4 | 81.9 | Benbow 397S | AB_397S_DSS | Kaybob 346S JCT | AB_346S_JCT | AESO. 2016. Fox Creek Connection Assessment |  | 891
| 720L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  | 129 | 157 | 0.9 | n/a | 116.1 | 141.3 | Benbow 397S | AB_397S_DSS | Fox Creek Altalink 347S | AB_347S_DSS | AESO. 2020. Cascade Connection Assessment |  | 438
| 7L199 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  | 109.2 | 138.9 | 0.9 | n/a | 98.28 | 125.01 | Fox Creek 741S | AB_741S_DSS | Fox Creek Altalink 347S | AB_347S_DSS | AESO. 2016. Fox Creek Connection Assessment |  | 685
| 854AL | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Marlboro 348S JCT | AB_348S_JCT | Marlboro 348S | AB_348S_DSS |  |  | 878
| 854L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 138 | 4.3357 |  |  | 263 | 263 | 0.9 | n/a | 236.7 | 236.7 | Bickerdike 39S | AB_39S_DSS | Marlboro 348S JCT | AB_348S_JCT | AESO. 2020. Cascade Connection Assessment |  | 876
| 197L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 144 | 6.13 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | East Stavely 928S | AB_928S_DSS | Stavely 349S | AB_349S_DSS |  |  | 133
| 123L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 69 | 6.9171 |  |  | 24 | 24 | 0.9 | n/a | 21.6 | 21.6 | Wabamun 19S | AB_19S_DSS | Onoway 352S | AB_352S_DSS | AESO. 2016. Gainford Connection Assessment |  | 83
| 728L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 138 | 13.0071 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | Lac La Biche 157S | AB_157S_DSS | Plamondon 353S | AB_353S_DSS | AESO. 2018. Kirby Connection Assessment |  | 455
| 624L | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 144 | 3.065 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Fidler 312S | AB_312S_DSS | Summerview 354S | AB_354S_GSS |  |  | 338
| 864BL | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 99 | 133 | 0.9 | n/a | 89.1 | 119.7 | Chevron Knight 355S JCT | AB_355S_JCT | Chevron Knight 355S | AB_355S_ISS | AESO. 2016. Fox Creek Connection Assessment |  | 895
| 864L | Altalink Management Ltd. | Alberta | 1 | ac | 8 | 4.9383 | 144 | 3.5029 |  |  | 99 | 133 | 0.9 | n/a | 89.1 | 119.7 | Kaybob 346S JCT | AB_346S_JCT | Chevron Knight 355S JCT | AB_355S_JCT | AESO. 2016. Fox Creek Connection Assessment |  | 892
| 935L | Altalink Management Ltd. | Alberta | 1 | ac | 60 | 37.037 | 240 | 28.6111 |  |  | 547 | 676 | 0.9 | n/a | 492.3 | 608.4 | Cassils 324S | AB_324S_DSS | Milo 356S | AB_356S_DSS | AESO. 2019. Travers Connection Assessment |  | 970
| 1005L | Altalink Management Ltd. | Alberta | 1 | ac | 84 | 51.8519 | 240 | 40.0556 |  |  | 481 | 581 | 0.9 | n/a | 432.9 | 522.9 | Picture Butte 120S | AB_120S_DSS | Milo 356S | AB_356S_DSS | AESO. 2019. Claresholm Connection Assessment |  | 9
| 1036L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 240 | 16.6898 |  |  | 481 | 581 | 0.9 | n/a | 432.9 | 522.9 | Travers 554S | AB_554S_DSS | Milo 356S | AB_356S_DSS | AESO. 2019. Claresholm Connection Assessment |  | 15
| 801L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Elk River 445S JCT | AB_445S_JCT | Brazeau 358S | AB_358S_DSS |  |  | 816
| 202AL | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 144 | 3.1526 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | West Pembina 359S JCT | AB_359S_JCT | West Pembina 359S | AB_359S_DSS |  |  | 148
| 202L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | Cynthia 178S | AB_178S_DSS | West Pembina 359S JCT | AB_359S_JCT | AESO. 2020. Cascade Connection Assessment |  | 145
| 85L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 96 | 96 | 0.9 | n/a | 86.4 | 86.4 | Rundle 35S JCT | AB_35S_JCT | Rundle 35S | AB_35S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 884
| 54L | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 138 | 3.035 |  |  | 153 | 189 | 0.9 | n/a | 137.7 | 170.1 | Canmore 118S | AB_118S_DSS | Rundle 35S JCT | AB_35S_JCT | AESO. 2018. Mount Allan Connection Assessment |  | 304
| 797L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Whitecourt 268S | AB_268S_DSS | Whitecourt Industrial 364S | AB_364S_ISS |  |  | 597
| 446L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Acheson 305S | AB_305S_DSS | Harry Smith 367S | AB_367S_DSS |  |  | 264
| 453L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Acheson 305S | AB_305S_DSS | Harry Smith 367S | AB_367S_DSS |  |  | 266
| 1043L | Altalink Management Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 240 | 21.4583 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Keephills 320P | AB_320P_GSS | Harry Smith 367S | AB_367S_DSS |  |  | 22
| 1139L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Petrolia 816S | AB_816S_DSS | Harry Smith 367S | AB_367S_DSS |  |  | 70
| 612L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 138 | 16.6925 |  |  | 85 | 94 | 0.9 | n/a | 76.5 | 84.6 | Fincastle 336S | AB_336S_DSS | Burdett 368S | AB_368S_GSS | AESO. 2018. Whitla Connection Assessment |  | 332
| 90L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 144 | 4.5975 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mt. Allan 115S | AB_115S_DSS | Three Sisters 36S | AB_36S_GSS |  | Line connection assumed | 941
| 172L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Chinook 181S | AB_181S_DSS | North Lethbridge 370S | AB_370S_DSS | AESO. 2019. Travers Connection Assessment |  | 118
| 667L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 174 | 215 | 0.9 | n/a | 156.6 | 193.5 | Macdonald 146S | AB_146S_DSS | North Lethbridge 370S | AB_370S_DSS | AESO. 2019. Travers Connection Assessment |  | 350
| 940L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  | 481 | 499 | 0.9 | n/a | 432.9 | 449.1 | Picture Butte 120S | AB_120S_DSS | North Lethbridge 370S | AB_370S_DSS | AESO. 2019. Travers Connection Assessment |  | 973
| 1041L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 240 | 18.3588 |  |  | 481 | 499 | 0.9 | n/a | 432.9 | 449.1 | Travers 554S | AB_554S_DSS | North Lethbridge 370S | AB_370S_DSS | AESO. 2019. Travers Connection Assessment |  | 20
| 967L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 240 | 18.3588 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Windy Flats 138S | AB_138S_DSS | North Lethbridge 370S | AB_370S_DSS | AESO. 2019. Travers Connection Assessment |  | 989
| 968L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 240 | 18.3588 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Windy Flats 138S | AB_138S_DSS | North Lethbridge 370S | AB_370S_DSS | AESO. 2019. Travers Connection Assessment |  | 990
| 189L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Madden 373S JCT | AB_373S_JCT | Madden 373S | AB_373S_DSS |  |  | 131
| 418L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Johnson 281S | AB_281S_DSS | Madden 373S JCT | AB_373S_JCT |  |  | 244
| 72CH11 | EPCOR | Alberta | 1 | ac | 8.625 | 5.3241 | 72 | 3.3329 |  |  | 40 | 40 | 0.9 | n/a | 36 | 36 | Clover Bar 987S | AB_987S_GSS | Hardisty 377S | AB_377S_DSS | AESO. 2019. EPCOR Connection Assessment |  | 461
| 72CH9 | EPCOR | Alberta | 1 | ac | 8.625 | 5.3241 | 72 | 3.3329 |  |  | 40 | 40 | 0.9 | n/a | 36 | 36 | Clover Bar 987S | AB_987S_GSS | Hardisty 377S | AB_377S_DSS | AESO. 2019. EPCOR Connection Assessment |  | 462
| 72LH8 | EPCOR | Alberta | 1 | ac | 3.45 | 2.1296 | 72 | 1.3332 |  |  | 90 | 124 | 0.9 | n/a | 81 | 111.6 | Lambton E803S | AB_E803S_DSS | Hardisty 377S | AB_377S_DSS | AESO. 2019. EPCOR Connection Assessment |  | 468
| 848L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Schrader Creek 531S JCT | AB_531S_JCT | Caroline 378S | AB_378S_GSS |  |  | 868
| 719L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sundre 575S | AB_575S_DSS | Caroline 378S | AB_378S_GSS |  |  | 431
| 185L | Altalink Management Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 69 | 21.1357 |  |  | 41 | 53 | 0.9 | n/a | 36.9 | 47.7 | Pincher Creek 396S | AB_396S_DSS | Waterton 379S | AB_379S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 128
| 726L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 138 | 10.8393 |  |  | 169 | 191 | 0.9 | n/a | 152.1 | 171.9 | Lamoureux 71S | AB_71S_DSS | North Calder 37S | AB_37S_DSS | AESO. 2018. Strathcona CG Connection Assessment |  | 451
| 898L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Viscount 92S | AB_92S_DSS | North Calder 37S | AB_37S_DSS | AESO. 2017. Heartland Connection Assessment |  | 921
| 920L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 240 | 5.7222 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Castle Downs 557S | AB_557S_DSS | North Calder 37S | AB_37S_DSS |  |  | 955
| 747L | Altalink Management Ltd. | Alberta | 1 | ac | 4.8 | 2.963 | 144 | 2.1017 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Inland Cement JCT | AB_XINL_JCT | North Calder 37S | AB_37S_DSS |  |  | 522
| 930L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 240 | 8.5833 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Poundmaker | AB_XPOU_DSS | North Calder 37S | AB_37S_DSS |  |  | 965
| 616AL | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 144 | 3.065 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Kettle's Hill 383S JCT | AB_383S_JCT | Kettle's Hill 383S | AB_383S_GSS |  |  | 337
| 616L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Goose Lake 103S | AB_103S_DSS | Kettle's Hill 383S JCT | AB_383S_JCT | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 335
| 834L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 158 | 191 | 0.9 | n/a | 142.2 | 171.9 | Keephills 320P | AB_320P_GSS | Keystone 384S | AB_384S_DSS | AESO. 2016. Gainford Connection Assessment |  | 854
| 225L | Altalink Management Ltd. | Alberta | 1 | ac | 28 | 17.284 | 69 | 10.76 |  |  | 22 | 28.6 | 0.9 | n/a | 19.8 | 25.74 | Glenwood 229S | AB_229S_DSS | Spring Coulee 385S | AB_385S_GSS | AESO. 2019. Mclaughlin Connection Assessment |  | 155
| 708AL | Altalink Management Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 144 | 7.356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Riverside 388S JCT | AB_388S_JCT | Riverside 388S | AB_388S_DSS |  |  | 419
| 708L | Altalink Management Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 138 | 17.3429 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Lamoureux 71S | AB_71S_DSS | Riverside 388S JCT | AB_388S_JCT | AESO. 2017. Heartland Connection Assessment |  | 417
| 915L | Altalink Management Ltd. | Alberta | 1 | ac | 8.05 | 4.9691 | 240 | 3.8387 |  |  | 492 | 499 | 0.9 | n/a | 442.8 | 449.1 | Clover Bar 987S | AB_987S_GSS | East Edmonton 38S | AB_38S_DSS | AESO. 2020. Summerside Connection Assessment |  | 949
| 908L | Altalink Management Ltd. | Alberta | 1 | ac | 2.875 | 1.7747 | 240 | 1.3709 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | East Industrial E52S JCT | AB_E52S_JCT | East Edmonton 38S | AB_38S_DSS | AESO. 2020. Summerside Connection Assessment |  | 936
| 761L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 138 | 13.0071 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | Lamoureux 71S | AB_71S_DSS | East Edmonton 38S | AB_38S_DSS | AESO. 2017. Heartland Connection Assessment |  | 549
| 1059L | Altalink Management Ltd. | Alberta | 1 | ac | 2.875 | 1.7747 | 240 | 1.3709 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | East Industrial E52S JCT | AB_E52S_JCT | East Edmonton 38S | AB_38S_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 38
| 738L | Altalink Management Ltd. | Alberta | 1 | ac | 6.325 | 3.9043 | 138 | 2.7423 |  |  | 111 | 141 | 0.9 | n/a | 99.9 | 126.9 | AT Plastic 4RS JCT | AB_4RS_JCT | East Edmonton 38S | AB_38S_DSS | AESO. 2016. Henday Connection Assessment |  | 496
| 946L | Altalink Management Ltd. | Alberta | 1 | ac | 16.1 | 9.9383 | 240 | 7.6773 |  |  | 494 | 499 | 0.9 | n/a | 444.6 | 449.1 | Ellerslie 89S | AB_89S_DSS | East Edmonton 38S | AB_38S_DSS | AESO. 2015. Broadmoor Connection Assessment |  | 978
| 162.81L | ENMAX Power Corporation | Alberta | 1 | ac | 4.25 | 2.6235 | 138 | 1.8427 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | Beddington 162S | AB_162S_DSS | Turbo Balzac 391S | AB_391S_DSS | AESO. 2018. East Crossfield Connection Assessment |  | 110
| 611L | Altalink Management Ltd. | Alberta | 1 | ac | 11.9 | 7.3457 | 138 | 5.1595 |  |  | 119 | 147 | 0.9 | n/a | 107.1 | 132.3 | Dry Creek 186S | AB_186S_DSS | Turbo Balzac 391S | AB_391S_DSS | AESO. 2018. East Crossfield Connection Assessment |  | 331
| 812L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Hartell 512S JCT | AB_512S_JCT | Black Diamond 392S | AB_392S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 830
| 158L | Altalink Management Ltd. | Alberta | 1 | ac | 11.9 | 7.3457 | 69 | 4.573 |  |  | 16 | 20 | 0.9 | n/a | 14.4 | 18 | High River 65S | AB_65S_DSS | Black Diamond 392S | AB_392S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 105
| 668L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 121 | 133 | 0.9 | n/a | 108.9 | 119.7 | Cypress 562S | AB_562S_DSS | Empress 394S | AB_394S_DSS | AESO. 2018. Whitla Connection Assessment |  | 351
| 174L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 138 | 13.0071 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Bardo 197S | AB_197S_DSS | North Holden 395S | AB_395S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 125
| 7L77 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 96 | 96 | 0.9 | n/a | 86.4 | 86.4 | Vegreville 709S | AB_709S_DSS | North Holden 395S | AB_395S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 784
| 412L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Russell 632S | AB_632S_DSS | Pincher Creek 396S | AB_396S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 242
| 740L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 112 | 135 | 0.9 | n/a | 100.8 | 121.5 | Edson 58S | AB_58S_GSS | Bickerdike 39S | AB_39S_DSS | AESO. 2020. Cascade Connection Assessment |  | 501
| 973L | Altalink Management Ltd. | Alberta | 1 | ac | 150 | 92.5926 | 240 | 71.5278 |  |  | 333 | 333 | 0.9 | n/a | 299.7 | 299.7 | Sundance 310P | AB_310P_GSS | Bickerdike 39S | AB_39S_DSS | AESO. 2018. Vista Connection Assessment |  | 992
| 974L | Altalink Management Ltd. | Alberta | 1 | ac | 150 | 92.5926 | 240 | 71.5278 |  |  | 333 | 333 | 0.9 | n/a | 299.7 | 299.7 | Sundance 310P | AB_310P_GSS | Bickerdike 39S | AB_39S_DSS | AESO. 2018. Vista Connection Assessment |  | 993
| 56L | Altalink Management Ltd. | Alberta | 1 | ac | 5.6 | 3.4568 | 144 | 2.452 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Seebe 245S | AB_245S_DSS | Horseshoe 3S | AB_3S_DSS |  | Line connection assumed | 313
| 807AL | Altalink Management Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 138 | 5.463 |  |  | 175 | 217 | 0.9 | n/a | 157.5 | 195.3 | Shell AOSP 402S JCT | AB_402S_JCT | Shell AOSP 402S | AB_402S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 824
| EX1-01L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 216 | 277 | 0.9 | n/a | 194.4 | 249.3 | Scotford Upgrader 879S | AB_879S_ISS | Shell AOSP 402S | AB_402S_DSS | AESO. 2018. Strathcona CG Connection Assessment |  | 1069
| ALC03L | Air Liquide Canada Inc. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Air Liquide 408S | AB_408S_ISS | Shell AOSP 402S | AB_402S_DSS |  |  | 1066
| 807L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 138 | 4.3357 |  |  | 175 | 217 | 0.9 | n/a | 157.5 | 195.3 | Josephburg 410S | AB_410S_DSS | Shell AOSP 402S JCT | AB_402S_JCT | AESO. 2019. Abee 993S Connection Assessment |  | 822
| 600L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 121 | 149 | 0.9 | n/a | 108.9 | 134.1 | Bullshead 523S | AB_523S_DSS | Peace Butte 404S | AB_404S_DSS | AESO. 2015. Rothbauer Connection Assessment |  | 318
| 728L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 138 | 13.0071 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | Plamondon 353S | AB_353S_DSS | Waupisoo 405S | AB_405S_DSS | AESO. 2018. Kirby Connection Assessment |  | 456
| 847L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 138 | 10.8393 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Bickerdike 39S | AB_39S_DSS | Fickle Lake 406S | AB_406S_DSS | AESO. 2020. Cascade Connection Assessment |  | 864
| 856L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 229 | 275 | 0.9 | n/a | 206.1 | 247.5 | Josephburg 410S | AB_410S_DSS | Scotford 409S | AB_409S_GSS | AESO. 2019. Abee 993S Connection Assessment |  | 879
| 857L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 246 | 287 | 0.9 | n/a | 221.4 | 258.3 | Josephburg 410S | AB_410S_DSS | Scotford 409S | AB_409S_GSS | AESO. 2019. Abee 993S Connection Assessment |  | 880
| ALC02L | Air Liquide Canada Inc. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 228 | 273 | 0.9 | n/a | 205.2 | 245.7 | Scotford Upgrader 879S | AB_879S_ISS | Scotford 409S | AB_409S_GSS | AESO. 2019. Abee 993S Connection Assessment |  | 1065
| ALC01L | Air Liquide Canada Inc. | Alberta | 1 | ac | 25.2 | 15.5556 | 144 | 11.034 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Air Liquide 408S | AB_408S_ISS | Scotford 409S | AB_409S_GSS |  |  | 1064
| 729L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 98 | 131.9 | 0.9 | n/a | 88.2 | 118.71 | Truweld Grating 6500S JCT | AB_6500S_JCT | Wetaskiwin 40S | AB_40S_DSS | AESO. 2016. Cooking Lake Connection Assessment |  | 459
| 858L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 121.9 | 147 | 0.9 | n/a | 109.71 | 132.3 | Wetaskiwin 40S JCT | AB_40S_JCT | Wetaskiwin 40S | AB_40S_DSS | AESO. 2016. Cooking Lake Connection Assessment |  | 882
| 804L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Wetaskiwin 40S JCT | AB_40S_JCT | Wetaskiwin 40S | AB_40S_DSS |  |  | 820
| 858L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 138 | 10.8393 |  |  | 121.9 | 147 | 0.9 | n/a | 109.71 | 132.3 | Saunders Lake 289S | AB_289S_DSS | Wetaskiwin 40S JCT | AB_40S_JCT | AESO. 2016. Cooking Lake Connection Assessment |  | 881
| 803L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Bigstone 86S | AB_86S_DSS | Wetaskiwin 40S JCT | AB_40S_JCT |  |  | 818
| 804L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Bigstone 86S | AB_86S_DSS | Wetaskiwin 40S JCT | AB_40S_JCT |  |  | 819
| 776L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 140 | 140 | 0.9 | n/a | 126 | 126 | ALBChem Beaverhill Creek 308S | AB_308S_ISS | Josephburg 410S | AB_410S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 570
| 1120L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 240 | 16.6898 |  |  | 594 | 706 | 0.9 | n/a | 534.6 | 635.4 | Amelia 108S | AB_108S_DSS | Josephburg 410S | AB_410S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 69
| 997L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Lamoureux 71S | AB_71S_DSS | Josephburg 410S | AB_410S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 1001
| 861L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Lamoureux 71S | AB_71S_DSS | Josephburg 410S | AB_410S_DSS |  |  | 887
| 745AL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Dalehurst 975S JCT | AB_975S_JCT | Mountain Coalbed 411S | AB_411S_DSS |  |  | 516
| 745L | Altalink Management Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 138 | 10.4057 |  |  | 172 | 212 | 0.9 | n/a | 154.8 | 190.8 | Bickerdike 39S | AB_39S_DSS | Mountain Coalbed 411S JCT | AB_411S_JCT | AESO. 2020. Cascade Connection Assessment |  | 513
| 719CL | Altalink Management Ltd. | Alberta | 1 | ac | 10.8 | 6.6667 | 144 | 4.7289 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sundre 575S | AB_575S_DSS | Eagle Creek 412S | AB_412S_DSS |  |  | 437
| 740AL | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 119 | 147 | 0.9 | n/a | 107.1 | 132.3 | Gulf Robb 414S JCT | AB_414S_JCT | Gulf Robb 414S | AB_414S_DSS | AESO. 2020. Cascade Connection Assessment |  | 505
| 740L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 99 | 133 | 0.9 | n/a | 89.1 | 119.7 | Bickerdike 39S | AB_39S_DSS | Gulf Robb 414S JCT | AB_414S_JCT | AESO. 2020. Cascade Connection Assessment |  | 502
| 164L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 111 | 144.3 | 0.9 | n/a | 99.9 | 129.87 | Goose Lake 103S | AB_103S_DSS | Drywood 415S | AB_415S_DSS | AESO. 2019. Drywood Connection Assessment |  | 112
| 185L | Altalink Management Ltd. | Alberta | 1 | ac | 28 | 17.284 | 69 | 10.76 |  |  | 57 | 69 | 0.9 | n/a | 51.3 | 62.1 | Waterton 379S | AB_379S_DSS | Drywood 415S | AB_415S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 129
| 608L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 144 | 16.8575 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Blue Trail 528S JCT | AB_528S_JCT | Ardenville Wind Farm 418S | AB_418S_GSS |  |  | 328
| 765L | Altalink Management Ltd. | Alberta | 1 | ac | 4.25 | 2.6235 | 138 | 1.8427 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Strathmore 151S | AB_151S_GSS | Chestermere 419S | AB_419S_DSS | AESO. 2016. Turbo Connection Assessment |  | 556
| 691L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Janet 74S | AB_74S_DSS | Chestermere 419S | AB_419S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 367
| 880L | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 138 | 3.035 |  |  | 123 | 135 | 0.9 | n/a | 110.7 | 121.5 | Al Rothbauer 321S | AB_321S_DSS | Medicine Hat 41S | AB_41S_GSS | AESO. 2018. Whitla Connection Assessment | Line connection assumed | 905
| 731L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Fiberglass 524S JCT | AB_524S_JCT | Broadmoor 420S | AB_420S_DSS | AESO. 2016. Henday Connection Assessment |  | 484
| 821L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 138 | 10.8393 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Vauxhall 158S | AB_158S_DSS | Hays 421S | AB_421S_GSS | AESO. 2018. Fincastle Connection Assessment |  | 838
| 795L | Altalink Management Ltd. | Alberta | 1 | ac | 60 | 37.037 | 138 | 26.0143 |  |  | 96 | 124.8 | 0.9 | n/a | 86.4 | 112.32 | Brooks 121S | AB_121S_GSS | Hays 421S | AB_421S_GSS | AESO. 2016. Bullshead Connection Assessment |  | 593
| 694L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Fort Sask. 54S | AB_54S_DSS | Westwood 422S | AB_422S_DSS | AESO. 2017. Heartland Connection Assessment |  | 369
| 700L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Sherwood Park 746S | AB_746S_DSS | Westwood 422S | AB_422S_DSS | AESO. 2016. Henday Connection Assessment |  | 403
| 740L | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 138 | 3.1217 |  |  | 119 | 147 | 0.9 | n/a | 107.1 | 132.3 | Coal Valley 527S JCT | AB_527S_JCT | Coalspur 426S | AB_426S_DSS | AESO. 2020. Cascade Connection Assessment |  | 504
| 501L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 72 | 4.6371 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Cadomin 983S JCT | AB_983S_JCT | Coalspur 426S | AB_426S_DSS |  |  | 280
| 733L | Altalink Management Ltd. | Alberta | 1 | ac | 3.4 | 2.0988 | 138 | 1.4741 |  |  | 120 | 143 | 0.9 | n/a | 108 | 128.7 | Strathmore 151S | AB_151S_GSS | Namaka 428S | AB_428S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 489
| 883L | Altalink Management Ltd. | Alberta | 1 | ac | 33 | 20.3704 | 144 | 14.4493 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Wolf Creek 288S | AB_288S_DSS | Nelson Lake 429S | AB_429S_DSS |  |  | 906
| 916L | Altalink Management Ltd. | Alberta | 1 | ac | 22.1 | 13.642 | 240 | 10.5384 |  |  | 408 | 494 | 0.9 | n/a | 367.2 | 444.6 | East Calgary 5S | AB_5S_DSS | Sarcee 42S | AB_42S_DSS | AESO. 2017. SS 7 Connection Assessment |  | 950
| 28.80L | ENMAX Power Corporation | Alberta | 1 | ac | 3.06 | 1.8889 | 138 | 1.3267 |  |  | 273 | 273 | 0.9 | n/a | 245.7 | 245.7 | SS-28 | AB_SS28_DSS | Sarcee 42S | AB_42S_DSS | AESO. 2017. SS 7 Connection Assessment |  | 171
| 7.82L | ENMAX Power Corporation | Alberta | 1 | ac | 6.8 | 4.1975 | 138 | 2.9483 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-7 | AB_SS07_DSS | Sarcee 42S | AB_42S_DSS | AESO. 2017. SS 7 Connection Assessment |  | 401
| 906L | Altalink Management Ltd. | Alberta | 1 | ac | 180 | 111.1111 | 240 | 85.8333 |  |  |  |  | 0.9 | 1.8975 | 277.4055 | 301.0958 | Benalto 17S | AB_17S_DSS | Sarcee 42S | AB_42S_DSS |  |  | 932
| 928L | Altalink Management Ltd. | Alberta | 1 | ac | 180 | 111.1111 | 240 | 85.8333 |  |  |  |  | 0.9 | 1.8975 | 277.4055 | 301.0958 | Benalto 17S | AB_17S_DSS | Sarcee 42S | AB_42S_DSS |  |  | 963
| 886L | Altalink Management Ltd. | Alberta | 1 | ac | 49 | 30.2469 | 138 | 21.245 |  |  | 119 | 147 | 0.9 | n/a | 107.1 | 132.3 | Namaka 428S | AB_428S_DSS | Hussar 431S | AB_431S_DSS | AESO. 2016. Turbo Connection Assessment |  | 908
| 790L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Bilby 105S JCT | AB_105S_JCT | Carvel 432S | AB_432S_DSS | AESO. 2016. Gainford Connection Assessment |  | 587
| 896L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 121 | 149 | 0.9 | n/a | 108.9 | 134.1 | Wabamun 19S | AB_19S_DSS | Carvel 432S | AB_432S_DSS | AESO. 2016. Gainford Connection Assessment |  | 919
| 452L | Altalink Management Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 144 | 10.5086 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Harry Smith 367S | AB_367S_DSS | Stony Plain 434S | AB_434S_DSS |  |  | 265
| 853AL | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 144 | 7.6625 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Bassano 435S JCT | AB_435S_JCT | Bassano 435S | AB_435S_DSS |  |  | 875
| 853L | Altalink Management Ltd. | Alberta | 1 | ac | 56 | 34.5679 | 138 | 24.28 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Queenstown 504S | AB_504S_DSS | Bassano 435S JCT | AB_435S_JCT | AESO. 2019. Travers Connection Assessment |  | 873
| 754L | Altalink Management Ltd. | Alberta | 1 | ac | 5.6 | 3.4568 | 138 | 2.428 |  |  | 153 | 189 | 0.9 | n/a | 137.7 | 170.1 | Exshaw 985S JCT | AB_985S_JCT | Baymag 437S | AB_437S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 536
| 723L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 86 | 91 | 0.9 | n/a | 77.4 | 81.9 | Flatbush 500S JCT | AB_500S_JCT | Westlock 438S | AB_438S_GSS | AESO. 2016. Plamondon Connection Assessment |  | 441
| 708AL | Altalink Management Ltd. | Alberta | 1 | ac | 1.68 | 1.037 | 144 | 0.7356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Scoria 318S | AB_318S_DSS | Opal 439S | AB_439S_DSS |  |  | 422
| 3AL | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 138 | 3.035 |  |  | 99 | 133 | 0.9 | n/a | 89.1 | 119.7 | Jumping Pound Junction 43S JCT | AB_43S_JCT | Jumping Pound Junction 43S | AB_43S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 237
| 3L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 118 | 146 | 0.9 | n/a | 106.2 | 131.4 | Springbank 272S | AB_272S_DSS | Jumping Pound Junction 43S JCT | AB_43S_JCT | AESO. 2018. Mount Allan Connection Assessment |  | 235
| 799L | Altalink Management Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 138 | 17.3429 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Entwistle 235S | AB_235S_DSS | South Mayerthorpe 443S | AB_443S_DSS | AESO. 2016. Gainford Connection Assessment |  | 599
| 801AL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Elk River 445S JCT | AB_445S_JCT | Elk River 445S | AB_445S_DSS |  |  | 817
| 801L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Brazeau Outlet Works 294S | AB_294S_DSS | Elk River 445S JCT | AB_445S_JCT |  |  | 815
| 763AL | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 96 | 124.8 | 0.9 | n/a | 86.4 | 112.32 | Enchant 447S JCT | AB_447S_JCT | Enchant 447S | AB_447S_DSS | AESO. 2016. Bullshead Connection Assessment |  | 554
| 763L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Vauxhall 158S | AB_158S_DSS | Enchant 447S JCT | AB_447S_JCT | AESO. 2018. Fincastle Connection Assessment |  | 552
| 860L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 108 | 139 | 0.9 | n/a | 97.2 | 125.1 | Cochrane 291S | AB_291S_DSS | Bearspaw Plant 44S | AB_44S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 885
| 36.81L | ENMAX Power Corporation | Alberta | 1 | ac | 5.1 | 3.1481 | 138 | 2.2112 |  |  | 143 | 172 | 0.9 | n/a | 128.7 | 154.8 | SS-36 | AB_SS36_DSS | Bearspaw Plant 44S | AB_44S_GSS | AESO. 2017. SS 7 Connection Assessment |  | 229
| 50L | Altalink Management Ltd. | Alberta | 1 | ac | 11.05 | 6.821 | 144 | 4.8383 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | SS-21 | AB_SS21_DSS | Bearspaw Plant 44S | AB_44S_GSS |  |  | 285
| 706AL | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | B.F.Goodrich Fort Sask. 452S JCT | AB_452S_JCT | B.F.Goodrich Fort Sask. 452S | AB_452S_ISS | AESO. 2019. Abee 993S Connection Assessment |  | 415
| 706L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Josephburg 410S | AB_410S_DSS | B.F.Goodrich Fort Sask. 452S JCT | AB_452S_JCT | AESO. 2019. Abee 993S Connection Assessment |  | 413
| 835AL | Altalink Management Ltd. | Alberta | 1 | ac | 10.8 | 6.6667 | 144 | 4.7289 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Buck Lake 454S JCT | AB_454S_JCT | Buck Lake 454S | AB_454S_GSS |  |  | 857
| 835L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Keystone 384S | AB_384S_DSS | Buck Lake 454S JCT | AB_454S_JCT |  |  | 855
| 897L | Altalink Management Ltd. | Alberta | 1 | ac | 9.775 | 6.034 | 138 | 4.2382 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | East Edmonton 38S | AB_38S_DSS | Bretona 45S | AB_45S_DSS | AESO. 2016. Henday Connection Assessment |  | 920
| 844L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Brazeau 358S | AB_358S_DSS | West Pembina 477S | AB_477S_GSS |  |  | 862
| 679L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 167 | 191 | 0.9 | n/a | 150.3 | 171.9 | Nilrem 574S | AB_574S_DSS | Tucuman 478S | AB_478S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 360
| 680L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 167 | 191 | 0.9 | n/a | 150.3 | 171.9 | Nilrem 574S | AB_574S_DSS | Tucuman 478S | AB_478S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 361
| 704L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 75 | 79 | 0.9 | n/a | 67.5 | 71.1 | Wainright 51S | AB_51S_DSS | Tucuman 478S | AB_478S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 411
| 681L | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 138 | 3.1217 |  |  | 143 | 172 | 0.9 | n/a | 128.7 | 154.8 | Hardisty 377S | AB_377S_DSS | Tucuman 478S | AB_478S_DSS | AESO. 2015. Vincent Connection Assessment |  | 362
| 784AL | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Haynes 482S JCT | AB_482S_JCT | Haynes 482S | AB_482S_DSS |  |  | 577
| 784L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Ellis 332S | AB_332S_DSS | Haynes 482S JCT | AB_482S_JCT |  |  | 575
| 825L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sagitawah 77S | AB_77S_DSS | Millar Western 484S | AB_484S_DSS |  |  | 842
| 1042L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 240 | 6.6759 |  |  | 488 | 606 | 0.9 | n/a | 439.2 | 545.4 | Travers 554S | AB_554S_DSS | Blackspring Ridge 485S | AB_485S_DSS | AESO. 2019. Travers Connection Assessment |  | 21
| 841L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | West Pembina 477S | AB_477S_GSS | Petro Canada Brazeau River 489S | AB_489S_ISS |  |  | 861
| 777L | Altalink Management Ltd. | Alberta | 1 | ac | 56 | 34.5679 | 138 | 24.28 |  |  | 96 | 115 | 0.9 | n/a | 86.4 | 103.5 | Seebe 245S | AB_245S_DSS | Pocaterra 48S | AB_48S_GSS | AESO. 2018. Mount Allan Connection Assessment |  | 571
| 1201L | Altalink Management Ltd. | Alberta | 1 | ac | 180 | 111.1111 | 500 | 71.1 |  |  |  |  | 0.9 | 1.8975 | 1612.901 | 2039.8454 | Bennett 520S | AB_520S_DSS | Chapel Rock 491S | AB_491S_DSS |  |  | 74
| 463AL | Altalink Management Ltd. | Alberta | 1 | ac | 3.5 | 2.1605 | 144 | 1.5325 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Monarch 492S JCT | AB_492S_JCT | Monarch 492S | AB_492S_DSS |  |  | 273
| 463L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Fort Macleod 15S | AB_15S_GSS | Monarch 492S JCT | AB_492S_JCT | AESO. 2018. Vulcan and Stavely Connection Assessment |  | 271
| 1034L | Altalink Management Ltd. | Alberta | 1 | ac | 94.5 | 58.3333 | 240 | 45.0625 |  |  | 931 | 1024 | 0.9 | n/a | 837.9 | 921.6 | Bowmanton 244S | AB_244S_DSS | Tilley 498S | AB_498S_DSS | AESO. 2018. Whitla Connection Assessment |  | 12
| 666L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 138 | 15.175 |  |  | 98 | 108 | 0.9 | n/a | 88.2 | 97.2 | West Brooks 28S | AB_28S_DSS | Tilley 498S | AB_498S_DSS | AESO. 2018. Whitla Connection Assessment |  | 349
| 777L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 144 | 4.5975 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Pocaterra 48S | AB_48S_GSS | Interlakes 49S | AB_49S_GSS |  | Line connection assumed | 572
| 738AL | Altalink Management Ltd. | Alberta | 1 | ac | 2.875 | 1.7747 | 144 | 1.2588 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | AT Plastic 4RS JCT | AB_4RS_JCT | AT Plastic 4RS | AB_4RS_ISS |  |  | 497
| 738L | Altalink Management Ltd. | Alberta | 1 | ac | 2.875 | 1.7747 | 138 | 1.2465 |  |  | 111 | 141 | 0.9 | n/a | 99.9 | 126.9 | Imperial Oil Edmonton 95S | AB_95S_ISS | AT Plastic 4RS JCT | AB_4RS_JCT | AESO. 2016. Henday Connection Assessment |  | 495
| 724L | Altalink Management Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 144 | 18.39 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Wap 1S JCT | AB_1S_JCT | Flatbush 500S | AB_500S_DSS |  |  | 444
| 723L | Altalink Management Ltd. | Alberta | 1 | ac | 65 | 40.1235 | 138 | 28.1821 |  |  | 86 | 91 | 0.9 | n/a | 77.4 | 81.9 | North Barrhead 69S | AB_69S_DSS | Flatbush 500S JCT | AB_500S_JCT | AESO. 2016. Gainford Connection Assessment |  | 440
| 591L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 72 | 5.41 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Waterton 379S | AB_379S_DSS | Shell Waterton 502S | AB_502S_ISS |  |  | 315
| 161L | Altalink Management Ltd. | Alberta | 1 | ac | 50 | 30.8642 | 138 | 21.6786 |  |  | 117 | 120 | 0.9 | n/a | 105.3 | 108 | Vulcan 255S | AB_255S_DSS | Queenstown 504S | AB_504S_DSS | AESO. 2019. Travers Connection Assessment |  | 109
| 7L696 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Ribstone Creek 892S | AB_892S_DSS | Lakesend 508S | AB_508S_DSS |  |  | 767
| 1325L | Altalink Management Ltd. | Alberta | 1 | ac | 300 | 185.1852 | 500 | 118.5 |  |  |  |  | 0.9 | 1.3548 | 1151.5915 | 1456.4246 | Sunnybrook 510S | AB_510S_DSS | Crossings 511S | AB_511S_DSS |  |  | 91
| 812AL | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 144 | 3.065 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Hartell 512S JCT | AB_512S_JCT | Hartell 512S | AB_512S_DSS |  |  | 831
| 812L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 48 | 48 | 0.9 | n/a | 43.2 | 43.2 | High River 65S | AB_65S_DSS | Hartell 512S JCT | AB_512S_JCT | AESO. 2016. Okotoks Connection Assessment |  | 829
| 514L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 72 | 8.115 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Cowley Ridge 322S JCT | AB_322S_JCT | Lundbreck 513S | AB_513S_DSS |  |  | 288
| 6L126 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Sarah Lake 743S | AB_743S_DSS | Fedpipe Judy Creek 515S | AB_515S_ISS |  |  | 387
| 780L | Altalink Management Ltd. | Alberta | 1 | ac | 12.65 | 7.8086 | 138 | 5.4847 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | East Edmonton 38S | AB_38S_DSS | Cooking Lake 522S | AB_522S_DSS | AESO. 2020. Summerside Connection Assessment |  | 573
| 174L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 138 | 15.175 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Saunders Lake 289S | AB_289S_DSS | Cooking Lake 522S | AB_522S_DSS | AESO. 2020. Summerside Connection Assessment |  | 123
| 874L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 85.1 | 90.1 | 0.9 | n/a | 76.59 | 81.09 | Bretona 45S | AB_45S_DSS | Cooking Lake 522S | AB_522S_DSS | AESO. 2016. Cooking Lake Connection Assessment |  | 900
| 746AL | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 144 | 3.1526 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Canada Liquid Air 337S JCT | AB_337S_JCT | Fiberglass 524S | AB_524S_DSS |  |  | 519
| 731L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 138 | 2.6014 |  |  | 172 | 212 | 0.9 | n/a | 154.8 | 190.8 | East Edmonton 38S | AB_38S_DSS | Fiberglass 524S JCT | AB_524S_JCT | AESO. 2016. Henday Connection Assessment |  | 485
| 7L129 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Bauer 918S JCT | AB_918S_JCT | Buffalo Creek 526S | AB_526S_DSS | AESO. 2017. Paintearth Connection Assessment |  | 640
| 7L50 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Jarrow 252S JCT | AB_252S_JCT | Buffalo Creek 526S | AB_526S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 731
| 743L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Coal Valley 527S JCT | AB_527S_JCT | Coal Valley 527S | AB_527S_DSS |  |  | 508
| 740L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 99 | 133 | 0.9 | n/a | 89.1 | 119.7 | Gulf Robb 414S JCT | AB_414S_JCT | Coal Valley 527S JCT | AB_527S_JCT | AESO. 2020. Cascade Connection Assessment |  | 503
| 608AL | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 144 | 4.5975 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Blue Trail 528S JCT | AB_528S_JCT | Blue Trail 528S | AB_528S_DSS |  |  | 329
| 608L | Altalink Management Ltd. | Alberta | 1 | ac | 8.4 | 5.1852 | 144 | 3.678 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Windy Flats 138S | AB_138S_DSS | Blue Trail 528S JCT | AB_528S_JCT |  |  | 327
| 848AL | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 144 | 3.1526 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Schrader Creek 531S JCT | AB_531S_JCT | Schrader Creek 531S | AB_531S_DSS |  |  | 869
| 848L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 144 | 15.325 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Benalto 17S | AB_17S_DSS | Schrader Creek 531S JCT | AB_531S_JCT |  |  | 867
| 758L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Eckville 534S JCT | AB_534S_JCT | Eckville 534S | AB_534S_DSS |  |  | 543
| 757L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Rimbey 297S | AB_297S_DSS | Eckville 534S JCT | AB_534S_JCT |  |  | 541
| 784L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 144 | 7.6625 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Haynes 482S JCT | AB_482S_JCT | Joffre 535S | AB_535S_GSS |  |  | 576
| 889L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Joffre 535S | AB_535S_GSS | Brookfield 536S | AB_536S_DSS |  |  | 911
| 729L | Altalink Management Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 138 | 10.4057 |  |  | 85.1 | 90.1 | 0.9 | n/a | 76.59 | 81.09 | East Camrose 285S | AB_285S_GSS | Ervick 542S | AB_542S_DSS | AESO. 2016. Cooking Lake Connection Assessment |  | 457
| 715L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | Hansman Lake 650S | AB_650S_DSS | Provost 545S | AB_545S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 427
| 706L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 138 | 2.1679 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | B.F.Goodrich Fort Sask. 452S JCT | AB_452S_JCT | Fort Sask. 54S | AB_54S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 414
| 864L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  | 99 | 133 | 0.9 | n/a | 89.1 | 119.7 | Chevron Knight 355S JCT | AB_355S_JCT | Chevron Kaybob 551S | AB_551S_ISS | AESO. 2016. Fox Creek Connection Assessment |  | 893
| 240CV5 | EPCOR | Alberta | 1 | ac | 3.45 | 2.1296 | 240 | 1.6451 |  |  | 475 | 503 | 0.9 | n/a | 427.5 | 452.7 | Blatchford | AB_XBLA_DSS | Castle Downs 557S | AB_557S_DSS | AESO. 2020. Summerside Connection Assessment |  | 168
| 920L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 240 | 9.537 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Lamoureux 71S | AB_71S_DSS | Castle Downs 557S | AB_557S_DSS |  |  | 954
| 402L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Monitor 774S | AB_774S_DSS | Eyre 558S | AB_558S_DSS |  |  | 239
| 658L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 138 | 16.6925 |  |  | 81 | 89 | 0.9 | n/a | 72.9 | 80.1 | Chappice Lake 649S | AB_649S_DSS | Cypress 562S | AB_562S_DSS | AESO. 2018. Whitla Connection Assessment |  | 348
| 945L | Altalink Management Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 240 | 33.3796 |  |  | 550 | 679 | 0.9 | n/a | 495 | 611.1 | Jenner 275S | AB_275S_GSS | Cypress 562S | AB_562S_DSS | AESO. 2016. Jenner Connection Assessment |  | 977
| 1011L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 240 | 16.6898 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | AMOCO Empress 163S | AB_163S_ISS | Cypress 562S | AB_562S_DSS |  |  | 11
| 710L | Altalink Management Ltd. | Alberta | 1 | ac | 37.8 | 23.3333 | 138 | 16.389 |  |  | 86 | 91 | 0.9 | n/a | 77.4 | 81.9 | Colinton 159S | AB_159S_DSS | Boyle 56S | AB_56S_DSS | AESO. 2016. Plamondon Connection Assessment |  | 424
| 633L | Altalink Management Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 138 | 12.747 |  |  | 86 | 91 | 0.9 | n/a | 77.4 | 81.9 | Waupisoo 405S | AB_405S_DSS | Boyle 56S | AB_56S_DSS | AESO. 2016. Plamondon Connection Assessment |  | 341
| 953L | Altalink Management Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 240 | 38.1481 |  |  | 520 | 663 | 0.9 | n/a | 468 | 596.7 | Cordel 755S | AB_755S_DSS | Nilrem 574S | AB_574S_DSS | AESO. 2017. Irma Connection Assessment |  | 982
| 719L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Harmattan 256S | AB_256S_GSS | Sundre 575S | AB_575S_DSS |  |  | 430
| 764L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Limestone 304S | AB_304S_DSS | Ricinus 581S | AB_581S_DSS |  |  | 555
| 719AL | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Ricinus 581S JCT | AB_581S_JCT | Ricinus 581S | AB_581S_DSS |  |  | 435
| 719L | Altalink Management Ltd. | Alberta | 1 | ac | 3 | 1.8519 | 144 | 1.3136 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Raven River 634S JCT | AB_634S_JCT | Ricinus 581S JCT | AB_581S_JCT |  |  | 433
| 671L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 172 | 212 | 0.9 | n/a | 154.8 | 190.8 | Bickerdike 39S | AB_39S_DSS | Edson 58S | AB_58S_GSS | AESO. 2020. Cascade Connection Assessment |  | 353
| 890L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 75 | 79 | 0.9 | n/a | 67.5 | 71.1 | Pinedale 207S | AB_207S_DSS | Edson 58S | AB_58S_GSS | AESO. 2020. Cascade Connection Assessment |  | 912
| 823L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 142 | 142 | 0.9 | n/a | 127.8 | 127.8 | Irrican Power 314S | AB_314S_GSS | Lakeview 593S | AB_593S_DSS | AESO. 2017. Stirling Connection Assessment |  | 840
| 823L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 142 | 142 | 0.9 | n/a | 127.8 | 127.8 | Macdonald 146S | AB_146S_DSS | Lakeview 593S | AB_593S_DSS | AESO. 2017. Stirling Connection Assessment |  | 840
| 677L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 108 | 114 | 0.9 | n/a | 97.2 | 102.6 | Acheson 305S | AB_305S_DSS | Spruce Grove 595S | AB_595S_DSS | AESO. 2017. Heartland Connection Assessment |  | 359
| 712L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 108 | 114 | 0.9 | n/a | 97.2 | 102.6 | North St. Albert 99S | AB_99S_DSS | Spruce Grove 595S | AB_595S_DSS | AESO. 2017. Heartland Connection Assessment |  | 426
| 1048L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 240 | 6.6759 |  |  | 611 | 751 | 0.9 | n/a | 549.9 | 675.9 | Windy Flats 138S | AB_138S_DSS | Peigan 59S | AB_59S_DSS | AESO. 2019. Mclaughlin Connection Assessment |  | 27
| 955L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 611 | 751 | 0.9 | n/a | 549.9 | 675.9 | Goose Lake 103S | AB_103S_DSS | Peigan 59S | AB_59S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 984
| 956L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 611 | 751 | 0.9 | n/a | 549.9 | 675.9 | Goose Lake 103S | AB_103S_DSS | Peigan 59S | AB_59S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 985
| 616L | Altalink Management Ltd. | Alberta | 1 | ac | 28 | 17.284 | 138 | 12.14 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Kettle's Hill 383S JCT | AB_383S_JCT | Peigan 59S | AB_59S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 336
| 1049L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 240 | 6.6759 |  |  | 611 | 751 | 0.9 | n/a | 549.9 | 675.9 | Windy Flats 138S | AB_138S_DSS | Peigan 59S | AB_59S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 28
| 738AL | Altalink Management Ltd. | Alberta | 1 | ac | 1.725 | 1.0648 | 144 | 0.7553 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | AT Plastic 4RS | AB_4RS_ISS | AT Plastic 5RS | AB_5RS_ISS |  |  | 498
| 833L | Altalink Management Ltd. | Alberta | 1 | ac | 0.17 | 0.10494 | 144 | 0.074436 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | SS-2 | AB_SS02_DSS | East Calgary 5S | AB_5S_DSS |  | Line connection assumed | 853
| 745L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 172 | 212 | 0.9 | n/a | 154.8 | 190.8 | Mountain Coalbed 411S JCT | AB_411S_JCT | Cold Creek 602S | AB_602S_DSS | AESO. 2020. Cascade Connection Assessment |  | 514
| 847L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Vista 1029S | AB_1029S_DSS | Cold Creek 602S | AB_602S_DSS | AESO. 2018. Vista Connection Assessment |  | 866
| 7L153 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 143 | 143 | 0.9 | n/a | 128.7 | 128.7 | Wintering Hills 804S | AB_804S_DSS | Wheatland 609S | AB_609S_GSS | AESO. 2018. Wheatland Connection Assessment |  | 664
| 824L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 167 | 201 | 0.9 | n/a | 150.3 | 180.9 | Lakeview 593S | AB_593S_DSS | Riverbend 618S | AB_618S_DSS | AESO. 2019. Travers Connection Assessment |  | 841
| 863L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Garden City 226S JCT | AB_226S_JCT | Riverbend 618S | AB_618S_DSS | AESO. 2019. Claresholm Connection Assessment |  | 890
| 725AL | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 138 | 3.035 |  |  | 120 | 148 | 0.9 | n/a | 108 | 133.2 | Riverbend 618S JCT | AB_618S_JCT | Riverbend 618S | AB_618S_DSS | AESO. 2019. Claresholm Connection Assessment |  | 449
| 725L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 122 | 150 | 0.9 | n/a | 109.8 | 135 | Bowron 674S | AB_674S_DSS | Riverbend 618S JCT | AB_618S_JCT | AESO. 2019. Travers Connection Assessment |  | 447
| 836L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Violet Grove 283S | AB_283S_DSS | Lodgepole 61S | AB_61S_DSS | AESO. 2020. Cascade Connection Assessment |  | 858
| 202L | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 138 | 3.1217 |  |  | 98 | 132 | 0.9 | n/a | 88.2 | 118.8 | West Pembina 359S JCT | AB_359S_JCT | Lodgepole 61S | AB_61S_DSS | AESO. 2020. Cascade Connection Assessment |  | 146
| 240BA2 | EPCOR | Alberta | 1 | ac | 7.2 | 4.4444 | 240 | 3.4333 |  |  | 400 | 479 | 0.9 | n/a | 360 | 431.1 | Bellamy 814S | AB_814S_DSS | Argyll 629S | AB_629S_DSS | AESO. 2020. Summerside Connection Assessment |  | 165
| 240BA3 | EPCOR | Alberta | 1 | ac | 7.2 | 4.4444 | 240 | 3.4333 |  |  | 400 | 479 | 0.9 | n/a | 360 | 431.1 | Bellamy 814S | AB_814S_DSS | Argyll 629S | AB_629S_DSS | AESO. 2020. Summerside Connection Assessment |  | 166
| 1056L | Altalink Management Ltd. | Alberta | 1 | ac | 33 | 20.3704 | 240 | 15.7361 |  |  | 419 | 517 | 0.9 | n/a | 377.1 | 465.3 | Ellerslie 89S | AB_89S_DSS | Argyll 629S | AB_629S_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 34
| 1055L | EPCOR | Alberta | 1 | ac | 36 | 22.2222 | 240 | 17.1667 |  |  | 419 | 517 | 0.9 | n/a | 377.1 | 465.3 | Petrolia 816S | AB_816S_DSS | Argyll 629S | AB_629S_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 33
| 202L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Lodgepole 61S | AB_61S_DSS | Brazeau 62S | AB_62S_GSS |  |  | 147
| 170L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Coleman 799S | AB_799S_DSS | Russell 632S | AB_632S_DSS | AESO. 2015. McLaughlin Aggregated Connection Assessment |  | 116
| 719BL | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Raven River 634S JCT | AB_634S_JCT | Raven River 634S | AB_634S_DSS |  |  | 436
| 719L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Caroline 378S | AB_378S_GSS | Raven River 634S JCT | AB_634S_JCT |  |  | 432
| 767CL | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 144 | 3.1526 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | New Rose Valley 635S JCT | AB_635S_JCT | New Rose Valley 635S | AB_635S_DSS |  |  | 561
| 767L | Altalink Management Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 138 | 18.21 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Marion 21S JCT | AB_21S_JCT | New Rose Valley 635S JCT | AB_635S_JCT | AESO. 2016. Gainford Connection Assessment |  | 558
| 526AL | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Esso Judy Creek 638S JCT | AB_638S_JCT | Esso Judy Creek 638S | AB_638S_ISS |  |  | 301
| 526L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Fedpipe Judy Creek 515S | AB_515S_ISS | Esso Judy Creek 638S JCT | AB_638S_JCT |  |  | 296
| 900L | Altalink Management Ltd. | Alberta | 1 | ac | 37.5 | 23.1481 | 240 | 17.8819 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Benalto 17S | AB_17S_DSS | Red Deer 63S | AB_63S_DSS |  |  | 925
| 901L | Altalink Management Ltd. | Alberta | 1 | ac | 110 | 67.9012 | 240 | 52.4537 |  |  |  |  | 0.9 | 2.6257 | 383.8564 | 416.6375 | East Crossfield 64S JCT | AB_64S_JCT | Red Deer 63S | AB_63S_DSS |  |  | 927
| 914L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 240 | 16.6898 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Gaetz 87S | AB_87S_DSS | Red Deer 63S | AB_63S_DSS |  |  | 948
| 925L | Altalink Management Ltd. | Alberta | 1 | ac | 154 | 95.0617 | 240 | 73.4352 |  |  |  |  | 0.9 | 2.1032 | 307.4662 | 333.7236 | Janet 74S | AB_74S_DSS | Red Deer 63S | AB_63S_DSS |  |  | 960
| 755L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Piper Creek 247S | AB_247S_DSS | Red Deer 63S | AB_63S_DSS |  |  | 539
| 426L | Altalink Management Ltd. | Alberta | 1 | ac | 7.5 | 4.6296 | 144 | 3.2839 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | South Red Deer 194S | AB_194S_DSS | Red Deer 63S | AB_63S_DSS |  |  | 255
| 648L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sylvan Lake 680S | AB_680S_DSS | Red Deer 63S | AB_63S_DSS |  |  | 347
| 1083L | Altalink Management Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 240 | 20.0278 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Wolf Creek 288S | AB_288S_DSS | Red Deer 63S | AB_63S_DSS |  |  | 49
| 472L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 121 | 150 | 0.9 | n/a | 108.9 | 135 | Sunken Lake 221S JCT | AB_221S_JCT | Metiskow 648S | AB_648S_DSS | AESO. 2018. Provost Connection Assessment |  | 275
| 901AL | Altalink Management Ltd. | Alberta | 1 | ac | 2.04 | 1.2593 | 240 | 0.97278 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | East Crossfield 64S JCT | AB_64S_JCT | East Crossfield 64S | AB_64S_DSS |  |  | 928
| 901L | Altalink Management Ltd. | Alberta | 1 | ac | 35.7 | 22.037 | 240 | 17.0236 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Janet 74S | AB_74S_DSS | East Crossfield 64S JCT | AB_64S_JCT |  |  | 926
| 729AL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Truweld Grating 6500S JCT | AB_6500S_JCT | Truweld Grating 6500S | AB_6500S_ISS |  |  | 460
| 729L | Altalink Management Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 138 | 19.5107 |  |  | 85.1 | 90.1 | 0.9 | n/a | 76.59 | 81.09 | Ervick 542S | AB_542S_DSS | Truweld Grating 6500S JCT | AB_6500S_JCT | AESO. 2016. Cooking Lake Connection Assessment |  | 458
| 948L | Altalink Management Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  | 507 | 613 | 0.9 | n/a | 456.3 | 551.7 | Paintearth 863S | AB_863S_DSS | Hansman Lake 650S | AB_650S_DSS | AESO. 2016. Wainright Connection Assessment |  | 980
| 885L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 138 | 2.6014 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | Metiskow 648S | AB_648S_DSS | Hansman Lake 650S | AB_650S_DSS | AESO. 2016. Hughenden Connection Assessment |  | 907
| 954L | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 240 | 2.8611 |  |  | 333 | 333 | 0.9 | n/a | 299.7 | 299.7 | Metiskow 648S | AB_648S_DSS | Hansman Lake 650S | AB_650S_DSS | AESO. 2016. Hughenden Connection Assessment |  | 983
| 966L | Altalink Management Ltd. | Alberta | 1 | ac | 60 | 37.037 | 240 | 28.6111 |  |  | 332 | 332 | 0.9 | n/a | 298.8 | 298.8 | Pemukan 932S | AB_932S_DSS | Hansman Lake 650S | AB_650S_DSS | AESO. 2016. Hughenden Connection Assessment |  | 988
| 1047L | Altalink Management Ltd. | Alberta | 1 | ac | 60 | 37.037 | 240 | 28.6111 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Nilrem 574S | AB_574S_DSS | Hansman Lake 650S | AB_650S_DSS | AESO. 2015. Vincent Connection Assessment |  | 26
| 457L | Altalink Management Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 138 | 7.284 |  |  | 121 | 149 | 0.9 | n/a | 108.9 | 134.1 | Ipiatik 167S | AB_167S_DSS | Kirby 651S | AB_651S_DSS | AESO. 2018. Kirby Connection Assessment |  | 269
| 688L | Altalink Management Ltd. | Alberta | 1 | ac | 0.85 | 0.52469 | 138 | 0.36854 |  |  | 121 | 148 | 0.9 | n/a | 108.9 | 133.2 | Summit 653S JCT | AB_653S_JCT | Summit 653S | AB_653S_DSS | AESO. 2018. East Crossfield Connection Assessment |  | 365
| 752L | Altalink Management Ltd. | Alberta | 1 | ac | 3.4 | 2.0988 | 138 | 1.4741 |  |  | 121 | 142 | 0.9 | n/a | 108.9 | 127.8 | Summit 653S JCT | AB_653S_JCT | Summit 653S | AB_653S_DSS | AESO. 2018. East Crossfield Connection Assessment |  | 532
| 688AL | Altalink Management Ltd. | Alberta | 1 | ac | 5.1 | 3.1481 | 144 | 2.2331 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Nose Creek 284S | AB_284S_DSS | Summit 653S | AB_653S_DSS |  |  | 366
| 752L | Altalink Management Ltd. | Alberta | 1 | ac | 20.4 | 12.5926 | 138 | 8.8449 |  |  | 119 | 136 | 0.9 | n/a | 107.1 | 122.4 | East Crossfield 64S | AB_64S_DSS | Summit 653S JCT | AB_653S_JCT | AESO. 2018. East Crossfield Connection Assessment |  | 531
| 769L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 86 | 115 | 0.9 | n/a | 77.4 | 103.5 | Rosyth 296S | AB_296S_DSS | Clipper 656S | AB_656S_DSS | AESO. 2016. Wainright Connection Assessment |  | 563
| 7LA114 | ATCO Electric Ltd. | Alberta | 1 | ac | 15.12 | 9.3333 | 144 | 6.6204 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Chard 658S JCT | AB_658S_JCT | Chard 658S | AB_658S_DSS |  |  | 624
| 7L114 | ATCO Electric Ltd. | Alberta | 1 | ac | 18.48 | 11.4074 | 144 | 8.0916 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Leismer 72S | AB_72S_DSS | Chard 658S JCT | AB_658S_JCT |  |  | 622
| 526BL | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Pegasus Lake 659S JCT | AB_659S_JCT | Pegasus Lake 659S | AB_659S_DSS |  |  | 302
| 526L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Laura Lake 661S JCT | AB_661S_JCT | Pegasus Lake 659S JCT | AB_659S_JCT |  |  | 298
| 753L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 121 | 143 | 0.9 | n/a | 108.9 | 128.7 | Blackie 253S | AB_253S_DSS | High River 65S | AB_65S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 534
| 434L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 138 | 4.3357 |  |  | 279 | 287 | 0.9 | n/a | 251.1 | 258.3 | Foothills 237S | AB_237S_DSS | High River 65S | AB_65S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 259
| 519L | Altalink Management Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 72 | 6.9557 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Imperial Oil Carson Lake 996S JCT | AB_996S_JCT | Laura Lake 661S | AB_661S_DSS |  |  | 291
| 526L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Esso Judy Creek 638S JCT | AB_638S_JCT | Laura Lake 661S JCT | AB_661S_JCT |  |  | 297
| 725L | Altalink Management Ltd. | Alberta | 1 | ac | 28 | 17.284 | 138 | 12.14 |  |  | 91 | 128 | 0.9 | n/a | 81.9 | 115.2 | Mcbride Lake 240S JCT | AB_240S_JCT | Bowron 674S | AB_674S_DSS | AESO. 2019. Claresholm Connection Assessment |  | 446
| 850L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 138 | 15.175 |  |  | 89 | 109 | 0.9 | n/a | 80.1 | 98.1 | Carseland 525S | AB_525S_GSS | Okotoks 678S | AB_678S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 871
| 646L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 138 | 15.175 |  |  | 230 | 285 | 0.9 | n/a | 207 | 256.5 | Foothills 237S | AB_237S_DSS | Okotoks 678S | AB_678S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 346
| 727AL | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 138 | 3.035 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Magcan 142S JCT | AB_142S_JCT | Okotoks 678S | AB_678S_DSS | AESO. 2016. Okotoks Connection Assessment |  | 454
| 7LA13 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Bear Creek 679S JCT | AB_679S_JCT | Bear Creek 679S | AB_679S_DSS |  |  | 645
| 7L13 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  | 140.9 | 179.2 | 0.9 | n/a | 126.81 | 161.28 | Big Mountain 845S | AB_845S_DSS | Bear Creek 679S JCT | AB_679S_JCT | AESO. 2016. Spirit River Connection Assessment |  | 642
| 225L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 69 | 8.07 |  |  | 25 | 32.5 | 0.9 | n/a | 22.5 | 29.25 | Raymond Reservoir 313S JCT | AB_313S_JCT | Stirling 67S | AB_67S_GSS | AESO. 2019. Mclaughlin Connection Assessment |  | 158
| 637L | Altalink Management Ltd. | Alberta | 1 | ac | 22.5 | 13.8889 | 144 | 9.8518 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Benalto 17S | AB_17S_DSS | Sylvan Lake 680S | AB_680S_DSS |  |  | 345
| 942L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 240 | 11.9213 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Lamoureux 71S | AB_71S_DSS | Bannerman 681S | AB_681S_DSS | AESO. 2018. Strathcona CG Connection Assessment |  | 974
| 1061L | Altalink Management Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 240 | 20.0278 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Heartland 12S | AB_12S_DSS | Bannerman 681S | AB_681S_DSS |  |  | 40
| 995AL | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 240 | 4.2917 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Willesdengreen 68S JCT | AB_68S_JCT | Willesdengreen 68S | AB_68S_DSS |  |  | 1000
| 995L | Altalink Management Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 240 | 11.4444 |  |  | 333 | 333 | 0.9 | n/a | 299.7 | 299.7 | Brazeau 62S | AB_62S_GSS | Willesdengreen 68S JCT | AB_68S_JCT | AESO. 2020. Cascade Connection Assessment |  | 998
| 1099L | Altalink Management Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 240 | 19.0741 |  |  | 549 | 701 | 0.9 | n/a | 494.1 | 630.9 | Black Spruce 154S | AB_154S_DSS | Jackfish 698S | AB_698S_DSS | AESO. 2019. Boreal 193S Connection Assessment |  | 56
| 1090L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  | 594 | 713 | 0.9 | n/a | 534.6 | 641.7 | Christina Lake 723S | AB_723S_GSS | Jackfish 698S | AB_698S_DSS | AESO. 2016. Bohn 931S Connection Assessment |  | 54
| 913L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  | 449 | 608 | 0.9 | n/a | 404.1 | 547.2 | Cherhill 338S | AB_338S_DSS | North Barrhead 69S | AB_69S_DSS | AESO. 2017. Heartland Connection Assessment |  | 944
| 7L230 | ATCO Electric Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 144 | 19.7036 |  |  | 86 | 91 | 0.9 | n/a | 77.4 | 81.9 | Fort Assiniboine 234S JCT | AB_234S_JCT | North Barrhead 69S | AB_69S_DSS | AESO. 2016. Gainford Connection Assessment |  | 695
| 7L89 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Lacorey 721S | AB_721S_DSS | Bonnyville 700S | AB_700S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 799
| 826L | Altalink Management Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 144 | 15.325 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sagitawah 77S | AB_77S_DSS | Blue Ridge Lumber 701S | AB_701S_ISS |  |  | 843
| 7L130 | ATCO Electric Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 138 | 15.175 |  |  | 71.9 | 86.3 | 0.9 | n/a | 64.71 | 77.67 | Vermilion 710S | AB_710S_DSS | Kitscoty 705S | AB_705S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 646
| 7L53 | ATCO Electric Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 138 | 10.4057 |  |  | 123.6 | 150.4 | 0.9 | n/a | 111.24 | 135.36 | Lindbergh 969S JCT | AB_969S_JCT | Irish Creek 706S | AB_706S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 735
| 7L70 | ATCO Electric Ltd. | Alberta | 1 | ac | 75 | 46.2963 | 144 | 32.8393 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Bonnyville 700S | AB_700S_DSS | St. Paul 707S | AB_707S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 768
| 7L92 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 138 | 7.8043 |  |  | 95 | 95 | 0.9 | n/a | 85.5 | 85.5 | Watt Lake 956S JCT | AB_956S_JCT | Vegreville 709S | AB_709S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 806
| 7L117 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 123.6 | 150.4 | 0.9 | n/a | 111.24 | 135.36 | Irish Creek 706S | AB_706S_DSS | Vermilion 710S | AB_710S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 626
| 7L65 | ATCO Electric Ltd. | Alberta | 1 | ac | 110 | 67.9012 | 144 | 48.1643 |  |  | 95 | 95 | 0.9 | n/a | 85.5 | 85.5 | Vegreville 709S | AB_709S_DSS | Vermilion 710S | AB_710S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 761
| 7L583 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  | 178.3 | 218.5 | 0.9 | n/a | 160.47 | 196.65 | Bourque 970S | AB_970S_DSS | Leming Lake 715S | AB_715S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 745
| 7L91 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Marguerite Lake 826S | AB_826S_DSS | Leming Lake 715S | AB_715S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 803
| 7L42 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  | 95 | 95 | 0.9 | n/a | 85.5 | 85.5 | Hill 751S | AB_751S_DSS | Lloydminster 716S | AB_716S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 717
| 7L66 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Leming Lake 715S | AB_715S_DSS | Ethel Lake 717S | AB_717S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 762
| 7L71 | ATCO Electric Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 144 | 11.034 |  |  | 100 | 100 | 0.9 | n/a | 90 | 90 | Dog Rib 2082S | AB_2082S_DSS | Parsons Creek 718S | AB_718S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 773
| 7L47 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 100 | 100 | 0.9 | n/a | 90 | 90 | Ruth Lake 848S | AB_848S_DSS | Parsons Creek 718S | AB_718S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 725
| 7L165 | ATCO Electric Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 144 | 12.873 |  |  | 116 | 150 | 0.9 | n/a | 104.4 | 135 | Tower Road 933S | AB_933S_DSS | Parsons Creek 718S | AB_718S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 674
| 9L56 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 488 | 624 | 0.9 | n/a | 439.2 | 561.6 | Brintnell 876S | AB_876S_DSS | Wabasca 720S | AB_720S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1036
| 7L89 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Marguerite Lake 826S | AB_826S_DSS | Lacorey 721S | AB_721S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 798
| 7L39 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Mercer Hill 728S JCT | AB_728S_JCT | Crystal Lake 722S | AB_722S_DSS | AESO. 2015. Eureka Connection Assessment |  | 714
| 6L37 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 72 | 11.5929 |  |  | 32 | 42 | 0.9 | n/a | 28.8 | 37.8 | Friedenstal 800S | AB_800S_DSS | Hines Creek 724S | AB_724S_DSS | AESO. 2015. Eureka Connection Assessment |  | 392
| 7L56 | ATCO Electric Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 144 | 15.325 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Little Smoky 813S | AB_813S_DSS | Goose River 725S | AB_725S_DSS |  |  | 739
| 6L99 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Slave Lake 745S | AB_745S_DSS | Kinuso 727S | AB_727S_DSS |  |  | 398
| 6L57 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 72 | 4.6371 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Swan River 735S | AB_735S_DSS | Kinuso 727S | AB_727S_DSS |  |  | 394
| 7LA39 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mercer Hill 728S JCT | AB_728S_JCT | Mercer Hill 728S | AB_728S_DSS |  |  | 715
| 7L39 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Clairmont Lake 811S | AB_811S_DSS | Mercer Hill 728S JCT | AB_728S_JCT | AESO. 2015. Eureka Connection Assessment |  | 713
| 7L162 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mitsue 732S | AB_732S_DSS | Otauwau 729S | AB_729S_DSS |  |  | 673
| 7L49 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mitsue 732S | AB_732S_DSS | Otauwau 729S | AB_729S_DSS |  |  | 729
| 6L73 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 72 | 7.7286 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Slave Lake 745S | AB_745S_DSS | Otauwau 729S | AB_729S_DSS |  |  | 395
| 9L930 | ATCO Electric Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  | 535 | 717 | 0.9 | n/a | 481.5 | 645.3 | Heart Lake 898S | AB_898S_DSS | Leismer 72S | AB_72S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1053
| 9L990 | ATCO Electric Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 240 | 12.0167 |  |  | 556 | 748 | 0.9 | n/a | 500.4 | 673.2 | Kettle River 2049S | AB_2049S_DSS | Leismer 72S | AB_72S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1061
| 957L | Altalink Management Ltd. | Alberta | 1 | ac | 33.6 | 20.7407 | 240 | 16.0222 |  |  | 594 | 713 | 0.9 | n/a | 534.6 | 641.7 | Christina Lake 723S | AB_723S_GSS | Leismer 72S | AB_72S_DSS | AESO. 2018. Kirby Connection Assessment |  | 986
| 7L73 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Boucher Creek 829S | AB_829S_DSS | Rycroft 730S | AB_730S_DSS | AESO. 2016. Hughes Connection Assessment |  | 776
| 7L69 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | Goodfare 815S | AB_815S_DSS | Elmworth 731S | AB_731S_DSS | AESO. 2016. Hughes Connection Assessment |  | 766
| 7L23 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Narrows Creek 858S | AB_858S_DSS | Mitsue 732S | AB_732S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 693
| 9L56 | ATCO Electric Ltd. | Alberta | 1 | ac | 100 | 61.7284 | 240 | 47.6852 |  |  | 488 | 624 | 0.9 | n/a | 439.2 | 561.6 | Wabasca 720S | AB_720S_DSS | Mitsue 732S | AB_732S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1037
| 913L | Altalink Management Ltd. | Alberta | 1 | ac | 140 | 86.4198 | 240 | 66.7593 |  |  |  |  | 0.9 | 2.2396 | 327.4129 | 355.3738 | North Barrhead 69S | AB_69S_DSS | Mitsue 732S | AB_732S_DSS |  |  | 945
| 7L80 | ATCO Electric Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 144 | 24.0821 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Kakwa Ridge 857S | AB_857S_DSS | Simonette 733S | AB_733S_DSS | AESO. 2016. Hughes Connection Assessment |  | 789
| 7L40 | ATCO Electric Ltd. | Alberta | 1 | ac | 60 | 37.037 | 144 | 26.2714 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Little Smoky 813S | AB_813S_DSS | Simonette 733S | AB_733S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 716
| 7L57 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Little Smoky 813S | AB_813S_DSS | Sturgeon 734S | AB_734S_DSS |  |  | 742
| 6L32 | ATCO Electric Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-1 | AB_E1S_ISS | Horseshoe 737S | AB_737S_DSS |  |  | 391
| 7L56 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Goose River 725S | AB_725S_DSS | Virginia Hills 738S | AB_738S_DSS |  |  | 740
| 6L97 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 72 | 4.6371 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Swan River 735S | AB_735S_DSS | Edith Lake 739S | AB_739S_DSS |  |  | 397
| 7L20 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 150 | 150 | 0.9 | n/a | 135 | 135 | Dome Cutbank 810S | AB_810S_DSS | H.R. Milner 740S | AB_740S_GSS | AESO. 2018. Ksituan Connection Assessment |  | 687
| 7L90 | ATCO Electric Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Muir 2018S JCT | AB_2018S_JCT | Fox Creek 741S | AB_741S_DSS | AESO. 2016. Fox Creek Connection Assessment |  | 801
| 6L11 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Swandive 854S | AB_854S_DSS | Freeman Lake 742S | AB_742S_DSS |  |  | 383
| 7L55 | ATCO Electric Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 144 | 15.325 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Louise Creek 809S | AB_809S_DSS | Sarah Lake 743S | AB_743S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 738
| 7L172 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Edith Lake 739S | AB_739S_DSS | Sarah Lake 743S | AB_743S_DSS |  |  | 678
| 6L11 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Freeman Lake 742S | AB_742S_DSS | Sarah Lake 743S | AB_743S_DSS |  |  | 384
| 6L96 | ATCO Electric Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 72 | 15.4571 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Swan River 735S | AB_735S_DSS | Sarah Lake 743S | AB_743S_DSS |  |  | 396
| 636L | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 138 | 3.1217 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Broadmoor 420S | AB_420S_DSS | Sherwood Park 746S | AB_746S_DSS | AESO. 2015. Broadmoor Connection Assessment |  | 344
| 7L64 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 75 | 90 | 0.9 | n/a | 67.5 | 81 | Haig River 748S | AB_748S_DSS | Bassett 747S | AB_747S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 759
| 7L64 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 75 | 90 | 0.9 | n/a | 67.5 | 81 | Chinchaga River 779S | AB_779S_DSS | Haig River 748S | AB_748S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 758
| 7L33 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 147 | 187 | 0.9 | n/a | 132.3 | 168.3 | CG&E 758S | AB_758S_DSS | Flying Shot Lake 749S | AB_749S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 708
| 7L84 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 165 | 199 | 0.9 | n/a | 148.5 | 179.1 | Crystal Lake 722S | AB_722S_DSS | Flying Shot Lake 749S | AB_749S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 793
| 7L03 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Wapiti 823S JCT | AB_823S_JCT | Flying Shot Lake 749S | AB_749S_DSS | AESO. 2016. Spirit River Connection Assessment |  | 604
| 1003L | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 240 | 3.338 |  |  | 973 | 1039 | 0.9 | n/a | 875.7 | 935.1 | Shepard SS-25 | AB_SS25_GSS | Janet 74S | AB_74S_DSS | AESO. 2017. SS 7 Connection Assessment |  | 8
| 985L | Altalink Management Ltd. | Alberta | 1 | ac | 7 | 4.321 | 240 | 3.338 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Shepard SS-25 | AB_SS25_GSS | Janet 74S | AB_74S_DSS |  |  | 995
| 7L14 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 71.9 | 86.3 | 0.9 | n/a | 64.71 | 77.67 | Kitscoty 705S | AB_705S_DSS | Hill 751S | AB_751S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 656
| 7L13 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Bear Creek 679S JCT | AB_679S_JCT | Albright & Wilson 752S | AB_752S_ISS |  |  | 643
| 7L10 | ATCO Electric Ltd. | Alberta | 1 | ac | 8 | 4.9383 | 144 | 3.5029 |  |  | 49 | 49 | 0.9 | n/a | 44.1 | 44.1 | Mowat 2033S JCT | AB_2033S_JCT | Ksituan River 754S | AB_754S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 613
| 6L08 | ATCO Electric Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 72 | 2.7823 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Battle River 757S | AB_757S_GSS | Bigfoot 756S | AB_756S_DSS |  |  | 378
| 6L03 | ATCO Electric Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 69 | 13.45 |  |  | 47 | 47 | 0.9 | n/a | 42.3 | 42.3 | Castor 759S | AB_759S_DSS | Battle River 757S | AB_757S_GSS | AESO. 2018. Wheatland Connection Assessment |  | 374
| 702L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 138 | 13.0071 |  |  | 109.3 | 118 | 0.9 | n/a | 98.37 | 106.2 | Sedgewick 137S JCT | AB_137S_JCT | Battle River 757S | AB_757S_GSS | AESO. 2017. Sharphills Connection Assessment |  | 406
| 9L79 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Cordel 755S | AB_755S_DSS | Battle River 757S | AB_757S_GSS | AESO. 2015. Vincent Connection Assessment |  | 1046
| 9L80 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  | 415 | 415 | 0.9 | n/a | 373.5 | 373.5 | Cordel 755S | AB_755S_DSS | Battle River 757S | AB_757S_GSS | AESO. 2015. Vincent Connection Assessment |  | 1047
| 7L701 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 139.9 | 179.2 | 0.9 | n/a | 125.91 | 161.28 | Heisler 764S JCT | AB_764S_JCT | Battle River 757S | AB_757S_GSS | AESO. 2015. Vincent Connection Assessment |  | 770
| 7LA701 | ATCO Electric Ltd. | Alberta | 1 | ac | 4.8 | 2.963 | 144 | 2.1017 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Heisler 764S JCT | AB_764S_JCT | Battle River 757S | AB_757S_GSS |  |  | 771
| 7L33 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 147 | 187 | 0.9 | n/a | 132.3 | 168.3 | Big Mountain 845S | AB_845S_DSS | CG&E 758S | AB_758S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 707
| 6L03 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 69 | 4.6114 |  |  | 47 | 47 | 0.9 | n/a | 42.3 | 42.3 | Sullivan Lake 775S | AB_775S_DSS | Castor 759S | AB_759S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 373
| 6L09 | ATCO Electric Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 69 | 9.2229 |  |  | 23 | 23 | 0.9 | n/a | 20.7 | 20.7 | Richdale 776S | AB_776S_DSS | Hanna 763S | AB_763S_DSS | AESO. 2016. Jenner Connection Assessment |  | 381
| 6L05 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 69 | 3.4586 |  |  | 54.6 | 69 | 0.9 | n/a | 49.14 | 62.1 | Big Knife Creek 843S | AB_843S_DSS | Heisler 764S | AB_764S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 376
| 7L701 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 139.9 | 179.2 | 0.9 | n/a | 125.91 | 161.28 | Strome 223S | AB_223S_DSS | Heisler 764S JCT | AB_764S_JCT | AESO. 2015. Vincent Connection Assessment |  | 769
| 6LA02 | ATCO Electric Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 72 | 2.3186 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Mannix Mine 765S JCT | AB_765S_JCT | Mannix Mine 765S | AB_765S_DSS |  |  | 372
| 6LA05 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 72 | 3.4779 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Big Knife Creek 843S | AB_843S_DSS | Mannix Mine 765S JCT | AB_765S_JCT |  |  | 377
| 912L | Altalink Management Ltd. | Alberta | 1 | ac | 60 | 37.037 | 240 | 28.6111 |  |  | 507 | 623 | 0.9 | n/a | 456.3 | 560.7 | Red Deer 63S | AB_63S_DSS | Nevis 766S | AB_766S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 943
| 9L20 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 488 | 498 | 0.9 | n/a | 439.2 | 448.2 | Cordel 755S | AB_755S_DSS | Nevis 766S | AB_766S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 1017
| 7L132 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 143 | 143 | 0.9 | n/a | 128.7 | 128.7 | Lanfine 959S | AB_959S_DSS | Oyen 767S | AB_767S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 648
| 7L760 | ATCO Electric Ltd. | Alberta | 1 | ac | 45.5 | 28.0864 | 144 | 19.9225 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Bindloss 914S JCT | AB_914S_JCT | Oyen 767S | AB_767S_DSS | AESO. 2016. Jenner Connection Assessment |  | 782
| 7L151 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Lanfine 959S | AB_959S_DSS | Oyen 767S | AB_767S_DSS |  |  | 663
| 7L137 | ATCO Electric Ltd. | Alberta | 1 | ac | 27 | 16.6667 | 138 | 11.7064 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Three Hills 770S | AB_770S_DSS | Rowley 768S | AB_768S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 651
| 6L02 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 69 | 5.7643 |  |  | 47 | 47 | 0.9 | n/a | 42.3 | 42.3 | Marion Lake 873S | AB_873S_DSS | Stettler 769S | AB_769S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 371
| 7L143 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 95 | 95 | 0.9 | n/a | 85.5 | 85.5 | Nevis 766S | AB_766S_DSS | Stettler 769S | AB_769S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 658
| 7L159 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 109.3 | 126.5 | 0.9 | n/a | 98.37 | 113.85 | Ghost Pine 114S JCT | AB_114S_JCT | Three Hills 770S | AB_770S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 668
| 7L79 | ATCO Electric Ltd. | Alberta | 1 | ac | 65 | 40.1235 | 138 | 28.1821 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Pemukan 932S | AB_932S_DSS | Veteran 771S | AB_771S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 786
| 6L09 | ATCO Electric Ltd. | Alberta | 1 | ac | 60 | 37.037 | 69 | 23.0571 |  |  | 23 | 23 | 0.9 | n/a | 20.7 | 20.7 | Oyen 767S | AB_767S_DSS | Youngstown 772S | AB_772S_DSS | AESO. 2016. Jenner Connection Assessment |  | 379
| 6L25 | ATCO Electric Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 72 | 2.3186 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Coronation 773S JCT | AB_773S_JCT | Coronation 773S | AB_773S_DSS |  |  | 390
| 6L12 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 69 | 11.5286 |  |  | 23 | 23 | 0.9 | n/a | 20.7 | 20.7 | Sullivan Lake 775S | AB_775S_DSS | Coronation 773S JCT | AB_773S_JCT | AESO. 2018. Wheatland Connection Assessment |  | 385
| 7L224 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 109.25 | 138.99 | 0.9 | n/a | 98.325 | 125.091 | Hansman Lake 650S | AB_650S_DSS | Monitor 774S | AB_774S_DSS | AESO. 2016. Hughenden Connection Assessment |  | 690
| 6L12 | ATCO Electric Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 72 | 27.05 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Coronation 773S JCT | AB_773S_JCT | Monitor 774S | AB_774S_DSS |  |  | 386
| 6L15 | ATCO Electric Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 69 | 17.2929 |  |  | 23 | 23 | 0.9 | n/a | 20.7 | 20.7 | Hanna 763S | AB_763S_DSS | Sullivan Lake 775S | AB_775S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 388
| 6L09 | ATCO Electric Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 69 | 9.2229 |  |  | 23 | 23 | 0.9 | n/a | 20.7 | 20.7 | Youngstown 772S | AB_772S_DSS | Richdale 776S | AB_776S_DSS | AESO. 2016. Jenner Connection Assessment |  | 380
| 7L92 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 95 | 95 | 0.9 | n/a | 85.5 | 85.5 | Whitby Lake 819S | AB_819S_DSS | Vilna 777S | AB_777S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 804
| 7L64 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 75 | 90 | 0.9 | n/a | 67.5 | 81 | Keg River 789S | AB_789S_DSS | Chinchaga River 779S | AB_779S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 757
| 799L | Altalink Management Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 138 | 19.5107 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | South Mayerthorpe 443S | AB_443S_DSS | Sagitawah 77S | AB_77S_DSS | AESO. 2016. Gainford Connection Assessment |  | 600
| 919L | Altalink Management Ltd. | Alberta | 1 | ac | 140 | 86.4198 | 240 | 66.7593 |  |  | 489 | 599 | 0.9 | n/a | 440.1 | 539.1 | Sundance 310P | AB_310P_GSS | Sagitawah 77S | AB_77S_DSS | AESO. 2016. Gainford Connection Assessment |  | 953
| 989L | Altalink Management Ltd. | Alberta | 1 | ac | 140 | 86.4198 | 240 | 66.7593 |  |  | 499 | 599 | 0.9 | n/a | 449.1 | 539.1 | Sundance 310P | AB_310P_GSS | Sagitawah 77S | AB_77S_DSS | AESO. 2016. Gainford Connection Assessment |  | 996
| 9L938 | ATCO Electric Ltd. | Alberta | 1 | ac | 95 | 58.642 | 240 | 45.3009 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Louise Creek 809S | AB_809S_DSS | Sagitawah 77S | AB_77S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1054
| 9L939 | ATCO Electric Ltd. | Alberta | 1 | ac | 95 | 58.642 | 240 | 45.3009 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Louise Creek 809S | AB_809S_DSS | Sagitawah 77S | AB_77S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1055
| 907L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Alberta Newsprint 122S | AB_122S_GSS | Sagitawah 77S | AB_77S_DSS |  |  | 933
| 798L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Whitecourt Industrial 364S | AB_364S_ISS | Sagitawah 77S | AB_77S_DSS |  |  | 598
| 7L63 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Norcen 812S | AB_812S_DSS | Lubicon 780S | AB_780S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 756
| 7L12 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Seal Lake 869S JCT | AB_869S_JCT | Lubicon 780S | AB_780S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 628
| 7L60 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Cranberry Lake 827S | AB_827S_DSS | Lubicon 780S | AB_780S_DSS |  |  | 750
| 7L63 | ATCO Electric Ltd. | Alberta | 1 | ac | 75 | 46.2963 | 144 | 32.8393 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Hotchkiss 788S | AB_788S_DSS | Cadotte River 783S | AB_783S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 754
| 7L06 | ATCO Electric Ltd. | Alberta | 1 | ac | 50 | 30.8642 | 144 | 21.8929 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | High Prairie 787S | AB_787S_DSS | Donnelly 784S | AB_784S_DSS | AESO. 2015. Eureka Connection Assessment |  | 607
| 7L78 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Morse River 851S | AB_851S_DSS | Judy Creek Gas Plant 785S | AB_785S_ISS |  |  | 785
| 7L59 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Melito 890S JCT | AB_890S_JCT | High Level 786S | AB_786S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 748
| 7L133 | ATCO Electric Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 144 | 39.4071 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Sulphur Point 828S | AB_828S_DSS | High Level 786S | AB_786S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 649
| 7L76 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Blumenort 832S | AB_832S_DSS | High Level 786S | AB_786S_DSS |  |  | 781
| 7L62 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | Kemp River 797S | AB_797S_DSS | Keg River 789S | AB_789S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 753
| 7L58 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | Meikle 905S | AB_905S_DSS | Keg River 789S | AB_789S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 744
| 7L07 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 109.3 | 139.9 | 0.9 | n/a | 98.37 | 125.91 | Goodfare 815S | AB_815S_DSS | Poplar Hill 790S | AB_790S_GSS | AESO. 2016. Spirit River Connection Assessment |  | 609
| 7L101 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  | 109.3 | 139.9 | 0.9 | n/a | 98.37 | 125.91 | Lowe Lake 944S | AB_944S_DSS | Poplar Hill 790S | AB_790S_GSS | AESO. 2016. Spirit River Connection Assessment |  | 615
| 7L22 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Saddle Hills 865S JCT | AB_865S_JCT | Poplar Hill 790S | AB_790S_GSS | AESO. 2015. Eureka Connection Assessment |  | 689
| 7L29 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Rainbow Cogen 850S | AB_850S_GSS | Rainbow Lake 791S | AB_791S_GSS |  |  | 702
| 7L75 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 146 | 149 | 0.9 | n/a | 131.4 | 134.1 | Friedenstal 800S | AB_800S_DSS | Westpeace 793S | AB_793S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 780
| 7L51 | ATCO Electric Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 144 | 24.0821 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Buchanan Creek 927S | AB_927S_DSS | Westpeace 793S | AB_793S_DSS | AESO. 2015. Eureka Connection Assessment |  | 733
| 7L06 | ATCO Electric Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 144 | 17.5143 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | Donnelly 784S | AB_784S_DSS | Westpeace 793S | AB_793S_DSS | AESO. 2015. Eureka Connection Assessment |  | 608
| 7L48 | ATCO Electric Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 144 | 17.5143 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Triangle 882S JCT | AB_882S_JCT | Valleyview 794S | AB_794S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 727
| 7L72 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sulphur Point 828S | AB_828S_DSS | Zama 795S | AB_795S_DSS |  |  | 774
| 7L61 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Lubicon 780S | AB_780S_DSS | Nipisi 796S | AB_796S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 751
| 7L62 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | Meikle 905S | AB_905S_DSS | Kemp River 797S | AB_797S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 752
| 7LA45 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Bridge Creek 798S JCT | AB_798S_JCT | Bridge Creek 798S | AB_798S_DSS |  |  | 723
| 7L45 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  | 146 | 187 | 0.9 | n/a | 131.4 | 168.3 | Big Mountain 845S | AB_845S_DSS | Bridge Creek 798S JCT | AB_798S_JCT | AESO. 2018. Ksituan Connection Assessment |  | 721
| 7L85 | ATCO Electric Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 138 | 10.4057 |  |  | 139.9 | 179.2 | 0.9 | n/a | 125.91 | 161.28 | Bullpound 803S | AB_803S_DSS | Anderson 801S | AB_801S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 795
| 9L70 | ATCO Electric Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 240 | 5.0069 |  |  | 432 | 432 | 0.9 | n/a | 388.8 | 388.8 | Oakland 946S | AB_946S_DSS | Anderson 801S | AB_801S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 1043
| 9L100 | ATCO Electric Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 240 | 5.0069 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Sheerness 807S | AB_807S_GSS | Anderson 801S | AB_801S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 1009
| 9L950 | ATCO Electric Ltd. | Alberta | 1 | ac | 75 | 46.2963 | 240 | 35.7639 |  |  | 519 | 663 | 0.9 | n/a | 467.1 | 596.7 | Ware Junction 132S | AB_132S_DSS | Anderson 801S | AB_801S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 1056
| 933L | Altalink Management Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 240 | 33.3796 |  |  | 519 | 663 | 0.9 | n/a | 467.1 | 596.7 | Ware Junction 132S | AB_132S_DSS | Anderson 801S | AB_801S_DSS | AESO. 2017. Paintearth Connection Assessment |  | 968
| 934L | Altalink Management Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 240 | 33.3796 |  |  | 519 | 663 | 0.9 | n/a | 467.1 | 596.7 | Ware Junction 132S | AB_132S_DSS | Anderson 801S | AB_801S_DSS | AESO. 2017. Paintearth Connection Assessment |  | 969
| 9L97 | ATCO Electric Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 240 | 5.0069 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Oakland 946S | AB_946S_DSS | Anderson 801S | AB_801S_DSS |  |  | 1059
| 9L99 | ATCO Electric Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 240 | 5.0069 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Sheerness 807S | AB_807S_GSS | Anderson 801S | AB_801S_DSS |  |  | 1060
| 6L56 | ATCO Electric Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 69 | 21.1357 |  |  | 35 | 35 | 0.9 | n/a | 31.5 | 31.5 | Hanna 763S | AB_763S_DSS | Michichi Creek 802S | AB_802S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 393
| 7L25 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 94.9 | 94.9 | 0.9 | n/a | 85.41 | 85.41 | Rowley 768S | AB_768S_DSS | Michichi Creek 802S | AB_802S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 699
| 7L85 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 139.9 | 179.2 | 0.9 | n/a | 125.91 | 161.28 | Wintering Hills 804S | AB_804S_DSS | Bullpound 803S | AB_803S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 794
| 7L171 | ATCO Electric Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 138 | 10.4057 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Michichi Creek 802S | AB_802S_DSS | Wintering Hills 804S | AB_804S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 677
| 1044L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 481 | 581 | 0.9 | n/a | 432.9 | 522.9 | Petrolia 816S | AB_816S_DSS | Jasper 805S | AB_805S_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 23
| 1098L | Altalink Management Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 240 | 3.4333 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Poundmaker | AB_XPOU_DSS | Jasper 805S | AB_805S_DSS |  |  | 55
| 893BL | Altalink Management Ltd. | Alberta | 1 | ac | 8.4 | 5.1852 | 144 | 3.678 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Windy Point 112S JCT | AB_112S_JCT | Oldman River 806S | AB_806S_GSS |  |  | 918
| 9L02 | ATCO Electric Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 240 | 33.3796 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Little Smoky 813S | AB_813S_DSS | Louise Creek 809S | AB_809S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1003
| 9L05 | ATCO Electric Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 240 | 33.3796 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Little Smoky 813S | AB_813S_DSS | Louise Creek 809S | AB_809S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1004
| 9L40 | ATCO Electric Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  | 332 | 332 | 0.9 | n/a | 298.8 | 298.8 | Mitsue 732S | AB_732S_DSS | Louise Creek 809S | AB_809S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1030
| 7L43 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Edith Lake 739S | AB_739S_DSS | Louise Creek 809S | AB_809S_DSS |  |  | 718
| 7L19 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Morse River 851S | AB_851S_DSS | Louise Creek 809S | AB_809S_DSS |  |  | 683
| 7L56 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Virginia Hills 738S | AB_738S_DSS | Louise Creek 809S | AB_809S_DSS |  |  | 741
| 7L20 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 150 | 150 | 0.9 | n/a | 135 | 135 | Thornton 2091S | AB_2091S_DSS | Dome Cutbank 810S | AB_810S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 686
| 7L68 | ATCO Electric Ltd. | Alberta | 1 | ac | 60 | 37.037 | 144 | 26.2714 |  |  | 114 | 132 | 0.9 | n/a | 102.6 | 118.8 | Rycroft 730S | AB_730S_DSS | Clairmont Lake 811S | AB_811S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 765
| 7L63 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Cadotte River 783S | AB_783S_DSS | Norcen 812S | AB_812S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 755
| 7L46 | ATCO Electric Ltd. | Alberta | 1 | ac | 100 | 61.7284 | 144 | 43.7857 |  |  | 147 | 187 | 0.9 | n/a | 132.3 | 168.3 | Big Mountain 845S | AB_845S_DSS | Little Smoky 813S | AB_813S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 724
| 7L45 | ATCO Electric Ltd. | Alberta | 1 | ac | 70 | 43.2099 | 144 | 30.65 |  |  | 146 | 187 | 0.9 | n/a | 131.4 | 168.3 | Bridge Creek 798S JCT | AB_798S_JCT | Little Smoky 813S | AB_813S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 722
| 7L32 | ATCO Electric Ltd. | Alberta | 1 | ac | 115 | 70.9877 | 144 | 50.3536 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | South Bezanson 862S | AB_862S_DSS | Little Smoky 813S | AB_813S_DSS | AESO. 2015. Eureka Connection Assessment |  | 706
| 9L11 | ATCO Electric Ltd. | Alberta | 1 | ac | 180 | 111.1111 | 240 | 85.8333 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Wesley Creek 834S | AB_834S_DSS | Little Smoky 813S | AB_813S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1011
| 7L54 | ATCO Electric Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 144 | 24.0821 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Valleyview 794S | AB_794S_DSS | Little Smoky 813S | AB_813S_DSS |  |  | 737
| 72RG1 | EPCOR | Alberta | 1 | ac | 0.23 | 0.14198 | 72 | 0.088879 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Rossdale | AB_XROS_DSS | Bellamy 814S | AB_814S_DSS |  |  | 474
| 72RG7 | EPCOR | Alberta | 1 | ac | 0.23 | 0.14198 | 72 | 0.088879 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Rossdale | AB_XROS_DSS | Bellamy 814S | AB_814S_DSS |  |  | 476
| 789L | Altalink Management Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 138 | 34.6857 |  |  | 86 | 91 | 0.9 | n/a | 77.4 | 81.9 | Heart Lake 898S | AB_898S_DSS | Winefred 818S | AB_818S_DSS | AESO. 2018. Kirby Connection Assessment |  | 585
| 428L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 121 | 149 | 0.9 | n/a | 108.9 | 134.1 | Ipiatik 167S | AB_167S_DSS | Winefred 818S | AB_818S_DSS | AESO. 2018. Kirby Connection Assessment |  | 256
| 7L139 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 138 | 13.0071 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Norberg 936S JCT | AB_936S_JCT | Whitby Lake 819S | AB_819S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 654
| 794L | Altalink Management Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 138 | 34.6857 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Lac La Biche 157S | AB_157S_DSS | Whitby Lake 819S | AB_819S_DSS | AESO. 2016. Plamondon Connection Assessment |  | 592
| 7L97 | ATCO Electric Ltd. | Alberta | 1 | ac | 33.6 | 20.7407 | 144 | 14.712 |  |  | 117 | 155 | 0.9 | n/a | 105.3 | 139.5 | Halfway 2014S JCT | AB_2014S_JCT | Hangingstone 820S | AB_820S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 812
| 512L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 69 | 7.6857 |  |  | 22 | 27 | 0.9 | n/a | 19.8 | 24.3 | Sundance 310P | AB_310P_GSS | Sundance SS 821S | AB_821S_DSS | AESO. 2016. Gainford Connection Assessment |  | 286
| 7L587 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  | 191.7 | 191.7 | 0.9 | n/a | 172.53 | 172.53 | Marguerite Lake 826S | AB_826S_DSS | Wolf Lake 822S | AB_822S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 746
| 7L09 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Wapiti 823S JCT | AB_823S_JCT | Wapiti 823S | AB_823S_DSS |  |  | 611
| 7L03 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Elmworth 731S | AB_731S_DSS | Wapiti 823S JCT | AB_823S_JCT | AESO. 2016. Spirit River Connection Assessment |  | 603
| 7L67 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Morse River 851S | AB_851S_DSS | Fieldgate 824S | AB_824S_DSS |  |  | 764
| 7L67 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sarah Lake 743S | AB_743S_DSS | Fieldgate 824S | AB_824S_DSS |  |  | 763
| 9L22 | ATCO Electric Ltd. | Alberta | 1 | ac | 75 | 46.2963 | 240 | 35.7639 |  |  | 457 | 578 | 0.9 | n/a | 411.3 | 520.2 | Heart Lake 898S | AB_898S_DSS | Whitefish Lake 825S | AB_825S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1018
| 9L960 | ATCO Electric Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Deerland 13S | AB_13S_DSS | Whitefish Lake 825S | AB_825S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 1057
| 9L961 | ATCO Electric Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Deerland 13S | AB_13S_DSS | Whitefish Lake 825S | AB_825S_DSS | AESO. 2019. Abee 993S Connection Assessment |  | 1058
| 9L81 | ATCO Electric Ltd. | Alberta | 1 | ac | 75 | 46.2963 | 240 | 35.7639 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Heart Lake 898S | AB_898S_DSS | Whitefish Lake 825S | AB_825S_DSS | AESO. 2018. Kirby Connection Assessment |  | 1048
| 9L36 | ATCO Electric Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Marguerite Lake 826S | AB_826S_DSS | Whitefish Lake 825S | AB_825S_DSS | AESO. 2016. Kent Connection Assessment |  | 1027
| 9L37 | ATCO Electric Ltd. | Alberta | 1 | ac | 90 | 55.5556 | 240 | 42.9167 |  |  | 498 | 498 | 0.9 | n/a | 448.2 | 448.2 | Marguerite Lake 826S | AB_826S_DSS | Whitefish Lake 825S | AB_825S_DSS | AESO. 2016. Kent Connection Assessment |  | 1028
| 7L73 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 138 | 13.0071 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Friedenstal 800S | AB_800S_DSS | Boucher Creek 829S | AB_829S_DSS | AESO. 2016. Hughes Connection Assessment |  | 775
| 7LA121 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mariana 833S JCT | AB_833S_JCT | Mariana 833S | AB_833S_DSS |  |  | 633
| 7L121 | ATCO Electric Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 144 | 7.356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Horse River 917S | AB_917S_DSS | Mariana 833S JCT | AB_833S_JCT |  |  | 631
| 7L27 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 109.3 | 139.9 | 0.9 | n/a | 98.37 | 125.91 | Westpeace 793S | AB_793S_DSS | Wesley Creek 834S | AB_834S_DSS | AESO. 2016. Spirit River Connection Assessment |  | 700
| 9L15 | ATCO Electric Ltd. | Alberta | 1 | ac | 230 | 141.9753 | 240 | 109.6759 |  |  | 549 | 701 | 0.9 | n/a | 494.1 | 630.9 | Brintnell 876S | AB_876S_DSS | Wesley Creek 834S | AB_834S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 1014
| 7L08 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Carmon 830S | AB_830S_DSS | Wesley Creek 834S | AB_834S_DSS |  |  | 610
| 29PL6-03 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-1 | AB_E1S_ISS | Steepbak River 836S | AB_836S_DSS |  |  | 174
| 29PL6-04 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-1 | AB_E1S_ISS | Steepbak River 836S | AB_836S_DSS |  |  | 175
| 7L157 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  | 180.2 | 210.8 | 0.9 | n/a | 162.18 | 189.72 | Bourque 970S | AB_970S_DSS | Mahihkan 837S | AB_837S_DSS | AESO. 2016. Kent Connection Assessment |  | 666
| 7L160 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  | 180.2 | 212.8 | 0.9 | n/a | 162.18 | 191.52 | Bourque 970S | AB_970S_DSS | Mahihkan 837S | AB_837S_DSS | AESO. 2016. Kent Connection Assessment |  | 671
| 75-PLH-3 | Canadian Natural Resources Limited | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Horizon Upgrading 842S | AB_842S_GSS | Horizon Mining 838S | AB_838S_ISS |  |  | 527
| 75-PLH-4 | Canadian Natural Resources Limited | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Horizon Upgrading 842S | AB_842S_GSS | Horizon Mining 838S | AB_838S_ISS |  |  | 528
| 75-PLH-901 | Canadian Natural Resources Limited | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Joslyn Creek 849S | AB_849S_DSS | Horizon Mining 838S | AB_838S_ISS |  |  | 529
| 75-PLH-902 | Canadian Natural Resources Limited | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Joslyn Creek 849S | AB_849S_DSS | Horizon Mining 838S | AB_838S_ISS |  |  | 530
| 7L04 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Westpeace 793S | AB_793S_DSS | Daishowa 839S | AB_839S_GSS |  |  | 605
| 172L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 119 | 146 | 0.9 | n/a | 107.1 | 131.4 | Hillridge 139S JCT | AB_139S_JCT | Taber 83S | AB_83S_DSS | AESO. 2018. Fincastle Connection Assessment |  | 121
| 830L | Altalink Management Ltd. | Alberta | 1 | ac | 28 | 17.284 | 144 | 12.26 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Cypress 562S | AB_562S_DSS | Mcneill Station 840S | AB_840S_DSS |  |  | 846
| 7L15 | ATCO Electric Ltd. | Alberta | 1 | ac | 1.68 | 1.037 | 144 | 0.7356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Long Lake Cogen 864S | AB_864S_GSS | Long Lake 841S | AB_841S_DSS |  |  | 662
| 6L05 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 69 | 3.4586 |  |  | 54.6 | 69 | 0.9 | n/a | 49.14 | 62.1 | Battle River 757S | AB_757S_GSS | Big Knife Creek 843S | AB_843S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 375
| 7L30 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mitsue 732S | AB_732S_DSS | AEC Mills 844S | AB_844S_ISS |  |  | 703
| 7L31 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mitsue 732S | AB_732S_DSS | AEC Mills 844S | AB_844S_ISS |  |  | 704
| 7L44 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 146 | 187 | 0.9 | n/a | 131.4 | 168.3 | Flying Shot Lake 749S | AB_749S_DSS | Big Mountain 845S | AB_845S_DSS | AESO. 2018. Ksituan Connection Assessment |  | 720
| 7L24 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Beartrap 940S JCT | AB_940S_JCT | Grand Centre 846S | AB_846S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 697
| 7L28 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Ethel Lake 717S | AB_717S_DSS | Grand Centre 846S | AB_846S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 701
| 9L66 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 240 | 9.537 |  |  | 380 | 515 | 0.9 | n/a | 342 | 463.5 | Joslyn Creek 849S | AB_849S_DSS | Muskeg River 847S | AB_847S_GSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1041
| 9LJH1 | ATCO Electric Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 240 | 14.0194 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Jack Pine 920S | AB_920S_DSS | Muskeg River 847S | AB_847S_GSS |  |  | 1062
| 9LJH2 | ATCO Electric Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 240 | 14.0194 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Jack Pine 920S | AB_920S_DSS | Muskeg River 847S | AB_847S_GSS |  |  | 1063
| 9L58 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  | 416 | 565 | 0.9 | n/a | 374.4 | 508.5 | Dover 888S | AB_888S_DSS | Ruth Lake 848S | AB_848S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1039
| 9L08 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 457 | 578 | 0.9 | n/a | 411.3 | 520.2 | Dover 888S | AB_888S_DSS | Joslyn Creek 849S | AB_849S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1006
| 9L09 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 457 | 578 | 0.9 | n/a | 411.3 | 520.2 | Dover 888S | AB_888S_DSS | Joslyn Creek 849S | AB_849S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1007
| 1086L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  | 603 | 723 | 0.9 | n/a | 542.7 | 650.7 | Round Hill 852S JCT | AB_852S_JCT | Round Hill 852S | AB_852S_DSS | AESO. 2018. Kirby Connection Assessment |  | 51
| 1085L | Altalink Management Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Round Hill 852S JCT | AB_852S_JCT | Round Hill 852S | AB_852S_DSS |  |  | 50
| 9L47 | ATCO Electric Ltd. | Alberta | 1 | ac | 155 | 95.679 | 240 | 73.912 |  |  | 550 | 702 | 0.9 | n/a | 495 | 631.8 | Heart Lake 898S | AB_898S_DSS | Round Hill 852S JCT | AB_852S_JCT | AESO. 2018. Kirby Connection Assessment |  | 1034
| 9L55 | ATCO Electric Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 240 | 8.0111 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Mcmillan 885S | AB_885S_DSS | Round Hill 852S JCT | AB_852S_JCT |  |  | 1035
| 6L11 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Edith Lake 739S | AB_739S_DSS | Swandive 854S | AB_854S_DSS |  |  | 382
| 7L82 | ATCO Electric Ltd. | Alberta | 1 | ac | 50 | 30.8642 | 144 | 21.8929 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Hotchkiss 788S | AB_788S_DSS | Hamburg 855S | AB_855S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 792
| 7L82 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Ring Creek 853S | AB_853S_DSS | Hamburg 855S | AB_855S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 791
| 9L85 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 559 | 750 | 0.9 | n/a | 503.1 | 675 | Salt Creek 977S | AB_977S_DSS | Kinosis 856S | AB_856S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1050
| 9L45 | ATCO Electric Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 240 | 14.0194 |  |  | 332 | 332 | 0.9 | n/a | 298.8 | 298.8 | Kettle River 2049S | AB_2049S_DSS | Kinosis 856S | AB_856S_DSS | AESO. 2016. Bohn 931S Connection Assessment |  | 1032
| 7L80 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | H.R. Milner 740S | AB_740S_GSS | Kakwa Ridge 857S | AB_857S_DSS | AESO. 2016. Hughes Connection Assessment |  | 788
| 7L23 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Nipisi 796S | AB_796S_DSS | Narrows Creek 858S | AB_858S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 692
| 7L35 | ATCO Electric Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 144 | 10.5086 |  |  | 140 | 143 | 0.9 | n/a | 126 | 128.7 | Wolf Lake 822S | AB_822S_DSS | Primrose 859S | AB_859S_GSS | AESO. 2016. Bauer 918S Connection Assessment |  | 710
| 7L121 | ATCO Electric Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 144 | 11.034 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mariana 833S JCT | AB_833S_JCT | Crow 860S | AB_860S_DSS |  |  | 632
| 6L16 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 72 | 7.7286 |  |  | 24 | 24 | 0.9 | n/a | 21.6 | 21.6 | Hines Creek 724S | AB_724S_DSS | Eureka River 861S | AB_861S_DSS | AESO. 2015. Eureka Connection Assessment |  | 389
| 7L32 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | Clairmont Lake 811S | AB_811S_DSS | South Bezanson 862S | AB_862S_DSS | AESO. 2015. Eureka Connection Assessment |  | 705
| 9L27 | ATCO Electric Ltd. | Alberta | 1 | ac | 50 | 30.8642 | 240 | 23.8426 |  |  | 399 | 399 | 0.9 | n/a | 359.1 | 359.1 | Cordel 755S | AB_755S_DSS | Paintearth 863S | AB_863S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 1021
| 7L15 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Kinosis 856S | AB_856S_DSS | Long Lake Cogen 864S | AB_864S_GSS |  |  | 661
| 7L88 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Saddle Hills 865S JCT | AB_865S_JCT | Saddle Hills 865S | AB_865S_GSS |  |  | 797
| 7L22 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Clairmont Lake 811S | AB_811S_DSS | Saddle Hills 865S JCT | AB_865S_JCT | AESO. 2015. Eureka Connection Assessment |  | 688
| 521AL | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 72 | 7.7286 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Sundance Blow-Down 867S JCT | AB_867S_JCT | Sundance Blow-Down 867S | AB_867S_DSS |  |  | 295
| 521L | Altalink Management Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 72 | 11.5929 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Sundance 310P | AB_310P_GSS | Sundance Blow-Down 867S JCT | AB_867S_JCT |  |  | 294
| 7LA12 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Seal Lake 869S JCT | AB_869S_JCT | Seal Lake 869S | AB_869S_DSS |  |  | 629
| 7L12 | ATCO Electric Ltd. | Alberta | 1 | ac | 35 | 21.6049 | 144 | 15.325 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Wesley Creek 834S | AB_834S_DSS | Seal Lake 869S JCT | AB_869S_JCT | AESO. 2014. Carmon Creek Connection Assessment |  | 627
| 805L | Altalink Management Ltd. | Alberta | 1 | ac | 60 | 37.037 | 144 | 26.2714 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Pigeon Lake 964S | AB_964S_DSS | Bigstone 86S | AB_86S_DSS |  |  | 821
| 914L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 240 | 11.9213 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Saunders Lake 289S | AB_289S_DSS | Bigstone 86S | AB_86S_DSS |  |  | 946
| 6L02 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 72 | 6.9557 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Mannix Mine 765S JCT | AB_765S_JCT | Marion Lake 873S | AB_873S_DSS |  |  | 370
| 9L43 | ATCO Electric Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 240 | 2.8611 |  |  | 457 | 578 | 0.9 | n/a | 411.3 | 520.2 | Dover 888S | AB_888S_DSS | Mackay River 874S | AB_874S_GSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1031
| 7L170 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Dawes 2011S | AB_2011S_DSS | Algar 875S | AB_875S_DSS |  |  | 676
| 7L38 | ATCO Electric Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 144 | 7.356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Horse River 917S | AB_917S_DSS | Algar 875S | AB_875S_DSS |  |  | 712
| 9L10 | ATCO Electric Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 240 | 19.0741 |  |  | 491 | 658 | 0.9 | n/a | 441.9 | 592.2 | Livock 939S | AB_939S_DSS | Brintnell 876S | AB_876S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1008
| 7L94 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Cranberry Lake 827S | AB_827S_DSS | Kidney Lake 878S | AB_878S_DSS |  |  | 809
| 914L | Altalink Management Ltd. | Alberta | 1 | ac | 100 | 61.7284 | 240 | 47.6852 |  |  |  |  | 0.9 | 2.796 | 408.7589 | 443.6667 | Bigstone 86S | AB_86S_DSS | Gaetz 87S | AB_87S_DSS |  |  | 947
| 756L | Altalink Management Ltd. | Alberta | 1 | ac | 22.5 | 13.8889 | 144 | 9.8518 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Joffre 535S | AB_535S_GSS | Gaetz 87S | AB_87S_DSS |  |  | 540
| 793L | Altalink Management Ltd. | Alberta | 1 | ac | 22.5 | 13.8889 | 144 | 9.8518 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Joffre 535S | AB_535S_GSS | Gaetz 87S | AB_87S_DSS |  |  | 591
| 7LB749 | ATCO Electric Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Briker 880S JCT | AB_880S_JCT | Briker 880S | AB_880S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 779
| 7L749 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Lloydminster 716S | AB_716S_DSS | Briker 880S JCT | AB_880S_JCT | AESO. 2017. Irma Connection Assessment |  | 777
| 7L01 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Little Smoky 813S | AB_813S_DSS | Sturgeon 2 881S | AB_881S_DSS |  |  | 601
| 7LA48 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Triangle 882S JCT | AB_882S_JCT | Triangle 882S | AB_882S_DSS |  |  | 728
| 7L48 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | High Prairie 787S | AB_787S_DSS | Triangle 882S JCT | AB_882S_JCT | AESO. 2014. Carmon Creek Connection Assessment |  | 726
| 7L02 | ATCO Electric Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 144 | 5.517 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Crow 860S | AB_860S_DSS | Mcmillan 885S | AB_885S_DSS |  |  | 602
| 7L34 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | Goodfare 815S | AB_815S_DSS | Updike 886S | AB_886S_DSS | AESO. 2016. Hughes Connection Assessment |  | 709
| 520L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Mobil Oil Carson Creek 887S JCT | AB_887S_JCT | Mobil Oil Carson Creek 887S | AB_887S_ISS |  |  | 293
| 526L | Altalink Management Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Pegasus Lake 659S JCT | AB_659S_JCT | Mobil Oil Carson Creek 887S JCT | AB_887S_JCT |  |  | 299
| 7L95 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  | 190 | 190 | 0.9 | n/a | 171 | 171 | Leming Lake 715S | AB_715S_DSS | Mahkeses 889S | AB_889S_GSS | AESO. 2016. Bauer 918S Connection Assessment |  | 810
| 7LA59 | ATCO Electric Ltd. | Alberta | 1 | ac | 10 | 6.1728 | 144 | 4.3786 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Melito 890S JCT | AB_890S_JCT | Melito 890S | AB_890S_DSS |  |  | 749
| 7L59 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Keg River 789S | AB_789S_DSS | Melito 890S JCT | AB_890S_JCT | AESO. 2014. Carmon Creek Connection Assessment |  | 747
| 7L79 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Veteran 771S | AB_771S_DSS | Ribstone Creek 892S | AB_892S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 787
| 100L | Altalink Management Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 138 | 19.5107 |  |  | 78 | 86 | 0.9 | n/a | 70.2 | 77.4 | Tilley 498S | AB_498S_DSS | Suffield 895S | AB_895S_GSS | AESO. 2018. Whitla Connection Assessment |  | 10
| 7L749 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 88 | 127 | 0.9 | n/a | 79.2 | 114.3 | Briker 880S JCT | AB_880S_JCT | Edgerton 899S | AB_899S_DSS | AESO. 2017. Irma Connection Assessment |  | 778
| 749L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 88 | 96 | 0.9 | n/a | 79.2 | 86.4 | Killarney Lake 267S JCT | AB_267S_JCT | Edgerton 899S | AB_899S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 525
| 947L | Altalink Management Ltd. | Alberta | 1 | ac | 23.575 | 14.5525 | 240 | 11.2418 |  |  | 493 | 611 | 0.9 | n/a | 443.7 | 549.9 | Clover Bar 987S | AB_987S_GSS | Ellerslie 89S | AB_89S_DSS | AESO. 2020. Summerside Connection Assessment |  | 979
| 909L | Altalink Management Ltd. | Alberta | 1 | ac | 27 | 16.6667 | 240 | 12.875 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Dome 665S | AB_665S_DSS | Ellerslie 89S | AB_89S_DSS | AESO. 2020. Summerside Connection Assessment |  | 938
| 908L | Altalink Management Ltd. | Alberta | 1 | ac | 39 | 24.0741 | 240 | 18.5972 |  |  | 505 | 648 | 0.9 | n/a | 454.5 | 583.2 | Petrolia 816S | AB_816S_DSS | Ellerslie 89S | AB_89S_DSS | AESO. 2020. Summerside Connection Assessment |  | 934
| 1057L | Altalink Management Ltd. | Alberta | 1 | ac | 4.6 | 2.8395 | 240 | 2.1935 |  |  | 594 | 713 | 0.9 | n/a | 534.6 | 641.7 | Summerside 657S | AB_657S_DSS | Ellerslie 89S | AB_89S_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 35
| 1112L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Saunders Lake 289S | AB_289S_DSS | Ellerslie 89S | AB_89S_DSS |  |  | 63
| 1140L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Saunders Lake 289S | AB_289S_DSS | Ellerslie 89S | AB_89S_DSS |  |  | 72
| 7L110 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Monitor 774S | AB_774S_DSS | Loyalist 903S | AB_903S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 620
| 7L131 | ATCO Electric Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 144 | 35.0286 |  |  | 299 | 299 | 0.9 | n/a | 269.1 | 269.1 | Wesley Creek 834S | AB_834S_DSS | Meikle 905S | AB_905S_DSS | AESO. 2015. Eureka Connection Assessment |  | 647
| 7L120 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Hotchkiss 788S | AB_788S_DSS | Meikle 905S | AB_905S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 630
| 7L138 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 144 | 13.1357 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Hotchkiss 788S | AB_788S_DSS | Meikle 905S | AB_905S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 652
| 7L106 | ATCO Electric Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 144 | 35.0286 |  |  | 300 | 300 | 0.9 | n/a | 270 | 270 | Wesley Creek 834S | AB_834S_DSS | Meikle 905S | AB_905S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 618
| 787AL | Altalink Management Ltd. | Alberta | 1 | ac | 2 | 1.2346 | 144 | 0.87571 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Ross Creek 906S JCT | AB_906S_JCT | Ross Creek 906S | AB_906S_DSS |  |  | 581
| 787L | Altalink Management Ltd. | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Lamoureux 71S | AB_71S_DSS | Ross Creek 906S JCT | AB_906S_JCT |  |  | 579
| 7L114 | ATCO Electric Ltd. | Alberta | 1 | ac | 18.48 | 11.4074 | 144 | 8.0916 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Chard 658S JCT | AB_658S_JCT | Waddel 907S | AB_907S_DSS |  |  | 623
| 7L105 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Mahihkan 837S | AB_837S_DSS | Mahno 909S | AB_909S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 617
| 7L116 | ATCO Electric Ltd. | Alberta | 1 | ac | 8 | 4.9383 | 138 | 3.4686 |  |  | 95 | 95 | 0.9 | n/a | 85.5 | 85.5 | Lanfine 959S | AB_959S_DSS | Excel 910S | AB_910S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 625
| 7LA760 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Bindloss 914S JCT | AB_914S_JCT | Bindloss 914S | AB_914S_DSS |  |  | 783
| 760L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 144 | 4.5975 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Empress Liquids 164S JCT | AB_164S_JCT | Bindloss 914S JCT | AB_914S_JCT |  |  | 547
| 7LA129 | ATCO Electric Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Bauer 918S JCT | AB_918S_JCT | Bauer 918S | AB_918S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 641
| 7L129 | ATCO Electric Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 138 | 5.2029 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | Vermilion 710S | AB_710S_DSS | Bauer 918S JCT | AB_918S_JCT | AESO. 2017. Paintearth Connection Assessment |  | 639
| 7L51 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 99 | 99 | 0.9 | n/a | 89.1 | 89.1 | Hotchkiss 788S | AB_788S_DSS | Buchanan Creek 927S | AB_927S_DSS | AESO. 2015. Eureka Connection Assessment |  | 732
| 180L | Altalink Management Ltd. | Alberta | 1 | ac | 24.5 | 15.1235 | 138 | 10.6225 |  |  | 112 | 135 | 0.9 | n/a | 100.8 | 121.5 | Fort Macleod 15S | AB_15S_GSS | East Stavely 928S | AB_928S_DSS | AESO. 2019. Travers Connection Assessment |  | 126
| 792L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 138 | 6.5036 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | N.W. Cardiff 191S | AB_191S_DSS | Viscount 92S | AB_92S_DSS | AESO. 2016. Plamondon Connection Assessment |  | 590
| 7L64 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 75 | 90 | 0.9 | n/a | 67.5 | 81 | Bassett 747S | AB_747S_DSS | Arcenciel 930S | AB_930S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 760
| 7L109 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 165 | 211 | 0.9 | n/a | 148.5 | 189.9 | Rainbow Lake 791S | AB_791S_GSS | Arcenciel 930S | AB_930S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 619
| 7L122 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 165 | 211 | 0.9 | n/a | 148.5 | 189.9 | Rainbow Lake 791S | AB_791S_GSS | Arcenciel 930S | AB_930S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 634
| 7L113 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  | 114 | 145 | 0.9 | n/a | 102.6 | 130.5 | Ring Creek 853S | AB_853S_DSS | Arcenciel 930S | AB_930S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 621
| 7L93 | ATCO Electric Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 144 | 8.7571 |  |  | 114 | 146 | 0.9 | n/a | 102.6 | 131.4 | Sulphur Point 828S | AB_828S_DSS | Arcenciel 930S | AB_930S_DSS | AESO. 2014. Carmon Creek Connection Assessment |  | 808
| 7L05 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Kettle River 2049S | AB_2049S_DSS | Bohn 931S | AB_931S_DSS |  |  | 606
| 7L127 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 126.5 | 126.5 | 0.9 | n/a | 113.85 | 113.85 | Monitor 774S | AB_774S_DSS | Pemukan 932S | AB_932S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 637
| 7L141 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Monitor 774S | AB_774S_DSS | Pemukan 932S | AB_932S_DSS |  |  | 657
| 9L39 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  | 560 | 753 | 0.9 | n/a | 504 | 677.7 | Green Stocking 925S | AB_925S_DSS | Black Fly 934S | AB_934S_ISS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1029
| 9L77 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  | 560 | 753 | 0.9 | n/a | 504 | 677.7 | Green Stocking 925S | AB_925S_DSS | Black Fly 934S | AB_934S_ISS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1045
| 9L69 | ATCO Electric Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 240 | 14.0194 |  |  | 777 | 831 | 0.9 | n/a | 699.3 | 747.9 | Mcclelland 957S | AB_957S_DSS | Black Fly 934S | AB_934S_ISS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1042
| 9L84 | ATCO Electric Ltd. | Alberta | 1 | ac | 60 | 37.037 | 240 | 28.6111 |  |  | 775 | 831 | 0.9 | n/a | 697.5 | 747.9 | Salt Creek 977S | AB_977S_DSS | Black Fly 934S | AB_934S_ISS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1049
| 7LA139 | ATCO Electric Ltd. | Alberta | 1 | ac | 4.8 | 2.963 | 144 | 2.1017 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Norberg 936S JCT | AB_936S_JCT | Norberg 936S | AB_936S_DSS |  |  | 655
| 7L139 | ATCO Electric Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 138 | 10.4057 |  |  | 109.3 | 139 | 0.9 | n/a | 98.37 | 125.1 | St. Paul 707S | AB_707S_DSS | Norberg 936S JCT | AB_936S_JCT | AESO. 2018. Wheatland Connection Assessment |  | 653
| 12L41 | Altalink Management Ltd. | Alberta | 1 | ac | 360 | 222.2222 | 500 | 142.2 |  |  |  |  | 0.9 | 1.2013 | 1021.1239 | 1291.4214 | Sunnybrook 510S | AB_510S_DSS | Livock 939S | AB_939S_DSS |  |  | 85
| 12L44 | Altalink Management Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 500 | 31.6 |  |  |  |  | 0.9 | 3 | 2550 | 3225 | Thickwood Hills 951S | AB_951S_DSS | Livock 939S | AB_939S_DSS |  |  | 86
| 7LA24 | ATCO Electric Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Beartrap 940S JCT | AB_940S_JCT | Beartrap 940S | AB_940S_DSS |  |  | 698
| 7L24 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  | 109 | 139 | 0.9 | n/a | 98.1 | 125.1 | Bonnyville 700S | AB_700S_DSS | Beartrap 940S JCT | AB_940S_JCT | AESO. 2016. Bauer 918S Connection Assessment |  | 696
| 9L32 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  | 761 | 831 | 0.9 | n/a | 684.9 | 747.9 | Joslyn Creek 849S | AB_849S_DSS | Bitumount 941S | AB_941S_ISS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1025
| 7L161 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mahno 909S | AB_909S_DSS | Nabiye 942S | AB_942S_GSS |  |  | 672
| 551L | Altalink Management Ltd. | Alberta | 1 | ac | 8.4 | 5.1852 | 72 | 3.246 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Banff 123S | AB_123S_DSS | Sunshine Village 945S | AB_945S_DSS |  |  | 310
| 7L437 | ATCO Electric Ltd. | Alberta | 1 | ac | 16.8 | 10.3704 | 144 | 7.356 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | ABEE 993S | AB_993S_DSS | Weasel Creek 947S | AB_947S_DSS |  |  | 719
| 808AL | Altalink Management Ltd. | Alberta | 1 | ac | 12.6 | 7.7778 | 144 | 5.517 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Weasel Creek 947S JCT | AB_947S_JCT | Weasel Creek 947S | AB_947S_DSS |  |  | 827
| 808L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 138 | 8.6714 |  |  | 98 | 114 | 0.9 | n/a | 88.2 | 102.6 | Redwater 171S | AB_171S_DSS | Weasel Creek 947S JCT | AB_947S_JCT | AESO. 2018. Strathcona CG Connection Assessment |  | 825
| 7L16 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 138 | 9.105 |  |  | 109.3 | 126.5 | 0.9 | n/a | 98.37 | 113.85 | Nevis 766S | AB_766S_DSS | Heatburg 948S | AB_948S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 670
| 7L125 | ATCO Electric Ltd. | Alberta | 1 | ac | 25.2 | 15.5556 | 144 | 11.034 |  |  | 164 | 210 | 0.9 | n/a | 147.6 | 189 | Livock 939S | AB_939S_DSS | Germain 950S | AB_950S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 635
| 9L07 | ATCO Electric Ltd. | Alberta | 1 | ac | 40 | 24.6914 | 240 | 19.0741 |  |  | 640 | 811 | 0.9 | n/a | 576 | 729.9 | Dawes 2011S | AB_2011S_DSS | Thickwood Hills 951S | AB_951S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1005
| 9L112 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 240 | 11.9213 |  |  | 457 | 578 | 0.9 | n/a | 411.3 | 520.2 | Dover 888S | AB_888S_DSS | Thickwood Hills 951S | AB_951S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1012
| 9L30 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 457 | 578 | 0.9 | n/a | 411.3 | 520.2 | Dover 888S | AB_888S_DSS | Thickwood Hills 951S | AB_951S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1024
| 9L01 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 240 | 11.9213 |  |  | 641 | 808 | 0.9 | n/a | 576.9 | 727.2 | Ruth Lake 848S | AB_848S_DSS | Thickwood Hills 951S | AB_951S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1002
| 551L | Altalink Management Ltd. | Alberta | 1 | ac | 8.4 | 5.1852 | 72 | 3.246 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Sunshine Village 945S | AB_945S_DSS | Lake Louise 953S | AB_953S_DSS |  |  | 311
| 7LA92 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Watt Lake 956S JCT | AB_956S_JCT | Watt Lake 956S | AB_956S_DSS |  |  | 807
| 7L92 | ATCO Electric Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 138 | 3.9021 |  |  | 95 | 95 | 0.9 | n/a | 85.5 | 85.5 | Vilna 777S | AB_777S_DSS | Watt Lake 956S JCT | AB_956S_JCT | AESO. 2018. Wheatland Connection Assessment |  | 805
| 9L46 | ATCO Electric Ltd. | Alberta | 1 | ac | 80 | 49.3827 | 240 | 38.1481 |  |  | 332 | 332 | 0.9 | n/a | 298.8 | 298.8 | Pemukan 932S | AB_932S_DSS | Lanfine 959S | AB_959S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 1033
| 9L24 | ATCO Electric Ltd. | Alberta | 1 | ac | 95 | 58.642 | 240 | 45.3009 |  |  | 332 | 332 | 0.9 | n/a | 298.8 | 298.8 | Oakland 946S | AB_946S_DSS | Lanfine 959S | AB_959S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 1020
| 737L | Altalink Management Ltd. | Alberta | 1 | ac | 7.475 | 4.6142 | 138 | 3.2409 |  |  | 103 | 135 | 0.9 | n/a | 92.7 | 121.5 | East Edmonton 38S | AB_38S_DSS | Imperial Oil Edmonton 95S | AB_95S_ISS | AESO. 2016. Henday Connection Assessment |  | 494
| 9L28 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  | 433 | 498 | 0.9 | n/a | 389.7 | 448.2 | AMR02 937S | AB_937S_ISS | Birchwood Creek 960S | AB_960S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1022
| 9L74 | ATCO Electric Ltd. | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  | 423 | 575 | 0.9 | n/a | 380.7 | 517.5 | Dover 888S | AB_888S_DSS | Birchwood Creek 960S | AB_960S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1044
| 9L57 | ATCO Electric Ltd. | Alberta | 1 | ac | 63 | 38.8889 | 240 | 30.0417 |  |  | 493 | 660 | 0.9 | n/a | 443.7 | 594 | Livock 939S | AB_939S_DSS | Birchwood Creek 960S | AB_960S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1038
| 9L19 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 240 | 10.0139 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | AMR02 937S | AB_937S_ISS | Birchwood Creek 960S | AB_960S_DSS |  |  | 1016
| 9L29 | ATCO Electric Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 240 | 20.0278 |  |  | 332 | 332 | 0.9 | n/a | 298.8 | 298.8 | Oakland 946S | AB_946S_DSS | Coyote Lake 963S | AB_963S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 1023
| 7L128 | ATCO Electric Ltd. | Alberta | 1 | ac | 27 | 16.6667 | 138 | 11.7064 |  |  | 180.1 | 217.5 | 0.9 | n/a | 162.09 | 195.75 | Michichi Creek 802S | AB_802S_DSS | Coyote Lake 963S | AB_963S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 638
| 837L | Altalink Management Ltd. | Alberta | 1 | ac | 42 | 25.9259 | 144 | 18.39 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Buford 538S | AB_538S_DSS | Pigeon Lake 964S | AB_964S_DSS |  |  | 859
| 7LA53 | ATCO Electric Ltd. | Alberta | 1 | ac | 18 | 11.1111 | 144 | 7.8814 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Lindbergh 969S JCT | AB_969S_JCT | Lindbergh 969S | AB_969S_GSS |  |  | 736
| 7L53 | ATCO Electric Ltd. | Alberta | 1 | ac | 50 | 30.8642 | 138 | 21.6786 |  |  | 123.6 | 150.4 | 0.9 | n/a | 111.24 | 135.36 | Bonnyville 700S | AB_700S_DSS | Lindbergh 969S JCT | AB_969S_JCT | AESO. 2018. Wheatland Connection Assessment |  | 734
| 7L146 | ATCO Electric Ltd. | Alberta | 1 | ac | 60 | 37.037 | 144 | 26.2714 |  |  | 191 | 191 | 0.9 | n/a | 171.9 | 171.9 | Bonnyville 700S | AB_700S_DSS | Bourque 970S | AB_970S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 659
| 7L574 | ATCO Electric Ltd. | Alberta | 1 | ac | 24 | 14.8148 | 144 | 10.5086 |  |  | 247 | 286 | 0.9 | n/a | 222.3 | 257.4 | Wolf Lake 822S | AB_822S_DSS | Bourque 970S | AB_970S_DSS | AESO. 2016. Bauer 918S Connection Assessment |  | 743
| 9L16 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  | 549 | 663 | 0.9 | n/a | 494.1 | 596.7 | Cordel 755S | AB_755S_DSS | Tinchebray 972S | AB_972S_DSS | AESO. 2018. Wheatland Connection Assessment |  | 1015
| 9L59 | ATCO Electric Ltd. | Alberta | 1 | ac | 120 | 74.0741 | 240 | 57.2222 |  |  | 549 | 701 | 0.9 | n/a | 494.1 | 630.9 | Anderson 801S | AB_801S_DSS | Tinchebray 972S | AB_972S_DSS | AESO. 2017. Sharphills Connection Assessment |  | 1040
| 9L93 | ATCO Electric Ltd. | Alberta | 1 | ac | 7.2 | 4.4444 | 240 | 3.4333 |  |  | 249 | 249 | 0.9 | n/a | 224.1 | 224.1 | Halkirk 615S | AB_615S_GSS | Tinchebray 972S | AB_972S_DSS | AESO. 2017. Paintearth Connection Assessment |  | 1052
| 745A1L | Altalink Management Ltd. | Alberta | 1 | ac | 9 | 5.5556 | 144 | 3.9407 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Dalehurst 975S JCT | AB_975S_JCT | Dalehurst 975S | AB_975S_DSS |  |  | 517
| 745AL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 144 | 2.6271 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mountain Coalbed 411S JCT | AB_411S_JCT | Dalehurst 975S JCT | AB_975S_JCT |  |  | 515
| 7L135 | ATCO Electric Ltd. | Alberta | 1 | ac | 29.4 | 18.1481 | 144 | 12.873 |  |  | 151 | 190 | 0.9 | n/a | 135.9 | 171 | Hangingstone 820S | AB_820S_DSS | Salt Creek 977S | AB_977S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 650
| 9L23 | ATCO Electric Ltd. | Alberta | 1 | ac | 55 | 33.9506 | 240 | 26.2269 |  |  | 553 | 742 | 0.9 | n/a | 497.7 | 667.8 | Ruth Lake 848S | AB_848S_DSS | Salt Creek 977S | AB_977S_DSS | AESO. 2020. Suncor Base Plant Connection Assessment |  | 1019
| 501CL | Altalink Management Ltd. | Alberta | 1 | ac | 6 | 3.7037 | 72 | 2.3186 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Cadomin 983S JCT | AB_983S_JCT | Cadomin 983S | AB_983S_DSS |  |  | 281
| 501L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 72 | 4.6371 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Cardinal River 302S | AB_302S_DSS | Cadomin 983S JCT | AB_983S_JCT |  |  | 279
| 742L | Altalink Management Ltd. | Alberta | 1 | ac | 10.5 | 6.4815 | 138 | 4.5525 |  |  | 85 | 90 | 0.9 | n/a | 76.5 | 81 | Exshaw 985S JCT | AB_985S_JCT | Exshaw 985S | AB_985S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 507
| 754L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 112 | 120 | 0.9 | n/a | 100.8 | 108 | Seebe 245S | AB_245S_DSS | Exshaw 985S JCT | AB_985S_JCT | AESO. 2018. Mount Allan Connection Assessment |  | 535
| 921L | Altalink Management Ltd. | Alberta | 1 | ac | 20 | 12.3457 | 240 | 9.537 |  |  | 417 | 499 | 0.9 | n/a | 375.3 | 449.1 | Lamoureux 71S | AB_71S_DSS | Clover Bar 987S | AB_987S_GSS | AESO. 2020. Summerside Connection Assessment |  | 956
| 7L167 | ATCO Electric Ltd. | Alberta | 1 | ac | 21 | 12.963 | 144 | 9.195 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Engstrom 2060S | AB_2060S_DSS | Quigley 989S | AB_989S_DSS |  |  | 675
| 7L104 | ATCO Electric Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 144 | 10.9464 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Kinosis 856S | AB_856S_DSS | Quigley 989S | AB_989S_DSS |  |  | 616
| L9900 | Imperial Oil | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Mcclelland 957S | AB_957S_DSS | Kearl 9900S | AB_9900S_GSS |  |  | 1072
| 185AL | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 72 | 5.41 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Drywood 415S | AB_415S_DSS | Rangeland Yarrow 995S | AB_995S_DSS |  |  | 130
| 519AL | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 72 | 4.6371 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Imperial Oil Carson Lake 996S JCT | AB_996S_JCT | Imperial Oil Carson Lake 996S | AB_996S_ISS |  |  | 292
| 519L | Altalink Management Ltd. | Alberta | 1 | ac | 45 | 27.7778 | 72 | 17.3893 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Laura Lake 661S JCT | AB_661S_JCT | Imperial Oil Carson Lake 996S JCT | AB_996S_JCT |  |  | 290
| 7L13 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Albright & Wilson 752S | AB_752S_ISS | P&G A808S | AB_A808S_DSS |  |  | 644
| KVAL-1 | Syncrude | Alberta | 1 | ac | 71.4 | 44.0741 | 240 | 34.0472 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Aurora G01 | AB_G01S_DSS | Syncrude D05 | AB_D05S_ISS |  |  | 1070
| KVAL-2 | Syncrude | Alberta | 1 | ac | 71.4 | 44.0741 | 240 | 34.0472 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Aurora G01 | AB_G01S_DSS | Syncrude D05 | AB_D05S_ISS |  |  | 1071
| RL1 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Ruth Lake 848S | AB_848S_DSS | Syncrude D05 | AB_D05S_ISS |  |  | 1076
| RL2 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Ruth Lake 848S | AB_848S_DSS | Syncrude D05 | AB_D05S_ISS |  |  | 1077
| 29PL6-24 | Suncor | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-8 | AB_E8S_ISS | 29EDD-10 | AB_E10S_ISS |  |  | 190
| 29PL7-2 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | 29EDD-0063 | AB_E63S_ISS | 29EDD-18 | AB_E18S_ISS |  |  | 204
| 29PL7-5 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | 29EDD-71 | AB_E71S_ISS | 29EDD-18 | AB_E18S_ISS |  |  | 207
| 29PL6-23 | Suncor | Alberta | 1 | ac | 20 | 12.3457 | 72 | 7.7286 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-0056 | AB_E56S_ISS | 29EDD-19 | AB_E19S_ISS |  |  | 186
| 29PL6-28 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-29 | AB_E29S_ISS | 29EDD-19 | AB_E19S_ISS |  |  | 200
| 29PL6-23 | Suncor | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-33 | AB_E33S_ISS | 29EDD-19 | AB_E19S_ISS |  |  | 187
| 29PL9-1 | Suncor | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Ruth Lake 848S | AB_848S_DSS | 29EDD-1 | AB_E1S_ISS |  |  | 208
| 29PL9-2 | Suncor | Alberta | 1 | ac | 10 | 6.1728 | 240 | 4.7685 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Ruth Lake 848S | AB_848S_DSS | 29EDD-1 | AB_E1S_ISS |  |  | 217
| 29PL6-14 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-0056 | AB_E56S_ISS | Athabasca Crossing EDD200 | AB_E200S_ISS |  |  | 181
| 29PL9-16 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-0056 | AB_E56S_ISS | Athabasca Crossing EDD200 | AB_E200S_ISS |  |  | 213
| 29PL6-20 | Suncor | Alberta | 1 | ac | 12.6 | 7.7778 | 72 | 4.869 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Horseshoe 737S | AB_737S_DSS | 29EDD-20 | AB_E20S_ISS |  |  | 183
| 29PL6-05 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-2 | AB_E2S_ISS | 29EDD-22 | AB_E22S_ISS |  |  | 177
| 29PL6-06 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-2 | AB_E2S_ISS | 29EDD-22 | AB_E22S_ISS |  |  | 179
| 29PL6-22 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-2 | AB_E2S_ISS | 29EDD-22 | AB_E22S_ISS |  |  | 185
| 29PL6-05 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-1 | AB_E1S_ISS | 29EDD-2 | AB_E2S_ISS |  |  | 176
| 29PL6-06 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-1 | AB_E1S_ISS | 29EDD-2 | AB_E2S_ISS |  |  | 178
| 29PL6-22 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-1 | AB_E1S_ISS | 29EDD-2 | AB_E2S_ISS |  |  | 184
| 29PL6-25 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-33 | AB_E33S_ISS | 29EDD-31 | AB_E31S_ISS |  |  | 193
| 29PL6-24 | Suncor | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-45 | AB_E45S_ISS | 29EDD-33 | AB_E33S_ISS |  |  | 192
| 29PL9-14 | Suncor | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-0056 | AB_E56S_ISS | 29EDD-34 | AB_E34S_ISS |  |  | 211
| 29PL9-15 | Suncor | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-0056 | AB_E56S_ISS | 29EDD-34 | AB_E34S_ISS |  |  | 212
| 29PL9-5 | Suncor | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-1 | AB_E1S_ISS | 29EDD-34 | AB_E34S_ISS |  |  | 220
| 29PL9-6 | Suncor | Alberta | 1 | ac | 30 | 18.5185 | 240 | 14.3056 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-1 | AB_E1S_ISS | 29EDD-34 | AB_E34S_ISS |  |  | 221
| 29PL7-1 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | 29EDD-18 | AB_E18S_ISS | 29EDD-34 | AB_E34S_ISS |  |  | 203
| 29PL9-12 | Suncor | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-65 | AB_E65S_ISS | 29EDD-34 | AB_E34S_ISS |  |  | 209
| 29PL9-13 | Suncor | Alberta | 1 | ac | 15 | 9.2593 | 240 | 7.1528 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-65 | AB_E65S_ISS | 29EDD-34 | AB_E34S_ISS |  |  | 210
| 29PL9-3 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-1 | AB_E1S_ISS | 29EDD-3 | AB_E3S_ISS |  |  | 218
| 29PL9-4 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-1 | AB_E1S_ISS | 29EDD-3 | AB_E3S_ISS |  |  | 219
| 29PL6-24 | Suncor | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-10 | AB_E10S_ISS | 29EDD-45 | AB_E45S_ISS |  |  | 191
| 29PL6-25 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-31 | AB_E31S_ISS | 29EDD-46 | AB_E46S_ISS |  |  | 194
| 1059AL | Altalink Management Ltd. | Alberta | 1 | ac | 2.07 | 1.2778 | 240 | 0.98708 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | East Industrial E52S JCT | AB_E52S_JCT | East Industrial E52S | AB_E52S_DSS | AESO. 2020. Summerside Connection Assessment |  | 39
| 908AL | Altalink Management Ltd. | Alberta | 1 | ac | 2.3 | 1.4198 | 240 | 1.0968 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | East Industrial E52S JCT | AB_E52S_JCT | East Industrial E52S | AB_E52S_DSS | AESO. 2020. Summerside Connection Assessment |  | 937
| 908L | Altalink Management Ltd. | Alberta | 1 | ac | 11.5 | 7.0988 | 240 | 5.4838 |  |  | 505 | 648 | 0.9 | n/a | 454.5 | 583.2 | Ellerslie 89S | AB_89S_DSS | East Industrial E52S JCT | AB_E52S_JCT | AESO. 2017. Clover Bar Connection Assessment |  | 935
| 1059L | Altalink Management Ltd. | Alberta | 1 | ac | 4.6 | 2.8395 | 240 | 2.1935 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Lambton E803S | AB_E803S_DSS | East Industrial E52S JCT | AB_E52S_JCT | AESO. 2015. Broadmoor Connection Assessment |  | 37
| 29PL6-01 | Suncor | Alberta | 1 | ac | 10.08 | 6.2222 | 72 | 3.8952 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Steepbak River 836S | AB_836S_DSS | 29EDD-55 | AB_E55S_ISS |  |  | 172
| 29PL6-02 | Suncor | Alberta | 1 | ac | 10.08 | 6.2222 | 72 | 3.8952 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Steepbak River 836S | AB_836S_DSS | 29EDD-55 | AB_E55S_ISS |  |  | 173
| 29PL6-07 | Suncor | Alberta | 1 | ac | 8.4 | 5.1852 | 72 | 3.246 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Steepbak River 836S | AB_836S_DSS | 29EDD-5 | AB_E5S_ISS |  |  | 180
| 29PL6-27 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-29 | AB_E29S_ISS | 29EDD-62 | AB_E62S_ISS |  |  | 199
| 29PL6-26 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-33 | AB_E33S_ISS | 29EDD-62 | AB_E62S_ISS |  |  | 198
| 29PL6-25 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-46 | AB_E46S_ISS | 29EDD-64 | AB_E64S_ISS |  |  | 195
| 29PL7-3 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | 29EDD-71 | AB_E71S_ISS | 29EDD-65 | AB_E65S_ISS |  |  | 205
| 29PL7-4 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 144 | 2.1893 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | 29EDD-71 | AB_E71S_ISS | 29EDD-65 | AB_E65S_ISS |  |  | 206
| 29PL6-29 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-0056 | AB_E56S_ISS | 29EDD-67 | AB_E67S_ISS |  |  | 201
| 29PL6-14 | Suncor | Alberta | 1 | ac | 12.6 | 7.7778 | 72 | 4.869 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Athabasca Crossing EDD200 | AB_E200S_ISS | 29EDD-7 | AB_E7S_ISS |  |  | 182
| 29PL9-16 | Suncor | Alberta | 1 | ac | 12.6 | 7.7778 | 72 | 4.869 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Athabasca Crossing EDD200 | AB_E200S_ISS | 29EDD-7 | AB_E7S_ISS |  |  | 214
| 1058L | Altalink Management Ltd. | Alberta | 1 | ac | 2.3 | 1.4198 | 240 | 1.0968 |  |  | 499 | 499 | 0.9 | n/a | 449.1 | 449.1 | Summerside 657S | AB_657S_DSS | Lambton E803S | AB_E803S_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 36
| 29PL6-25 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-84 | AB_E84S_ISS | 29EDD-83 | AB_E83S_ISS |  |  | 197
| 29PL6-25 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-64 | AB_E64S_ISS | 29EDD-84 | AB_E84S_ISS |  |  | 196
| 29PL6-24 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-9 | AB_E9S_ISS | 29EDD-8 | AB_E8S_ISS |  |  | 189
| 29PL6-29 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 72 | 1.9321 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-67 | AB_E67S_ISS | 29EDD-93 | AB_E93S_ISS |  |  | 202
| 29PL9-16 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-1 | AB_E1S_ISS | 29EDD-94 | AB_E94S_ISS |  |  | 215
| 29PL9-17 | Suncor | Alberta | 1 | ac | 5 | 3.0864 | 240 | 2.3843 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | 29EDD-1 | AB_E1S_ISS | 29EDD-94 | AB_E94S_ISS |  |  | 216
| 29PL6-24 | Suncor | Alberta | 1 | ac | 10 | 6.1728 | 72 | 3.8643 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | 29EDD-0056 | AB_E56S_ISS | 29EDD-9 | AB_E9S_ISS |  |  | 188
| 444L | Altalink Management Ltd. | Alberta | 1 | ac | 2.5 | 1.5432 | 144 | 1.0946 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | North Red Deer 217S | AB_217S_DSS | Red Deer North RD14S | AB_RD14S_DSS |  |  | 262
| 425L | Altalink Management Ltd. | Alberta | 1 | ac | 2.5 | 1.5432 | 144 | 1.0946 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | South Red Deer 194S | AB_194S_DSS | Red Deer Downtown RD15S | AB_RD15S_DSS |  |  | 253
| 426L | Altalink Management Ltd. | Alberta | 1 | ac | 2.5 | 1.5432 | 144 | 1.0946 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | South Red Deer 194S | AB_194S_DSS | Red Deer Downtown RD15S | AB_RD15S_DSS |  |  | 254
| 833L | Altalink Management Ltd. | Alberta | 1 | ac | 8.5 | 5.2469 | 144 | 3.7218 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | SS-12 | AB_SS12_DSS | SS-2 | AB_SS02_DSS |  |  | 852
| 3.82L | ENMAX Power Corporation | Alberta | 1 | ac | 5.1 | 3.1481 | 138 | 2.2112 |  |  | 156 | 191 | 0.9 | n/a | 140.4 | 171.9 | SS-8 | AB_SS08_DSS | SS-3 | AB_SS03_DSS | AESO. 2017. SS 7 Connection Assessment |  | 222
| 2.83L | ENMAX Power Corporation | Alberta | 1 | ac | 4 | 2.4691 | 138 | 1.7343 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-2 | AB_SS02_DSS | SS-5 | AB_SS05_DSS | AESO. 2017. SS 7 Connection Assessment |  | 140
| 1.82L | ENMAX Power Corporation | Alberta | 1 | ac | 3.4 | 2.0988 | 138 | 1.4741 |  |  | 226 | 228 | 0.9 | n/a | 203.4 | 205.2 | SS-1 | AB_SS01_DSS | SS-5 | AB_SS05_DSS | AESO. 2017. SS 7 Connection Assessment |  | 3
| 1.84L | ENMAX Power Corporation | Alberta | 1 | ac | 3.4 | 2.0988 | 138 | 1.4741 |  |  | 226 | 228 | 0.9 | n/a | 203.4 | 205.2 | SS-1 | AB_SS01_DSS | SS-5 | AB_SS05_DSS | AESO. 2017. SS 7 Connection Assessment |  | 5
| 2.82L | ENMAX Power Corporation | Alberta | 1 | ac | 5.95 | 3.6728 | 138 | 2.5798 |  |  | 322 | 349 | 0.9 | n/a | 289.8 | 314.1 | SS-2 | AB_SS02_DSS | SS-5 | AB_SS05_DSS | AESO. 2017. SS 7 Connection Assessment |  | 139
| 1.83L | ENMAX Power Corporation | Alberta | 1 | ac | 4.25 | 2.6235 | 138 | 1.8427 |  |  | 218 | 232 | 0.9 | n/a | 196.2 | 208.8 | SS-1 | AB_SS01_DSS | SS-8 | AB_SS08_DSS | AESO. 2017. SS 7 Connection Assessment |  | 4
| 1.85L | ENMAX Power Corporation | Alberta | 1 | ac | 4.25 | 2.6235 | 138 | 1.8427 |  |  | 218 | 232 | 0.9 | n/a | 196.2 | 208.8 | SS-1 | AB_SS01_DSS | SS-8 | AB_SS08_DSS | AESO. 2017. SS 7 Connection Assessment |  | 6
| 2.81L | ENMAX Power Corporation | Alberta | 1 | ac | 11.05 | 6.821 | 138 | 4.791 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-2 | AB_SS02_DSS | SS-9 | AB_SS09_DSS | AESO. 2017. SS 7 Connection Assessment |  | 138
| 9.80L | ENMAX Power Corporation | Alberta | 1 | ac | 5.1 | 3.1481 | 138 | 2.2112 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-31 | AB_SS31_DSS | SS-9 | AB_SS09_DSS | AESO. 2017. SS 7 Connection Assessment |  | 923
| 9.83L | ENMAX Power Corporation | Alberta | 1 | ac | 5.95 | 3.6728 | 138 | 2.5798 |  |  | 191 | 191 | 0.9 | n/a | 171.9 | 171.9 | SS-43 | AB_SS43_DSS | SS-9 | AB_SS09_DSS | AESO. 2017. SS 7 Connection Assessment |  | 924
| 693L | Altalink Management Ltd. | Alberta | 1 | ac | 7.65 | 4.7222 | 144 | 3.3496 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sarcee 42S | AB_42S_DSS | SS-10 | AB_SS10_DSS |  |  | 368
| 832L | Altalink Management Ltd. | Alberta | 1 | ac | 4.25 | 2.6235 | 144 | 1.8609 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | SS-12 | AB_SS12_DSS | SS-10 | AB_SS10_DSS |  |  | 851
| 11.83L | ENMAX Power Corporation | Alberta | 1 | ac | 5.95 | 3.6728 | 138 | 2.5798 |  |  | 305 | 379 | 0.9 | n/a | 274.5 | 341.1 | Beddington 162S | AB_162S_DSS | SS-11 | AB_SS11_DSS | AESO. 2017. SS 7 Connection Assessment |  | 59
| 11.81L | ENMAX Power Corporation | Alberta | 1 | ac | 2.55 | 1.5741 | 138 | 1.1056 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-11 | AB_SS11_DSS | SS-13 | AB_SS13_DSS | AESO. 2017. SS 7 Connection Assessment |  | 57
| 13.82L | ENMAX Power Corporation | Alberta | 1 | ac | 3.91 | 2.4136 | 138 | 1.6953 |  |  | 161 | 204 | 0.9 | n/a | 144.9 | 183.6 | SS-22 | AB_SS22_DSS | SS-13 | AB_SS13_DSS | AESO. 2017. SS 7 Connection Assessment |  | 90
| 13.60L | ENMAX Power Corporation | Alberta | 1 | ac | 6.8 | 4.1975 | 69 | 2.6131 |  |  | 66 | 72 | 0.9 | n/a | 59.4 | 64.8 | SS-27 | AB_SS27_DSS | SS-13 | AB_SS13_DSS | AESO. 2017. SS 7 Connection Assessment |  | 89
| 3.84L | ENMAX Power Corporation | Alberta | 1 | ac | 6.8 | 4.1975 | 138 | 2.9483 |  |  | 161 | 191 | 0.9 | n/a | 144.9 | 171.9 | SS-3 | AB_SS03_DSS | SS-13 | AB_SS13_DSS | AESO. 2017. SS 7 Connection Assessment |  | 223
| 2.83L | ENMAX Power Corporation | Alberta | 1 | ac | 5 | 3.09 | 138 | 2.1679 |  |  | 338 | 354 | 0.9 | n/a | 304.2 | 318.6 | SS-5 | AB_SS05_DSS | SS-13 | AB_SS13_DSS | AESO. 2017. SS 7 Connection Assessment |  | 142
| 11.82L | ENMAX Power Corporation | Alberta | 1 | ac | 8.5 | 5.2469 | 138 | 3.6854 |  |  | 161 | 191 | 0.9 | n/a | 144.9 | 171.9 | SS-11 | AB_SS11_DSS | SS-14 | AB_SS14_DSS | AESO. 2017. SS 7 Connection Assessment |  | 58
| 14.83L | ENMAX Power Corporation | Alberta | 1 | ac | 10.2 | 6.2963 | 138 | 4.4224 |  |  | 176 | 215 | 0.9 | n/a | 158.4 | 193.5 | SS-36 | AB_SS36_DSS | SS-14 | AB_SS14_DSS | AESO. 2017. SS 7 Connection Assessment |  | 96
| 15.62L | ENMAX Power Corporation | Alberta | 1 | ac | 5.1 | 3.1481 | 69 | 1.9599 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | SS-15 | AB_SS15_DSS | SS-16 | AB_SS16_DSS | AESO. 2017. SS 7 Connection Assessment |  | 98
| 16.61L | ENMAX Power Corporation | Alberta | 1 | ac | 3.4 | 2.0988 | 69 | 1.3066 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | SS-27 | AB_SS27_DSS | SS-16 | AB_SS16_DSS | AESO. 2017. SS 7 Connection Assessment |  | 107
| 16.60L | ENMAX Power Corporation | Alberta | 1 | ac | 3.4 | 2.0988 | 69 | 1.3066 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | SS-34 | AB_SS34_DSS | SS-16 | AB_SS16_DSS | AESO. 2017. SS 7 Connection Assessment |  | 106
| 16.63L | ENMAX Power Corporation | Alberta | 1 | ac | 5.95 | 3.6728 | 69 | 2.2865 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | SS-36 | AB_SS36_DSS | SS-16 | AB_SS16_DSS | AESO. 2017. SS 7 Connection Assessment |  | 108
| 1.81L | ENMAX Power Corporation | Alberta | 1 | ac | 7.65 | 4.7222 | 138 | 3.3168 |  |  | 160 | 177 | 0.9 | n/a | 144 | 159.3 | SS-1 | AB_SS01_DSS | SS-20 | AB_SS20_DSS | AESO. 2017. SS 7 Connection Assessment |  | 2
| 20.82L | ENMAX Power Corporation | Alberta | 1 | ac | 5.1 | 3.1481 | 138 | 2.2112 |  |  | 160 | 191 | 0.9 | n/a | 144 | 171.9 | SS-21 | AB_SS21_DSS | SS-20 | AB_SS20_DSS | AESO. 2017. SS 7 Connection Assessment |  | 143
| 21.80L | ENMAX Power Corporation | Alberta | 1 | ac | 5.95 | 3.6728 | 138 | 2.5798 |  |  | 236 | 262 | 0.9 | n/a | 212.4 | 235.8 | Sarcee 42S | AB_42S_DSS | SS-21 | AB_SS21_DSS | AESO. 2017. SS 7 Connection Assessment |  | 151
| 15.60L | ENMAX Power Corporation | Alberta | 1 | ac | 8.5 | 5.2469 | 69 | 3.2664 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | SS-15 | AB_SS15_DSS | SS-21 | AB_SS21_DSS | AESO. 2017. SS 7 Connection Assessment |  | 97
| 21.61L | ENMAX Power Corporation | Alberta | 1 | ac | 12.75 | 7.8704 | 69 | 4.8996 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | SS-34 | AB_SS34_DSS | SS-21 | AB_SS21_DSS | AESO. 2017. SS 7 Connection Assessment |  | 150
| 23.80L | ENMAX Power Corporation | Alberta | 1 | ac | 4.25 | 2.6235 | 138 | 1.8427 |  |  | 285 | 287 | 0.9 | n/a | 256.5 | 258.3 | Janet 74S | AB_74S_DSS | SS-23 | AB_SS23_DSS | AESO. 2017. SS 7 Connection Assessment |  | 160
| 2.80L | ENMAX Power Corporation | Alberta | 1 | ac | 7.65 | 4.7222 | 138 | 3.3168 |  |  | 285 | 350 | 0.9 | n/a | 256.5 | 315 | SS-2 | AB_SS02_DSS | SS-23 | AB_SS23_DSS | AESO. 2017. SS 7 Connection Assessment |  | 137
| 24.83L | ENMAX Power Corporation | Alberta | 1 | ac | 10.2 | 6.2963 | 138 | 4.4224 |  |  | 322 | 408 | 0.9 | n/a | 289.8 | 367.2 | Janet 74S | AB_74S_DSS | SS-24 | AB_SS24_DSS | AESO. 2017. SS 7 Connection Assessment |  | 164
| 24.81L | ENMAX Power Corporation | Alberta | 1 | ac | 7.65 | 4.7222 | 138 | 3.3168 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-31 | AB_SS31_DSS | SS-24 | AB_SS24_DSS | AESO. 2017. SS 7 Connection Assessment |  | 162
| 24.82L | ENMAX Power Corporation | Alberta | 1 | ac | 11.05 | 6.821 | 138 | 4.791 |  |  | 285 | 350 | 0.9 | n/a | 256.5 | 315 | SS-65 | AB_SS65_DSS | SS-24 | AB_SS24_DSS | AESO. 2017. SS 7 Connection Assessment |  | 163
| 1080L | Altalink Management Ltd. | Alberta | 1 | ac | 11.05 | 6.821 | 240 | 5.2692 |  |  | 487 | 604 | 0.9 | n/a | 438.3 | 543.6 | SS-65 | AB_SS65_DSS | Shepard SS-25 | AB_SS25_GSS | AESO. 2017. SS 7 Connection Assessment |  | 46
| 1109L | Altalink Management Ltd. | Alberta | 1 | ac | 11.05 | 6.821 | 240 | 5.2692 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | SS-65 | AB_SS65_DSS | Shepard SS-25 | AB_SS25_GSS |  |  | 62
| 1.80L | ENMAX Power Corporation | Alberta | 1 | ac | 16.15 | 9.9691 | 138 | 7.0022 |  |  | 160 | 199 | 0.9 | n/a | 144 | 179.1 | SS-1 | AB_SS01_DSS | SS-28 | AB_SS28_DSS | AESO. 2017. SS 7 Connection Assessment |  | 1
| 26.81L | ENMAX Power Corporation | Alberta | 1 | ac | 10.2 | 6.2963 | 138 | 4.4224 |  |  | 260 | 287 | 0.9 | n/a | 234 | 258.3 | SS-26 | AB_SS26_DSS | SS-32 | AB_SS32_DSS | AESO. 2017. SS 7 Connection Assessment |  | 169
| 31.84L | ENMAX Power Corporation | Alberta | 1 | ac | 6.8 | 4.1975 | 138 | 2.9483 |  |  | 161 | 191 | 0.9 | n/a | 144.9 | 171.9 | SS-31 | AB_SS31_DSS | SS-32 | AB_SS32_DSS | AESO. 2017. SS 7 Connection Assessment |  | 224
| 33.83L | ENMAX Power Corporation | Alberta | 1 | ac | 5.1 | 3.1481 | 138 | 2.2112 |  |  | 191 | 191 | 0.9 | n/a | 171.9 | 171.9 | SS-41 | AB_SS41_DSS | SS-33 | AB_SS33_DSS | AESO. 2017. SS 7 Connection Assessment |  | 226
| 33.84L | ENMAX Power Corporation | Alberta | 1 | ac | 3.06 | 1.8889 | 138 | 1.3267 |  |  | 191 | 191 | 0.9 | n/a | 171.9 | 171.9 | SS-43 | AB_SS43_DSS | SS-33 | AB_SS33_DSS | AESO. 2017. SS 7 Connection Assessment |  | 227
| 6.80L | ENMAX Power Corporation | Alberta | 1 | ac | 2.55 | 1.5741 | 138 | 1.1056 |  |  | 164 | 191 | 0.9 | n/a | 147.6 | 171.9 | SS-6 | AB_SS06_DSS | SS-35 | AB_SS35_DSS | AESO. 2017. SS 7 Connection Assessment |  | 316
| 35.81L | ENMAX Power Corporation | Alberta | 1 | ac | 6.8 | 4.1975 | 144 | 2.9774 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Sarcee 42S | AB_42S_DSS | SS-35 | AB_SS35_DSS |  |  | 228
| 7.84L | ENMAX Power Corporation | Alberta | 1 | ac | 12.75 | 7.8704 | 138 | 5.528 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-7 | AB_SS07_DSS | SS-36 | AB_SS36_DSS | AESO. 2017. SS 7 Connection Assessment |  | 402
| 37.82L | ENMAX Power Corporation | Alberta | 1 | ac | 4.76 | 2.9383 | 138 | 2.0638 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | Janet 74S | AB_74S_DSS | SS-37 | AB_SS37_DSS | AESO. 2017. SS 7 Connection Assessment |  | 231
| 37.81L | ENMAX Power Corporation | Alberta | 1 | ac | 4.25 | 2.6235 | 138 | 1.8427 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-38 | AB_SS38_DSS | SS-37 | AB_SS37_DSS | AESO. 2017. SS 7 Connection Assessment |  | 230
| 39.82L | ENMAX Power Corporation | Alberta | 1 | ac | 5.95 | 3.6728 | 138 | 2.5798 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | Beddington 162S | AB_162S_DSS | SS-39 | AB_SS39_DSS | AESO. 2017. SS 7 Connection Assessment |  | 233
| 22.81L | ENMAX Power Corporation | Alberta | 1 | ac | 5.95 | 3.6728 | 138 | 2.5798 |  |  | 285 | 287 | 0.9 | n/a | 256.5 | 258.3 | SS-22 | AB_SS22_DSS | SS-39 | AB_SS39_DSS | AESO. 2017. SS 7 Connection Assessment |  | 153
| 38.83L | ENMAX Power Corporation | Alberta | 1 | ac | 9.69 | 5.9815 | 138 | 4.2013 |  |  | 287 | 287 | 0.9 | n/a | 258.3 | 258.3 | SS-38 | AB_SS38_DSS | SS-39 | AB_SS39_DSS | AESO. 2017. SS 7 Connection Assessment |  | 232
| 32.83L | ENMAX Power Corporation | Alberta | 1 | ac | 5.1 | 3.1481 | 138 | 2.2112 |  |  | 164 | 191 | 0.9 | n/a | 147.6 | 171.9 | SS-32 | AB_SS32_DSS | SS-40 | AB_SS40_DSS | AESO. 2017. SS 7 Connection Assessment |  | 225
| 40.81L | ENMAX Power Corporation | Alberta | 1 | ac | 3.91 | 2.4136 | 138 | 1.6953 |  |  | 161 | 191 | 0.9 | n/a | 144.9 | 171.9 | SS-41 | AB_SS41_DSS | SS-40 | AB_SS40_DSS | AESO. 2017. SS 7 Connection Assessment |  | 238
| 6.82L | ENMAX Power Corporation | Alberta | 1 | ac | 7.65 | 4.7222 | 138 | 3.3168 |  |  | 161 | 191 | 0.9 | n/a | 144.9 | 171.9 | SS-6 | AB_SS06_DSS | SS-41 | AB_SS41_DSS | AESO. 2017. SS 7 Connection Assessment |  | 317
| 41.84L | ENMAX Power Corporation | Alberta | 1 | ac | 8.5 | 5.2469 | 144 | 3.7218 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | SS-54 | AB_SS54_DSS | SS-41 | AB_SS41_DSS |  |  | 241
| 771L | Altalink Management Ltd. | Alberta | 1 | ac | 9.35 | 5.7716 | 144 | 4.094 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Beddington 162S | AB_162S_DSS | SS-47 | AB_SS47_DSS |  |  | 566
| 1106L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 240 | 11.9213 |  |  | 971 | 1207 | 0.9 | n/a | 873.9 | 1086.3 | Foothills 237S | AB_237S_DSS | SS-65 | AB_SS65_DSS | AESO. 2017. SS 7 Connection Assessment |  | 60
| 1107L | Altalink Management Ltd. | Alberta | 1 | ac | 25 | 15.4321 | 240 | 11.9213 |  |  | 971 | 1207 | 0.9 | n/a | 873.9 | 1086.3 | Foothills 237S | AB_237S_DSS | SS-65 | AB_SS65_DSS | AESO. 2017. SS 7 Connection Assessment |  | 61
| 26.83L | ENMAX Power Corporation | Alberta | 1 | ac | 9.35 | 5.7716 | 138 | 4.0539 |  |  | 285 | 350 | 0.9 | n/a | 256.5 | 315 | SS-26 | AB_SS26_DSS | SS-65 | AB_SS65_DSS | AESO. 2017. SS 7 Connection Assessment |  | 170
| 54.81L | Altalink Management Ltd. | Alberta | 1 | ac | 15.3 | 9.4444 | 144 | 6.6992 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | SS-54 | AB_SS54_DSS | SS-65 | AB_SS65_DSS |  |  | 303
| 54AL | Altalink Management Ltd. | Alberta | 1 | ac | 5.6 | 3.4568 | 138 | 2.428 |  |  | 130 | 160 | 0.9 | n/a | 117 | 144 | Cascade 29S | AB_29S_GSS | Cascade Control Dam T756S | AB_T756S_DSS | AESO. 2018. Mount Allan Connection Assessment | Line connection assumed | 309
| 859L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 120 | 143 | 0.9 | n/a | 108 | 128.7 | Ghost 20S | AB_20S_GSS | Horse Creek T793S | AB_T793S_DSS | AESO. 2018. Mount Allan Connection Assessment |  | 883
| EMF1 | Syncrude | Alberta | 1 | ac | 16.8 | 10.3704 | 72 | 6.492 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Syncrude D05 | AB_D05S_ISS | Plant 30-2 UE-1 | AB_UE1S_DSS |  | EMF = East Mine Feeder | 1067
| EMF2 | Syncrude | Alberta | 1 | ac | 16.8 | 10.3704 | 72 | 6.492 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Syncrude D05 | AB_D05S_ISS | Plant 30-2 UE-1 | AB_UE1S_DSS |  | EMF = East Mine Feeder | 1067
| PCESO2L | ENMAX Power Corporation | Alberta | 1 | ac | 3.4 | 2.0988 | 144 | 1.4887 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Turbo Balzac 391S | AB_391S_DSS | Balzac Cogen | AB_XBAL_GSS |  |  | 1075
| 240CV5 | EPCOR | Alberta | 1 | ac | 4.6 | 2.8395 | 240 | 2.1935 |  |  | 475 | 503 | 0.9 | n/a | 427.5 | 452.7 | Victoria E511S | AB_E511S_DSS | Blatchford | AB_XBLA_DSS | AESO. 2020. Summerside Connection Assessment |  | 167
| PCESO1L | ENMAX Power Corporation | Alberta | 1 | ac | 14 | 8.642 | 144 | 6.13 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Namaka 428S | AB_428S_DSS | Cavalier | AB_XCAV_DSS |  |  | 1074
| 918L | Altalink Management Ltd. | Alberta | 1 | ac | 0.85 | 0.52469 | 240 | 0.40532 |  |  |  |  | 0.9 | 3 | 438.5787 | 476.0331 | Beddington 162S | AB_162S_DSS | Calgary Energy Center CEC | AB_XCEC_GSS |  |  | 952
| 72MG16 | EPCOR | Alberta | 1 | ac | 5.75 | 3.5494 | 69 | 2.2096 |  |  | 57.4 | 62.7 | 0.9 | n/a | 51.66 | 56.43 | Meadowlark | AB_XMEA_DSS | Garneau | AB_XGAR_DSS | AESO. 2020. Summerside Connection Assessment |  | 470
| 711L | Altalink Management Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 144 | 6.5679 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Inland Cement JCT | AB_XINL_JCT | Inland Cement | AB_XINL_DSS |  |  | 425
| 747L | Altalink Management Ltd. | Alberta | 1 | ac | 12 | 7.4074 | 144 | 5.2543 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | North St. Albert 99S | AB_99S_DSS | Inland Cement JCT | AB_XINL_JCT |  |  | 521
| 72CK12 | EPCOR | Alberta | 1 | ac | 6.9 | 4.2593 | 72 | 2.6664 |  |  | 48 | 56 | 0.9 | n/a | 43.2 | 50.4 | Clover Bar 987S | AB_987S_GSS | Kennedale | AB_XKEN_DSS | AESO. 2019. EPCOR Connection Assessment |  | 463
| 72CK13 | EPCOR | Alberta | 1 | ac | 6.9 | 4.2593 | 72 | 2.6664 |  |  | 48 | 56 | 0.9 | n/a | 43.2 | 50.4 | Clover Bar 987S | AB_987S_GSS | Kennedale | AB_XKEN_DSS | AESO. 2019. EPCOR Connection Assessment |  | 464
| 72NK23 | EPCOR | Alberta | 1 | ac | 6.9 | 4.2593 | 69 | 2.6516 |  |  | 57 | 57 | 0.9 | n/a | 51.3 | 51.3 | Namao | AB_XNAM_DSS | Kennedale | AB_XKEN_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 471
| 72JM18 | EPCOR | Alberta | 1 | ac | 5.75 | 3.5494 | 69 | 2.2096 |  |  | 57.5 | 62.3 | 0.9 | n/a | 51.75 | 56.07 | Jasper 805S | AB_805S_DSS | Meadowlark | AB_XMEA_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 466
| 6LML1 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Ruth Lake 848S | AB_848S_DSS | Mildred Lake | AB_XMIL_GSS |  |  | 399
| 6LML2 | ATCO Electric Ltd. | Alberta | 1 | ac | 15 | 9.2593 | 72 | 5.7964 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Ruth Lake 848S | AB_848S_DSS | Mildred Lake | AB_XMIL_GSS |  |  | 400
| DML | Syncrude | Alberta | 1 | ac | 10.08 | 6.2222 | 72 | 3.8952 |  |  |  |  | 0.9 | 3 | 38.88 | 42.4918 | Syncrude D05 | AB_D05S_ISS | Mildred Lake | AB_XMIL_GSS |  |  | 1068
| 72CN10 | EPCOR | Alberta | 1 | ac | 10.35 | 6.3889 | 69 | 3.9774 |  |  | 57.5 | 57.5 | 0.9 | n/a | 51.75 | 51.75 | Clover Bar 987S | AB_987S_GSS | Namao | AB_XNAM_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 465
| 72VN21 | EPCOR | Alberta | 1 | ac | 4.025 | 2.4846 | 69 | 1.5467 |  |  | 57.5 | 62.3 | 0.9 | n/a | 51.75 | 56.07 | Victoria E511S | AB_E511S_DSS | Namao | AB_XNAM_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 481
| 72RG1 | EPCOR | Alberta | 1 | ac | 2.3 | 1.4198 | 72 | 0.88879 |  |  | 60 | 60 | 0.9 | n/a | 54 | 54 | Garneau | AB_XGAR_DSS | Rossdale | AB_XROS_DSS | AESO. 2019. EPCOR Connection Assessment |  | 473
| 72RG7 | EPCOR | Alberta | 1 | ac | 2.3 | 1.4198 | 72 | 0.88879 |  |  | 80 | 80 | 0.9 | n/a | 72 | 72 | Garneau | AB_XGAR_DSS | Rossdale | AB_XROS_DSS | AESO. 2019. EPCOR Connection Assessment |  | 475
| 72RV2 | EPCOR | Alberta | 1 | ac | 2.3 | 1.4198 | 69 | 0.88386 |  |  | 63.9 | 63.9 | 0.9 | n/a | 57.51 | 57.51 | Victoria E511S | AB_E511S_DSS | Rossdale | AB_XROS_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 477
| 72RV4 | EPCOR | Alberta | 1 | ac | 2.3 | 1.4198 | 69 | 0.88386 |  |  | 63.9 | 63.9 | 0.9 | n/a | 57.51 | 57.51 | Victoria E511S | AB_E511S_DSS | Rossdale | AB_XROS_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 478
| 72RV6 | EPCOR | Alberta | 1 | ac | 2.3 | 1.4198 | 69 | 0.88386 |  |  | 63.9 | 63.9 | 0.9 | n/a | 57.51 | 57.51 | Victoria E511S | AB_E511S_DSS | Rossdale | AB_XROS_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 479
| 72RW3 | EPCOR | Alberta | 1 | ac | 10.35 | 6.3889 | 69 | 3.9774 |  |  | 57 | 62 | 0.9 | n/a | 51.3 | 55.8 | Woodcroft | AB_XWOO_DSS | Rossdale | AB_XROS_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 480
| 72LS24 | EPCOR | Alberta | 1 | ac | 6.9 | 4.2593 | 72 | 2.6664 |  |  | 90 | 124 | 0.9 | n/a | 81 | 111.6 | Lambton E803S | AB_E803S_DSS | Strathcona | AB_XSTR_GSS | AESO. 2019. EPCOR Connection Assessment |  | 469
| 72JW19 | EPCOR | Alberta | 1 | ac | 6.9 | 4.2593 | 69 | 2.6516 |  |  | 57.5 | 62.3 | 0.9 | n/a | 51.75 | 56.07 | Jasper 805S | AB_805S_DSS | Woodcroft | AB_XWOO_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 467
| 72NW15 | EPCOR | Alberta | 1 | ac | 5.75 | 3.5494 | 69 | 2.2096 |  |  | 61.3 | 85.3 | 0.9 | n/a | 55.17 | 76.77 | Namao | AB_XNAM_DSS | Woodcroft | AB_XWOO_DSS | AESO. 2017. Clover Bar Connection Assessment |  | 472
| 830L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 144 | 6.13 |  |  |  |  | 0.9 | 3 | 153.6 | 169.9672 | Mcneill Station 840S | AB_840S_DSS | IPT McNeill | PP_ABSK1_IPT |  |  | 847
| 786L | Altalink Management Ltd. | Alberta | 1 | ac | 14 | 8.642 | 138 | 6.07 |  |  | 99 | 132 | 0.9 | n/a | 89.1 | 118.8 | Coleman 799S | AB_799S_DSS | IPT Natal Coleman | PP_BCAB1_IPT | AESO. 2019. Travers Connection Assessment |  | 578
| 1201L | Altalink Management Ltd. | Alberta | 1 | ac | 38.5 | 23.7654 | 500 | 15.2075 |  |  |  |  | 0.9 | 3 | 2550 | 3225 | Chapel Rock 491S | AB_491S_DSS | IPT Cranbrook Chapel Rock | PP_BCAB2_IPT |  |  | 75
| 887L | Altalink Management Ltd. | Alberta | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 |  |  | 72 | 72 | 0.9 | n/a | 64.8 | 64.8 | Pocaterra 48S | AB_48S_GSS | IPT Natal Pocaterra | PP_BCAB3_IPT | AESO. 2018. Mount Allan Connection Assessment |  | 909
| 7L81 | ATCO Electric Ltd. | Alberta | 1 | ac | 23 | 14.1975 | 144 | 10.0707 |  |  | 149 | 149 | 0.9 | n/a | 134.1 | 134.1 | Rainbow Lake 791S | AB_791S_GSS | IPT Nelson Rainbow | PP_BCAB4_IPT | AESO. 2014. Carmon Creek Connection Assessment |  | 790
| MATL | Altalink Management Ltd. | Alberta | 1 | ac | 150 | 92.5926 | 240 | 71.5278 |  |  |  |  | 0.9 | 2.14 | 300 | 300 | Picture Butte 120S | AB_120S_DSS | INT Butte Montana | XX_ABUS1_INT | AESO. 2018. Information Document: Available Transfer Capability and Transfer Path Management ID #2011-001R | Summer capacity = winter capacity = export capacity = import capacity | 1073
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## Nodes
AB | EXISTING NODES
| Node Name | Node Code | Owner | Latitude | Longitude | Operating Region | Other References | Notes
| 29EDD-0056 | AB_E56S_ISS | Suncor |  |  | Alberta
| 29EDD-0063 | AB_E63S_ISS | Suncor |  |  | Alberta
| 29EDD-1 | AB_E1S_ISS | Suncor |  |  | Alberta
| 29EDD-10 | AB_E10S_ISS | Suncor |  |  | Alberta
| 29EDD-18 | AB_E18S_ISS | Suncor |  |  | Alberta
| 29EDD-19 | AB_E19S_ISS | Suncor |  |  | Alberta
| 29EDD-2 | AB_E2S_ISS | Suncor |  |  | Alberta
| 29EDD-20 | AB_E20S_ISS | Suncor |  |  | Alberta
| 29EDD-22 | AB_E22S_ISS | Suncor |  |  | Alberta
| 29EDD-29 | AB_E29S_ISS | Suncor |  |  | Alberta
| 29EDD-3 | AB_E3S_ISS | Suncor |  |  | Alberta
| 29EDD-31 | AB_E31S_ISS | Suncor |  |  | Alberta
| 29EDD-33 | AB_E33S_ISS | Suncor |  |  | Alberta
| 29EDD-34 | AB_E34S_ISS | Suncor |  |  | Alberta
| 29EDD-45 | AB_E45S_ISS | Suncor |  |  | Alberta
| 29EDD-46 | AB_E46S_ISS | Suncor |  |  | Alberta
| 29EDD-5 | AB_E5S_ISS | Suncor |  |  | Alberta
| 29EDD-55 | AB_E55S_ISS | Suncor |  |  | Alberta
| 29EDD-62 | AB_E62S_ISS | Suncor |  |  | Alberta
| 29EDD-64 | AB_E64S_ISS | Suncor |  |  | Alberta
| 29EDD-65 | AB_E65S_ISS | Suncor |  |  | Alberta
| 29EDD-67 | AB_E67S_ISS | Suncor |  |  | Alberta
| 29EDD-7 | AB_E7S_ISS | Suncor |  |  | Alberta
| 29EDD-71 | AB_E71S_ISS | Suncor |  |  | Alberta
| 29EDD-8 | AB_E8S_ISS | Suncor |  |  | Alberta
| 29EDD-83 | AB_E83S_ISS | Suncor |  |  | Alberta
| 29EDD-84 | AB_E84S_ISS | Suncor |  |  | Alberta
| 29EDD-9 | AB_E9S_ISS | Suncor |  |  | Alberta
| 29EDD-93 | AB_E93S_ISS | Suncor |  |  | Alberta
| 29EDD-94 | AB_E94S_ISS | Suncor |  |  | Alberta
| ABEE 993S | AB_993S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Acheson 305S | AB_305S_DSS | Altalink Management Ltd. | 53.5129 | -113.7758 | Alberta
| AEC Mills 844S | AB_844S_ISS | ATCO Electric Ltd. |  |  | Alberta
| AHS 01 279S | AB_279S_ISS | ATCO Electric Ltd. |  |  | Alberta
| Air Liquide 408S | AB_408S_ISS | Air Liquide Canada Inc. |  |  | Alberta
| Al Rothbauer 321S | AB_321S_DSS | Altalink Management Ltd. |  |  | Alberta
| ALBChem Beaverhill Creek 308S | AB_308S_ISS | Altalink Management Ltd. |  |  | Alberta
| Alberta Newsprint 122S | AB_122S_GSS | Altalink Management Ltd. | 54.1279 | -115.6659 | Alberta
| Albright & Wilson 752S | AB_752S_ISS | ATCO Electric Ltd. |  |  | Alberta
| Algar 875S | AB_875S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Amelia 108S | AB_108S_DSS | Altalink Management Ltd. |  |  | Alberta
| AMOCO Empress 163S | AB_163S_ISS | Altalink Management Ltd. |  |  | Alberta
| AMR02 937S | AB_937S_ISS | ATCO Electric Ltd. |  |  | Alberta
| Anderson 801S | AB_801S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Arcenciel 930S | AB_930S_DSS | ATCO Electric Ltd. | 58.4155 | -119.2894 | Alberta
| Ardenville Wind Farm 418S | AB_418S_GSS | Altalink Management Ltd. | 49.583 | -113.4351 | Alberta
| Argyll 629S | AB_629S_DSS | EPCOR | 53.5045 | -113.4495 | Alberta
| AT Plastic 4RS | AB_4RS_ISS | Altalink Management Ltd. |  |  | Alberta
| AT Plastic 4RS JCT | AB_4RS_JCT | Altalink Management Ltd. |  |  | Alberta
| AT Plastic 5RS | AB_5RS_ISS | Altalink Management Ltd. |  |  | Alberta
| Athabasca Crossing EDD200 | AB_E200S_ISS | Suncor |  |  | Alberta
| Aurora G01 | AB_G01S_DSS | Syncrude |  |  | Alberta
| B.F.Goodrich Fort Sask. 452S | AB_452S_ISS | Altalink Management Ltd. |  |  | Alberta
| B.F.Goodrich Fort Sask. 452S JCT | AB_452S_JCT | Altalink Management Ltd. |  |  | Alberta
| Balzac Cogen | AB_XBAL_GSS | ENMAX Power Corporation |  |  | Alberta
| Banff 123S | AB_123S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bannerman 681S | AB_681S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bardo 197S | AB_197S_DSS | Altalink Management Ltd. |  |  | Alberta
| Barrier 32S | AB_32S_GSS | Altalink Management Ltd. |  |  | Alberta
| Baseline 317S | AB_317S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bassano 435S | AB_435S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bassano 435S JCT | AB_435S_JCT | Altalink Management Ltd. |  |  | Alberta
| Bassett 747S | AB_747S_DSS | ATCO Electric Ltd. | 58.3085 | -118.5214 | Alberta |  | Location approximate
| Battle River 757S | AB_757S_GSS | ATCO Electric Ltd. | 52.4685 | -112.1339 | Alberta
| Bauer 918S | AB_918S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bauer 918S JCT | AB_918S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Baymag 437S | AB_437S_DSS | Altalink Management Ltd. |  |  | Alberta
| Beamer 233S | AB_233S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bear Creek 679S | AB_679S_DSS | ATCO Electric Ltd. | 55.0715 | -118.6921 | Alberta
| Bear Creek 679S JCT | AB_679S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Bearspaw Plant 44S | AB_44S_GSS | Altalink Management Ltd. | 51.1012 | -114.2823 | Alberta
| Beartrap 940S | AB_940S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Beartrap 940S JCT | AB_940S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Beddington 162S | AB_162S_DSS | ENMAX Power Corporation | 51.1789 | -113.9383 | Alberta
| Bellamy 814S | AB_814S_DSS | EPCOR | 53.53 | -113.4995 | Alberta
| Benalto 17S | AB_17S_DSS | Altalink Management Ltd. |  |  | Alberta
| Benbow 397S | AB_397S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bennett 520S | AB_520S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bernese 293S | AB_293S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bickerdike 39S | AB_39S_DSS | Altalink Management Ltd. |  |  | Alberta
| Big Knife Creek 843S | AB_843S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Big Mountain 845S | AB_845S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bigfoot 756S | AB_756S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bighorn Plant 250P | AB_250P_GSS | Altalink Management Ltd. | 52.3081 | -116.3245 | Alberta
| Bigstone 86S | AB_86S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bilby 105S | AB_105S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bilby 105S JCT | AB_105S_JCT | Altalink Management Ltd. |  |  | Alberta
| Bindloss 914S | AB_914S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bindloss 914S JCT | AB_914S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Birchwood Creek 960S | AB_960S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bitumount 941S | AB_941S_ISS | ATCO Electric Ltd. |  |  | Alberta
| Black Diamond 392S | AB_392S_DSS | Altalink Management Ltd. |  |  | Alberta
| Black Fly 934S | AB_934S_ISS | ATCO Electric Ltd. |  |  | Alberta
| Black Spruce 154S | AB_154S_DSS | Altalink Management Ltd. |  |  | Alberta
| Blackfalds 198S | AB_198S_DSS | Altalink Management Ltd. | 52.3813 | -113.7967 | Alberta
| Blackie 253S | AB_253S_DSS | Altalink Management Ltd. |  |  | Alberta
| Blackmud 155S | AB_155S_DSS | Altalink Management Ltd. |  |  | Alberta
| Blackspring Ridge 485S | AB_485S_DSS | Altalink Management Ltd. | 50.1525 | -112.8226 | Alberta
| Blatchford | AB_XBLA_DSS | EPCOR | 53.5697 | -113.5147 | Alberta |  | Location approximate
| Blue Ridge Lumber 701S | AB_701S_ISS | Altalink Management Ltd. |  |  | Alberta
| Blue Trail 528S | AB_528S_DSS | Altalink Management Ltd. |  |  | Alberta
| Blue Trail 528S JCT | AB_528S_JCT | Altalink Management Ltd. |  |  | Alberta
| Blumenort 832S | AB_832S_DSS | ATCO Electric Ltd. | 58.3689 | -116.2042 | Alberta
| Bohn 931S | AB_931S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bonnyville 700S | AB_700S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Boucher Creek 829S | AB_829S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bourque 970S | AB_970S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bowmanton 244S | AB_244S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bowron 674S | AB_674S_DSS | Altalink Management Ltd. |  |  | Alberta
| Boyle 56S | AB_56S_DSS | Altalink Management Ltd. |  |  | Alberta
| Brazeau 358S | AB_358S_DSS | Altalink Management Ltd. |  |  | Alberta
| Brazeau 62S | AB_62S_GSS | Altalink Management Ltd. | 52.9101 | -115.3754 | Alberta
| Brazeau Outlet Works 294S | AB_294S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bretona 45S | AB_45S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bretville 185S | AB_185S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bridge Creek 798S | AB_798S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bridge Creek 798S JCT | AB_798S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Briker 880S | AB_880S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Briker 880S JCT | AB_880S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Brintnell 876S | AB_876S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Broadmoor 420S | AB_420S_DSS | Altalink Management Ltd. |  |  | Alberta
| Brookfield 536S | AB_536S_DSS | Altalink Management Ltd. |  |  | Alberta
| Brooks 121S | AB_121S_GSS | Altalink Management Ltd. | 50.5833 | -111.8808 | Alberta
| Bruderheim 127S | AB_127S_DSS | Altalink Management Ltd. |  |  | Alberta
| Buchanan Creek 927S | AB_927S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Buck Lake 454S | AB_454S_GSS | Altalink Management Ltd. | 52.9534 | -114.7955 | Alberta
| Buck Lake 454S JCT | AB_454S_JCT | Altalink Management Ltd. |  |  | Alberta
| Buffalo Creek 526S | AB_526S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Buford 538S | AB_538S_DSS | Altalink Management Ltd. |  |  | Alberta
| Bullpound 803S | AB_803S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Bullshead 523S | AB_523S_DSS | Altalink Management Ltd. |  |  | Alberta
| Burdett 368S | AB_368S_GSS | Altalink Management Ltd. | 49.8434 | -111.5631 | Alberta
| Cadomin 983S | AB_983S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cadomin 983S JCT | AB_983S_JCT | Altalink Management Ltd. |  |  | Alberta
| Cadotte River 783S | AB_783S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Calgary Energy Center CEC | AB_XCEC_GSS | Altalink Management Ltd. |  |  | Alberta
| Canada Liquid Air 337S | AB_337S_ISS | Altalink Management Ltd. |  |  | Alberta
| Canada Liquid Air 337S JCT | AB_337S_JCT | Altalink Management Ltd. |  |  | Alberta
| Canadian Oxy Astotin Creek 365S | AB_365S_ISS | Altalink Management Ltd. |  |  | Alberta
| Canmore 118S | AB_118S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cardinal River 302S | AB_302S_DSS | Altalink Management Ltd. |  |  | Alberta
| Carmon 830S | AB_830S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Caroline 378S | AB_378S_GSS | Altalink Management Ltd. |  |  | Alberta
| Carseland 525S | AB_525S_GSS | Altalink Management Ltd. | 50.8466 | -113.5816 | Alberta
| Carvel 432S | AB_432S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cascade 29S | AB_29S_GSS | Altalink Management Ltd. | 51.2002 | -115.5021 | Alberta
| Cascade 29S JCT | AB_29S_JCT | Altalink Management Ltd. |  |  | Alberta
| Cascade Control Dam T756S | AB_T756S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cassils 324S | AB_324S_DSS | Altalink Management Ltd. |  |  | Alberta
| Castle Downs 557S | AB_557S_DSS | EPCOR | 53.6245 | -113.49 | Alberta
| Castle River 239S | AB_239S_GSS | Altalink Management Ltd. | 49.516 | -114.0276 | Alberta
| Castle Rock Ridge 205S | AB_205S_GSS | Altalink Management Ltd. | 49.5561 | -113.963 | Alberta
| Castor 759S | AB_759S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Cavalier | AB_XCAV_DSS | ENMAX Power Corporation | 51.0056 | -113.1716 | Alberta
| CG&E 758S | AB_758S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Chapel Rock 491S | AB_491S_DSS | Altalink Management Ltd. |  |  | Alberta
| Chappice Lake 649S | AB_649S_DSS | Altalink Management Ltd. | 50.2211 | -110.4461 | Alberta
| Chard 658S | AB_658S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Chard 658S JCT | AB_658S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Cherhill 338S | AB_338S_DSS | Altalink Management Ltd. |  |  | Alberta
| Chestermere 419S | AB_419S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cheviot 101S | AB_101S_DSS | Altalink Management Ltd. |  |  | Alberta
| Chevron Kaybob 551S | AB_551S_ISS | Altalink Management Ltd. |  |  | Alberta
| Chevron Knight 355S | AB_355S_ISS | Altalink Management Ltd. |  |  | Alberta
| Chevron Knight 355S JCT | AB_355S_JCT | Altalink Management Ltd. |  |  | Alberta
| Chickadee Creek 259S | AB_259S_DSS | Altalink Management Ltd. |  |  | Alberta
| Chickadee Creek 259S JCT | AB_259S_JCT | Altalink Management Ltd. |  |  | Alberta
| Chin Chute 315S | AB_315S_GSS | Altalink Management Ltd. | 49.6756 | -112.3446 | Alberta
| Chin Chute 315S JCT | AB_315S_JCT | Altalink Management Ltd. |  |  | Alberta
| Chinchaga River 779S | AB_779S_DSS | ATCO Electric Ltd. | 57.9129 | -118.2179 | Alberta |  | Location approximate
| Chinook 181S | AB_181S_DSS | Altalink Management Ltd. |  |  | Alberta
| Christina Lake 723S | AB_723S_GSS | Altalink Management Ltd. | 55.5628 | -110.9135 | Alberta
| Clairmont Lake 811S | AB_811S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Clipper 656S | AB_656S_DSS | Altalink Management Ltd. |  |  | Alberta
| Clover Bar 987S | AB_987S_GSS | EPCOR | 53.5956 | -113.3322 | Alberta
| Clyde 150S | AB_150S_DSS | Altalink Management Ltd. |  |  | Alberta
| Coal Valley 527S | AB_527S_DSS | Altalink Management Ltd. |  |  | Alberta
| Coal Valley 527S JCT | AB_527S_JCT | Altalink Management Ltd. |  |  | Alberta
| Coalbanks 111S | AB_111S_DSS | Altalink Management Ltd. |  |  | Alberta
| Coaldale 254S | AB_254S_GSS | Altalink Management Ltd. | 49.7362 | -112.5622 | Alberta
| Coalspur 426S | AB_426S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cochrane 291S | AB_291S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cold Creek 602S | AB_602S_DSS | Altalink Management Ltd. |  |  | Alberta
| Coleman 799S | AB_799S_DSS | Altalink Management Ltd. |  |  | Alberta
| Colinton 159S | AB_159S_DSS | Altalink Management Ltd. |  |  | Alberta
| Conklin 762S | AB_762S_DSS | Altalink Management Ltd. |  |  | Alberta
| Conrad 135S | AB_135S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cooking Lake 522S | AB_522S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cordel 755S | AB_755S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Coronation 773S | AB_773S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Coronation 773S JCT | AB_773S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Cowley Ridge 322S | AB_322S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cowley Ridge 322S JCT | AB_322S_JCT | Altalink Management Ltd. |  |  | Alberta
| Coyote Lake 963S | AB_963S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Cranberry Lake 827S | AB_827S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Crossings 511S | AB_511S_DSS | Altalink Management Ltd. |  |  | Alberta
| Crow 860S | AB_860S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Crystal Lake 722S | AB_722S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Cutting Lake 227S | AB_227S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cutting Lake 227S JCT | AB_227S_JCT | Altalink Management Ltd. |  |  | Alberta
| Cynthia 178S | AB_178S_DSS | Altalink Management Ltd. |  |  | Alberta
| Cypress 562S | AB_562S_DSS | Altalink Management Ltd. |  |  | Alberta
| Daishowa 839S | AB_839S_GSS | ATCO Electric Ltd. | 56.3711 | -117.1856 | Alberta
| Dalehurst 975S | AB_975S_DSS | Altalink Management Ltd. |  |  | Alberta
| Dalehurst 975S JCT | AB_975S_JCT | Altalink Management Ltd. |  |  | Alberta
| Dawes 2011S | AB_2011S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Deer Hill 1012S | AB_1012S_DSS | Altalink Management Ltd. |  |  | Alberta
| Deerland 13S | AB_13S_DSS | Altalink Management Ltd. |  |  | Alberta
| Devon 14S | AB_14S_DSS | Altalink Management Ltd. |  |  | Alberta
| Dog Rib 2082S | AB_2082S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Dome 665S | AB_665S_DSS | EPCOR | 53.4566 | -113.4812 | Alberta
| Dome Cutbank 810S | AB_810S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Donnelly 784S | AB_784S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Dover 888S | AB_888S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Dow Chemical Fort Sask. 166S | AB_166S_ISS | Altalink Management Ltd. | 53.734 | -113.1714 | Alberta
| Dow Hydro Carbons 258S | AB_258S_ISS | Altalink Management Ltd. |  |  | Alberta
| Dry Creek 186S | AB_186S_DSS | Altalink Management Ltd. |  |  | Alberta
| Drywood 415S | AB_415S_DSS | Altalink Management Ltd. |  |  | Alberta
| Duchess 339S | AB_339S_DSS | Altalink Management Ltd. |  |  | Alberta
| Eagle Creek 412S | AB_412S_DSS | Altalink Management Ltd. |  |  | Alberta
| East Airdrie 199S | AB_199S_DSS | Altalink Management Ltd. |  |  | Alberta
| East Calgary 5S | AB_5S_DSS | Altalink Management Ltd. |  |  | Alberta
| East Camrose 285S | AB_285S_GSS | Altalink Management Ltd. |  |  | Alberta
| East Crossfield 64S | AB_64S_DSS | Altalink Management Ltd. |  |  | Alberta
| East Crossfield 64S JCT | AB_64S_JCT | Altalink Management Ltd. |  |  | Alberta
| East Edmonton 38S | AB_38S_DSS | Altalink Management Ltd. |  |  | Alberta
| East Industrial E52S | AB_E52S_DSS | Altalink Management Ltd. |  |  | Alberta
| East Industrial E52S JCT | AB_E52S_JCT | Altalink Management Ltd. |  |  | Alberta
| East Stavely 928S | AB_928S_DSS | Altalink Management Ltd. |  |  | Alberta
| Eckville 534S | AB_534S_DSS | Altalink Management Ltd. |  |  | Alberta
| Eckville 534S JCT | AB_534S_JCT | Altalink Management Ltd. |  |  | Alberta
| Edgerton 899S | AB_899S_DSS | Altalink Management Ltd. |  |  | Alberta
| Edith Lake 739S | AB_739S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Edson 58S | AB_58S_GSS | Altalink Management Ltd. | 53.5577 | -116.5474 | Alberta
| Elk River 445S | AB_445S_DSS | Altalink Management Ltd. |  |  | Alberta
| Elk River 445S JCT | AB_445S_JCT | Altalink Management Ltd. |  |  | Alberta
| Ellerslie 89S | AB_89S_DSS | Altalink Management Ltd. | 53.4338 | -113.4595 | Alberta
| Ellis 332S | AB_332S_DSS | Altalink Management Ltd. |  |  | Alberta
| Elmworth 731S | AB_731S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Empress 394S | AB_394S_DSS | Altalink Management Ltd. |  |  | Alberta
| Empress Liquids 164S | AB_164S_ISS | Altalink Management Ltd. |  |  | Alberta
| Empress Liquids 164S JCT | AB_164S_JCT | Altalink Management Ltd. |  |  | Alberta
| Enchant 447S | AB_447S_DSS | Altalink Management Ltd. |  |  | Alberta
| Enchant 447S JCT | AB_447S_JCT | Altalink Management Ltd. |  |  | Alberta
| Engstrom 2060S | AB_2060S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Entwistle 235S | AB_235S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ervick 542S | AB_542S_DSS | Altalink Management Ltd. |  |  | Alberta
| Esso Judy Creek 638S | AB_638S_ISS | Altalink Management Ltd. |  |  | Alberta
| Esso Judy Creek 638S JCT | AB_638S_JCT | Altalink Management Ltd. |  |  | Alberta
| Ethel Lake 717S | AB_717S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Eureka River 861S | AB_861S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Excel 910S | AB_910S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Exshaw 985S | AB_985S_DSS | Altalink Management Ltd. |  |  | Alberta
| Exshaw 985S JCT | AB_985S_JCT | Altalink Management Ltd. |  |  | Alberta
| Eyre 558S | AB_558S_DSS | Altalink Management Ltd. |  |  | Alberta
| Fedpipe Judy Creek 515S | AB_515S_ISS | Altalink Management Ltd. |  |  | Alberta
| Fiberglass 524S | AB_524S_DSS | Altalink Management Ltd. |  |  | Alberta
| Fiberglass 524S JCT | AB_524S_JCT | Altalink Management Ltd. |  |  | Alberta
| Fickle Lake 406S | AB_406S_DSS | Altalink Management Ltd. |  |  | Alberta
| Fidler 312S | AB_312S_DSS | Altalink Management Ltd. |  |  | Alberta
| Fieldgate 824S | AB_824S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Fincastle 336S | AB_336S_DSS | Altalink Management Ltd. |  |  | Alberta
| Flat Lake 242S | AB_242S_DSS | Altalink Management Ltd. |  |  | Alberta
| Flat Lake 242S JCT | AB_242S_JCT | Altalink Management Ltd. |  |  | Alberta
| Flatbush 500S | AB_500S_DSS | Altalink Management Ltd. |  |  | Alberta
| Flatbush 500S JCT | AB_500S_JCT | Altalink Management Ltd. |  |  | Alberta
| Flying Shot Lake 749S | AB_749S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Foothills 237S | AB_237S_DSS | Altalink Management Ltd. |  |  | Alberta
| Fort Assiniboine 234S | AB_234S_DSS | Altalink Management Ltd. |  |  | Alberta
| Fort Assiniboine 234S JCT | AB_234S_JCT | Altalink Management Ltd. |  |  | Alberta
| Fort Hills 505S | AB_505S_GSS | Suncor | 57.3954 | -111.5714 | Alberta
| Fort Macleod 15S | AB_15S_GSS | Altalink Management Ltd. | 49.7229 | -113.4044 | Alberta
| Fort Sask. 54S | AB_54S_DSS | Altalink Management Ltd. |  |  | Alberta
| Fort Sask. Cogen 218S | AB_218S_GSS | Altalink Management Ltd. |  |  | Alberta
| Foster Creek 1200S | AB_1200S_GSS | ATCO Electric Ltd. | 55.0674 | -110.536 | Alberta
| Fox Creek 741S | AB_741S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Fox Creek Altalink 347S | AB_347S_DSS | Altalink Management Ltd. |  |  | Alberta
| Freeman Lake 742S | AB_742S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Friedenstal 800S | AB_800S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Gaetz 87S | AB_87S_DSS | Altalink Management Ltd. |  |  | Alberta
| Garden City 226S | AB_226S_DSS | Altalink Management Ltd. |  |  | Alberta
| Garden City 226S JCT | AB_226S_JCT | Altalink Management Ltd. |  |  | Alberta
| Garneau | AB_XGAR_DSS | EPCOR | 53.5207 | -113.5187 | Alberta
| Genesee 330P | AB_330P_DSS | Altalink Management Ltd. |  |  | Alberta
| Germain 950S | AB_950S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Ghost 20S | AB_20S_GSS | Altalink Management Ltd. | 51.2188 | -114.7078 | Alberta
| Ghost Pine 114S | AB_114S_DSS | ATCO Electric Ltd. | 51.8723 | -113.3181 | Alberta
| Ghost Pine 114S JCT | AB_114S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Gleichen 179S | AB_179S_DSS | Altalink Management Ltd. |  |  | Alberta
| Glenwood 229S | AB_229S_DSS | Altalink Management Ltd. |  |  | Alberta
| Goodfare 815S | AB_815S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Goose Lake 103S | AB_103S_DSS | Altalink Management Ltd. |  |  | Alberta
| Goose River 725S | AB_725S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Grand Centre 846S | AB_846S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Granite 342S | AB_342S_DSS | Altalink Management Ltd. |  |  | Alberta
| Grassland 282S | AB_282S_DSS | Altalink Management Ltd. |  |  | Alberta
| Green Stocking 925S | AB_925S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Gregoire 883S | AB_883S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Gulf Robb 414S | AB_414S_DSS | Altalink Management Ltd. |  |  | Alberta
| Gulf Robb 414S JCT | AB_414S_JCT | Altalink Management Ltd. |  |  | Alberta
| H.R. Milner 740S | AB_740S_GSS | ATCO Electric Ltd. | 54.0082 | -119.1022 | Alberta
| Haig River 748S | AB_748S_DSS | ATCO Electric Ltd. | 58.0539 | -118.4709 | Alberta
| Halfway 2014S | AB_2014S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Halfway 2014S JCT | AB_2014S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Halkirk 615S | AB_615S_GSS | ATCO Electric Ltd. | 52.2609 | -112.0271 | Alberta
| Hamburg 855S | AB_855S_DSS | ATCO Electric Ltd. | 57.3652 | -119.7555 | Alberta
| Hangingstone 820S | AB_820S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Hanna 763S | AB_763S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Hansman Lake 650S | AB_650S_DSS | Altalink Management Ltd. |  |  | Alberta
| Hardisty 377S | AB_377S_DSS | Altalink Management Ltd. |  |  | Alberta
| Harmattan 256S | AB_256S_GSS | Altalink Management Ltd. |  |  | Alberta
| Harry Smith 367S | AB_367S_DSS | Altalink Management Ltd. | 53.4821 | -113.8517 | Alberta
| Hartell 512S | AB_512S_DSS | Altalink Management Ltd. |  |  | Alberta
| Hartell 512S JCT | AB_512S_JCT | Altalink Management Ltd. |  |  | Alberta
| Haynes 482S | AB_482S_DSS | Altalink Management Ltd. |  |  | Alberta
| Haynes 482S JCT | AB_482S_JCT | Altalink Management Ltd. |  |  | Alberta
| Hays 421S | AB_421S_GSS | Altalink Management Ltd. |  |  | Alberta
| Hayter 277S | AB_277S_DSS | Altalink Management Ltd. |  |  | Alberta
| Hazelwood 287S | AB_287S_DSS | Altalink Management Ltd. |  |  | Alberta
| Heart Lake 898S | AB_898S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Heartland 12S | AB_12S_DSS | Altalink Management Ltd. |  |  | Alberta
| Heatburg 948S | AB_948S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Heathfield 2029S | AB_2029S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Heisler 764S | AB_764S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Heisler 764S JCT | AB_764S_JCT | ATCO Electric Ltd. |  |  | Alberta
| High Level 786S | AB_786S_DSS | ATCO Electric Ltd. | 58.5047 | -117.1478 | Alberta
| High Prairie 787S | AB_787S_DSS | ATCO Electric Ltd. |  |  | Alberta
| High River 65S | AB_65S_DSS | Altalink Management Ltd. |  |  | Alberta
| Hill 751S | AB_751S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Hillridge 139S | AB_139S_DSS | Altalink Management Ltd. |  |  | Alberta
| Hillridge 139S JCT | AB_139S_JCT | Altalink Management Ltd. |  |  | Alberta
| Hines Creek 724S | AB_724S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Horizon Mining 838S | AB_838S_ISS | Canadian Natural Resources Limited |  |  | Alberta
| Horizon Upgrading 842S | AB_842S_GSS | Canadian Natural Resources Limited | 57.3393 | -111.7578 | Alberta
| Horse Creek T793S | AB_T793S_DSS | Altalink Management Ltd. |  |  | Alberta
| Horse River 917S | AB_917S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Horseshoe 3S | AB_3S_DSS | Altalink Management Ltd. |  |  | Alberta
| Horseshoe 737S | AB_737S_DSS | Suncor |  |  | Alberta
| Hotchkiss 788S | AB_788S_DSS | ATCO Electric Ltd. | 57.0906 | -117.5797 | Alberta
| HRT Express 329S | AB_329S_DSS | Altalink Management Ltd. |  |  | Alberta
| HRT Express 329S JCT | AB_329S_JCT | Altalink Management Ltd. |  |  | Alberta
| Hughenden 213S | AB_213S_DSS | Altalink Management Ltd. |  |  | Alberta
| Hull 257S | AB_257S_DSS | Altalink Management Ltd. |  |  | Alberta
| Hussar 431S | AB_431S_DSS | Altalink Management Ltd. |  |  | Alberta
| Imperial Oil Carson Lake 996S | AB_996S_ISS | Altalink Management Ltd. |  |  | Alberta
| Imperial Oil Carson Lake 996S JCT | AB_996S_JCT | Altalink Management Ltd. |  |  | Alberta
| Imperial Oil Edmonton 95S | AB_95S_ISS | Altalink Management Ltd. |  |  | Alberta
| Inland Cement | AB_XINL_DSS | Altalink Management Ltd. |  |  | Alberta
| Inland Cement JCT | AB_XINL_JCT | Altalink Management Ltd. |  |  | Alberta
| Innisfail 214S | AB_214S_GSS | Altalink Management Ltd. | 52.0481 | -113.9768 | Alberta
| INT Butte Montana | XX_ABUS1_INT | AB-US Border | 48.9987 | -112.2097 | Alberta
| Interlakes 49S | AB_49S_GSS | Altalink Management Ltd. | 50.6335 | -115.1392 | Alberta
| Ipiatik 167S | AB_167S_DSS | Altalink Management Ltd. |  |  | Alberta
| IPT Cranbrook Chapel Rock | PP_BCAB2_IPT | BC-AB Border | 49.6448 | -114.6619 | Alberta
| IPT McNeill | PP_ABSK1_IPT | AB-SK Border | 50.5894 | -110.004 | Alberta
| IPT Natal Coleman | PP_BCAB1_IPT | BC-AB Border | 49.6454 | -114.6618 | Alberta
| IPT Natal Pocaterra | PP_BCAB3_IPT | BC-AB Border | 50.5868 | -115.0705 | Alberta
| IPT Nelson Rainbow | PP_BCAB4_IPT | BC-AB Border | 58.5444 | -120 | Alberta
| Irish Creek 706S | AB_706S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Irrican Power 314S | AB_314S_GSS | Altalink Management Ltd. | 49.4526 | -112.7165 | Alberta
| Jack Pine 920S | AB_920S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Jackfish 698S | AB_698S_DSS | Altalink Management Ltd. |  |  | Alberta
| Janet 74S | AB_74S_DSS | Altalink Management Ltd. |  |  | Alberta
| Jarrow 252S | AB_252S_DSS | Altalink Management Ltd. |  |  | Alberta
| Jarrow 252S JCT | AB_252S_JCT | Altalink Management Ltd. |  |  | Alberta
| Jasper 805S | AB_805S_DSS | EPCOR | 53.5495 | -113.6167 | Alberta
| Jenner 275S | AB_275S_GSS | Altalink Management Ltd. | 50.7486 | -111.0489 | Alberta
| Joffre 535S | AB_535S_GSS | Altalink Management Ltd. | 52.3078 | -113.5468 | Alberta
| Johnson 281S | AB_281S_DSS | Altalink Management Ltd. |  |  | Alberta
| Josephburg 410S | AB_410S_DSS | Altalink Management Ltd. |  |  | Alberta
| Joslyn Creek 849S | AB_849S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Judy Creek Gas Plant 785S | AB_785S_ISS | ATCO Electric Ltd. |  |  | Alberta
| Jumping Pound 271S | AB_271S_DSS | Altalink Management Ltd. |  |  | Alberta
| Jumping Pound 271S JCT | AB_271S_JCT | Altalink Management Ltd. |  |  | Alberta
| Jumping Pound Junction 43S | AB_43S_DSS | Altalink Management Ltd. |  |  | Alberta
| Jumping Pound Junction 43S JCT | AB_43S_JCT | Altalink Management Ltd. |  |  | Alberta
| Kakwa Ridge 857S | AB_857S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Kananaskis 2S | AB_2S_GSS | Altalink Management Ltd. | 51.0969 | -115.0582 | Alberta
| Kaybob 346S | AB_346S_GSS | Altalink Management Ltd. | 54.099 | -116.6138 | Alberta
| Kaybob 346S JCT | AB_346S_JCT | Altalink Management Ltd. |  |  | Alberta
| Kearl 9900S | AB_9900S_GSS | Imperial Oil | 57.421 | -110.9264 | Alberta
| Keephills 320P | AB_320P_GSS | Altalink Management Ltd. | 53.3446 | -114.3049 | Alberta
| Keg River 789S | AB_789S_DSS | ATCO Electric Ltd. | 57.7893 | -117.615 | Alberta
| Kemp River 797S | AB_797S_DSS | ATCO Electric Ltd. | 57.5917 | -117.5206 | Alberta
| Kennedale | AB_XKEN_DSS | EPCOR | 53.5871 | -113.4194 | Alberta
| Kettle River 2049S | AB_2049S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Kettle's Hill 383S | AB_383S_GSS | Altalink Management Ltd. | 49.5159 | -113.8218 | Alberta
| Kettle's Hill 383S JCT | AB_383S_JCT | Altalink Management Ltd. |  |  | Alberta
| Keystone 384S | AB_384S_DSS | Altalink Management Ltd. |  |  | Alberta
| Kidney Lake 878S | AB_878S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Killarney Lake 267S | AB_267S_DSS | Altalink Management Ltd. |  |  | Alberta
| Killarney Lake 267S JCT | AB_267S_JCT | Altalink Management Ltd. |  |  | Alberta
| Kingman 299S | AB_299S_DSS | Altalink Management Ltd. |  |  | Alberta
| Kingman 299S JCT | AB_299S_JCT | Altalink Management Ltd. |  |  | Alberta
| Kinosis 856S | AB_856S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Kinuso 727S | AB_727S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Kirby 651S | AB_651S_DSS | Altalink Management Ltd. |  |  | Alberta
| Kitscoty 705S | AB_705S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Knightsbridge 216S | AB_216S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ksituan River 754S | AB_754S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Lac La Biche 157S | AB_157S_DSS | Altalink Management Ltd. |  |  | Alberta
| Lacorey 721S | AB_721S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Lake Louise 953S | AB_953S_DSS | Altalink Management Ltd. |  |  | Alberta
| Lakesend 508S | AB_508S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Lakeview 593S | AB_593S_DSS | Altalink Management Ltd. |  |  | Alberta
| Lambton E803S | AB_E803S_DSS | EPCOR | 53.4973 | -113.4168 | Alberta
| Lamoureux 71S | AB_71S_DSS | Altalink Management Ltd. |  |  | Alberta
| Lanfine 959S | AB_959S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Langdon 102S | AB_102S_DSS | Altalink Management Ltd. |  |  | Alberta
| Laura Lake 661S | AB_661S_DSS | Altalink Management Ltd. |  |  | Alberta
| Laura Lake 661S JCT | AB_661S_JCT | Altalink Management Ltd. |  |  | Alberta
| Leduc 325S | AB_325S_DSS | Altalink Management Ltd. |  |  | Alberta
| Leismer 72S | AB_72S_DSS | Altalink Management Ltd. |  |  | Alberta
| Leming Lake 715S | AB_715S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Limestone 304S | AB_304S_DSS | Altalink Management Ltd. |  |  | Alberta
| Lindbergh 969S | AB_969S_GSS | ATCO Electric Ltd. | 53.8753 | -110.6737 | Alberta
| Lindbergh 969S JCT | AB_969S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Little Smoky 813S | AB_813S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Livock 939S | AB_939S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Lloydminster 716S | AB_716S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Lodgepole 61S | AB_61S_DSS | Altalink Management Ltd. |  |  | Alberta
| Long Lake 841S | AB_841S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Long Lake Cogen 864S | AB_864S_GSS | ATCO Electric Ltd. |  |  | Alberta
| Louise Creek 809S | AB_809S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Lowe Lake 944S | AB_944S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Loyalist 903S | AB_903S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Lubicon 780S | AB_780S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Lundbreck 513S | AB_513S_DSS | Altalink Management Ltd. |  |  | Alberta
| Macdonald 146S | AB_146S_DSS | Altalink Management Ltd. |  |  | Alberta
| Mackay River 874S | AB_874S_GSS | ATCO Electric Ltd. | 57.0413 | -111.9055 | Alberta
| Madden 373S | AB_373S_DSS | Altalink Management Ltd. |  |  | Alberta
| Madden 373S JCT | AB_373S_JCT | Altalink Management Ltd. |  |  | Alberta
| Magcan 142S | AB_142S_DSS | Altalink Management Ltd. |  |  | Alberta
| Magcan 142S JCT | AB_142S_JCT | Altalink Management Ltd. |  |  | Alberta
| Magrath 225S | AB_225S_GSS | Altalink Management Ltd. | 49.3859 | -112.9488 | Alberta
| Mahihkan 837S | AB_837S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mahkeses 889S | AB_889S_GSS | ATCO Electric Ltd. | 54.5838 | -110.3934 | Alberta
| Mahno 909S | AB_909S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mannix Mine 765S | AB_765S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mannix Mine 765S JCT | AB_765S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Marguerite Lake 826S | AB_826S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mariana 833S | AB_833S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mariana 833S JCT | AB_833S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Marion 21S | AB_21S_DSS | Altalink Management Ltd. |  |  | Alberta
| Marion 21S JCT | AB_21S_JCT | Altalink Management Ltd. |  |  | Alberta
| Marion Lake 873S | AB_873S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Marlboro 348S | AB_348S_DSS | Altalink Management Ltd. |  |  | Alberta
| Marlboro 348S JCT | AB_348S_JCT | Altalink Management Ltd. |  |  | Alberta
| Mcbride Lake 240S | AB_240S_GSS | Altalink Management Ltd. | 49.6123 | -113.4815 | Alberta
| Mcbride Lake 240S JCT | AB_240S_JCT | Altalink Management Ltd. |  |  | Alberta
| Mcclelland 957S | AB_957S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mcmillan 885S | AB_885S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mcneill Station 840S | AB_840S_DSS | Altalink Management Ltd. |  |  | Alberta
| Meadow Creek 2081S | AB_2081S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Meadow Creek 2081S JCT | AB_2081S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Meadowlark | AB_XMEA_DSS | EPCOR | 53.5176 | -113.5869 | Alberta
| Medicine Hat 41S | AB_41S_GSS | Altalink Management Ltd. | 50.1004 | -110.7276 | Alberta
| Meikle 905S | AB_905S_DSS | ATCO Electric Ltd. | 57.1031 | -117.5648 | Alberta
| Melito 890S | AB_890S_DSS | ATCO Electric Ltd. | 58.4416 | -117.2193 | Alberta
| Melito 890S JCT | AB_890S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Mercer Hill 728S | AB_728S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mercer Hill 728S JCT | AB_728S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Metiskow 648S | AB_648S_DSS | Altalink Management Ltd. |  |  | Alberta
| Michichi Creek 802S | AB_802S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mildred Lake | AB_XMIL_GSS | Syncrude |  |  | Alberta
| Millar Western 484S | AB_484S_DSS | Altalink Management Ltd. |  |  | Alberta
| Milo 356S | AB_356S_DSS | Altalink Management Ltd. |  |  | Alberta
| Mitsue 732S | AB_732S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mobil Oil Carson Creek 887S | AB_887S_ISS | Altalink Management Ltd. |  |  | Alberta
| Mobil Oil Carson Creek 887S JCT | AB_887S_JCT | Altalink Management Ltd. |  |  | Alberta
| Monarch 492S | AB_492S_DSS | Altalink Management Ltd. |  |  | Alberta
| Monarch 492S JCT | AB_492S_JCT | Altalink Management Ltd. |  |  | Alberta
| Monitor 774S | AB_774S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Moon Lake 131S | AB_131S_DSS | Altalink Management Ltd. |  |  | Alberta
| Morse River 851S | AB_851S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mountain Coalbed 411S | AB_411S_DSS | Altalink Management Ltd. |  |  | Alberta
| Mountain Coalbed 411S JCT | AB_411S_JCT | Altalink Management Ltd. |  |  | Alberta
| Mowat 2033S | AB_2033S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Mowat 2033S JCT | AB_2033S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Mt. Allan 115S | AB_115S_DSS | Altalink Management Ltd. |  |  | Alberta
| Muir 2018S | AB_2018S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Muir 2018S JCT | AB_2018S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Muskeg River 847S | AB_847S_GSS | ATCO Electric Ltd. | 57.2537 | -111.5064 | Alberta
| N.E. Lacombe 212S | AB_212S_DSS | Altalink Management Ltd. |  |  | Alberta
| N.W. Cardiff 191S | AB_191S_DSS | Altalink Management Ltd. |  |  | Alberta
| Nabiye 942S | AB_942S_GSS | ATCO Electric Ltd. | 54.7265 | -110.3441 | Alberta
| Namaka 428S | AB_428S_DSS | Altalink Management Ltd. |  |  | Alberta
| Namao | AB_XNAM_DSS | EPCOR | 53.5852 | -113.4929 | Alberta
| Narrows Creek 858S | AB_858S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Nelson Lake 429S | AB_429S_DSS | Altalink Management Ltd. |  |  | Alberta
| Nevis 766S | AB_766S_DSS | ATCO Electric Ltd. |  |  | Alberta
| New Rose Valley 635S | AB_635S_DSS | Altalink Management Ltd. |  |  | Alberta
| New Rose Valley 635S JCT | AB_635S_JCT | Altalink Management Ltd. |  |  | Alberta
| Newell 2075S | AB_2075S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Nilrem 574S | AB_574S_DSS | Altalink Management Ltd. |  |  | Alberta
| Nipisi 796S | AB_796S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Nisku 149S | AB_149S_DSS | Altalink Management Ltd. |  |  | Alberta
| Norberg 936S | AB_936S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Norberg 936S JCT | AB_936S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Norcen 812S | AB_812S_DSS | ATCO Electric Ltd. |  |  | Alberta
| North Barrhead 69S | AB_69S_DSS | Altalink Management Ltd. |  |  | Alberta
| North Calder 37S | AB_37S_DSS | Altalink Management Ltd. |  |  | Alberta
| North Holden 395S | AB_395S_DSS | Altalink Management Ltd. |  |  | Alberta
| North Lethbridge 370S | AB_370S_DSS | Altalink Management Ltd. |  |  | Alberta
| North Red Deer 217S | AB_217S_DSS | Altalink Management Ltd. |  |  | Alberta
| North St. Albert 99S | AB_99S_DSS | Altalink Management Ltd. |  |  | Alberta
| Nose Creek 284S | AB_284S_DSS | Altalink Management Ltd. |  |  | Alberta
| Oakland 946S | AB_946S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Okotoks 678S | AB_678S_DSS | Altalink Management Ltd. |  |  | Alberta
| Oldman River 806S | AB_806S_GSS | Altalink Management Ltd. | 49.561 | -113.896 | Alberta
| Olds 55S | AB_55S_DSS | Altalink Management Ltd. |  |  | Alberta
| Onoway 352S | AB_352S_DSS | Altalink Management Ltd. |  |  | Alberta
| Opal 439S | AB_439S_DSS | Altalink Management Ltd. |  |  | Alberta
| Otauwau 729S | AB_729S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Oyen 767S | AB_767S_DSS | ATCO Electric Ltd. |  |  | Alberta
| P&G A808S | AB_A808S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Paddle River 106S | AB_106S_DSS | Altalink Management Ltd. |  |  | Alberta
| Paddle River 106S JCT | AB_106S_JCT | Altalink Management Ltd. |  |  | Alberta
| Paintearth 863S | AB_863S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Parsons Creek 718S | AB_718S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Peace Butte 404S | AB_404S_DSS | Altalink Management Ltd. |  |  | Alberta
| Pegasus Lake 659S | AB_659S_DSS | Altalink Management Ltd. |  |  | Alberta
| Pegasus Lake 659S JCT | AB_659S_JCT | Altalink Management Ltd. |  |  | Alberta
| Peigan 59S | AB_59S_DSS | Altalink Management Ltd. |  |  | Alberta
| Pemukan 932S | AB_932S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Petro Canada Brazeau River 489S | AB_489S_ISS | Altalink Management Ltd. |  |  | Alberta
| Petro Canada Edmonton 184S | AB_184S_DSS | Altalink Management Ltd. |  |  | Alberta
| Petrolia 816S | AB_816S_DSS | EPCOR | 53.4622 | -113.5623 | Alberta
| Picture Butte 120S | AB_120S_DSS | Altalink Management Ltd. |  |  | Alberta
| Pigeon Lake 964S | AB_964S_DSS | Altalink Management Ltd. |  |  | Alberta
| Pike 170S | AB_170S_DSS | Altalink Management Ltd. |  |  | Alberta
| Pincher Creek 396S | AB_396S_DSS | Altalink Management Ltd. |  |  | Alberta
| Pinedale 207S | AB_207S_DSS | Altalink Management Ltd. |  |  | Alberta
| Piper Creek 247S | AB_247S_DSS | Altalink Management Ltd. |  |  | Alberta
| Plamondon 353S | AB_353S_DSS | Altalink Management Ltd. |  |  | Alberta
| Plant 30-2 UE-1 | AB_UE1S_DSS | Syncrude |  |  | Alberta
| Pocaterra 48S | AB_48S_GSS | Altalink Management Ltd. | 50.6993 | -115.1194 | Alberta
| Ponoka 331S | AB_331S_DSS | Altalink Management Ltd. |  |  | Alberta
| Poplar Hill 790S | AB_790S_GSS | ATCO Electric Ltd. | 57.008 | -111.4868 | Alberta
| Poundmaker | AB_XPOU_DSS | EPCOR | 53.5494 | -113.6508 | Alberta
| Primrose 859S | AB_859S_GSS | ATCO Electric Ltd. | 54.6963 | -110.7238 | Alberta
| Provost 545S | AB_545S_DSS | Altalink Management Ltd. |  |  | Alberta
| Queensland 301S | AB_301S_DSS | Altalink Management Ltd. |  |  | Alberta
| Queensland 301S JCT | AB_301S_JCT | Altalink Management Ltd. |  |  | Alberta
| Queenstown 504S | AB_504S_DSS | Altalink Management Ltd. |  |  | Alberta
| Quigley 989S | AB_989S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Rainbow Cogen 850S | AB_850S_GSS | ATCO Electric Ltd. | 58.4471 | -119.2383 | Alberta
| Rainbow Lake 791S | AB_791S_GSS | ATCO Electric Ltd. | 58.4471 | -119.2383 | Alberta
| Rangeland Yarrow 995S | AB_995S_DSS | Altalink Management Ltd. |  |  | Alberta
| Raven River 634S | AB_634S_DSS | Altalink Management Ltd. |  |  | Alberta
| Raven River 634S JCT | AB_634S_JCT | Altalink Management Ltd. |  |  | Alberta
| Raymond Reservoir 313S | AB_313S_GSS | Altalink Management Ltd. | 49.4071 | -112.6924 | Alberta
| Raymond Reservoir 313S JCT | AB_313S_JCT | Altalink Management Ltd. |  |  | Alberta
| Red Deer 63S | AB_63S_DSS | Altalink Management Ltd. |  |  | Alberta
| Red Deer Downtown RD15S | AB_RD15S_DSS | Altalink Management Ltd. |  |  | Alberta
| Red Deer North RD14S | AB_RD14S_DSS | Altalink Management Ltd. |  |  | Alberta
| Redwater 171S | AB_171S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ribstone Creek 892S | AB_892S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Richdale 776S | AB_776S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Ricinus 581S | AB_581S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ricinus 581S JCT | AB_581S_JCT | Altalink Management Ltd. |  |  | Alberta
| Rimbey 297S | AB_297S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ring Creek 853S | AB_853S_DSS | ATCO Electric Ltd. | 57.7425 | -119.992 | Alberta
| Riverbend 618S | AB_618S_DSS | Altalink Management Ltd. |  |  | Alberta
| Riverbend 618S JCT | AB_618S_JCT | Altalink Management Ltd. |  |  | Alberta
| Riverside 388S | AB_388S_DSS | Altalink Management Ltd. | 53.8162 | -113.1263 | Alberta
| Riverside 388S JCT | AB_388S_JCT | Altalink Management Ltd. |  |  | Alberta
| Rocky Mountain House 262S | AB_262S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ross Creek 906S | AB_906S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ross Creek 906S JCT | AB_906S_JCT | Altalink Management Ltd. |  |  | Alberta
| Rossdale | AB_XROS_DSS | EPCOR | 53.53 | -113.4995 | Alberta
| Rosyth 296S | AB_296S_DSS | Altalink Management Ltd. |  |  | Alberta
| Round Hill 852S | AB_852S_DSS | Altalink Management Ltd. |  |  | Alberta
| Round Hill 852S JCT | AB_852S_JCT | Altalink Management Ltd. |  |  | Alberta
| Rowley 768S | AB_768S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Rundle 35S | AB_35S_GSS | Altalink Management Ltd. | 51.0887 | -115.3736 | Alberta
| Rundle 35S JCT | AB_35S_JCT | Altalink Management Ltd. |  |  | Alberta
| Russell 632S | AB_632S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ruth Lake 848S | AB_848S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Rycroft 730S | AB_730S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Saddle Hills 865S | AB_865S_GSS | ATCO Electric Ltd. | 55.6693 | -118.9178 | Alberta
| Saddle Hills 865S JCT | AB_865S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Sagitawah 77S | AB_77S_DSS | Altalink Management Ltd. |  |  | Alberta
| Salt Creek 977S | AB_977S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Sand Hills Sub 341S | AB_341S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sandy Point 204S | AB_204S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sarah Lake 743S | AB_743S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Sarcee 42S | AB_42S_DSS | Altalink Management Ltd. | 51.0104 | -114.167 | Alberta
| Saunders Lake 289S | AB_289S_DSS | Altalink Management Ltd. |  |  | Alberta
| SC1 266S | AB_266S_DSS | Altalink Management Ltd. |  |  | Alberta
| Schrader Creek 531S | AB_531S_DSS | Altalink Management Ltd. |  |  | Alberta
| Schrader Creek 531S JCT | AB_531S_JCT | Altalink Management Ltd. |  |  | Alberta
| Scoria 318S | AB_318S_DSS | Altalink Management Ltd. |  |  | Alberta
| Scotford 409S | AB_409S_GSS | Altalink Management Ltd. | 53.7985 | -113.0943 | Alberta
| Scotford Upgrader 879S | AB_879S_ISS | Altalink Management Ltd. |  |  | Alberta
| Seal Lake 869S | AB_869S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Seal Lake 869S JCT | AB_869S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Secord 2005S | AB_2005S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Sedgewick 137S | AB_137S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sedgewick 137S JCT | AB_137S_JCT | Altalink Management Ltd. |  |  | Alberta
| Seebe 245S | AB_245S_DSS | Altalink Management Ltd. |  |  | Alberta
| Shamrock 1018S | AB_1018S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sheerness 807S | AB_807S_GSS | ATCO Electric Ltd. | 51.4426 | -111.7919 | Alberta
| Shell AOSP 402S | AB_402S_DSS | Altalink Management Ltd. |  |  | Alberta
| Shell AOSP 402S JCT | AB_402S_JCT | Altalink Management Ltd. |  |  | Alberta
| Shell Harmattan 238S | AB_238S_GSS | Altalink Management Ltd. | 51.6584 | -114.1365 | Alberta
| Shell Harmattan 238S JCT | AB_238S_JCT | Altalink Management Ltd. |  |  | Alberta
| Shell Waterton 502S | AB_502S_ISS | Altalink Management Ltd. |  |  | Alberta
| Shepard SS-25 | AB_SS25_GSS | Altalink Management Ltd. | 50.9713 | -113.8858 | Alberta
| Sherritt Gordon 172S | AB_172S_GSS | Altalink Management Ltd. | 53.7198 | -113.1905 | Alberta
| Sherwood Park 746S | AB_746S_DSS | Altalink Management Ltd. |  |  | Alberta
| Simonette 733S | AB_733S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Slave Lake 745S | AB_745S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Soderglen 243S | AB_243S_GSS | Altalink Management Ltd. | 49.5385 | -113.5231 | Alberta
| South Bezanson 862S | AB_862S_DSS | ATCO Electric Ltd. |  |  | Alberta
| South Mayerthorpe 443S | AB_443S_DSS | Altalink Management Ltd. |  |  | Alberta
| South Red Deer 194S | AB_194S_DSS | Altalink Management Ltd. |  |  | Alberta
| Spray 33S | AB_33S_GSS | Altalink Management Ltd. | 51.0745 | -115.4024 | Alberta
| Spring Coulee 385S | AB_385S_GSS | Altalink Management Ltd. | 49.2871 | -113.1577 | Alberta
| Springbank 272S | AB_272S_DSS | Altalink Management Ltd. |  |  | Alberta
| Spruce Grove 595S | AB_595S_DSS | Altalink Management Ltd. | 53.5672 | -113.7839 | Alberta
| SS-1 | AB_SS01_DSS | ENMAX Power Corporation | 51.0454 | -114.078 | Alberta
| SS-10 | AB_SS10_DSS | ENMAX Power Corporation | 51.0083 | -114.0955 | Alberta
| SS-11 | AB_SS11_DSS | ENMAX Power Corporation | 51.1243 | -114.0486 | Alberta
| SS-12 | AB_SS12_DSS | ENMAX Power Corporation | 51.0083 | -114.0667 | Alberta
| SS-13 | AB_SS13_DSS | ENMAX Power Corporation | 51.0821 | -114.0465 | Alberta
| SS-14 | AB_SS14_DSS | ENMAX Power Corporation | 51.1254 | -114.1867 | Alberta
| SS-15 | AB_SS15_DSS | ENMAX Power Corporation | 51.0696 | -114.1651 | Alberta
| SS-16 | AB_SS16_DSS | ENMAX Power Corporation | 51.1024 | -114.1634 | Alberta
| SS-2 | AB_SS02_DSS | ENMAX Power Corporation | 51.0265 | -114.0392 | Alberta
| SS-20 | AB_SS20_DSS | ENMAX Power Corporation | 51.0516 | -114.1188 | Alberta
| SS-21 | AB_SS21_DSS | ENMAX Power Corporation | 51.0518 | -114.1659 | Alberta
| SS-22 | AB_SS22_DSS | ENMAX Power Corporation | 51.0703 | -114.0027 | Alberta
| SS-23 | AB_SS23_DSS | ENMAX Power Corporation | 51.0093 | -114.0026 | Alberta
| SS-24 | AB_SS24_DSS | ENMAX Power Corporation | 50.9644 | -113.9361 | Alberta
| SS-26 | AB_SS26_DSS | ENMAX Power Corporation | 50.9012 | -113.9532 | Alberta
| SS-27 | AB_SS27_DSS | ENMAX Power Corporation | 51.0904 | -114.0935 | Alberta
| SS-28 | AB_SS28_DSS | ENMAX Power Corporation | 51.0103 | -114.1608 | Alberta
| SS-3 | AB_SS03_DSS | ENMAX Power Corporation | 51.0677 | -114.0643 | Alberta
| SS-31 | AB_SS31_DSS | ENMAX Power Corporation | 50.9801 | -113.9859 | Alberta
| SS-32 | AB_SS32_DSS | ENMAX Power Corporation | 50.951 | -114.0188 | Alberta
| SS-33 | AB_SS33_DSS | ENMAX Power Corporation | 50.9496 | -114.0781 | Alberta
| SS-34 | AB_SS34_DSS | ENMAX Power Corporation | 51.082 | -114.1394 | Alberta
| SS-35 | AB_SS35_DSS | ENMAX Power Corporation | 50.9791 | -114.1405 | Alberta
| SS-36 | AB_SS36_DSS | ENMAX Power Corporation | 51.1063 | -114.2364 | Alberta
| SS-37 | AB_SS37_DSS | ENMAX Power Corporation | 51.0093 | -113.9361 | Alberta
| SS-38 | AB_SS38_DSS | ENMAX Power Corporation | 51.0535 | -113.9361 | Alberta
| SS-39 | AB_SS39_DSS | ENMAX Power Corporation | 51.0952 | -113.9401 | Alberta
| SS-40 | AB_SS40_DSS | ENMAX Power Corporation | 50.914 | -114.0125 | Alberta
| SS-41 | AB_SS41_DSS | ENMAX Power Corporation | 50.9064 | -114.0694 | Alberta
| SS-43 | AB_SS43_DSS | ENMAX Power Corporation | 50.9804 | -114.0736 | Alberta
| SS-47 | AB_SS47_DSS | ENMAX Power Corporation | 51.1679 | -114.1061 | Alberta
| SS-5 | AB_SS05_DSS | ENMAX Power Corporation | 51.0435 | -114.0573 | Alberta
| SS-54 | AB_SS54_DSS | ENMAX Power Corporation | 50.8513 | -113.9765 | Alberta
| SS-6 | AB_SS06_DSS | ENMAX Power Corporation | 50.9062 | -114.1393 | Alberta
| SS-65 | AB_SS65_DSS | ENMAX Power Corporation | 50.9089 | -113.9012 | Alberta
| SS-7 | AB_SS07_DSS | ENMAX Power Corporation | 51.0658 | -114.2301 | Alberta
| SS-8 | AB_SS08_DSS | ENMAX Power Corporation | 51.0496 | -114.0813 | Alberta |  | Underground substation
| SS-9 | AB_SS09_DSS | ENMAX Power Corporation | 50.9954 | -114.0433 | Alberta
| St. Paul 707S | AB_707S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Stavely 349S | AB_349S_DSS | Altalink Management Ltd. |  |  | Alberta
| Steepbak River 836S | AB_836S_DSS | Suncor |  |  | Alberta
| Stelco Edmonton East 133S | AB_133S_DSS | Altalink Management Ltd. |  |  | Alberta
| Stettler 769S | AB_769S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Stirling 67S | AB_67S_GSS | Altalink Management Ltd. |  |  | Alberta
| Stony Plain 434S | AB_434S_DSS | Altalink Management Ltd. |  |  | Alberta
| Strachan 263S | AB_263S_DSS | Altalink Management Ltd. |  |  | Alberta
| Strathcona | AB_XSTR_GSS | EPCOR | 53.4887 | -113.4868 | Alberta
| Strathmore 151S | AB_151S_GSS | Altalink Management Ltd. | 51.0327 | -113.3767 | Alberta
| Strome 223S | AB_223S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sturgeon 2 881S | AB_881S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Sturgeon 734S | AB_734S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Suffield 895S | AB_895S_GSS | Altalink Management Ltd. | 50.2194 | -111.1597 | Alberta
| Sullivan Lake 775S | AB_775S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Sulphur Point 828S | AB_828S_DSS | ATCO Electric Ltd. | 58.588 | -118.9145 | Alberta
| Summerside 657S | AB_657S_DSS | Altalink Management Ltd. |  |  | Alberta
| Summerview 354S | AB_354S_GSS | Altalink Management Ltd. | 49.5829 | -113.7931 | Alberta
| Summit 653S | AB_653S_DSS | Altalink Management Ltd. |  |  | Alberta
| Summit 653S JCT | AB_653S_JCT | Altalink Management Ltd. |  |  | Alberta
| Sundance 310P | AB_310P_GSS | Altalink Management Ltd. | 53.5075 | -114.5569 | Alberta
| Sundance 310P JCT | AB_310P_JCT | Altalink Management Ltd. |  |  | Alberta
| Sundance Blow-Down 867S | AB_867S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sundance Blow-Down 867S JCT | AB_867S_JCT | Altalink Management Ltd. |  |  | Alberta
| Sundance SS 821S | AB_821S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sunday Creek 539S | AB_539S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sundre 575S | AB_575S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sunken Lake 221S | AB_221S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sunken Lake 221S JCT | AB_221S_JCT | Altalink Management Ltd. |  |  | Alberta
| Sunnybrook 510S | AB_510S_DSS | Altalink Management Ltd. |  |  | Alberta
| Sunshine Village 945S | AB_945S_DSS | Altalink Management Ltd. |  |  | Alberta
| Swan River 735S | AB_735S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Swandive 854S | AB_854S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Sweetheart Lake 2032S | AB_2032S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Sylvan Lake 680S | AB_680S_DSS | Altalink Management Ltd. |  |  | Alberta
| Syncrude D05 | AB_D05S_ISS | Syncrude |  |  | Alberta
| T.M.P.L. Gainford 165S | AB_165S_ISS | Altalink Management Ltd. |  |  | Alberta
| T.M.P.L. Gainford 165S JCT | AB_165S_JCT | Altalink Management Ltd. |  |  | Alberta
| Taber 83S | AB_83S_DSS | Altalink Management Ltd. | 49.7822 | -112.1501 | Alberta
| Taber Wind Farm 134S | AB_134S_GSS | Altalink Management Ltd. | 49.7184 | -111.9266 | Alberta
| Taber Wind Farm 134S JCT | AB_134S_JCT | Altalink Management Ltd. |  |  | Alberta
| Thickwood Hills 951S | AB_951S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Thompson 140S | AB_140S_DSS | Altalink Management Ltd. |  |  | Alberta
| Thompson 140S JCT | AB_140S_JCT | Altalink Management Ltd. |  |  | Alberta
| Thornton 2091S | AB_2091S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Three Hills 770S | AB_770S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Three Sisters 36S | AB_36S_GSS | Altalink Management Ltd. | 50.9985 | -115.3746 | Alberta
| Tilley 498S | AB_498S_DSS | Altalink Management Ltd. | 50.5339 | -111.6702 | Alberta
| Tinchebray 972S | AB_972S_DSS | ATCO Electric Ltd. |  |  | Alberta
| TMPL Niton 228S | AB_228S_ISS | Altalink Management Ltd. |  |  | Alberta
| Tower Road 933S | AB_933S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Travers 554S | AB_554S_DSS | Altalink Management Ltd. |  |  | Alberta
| Triangle 882S | AB_882S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Triangle 882S JCT | AB_882S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Truweld Grating 6500S | AB_6500S_ISS | Altalink Management Ltd. |  |  | Alberta
| Truweld Grating 6500S JCT | AB_6500S_JCT | Altalink Management Ltd. |  |  | Alberta
| Tucuman 478S | AB_478S_DSS | Altalink Management Ltd. |  |  | Alberta
| Turbo Balzac 391S | AB_391S_DSS | Altalink Management Ltd. |  |  | Alberta
| Underwood 183S | AB_183S_DSS | Altalink Management Ltd. |  |  | Alberta
| Union Carbide Prentiss 276S | AB_276S_ISS | Altalink Management Ltd. |  |  | Alberta
| Updike 886S | AB_886S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Uplands 241S | AB_241S_DSS | Altalink Management Ltd. |  |  | Alberta
| Valleyview 794S | AB_794S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Vauxhall 158S | AB_158S_DSS | Altalink Management Ltd. | 50.1091 | -112.1421 | Alberta
| Vegreville 709S | AB_709S_DSS | ATCO Electric Ltd. | 53.6934 | -111.9786 | Alberta
| Vermilion 710S | AB_710S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Veteran 771S | AB_771S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Victoria E511S | AB_E511S_DSS | EPCOR | 53.5489 | -113.4998 | Alberta
| Vilna 777S | AB_777S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Violet Grove 283S | AB_283S_DSS | Altalink Management Ltd. |  |  | Alberta
| Virginia Hills 738S | AB_738S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Viscount 92S | AB_92S_DSS | Altalink Management Ltd. |  |  | Alberta
| Vista 1029S | AB_1029S_DSS | Altalink Management Ltd. |  |  | Alberta
| Vulcan 255S | AB_255S_DSS | Altalink Management Ltd. |  |  | Alberta
| Wabamun 19S | AB_19S_DSS | Altalink Management Ltd. |  |  | Alberta
| Wabamun 2739S | AB_2739S_DSS | Altalink Management Ltd. |  |  | Alberta
| Wabasca 720S | AB_720S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Waddel 907S | AB_907S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Wainright 51S | AB_51S_DSS | Altalink Management Ltd. |  |  | Alberta
| Wap 1S | AB_1S_DSS | Dapp Power Corporation |  |  | Alberta
| Wap 1S JCT | AB_1S_JCT | Dapp Power Corporation |  |  | Alberta
| Wapiti 823S | AB_823S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Wapiti 823S JCT | AB_823S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Wardlow 230S | AB_230S_DSS | Altalink Management Ltd. |  |  | Alberta
| Ware Junction 132S | AB_132S_DSS | Altalink Management Ltd. |  |  | Alberta
| Warner 344S | AB_344S_DSS | Altalink Management Ltd. |  |  | Alberta
| Waterton 379S | AB_379S_DSS | Altalink Management Ltd. |  |  | Alberta
| Watson Creek 104S | AB_104S_DSS | Altalink Management Ltd. |  |  | Alberta
| Watt Lake 956S | AB_956S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Watt Lake 956S JCT | AB_956S_JCT | ATCO Electric Ltd. |  |  | Alberta
| Waupisoo 405S | AB_405S_DSS | Altalink Management Ltd. |  |  | Alberta
| Weasel Creek 947S | AB_947S_DSS | Altalink Management Ltd. |  |  | Alberta
| Weasel Creek 947S JCT | AB_947S_JCT | Altalink Management Ltd. |  |  | Alberta
| Wesley Creek 834S | AB_834S_DSS | ATCO Electric Ltd. |  |  | Alberta
| West Brooks 28S | AB_28S_DSS | Altalink Management Ltd. |  |  | Alberta
| West Cascade 177S | AB_177S_DSS | Altalink Management Ltd. |  |  | Alberta
| West Crossfield 316S | AB_316S_DSS | Altalink Management Ltd. |  |  | Alberta
| West Pembina 359S | AB_359S_DSS | Altalink Management Ltd. |  |  | Alberta
| West Pembina 359S JCT | AB_359S_JCT | Altalink Management Ltd. |  |  | Alberta
| West Pembina 477S | AB_477S_GSS | Altalink Management Ltd. | 53.0979 | -115.3157 | Alberta
| Westfield 107S | AB_107S_DSS | Altalink Management Ltd. |  |  | Alberta
| Westlock 438S | AB_438S_GSS | Altalink Management Ltd. |  |  | Alberta
| Westpeace 793S | AB_793S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Westwood 422S | AB_422S_DSS | Altalink Management Ltd. |  |  | Alberta
| Wetaskiwin 40S | AB_40S_DSS | Altalink Management Ltd. |  |  | Alberta
| Wetaskiwin 40S JCT | AB_40S_JCT | Altalink Management Ltd. |  |  | Alberta
| Wheatland 609S | AB_609S_GSS | ATCO Electric Ltd. | 51.2314 | -112.4079 | Alberta
| Whitby Lake 819S | AB_819S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Whitecourt 268S | AB_268S_DSS | Altalink Management Ltd. |  |  | Alberta
| Whitecourt Industrial 364S | AB_364S_ISS | Altalink Management Ltd. |  |  | Alberta
| Whitecourt Power 323S | AB_323S_GSS | Altalink Management Ltd. |  |  | Alberta
| Whitefish Lake 825S | AB_825S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Whitla 251S | AB_251S_DSS | Altalink Management Ltd. |  |  | Alberta
| Willesdengreen 68S | AB_68S_DSS | Altalink Management Ltd. |  |  | Alberta
| Willesdengreen 68S JCT | AB_68S_JCT | Altalink Management Ltd. |  |  | Alberta
| Willow Lake 2009S | AB_2009S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Windy Flats 138S | AB_138S_DSS | Altalink Management Ltd. |  |  | Alberta
| Windy Point 112S | AB_112S_DSS | Altalink Management Ltd. |  |  | Alberta
| Windy Point 112S JCT | AB_112S_JCT | Altalink Management Ltd. |  |  | Alberta
| Winefred 818S | AB_818S_DSS | Altalink Management Ltd. |  |  | Alberta
| Wintering Hills 804S | AB_804S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Wolf Creek 288S | AB_288S_DSS | Altalink Management Ltd. |  |  | Alberta
| Wolf Lake 822S | AB_822S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Woodcroft | AB_XWOO_DSS | EPCOR | 53.5711 | -113.5651 | Alberta
| Yasa 286S | AB_286S_DSS | Altalink Management Ltd. |  |  | Alberta
| Yeo 2015S | AB_2015S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Youngstown 772S | AB_772S_DSS | ATCO Electric Ltd. |  |  | Alberta
| Zama 795S | AB_795S_DSS | ATCO Electric Ltd. | 59.0671 | -118.8461 | Alberta
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## Distribution
AB | EXISTING TRANSFORMERS
| Substation Name | Substation Code | Owner | Latitude | Longitude | Operating Region | Transformers | Primary Voltage | Secondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Other References | Notes | Count
[8 empty] | (kV) | (kV) | (MVA) | (MVA) |  | (MW) | (MW)
| 29EDD-0056 | AB_E56S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 1
| 29EDD-0063 | AB_E63S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 2
| 29EDD-1 | AB_E1S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 3
| 29EDD-10 | AB_E10S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 4
| 29EDD-18 | AB_E18S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 5
| 29EDD-19 | AB_E19S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 6
| 29EDD-2 | AB_E2S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 7
| 29EDD-20 | AB_E20S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 8
| 29EDD-22 | AB_E22S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 9
| 29EDD-29 | AB_E29S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 10
| 29EDD-3 | AB_E3S_ISS |  |  |  | Alberta |  | 240 | [8 empty] | 11
| 29EDD-31 | AB_E31S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 12
| 29EDD-33 | AB_E33S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 13
| 29EDD-34 | AB_E34S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 14
| 29EDD-45 | AB_E45S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 15
| 29EDD-46 | AB_E46S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 16
| 29EDD-5 | AB_E5S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 17
| 29EDD-55 | AB_E55S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 18
| 29EDD-62 | AB_E62S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 19
| 29EDD-64 | AB_E64S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 20
| 29EDD-65 | AB_E65S_ISS |  |  |  | Alberta |  | 240 | [8 empty] | 21
| 29EDD-67 | AB_E67S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 22
| 29EDD-7 | AB_E7S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 23
| 29EDD-71 | AB_E71S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 24
| 29EDD-8 | AB_E8S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 25
| 29EDD-83 | AB_E83S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 26
| 29EDD-84 | AB_E84S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 27
| 29EDD-9 | AB_E9S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 28
| 29EDD-93 | AB_E93S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 29
| 29EDD-94 | AB_E94S_ISS |  |  |  | Alberta |  | 240 | [8 empty] | 30
| ABEE 993S | AB_993S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 31
| ACHESON 305S | AB_305S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 32
| AEC MILLS 844S | AB_844S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 33
| AHS 01 279S | AB_279S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 34
| AIR LIQUIDE 408S | AB_408S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 35
| AL ROTHBAUER 321S | AB_321S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 36
| ALBCHEM BEAVERHILL CREEK 308S | AB_308S_ISS |  |  |  | Alberta | T1 | 138 | 13.8 | 50 | 60 | 0.9 | 45 | 54 | AESO. 2019. Abee 993S Connection Assessment |  | 37
| ALBERTA NEWSPRINT 122S | AB_122S_GSS |  | 54.1279 | -115.6659 | Alberta |  | 240 | [8 empty] | 38
| ALBRIGHT & WILSON 752S | AB_752S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 39
| ALGAR 875S | AB_875S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 40
| AMELIA 108S | AB_108S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 41
| AMOCO EMPRESS 163S | AB_163S_ISS |  |  |  | Alberta | T5A | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2016. Jenner Connection Assessment |  | 42
| AMR02 937S | AB_937S_ISS |  |  |  | Alberta |  | 240 | [8 empty] | 43
| ANDERSON 801S | AB_801S_DSS |  |  |  | Alberta | T1 | 240 | 144 | 125 | 150 | 0.9 | 112.5 | 135 | AESO. 2017. Sharphills Connection Assessment |  | 44
| ARCENIEL 930S | AB_930S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 45
| ARDENVILLE WIND FARM 418S | AB_418S_GSS |  | 49.583 | -113.4351 | Alberta |  | 144 | [8 empty] | 46
| ARGYLL | AB_XARG_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 47
| AT PLASTIC 4RS | AB_4RS_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 48
| AT PLASTIC 5RS | AB_5RS_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 49
| ATHABASCA CROSSING EDD200 | AB_E200S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 50
| AURORA AURS | 0 |  |  |  | Alberta |  | 240 | [8 empty] | 51
| B.F.GOODRICH FORT SASK. 452S | AB_452S_ISS |  |  |  | Alberta |  | 138 | [8 empty] | 52
| BALZAC CO-GEN | AB_XBAL_GSS |  |  |  | Alberta |  | 144 | [8 empty] | 53
| BANFF 123S | AB_123S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 54
| BANNERMAN 681S | AB_681S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 55
| BARDO 197S | AB_197S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 56
| BARRIER 32S | AB_32S_GSS |  |  |  | Alberta |  | 138 | [8 empty] | 57
| BASELINE 317S | AB_317S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 58
| BASSANO 435S | AB_435S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 59
| BASSETT 747S | AB_747S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 60
| BATTLE RIVER 757S | AB_757S_GSS |  | 52.4685 | -112.1339 | Alberta | 912T | 240 | 144 | 224 | 268.8 | 0.9 | 201.6 | 241.92 | AESO. 2017. Sharphills Connection Assessment |  | 61
| BATTLE RIVER 757S | AB_757S_GSS |  | 52.4685 | -112.1339 | Alberta | 701T | 144 | 72 | 75 | 90 | 0.9 | 67.5 | 81 | AESO. 2017. Sharphills Connection Assessment |  | 62
| BAUER 918S | AB_918S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 63
| BAYMAG 437S | AB_437S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 64
| BEAMER 233S | AB_233S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 65
| BEAR CREEK 679S | AB_679S_DSS |  | 55.0715 | -118.6921 | Alberta |  | 144 | [8 empty] | 66
| BEARSPAW PLANT 44S | AB_44S_GSS |  | 51.1012 | -114.2823 | Alberta |  | 138 | [8 empty] | 67
| BEARTRAP 940S | AB_940S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 68
| BEDDINGTON SS-162 | AB_SS162_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2016. Beddington Connection Assessment |  | 69
| BEDDINGTON SS-162 | AB_SS162_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2016. Beddington Connection Assessment |  | 70
| BELLAMY | AB_XBEL_DSS |  |  |  | Alberta | T1 | 240 | 72 | 375 | 450 | 0.9 | 337.5 | 405 | AESO. 2017. Clover Bar Connection Assessment |  | 71
| BELLAMY | AB_XBEL_DSS |  |  |  | Alberta | T2 | 240 | 72 | 375 | 450 | 0.9 | 337.5 | 405 | AESO. 2017. Clover Bar Connection Assessment |  | 72
| BENALTO 17S | AB_17S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 73
| BENBOW 397S | AB_397S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 74
| BENNETT 520S | AB_520S_DSS |  |  |  | Alberta |  | 500 | [8 empty] | 75
| BERNESE 293S | AB_293S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 76
| BICKERDIKE 39S | AB_39S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 269 | 322.8 | 0.9 | 242.1 | 290.52 | AESO. 2018. Vista Connection Assessment |  | 78
| BICKERDIKE 39S | AB_39S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 269 | 322.8 | 0.9 | 242.1 | 290.52 | AESO. 2018. Vista Connection Assessment |  | 79
| BIG KNIFE CREEK 843S | AB_843S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 80
| BIG MOUNTAIN 845S | AB_845S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 81
| BIGFOOT 756S | AB_756S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 82
| BIGHORN PLANT 250P | AB_250P_GSS |  | 52.3081 | -116.3245 | Alberta |  | 144 | [8 empty] | 83
| BIGSTONE 86S | AB_86S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2016. Cooking Lake Connection Assessment |  | 84
| BILBY 105S | AB_105S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 85
| BINDLOSS 914S | AB_914S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 86
| BIRCHWOOD CREEK 960S | AB_960S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 87
| BITUMOUNT 941S | AB_941S_ISS |  |  |  | Alberta |  | 240 | [8 empty] | 88
| BLACK DIAMOND 392S | AB_392S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 89
| BLACK FLY 934S | AB_934S_ISS |  |  |  | Alberta |  | 240 | [8 empty] | 90
| BLACK SPRUCE 154S | AB_154S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 91
| BLACKFALDS 198S | AB_198S_DSS |  | 52.3813 | -113.7967 | Alberta |  | 144 | [8 empty] | 92
| BLACKIE 253S | AB_253S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 93
| BLACKMUD 155S | AB_155S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 94
| BLACKSPRING RIDGE 485S | AB_485S_DSS |  | 50.1525 | -112.8226 | Alberta |  | 240 | [8 empty] | 95
| BLATCHFORD | AB_XBLA_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 96
| BLUE RIDGE LUMBER 701S | AB_701S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 97
| BLUE TRAIL 528S | AB_528S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 98
| BLUMENORT 832S | AB_832S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 99
| BOHN 931S | AB_931S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 100
| BONNYVILLE 700S | AB_700S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 101
| BOUCHER CREEK 829S | AB_829S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 102
| BOURQUE 970S | AB_970S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 103
| BOWMANTON 244S | AB_244S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2016. Bullshead Connection Assessment |  | 104
| BOWMANTON 244S | AB_244S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2016. Bullshead Connection Assessment |  | 105
| BOWRON 674S | AB_674S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 106
| BOYLE 56S | AB_56S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 107
| BRAZEAU 358S | AB_358S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 108
| BRAZEAU 62S | AB_62S_GSS |  | 52.9101 | -115.3754 | Alberta |  | 240 | [8 empty] | 109
| BRAZEAU OUTLET WORKS 294S | AB_294S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 110
| BRETONA 45S | AB_45S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Henday Connection Assessment |  | 111
| BRETVILLE 185S | AB_185S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 112
| BRIDGE CREEK 798S | AB_798S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 113
| BRIKER 880S | AB_880S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 114
| BRINTNELL 876S | AB_876S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 115
| BROADMOOR 420S | AB_420S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Henday Connection Assessment |  | 116
| BROOKFIELD 536S | AB_536S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 117
| BROOKS 121S | AB_121S_GSS |  | 50.5833 | -111.8808 | Alberta |  | 138 | [8 empty] | 118
| BRUDERHEIM 127S | AB_127S_DSS |  |  |  | Alberta | T1 | 138 | 26.5 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2019. Abee 993S Connection Assessment |  | 119
| BRUDERHEIM 127S | AB_127S_DSS |  |  |  | Alberta | T2 | 138 | 26.5 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2019. Abee 993S Connection Assessment |  | 120
| BUCHANAN CREEK 927S | AB_927S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 121
| BUCK LAKE 454S | AB_454S_GSS |  | 52.9534 | -114.7955 | Alberta |  | 144 | [8 empty] | 122
| BUFFALO CREEK 526S | AB_526S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 123
| BUFORD 538S | AB_538S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 124
| BULLPOUND 803S | AB_803S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 125
| BULLSHEAD 523S | AB_523S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 28 | 33.6 | 0.9 | 25.2 | 30.24 | AESO. 2016. Bullshead Connection Assessment |  | 126
| BULLSHEAD 523S | AB_523S_DSS |  |  |  | Alberta | T2 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Bullshead Connection Assessment |  | 127
| BURDETT 368S | AB_368S_GSS |  | 49.8434 | -111.5631 | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Fincastle Connection Assessment |  | 128
| BURDETT 368S | AB_368S_GSS |  | 49.8434 | -111.5631 | Alberta | T2 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Fincastle Connection Assessment |  | 129
| CADOMIN 983S | AB_983S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 130
| CADOTTE RIVER 783S | AB_783S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 131
| CALGARY ENERGY CENTER CEC | AB_XCEC_GSS |  |  |  | Alberta |  | 240 | [8 empty] | 132
| CANADA LIQUID AIR 337S | AB_337S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 133
| CANADIAN OXY ASTOTIN CREEK 365S | AB_365S_ISS |  |  |  | Alberta |  | 138 | [8 empty] | 134
| CANMORE 118S | AB_118S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 135
| CARDINAL RIVER 302S | AB_302S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 136
| CARMON 830S | AB_830S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 137
| CAROLINE 378S | AB_378S_GSS |  |  |  | Alberta |  | 144 | [8 empty] | 138
| CARSELAND 525S | AB_525S_GSS |  | 50.8466 | -113.5816 | Alberta |  | 138 | [8 empty] | 139
| CARVEL 432S | AB_432S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 140
| CASCADE 29S | AB_29S_GSS |  | 51.2002 | -115.5021 | Alberta |  | 138 | [8 empty] | 141
| CASCADE CONTROL DAM T756S | AB_T756S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 142
| CASSILS 324S | AB_324S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 143
| CASTLE DOWNS | AB_XCAS_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 144
| CASTLE RIVER 239S | AB_239S_GSS |  | 49.516 | -114.0276 | Alberta |  | 138 | [8 empty] | 145
| CASTLE ROCK RIDGE 205S | AB_205S_GSS |  | 49.5561 | -113.963 | Alberta |  | 240 | [8 empty] | 146
| CASTOR 759S | AB_759S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 147
| CAVALIER | AB_XCAV_DSS |  | 51.0056 | -113.1716 | Alberta |  | 144 | [8 empty] | 148
| CG&E 758S | AB_758S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 149
| CHAPEL ROCK 491S | AB_491S_DSS |  |  |  | Alberta |  | 500 | [8 empty] | 150
| CHAPPICE LAKE 649S | AB_649S_DSS |  | 50.2211 | -110.4461 | Alberta | T1 | 138 | 25 | 18.7 | 22.44 | 0.9 | 16.83 | 20.196 | AESO. 2015. Rothbauer Connection Assessment |  | 151
| CHARD 658S | AB_658S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 152
| CHERHILL 338S | AB_338S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 153
| CHESTERMERE 419S | AB_419S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 154
| CHEVIOT 101S | AB_101S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 155
| CHEVRON KAYBOB 551S | AB_551S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 156
| CHEVRON KNIGHT 355S | AB_355S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 157
| CHICKADEE CREEK 259S | AB_259S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 158
| CHIN CHUTE 315S | AB_315S_GSS |  | 49.6756 | -112.3446 | Alberta |  | 138 | [8 empty] | 159
| CHINCHAGA RIVER 779S | AB_779S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 160
| CHINOOK 181S | AB_181S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 161
| CHRISTINA LAKE 723S | AB_723S_GSS |  | 55.5628 | -110.9135 | Alberta |  | 240 | [8 empty] | 162
| CLAIRMONT LAKE 811S | AB_811S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 163
| CLIPPER 656S | AB_656S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 164
| CLOVER BAR 987S | AB_987S_GSS |  | 53.5956 | -113.3322 | Alberta | T1 | 240 | 69 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2020. Summerside Connection Assessment |  | 165
| CLOVER BAR 987S | AB_987S_GSS |  | 53.5956 | -113.3322 | Alberta | T2 | 240 | 69 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2020. Summerside Connection Assessment |  | 166
| CLYDE 150S | AB_150S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 167
| COAL VALLEY 527S | AB_527S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 168
| COALBANKS 111S | AB_111S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 169
| COALDALE 254S | AB_254S_GSS |  | 49.7362 | -112.5622 | Alberta |  | 138 | [8 empty] | 170
| COALSPUR 426S | AB_426S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 171
| COCHRANE 291S | AB_291S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 172
| COLD CREEK 602S | AB_602S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 173
| COLEMAN 799S | AB_799S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 174
| COLINTON 159S | AB_159S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 175
| CONKLIN 762S | AB_762S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 176
| CONRAD 135S | AB_135S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 177
| COOKING LAKE 522S | AB_522S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 178
| CORDEL 755S | AB_755S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 179
| CORONATION 773S | AB_773S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 180
| COWLEY RIDGE 322S | AB_322S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 181
| COYOTE LAKE 963S | AB_963S_DSS |  |  |  | Alberta | 901T | 240 | 144 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2017. Sharphills Connection Assessment |  | 182
| CRANBERRY LAKE 827S | AB_827S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 183
| CROSSINGS 511S | AB_511S_DSS |  |  |  | Alberta |  | 500 | [8 empty] | 184
| CROW 860S | AB_860S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 185
| CRYSTAL LAKE 722S | AB_722S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 186
| CUTTING LAKE 227S | AB_227S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 187
| CYNTHIA 178S | AB_178S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 188
| CYPRESS 562S | AB_562S_DSS |  |  |  | Alberta | T1 | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2016. Jenner Connection Assessment |  | 189
| CYPRESS 562S | AB_562S_DSS |  |  |  | Alberta | T2 | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2016. Jenner Connection Assessment |  | 190
| DAISHOWA 839S | AB_839S_GSS |  | 56.3711 | -117.1856 | Alberta |  | 144 | [8 empty] | 191
| DALEHURST 975S | AB_975S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 192
| DAWES 2011S | AB_2011S_DSS |  |  |  | Alberta | 901T | 250 | 144 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 193
| DEER HILL 1012S | AB_1012S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 194
| DEERLAND 13S | AB_13S_DSS |  |  |  | Alberta | T2 | 245 | 144 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2019. Abee 993S Connection Assessment |  | 195
| DEVON 14S | AB_14S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 196
| DOG RIB 2082S | AB_2082S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 197
| DOME | AB_XDOM_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 198
| DOME CUTBANK 810S | AB_810S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 199
| DONNELLY 784S | AB_784S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 200
| DOVER 888S | AB_888S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 201
| DOW CHEMICAL FORT SASK. 166S | AB_166S_ISS |  | 53.734 | -113.1714 | Alberta |  | 144 | [8 empty] | 202
| DOW HYDRO CARBONS 258S | AB_258S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 203
| DRY CREEK 186S | AB_186S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Dry Creek Connection Assessment |  | 204
| DRY CREEK 186S | AB_186S_DSS |  |  |  | Alberta | T2 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Dry Creek Connection Assessment |  | 205
| DRYWOOD 415S | AB_415S_DSS |  |  |  | Alberta | T1 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54 | AESO. 2019. Mclaughlin Connection Assessment |  | 206
| DUCHESS 339S | AB_339S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 207
| EAGLE CREEK 412S | AB_412S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 208
| EAST AIRDRIE 199S | AB_199S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2016. Dry Creek Connection Assessment |  | 209
| EAST AIRDRIE 199S | AB_199S_DSS |  |  |  | Alberta | T2 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Dry Creek Connection Assessment |  | 210
| EAST CALGARY 5S | AB_5S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. CEC Connection Assessment |  | 211
| EAST CALGARY 5S | AB_5S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. CEC Connection Assessment |  | 212
| EAST CAMROSE 285S | AB_285S_GSS |  |  |  | Alberta |  | 138 | [8 empty] | 213
| EAST CROSSFIELD 64S | AB_64S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 191 | 229.2 | 0.9 | 171.9 | 206.28 | AESO. 2016. Beddington Connection Assessment |  | 214
| EAST EDMONTON 38S | AB_38S_DSS |  |  |  | Alberta | T3 | 138 | 25 | 93.3 | 111.96 | 0.9 | 83.97 | 100.764 | AESO. 2015. Broadmoor Connection Assessment |  | 226
| EAST EDMONTON 38S | AB_38S_DSS |  |  |  | Alberta | T4 | 240 | 138 | 337 | 404.4 | 0.9 | 303.3 | 363.96 | AESO. 2015. Broadmoor Connection Assessment |  | 227
| EAST EDMONTON 38S | AB_38S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 341.8 | 410.16 | 0.9 | 307.62 | 369.144 | AESO. 2020. Summerside Connection Assessment |  | 215
| EAST EDMONTON 38S | AB_38S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 340.6 | 408.72 | 0.9 | 306.54 | 367.848 | AESO. 2020. Summerside Connection Assessment |  | 216
| EAST INDUSTRIAL E52S | AB_E52S_DSS |  |  |  | Alberta | T1 | 240 | 25 | 63 | 75.6 | 0.9 | 56.7 | 68.04 | AESO. 2020. Summerside Connection Assessment |  | 218
| EAST INDUSTRIAL E52S | AB_E52S_DSS |  |  |  | Alberta | T2 | 240 | 25 | 63 | 75.6 | 0.9 | 56.7 | 68.04 | AESO. 2020. Summerside Connection Assessment |  | 219
| EAST STAVELY 928S | AB_928S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 220
| ECKVILLE 534S | AB_534S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 221
| EDGERTON 899S | AB_899S_DSS |  |  |  | Alberta | T3 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2018. Wheatland Connection Assessment |  | 222
| EDITH LAKE 739S | AB_739S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 223
| EDSON 58S | AB_58S_GSS |  | 53.5577 | -116.5474 | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Vista Connection Assessment |  | 230
| EDSON 58S | AB_58S_GSS |  | 53.5577 | -116.5474 | Alberta | T2 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Vista Connection Assessment |  | 231
| ELK RIVER 445S | AB_445S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 232
| ELLERSLIE 89S | AB_89S_DSS |  |  |  | Alberta | T1 | 500 | 240 | 1200 | 1440 | 0.9 | 1080 | 1296 | AESO. 2020. Summerside Connection Assessment |  | 233
| ELLERSLIE 89S | AB_89S_DSS |  |  |  | Alberta | T2 | 500 | 240 | 1200 | 1440 | 0.9 | 1080 | 1296 | AESO. 2020. Summerside Connection Assessment |  | 234
| ELLIS 332S | AB_332S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 235
| ELMWORTH 731S | AB_731S_DSS |  |  |  | Alberta | T1 | 144 | 25 | 33 | 39.6 | 0.9 | 29.7 | 35.64 | AESO. 2016. Hughes Connection Assessment |  | 236
| EMPRESS 394S | AB_394S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 237
| EMPRESS LIQUIDS 164S | AB_164S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 238
| ENCHANT 447S | AB_447S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 239
| ENGSTROM 2060S | AB_2060S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 240
| ENTWISTLE 235S | AB_235S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 241
| ERVICK 542S | AB_542S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 242
| ESSO JUDY CREEK 638S | AB_638S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 243
| ETHEL LAKE 717S | AB_717S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 244
| EUREKA RIVER 861S | AB_861S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 245
| EXCEL 910S | AB_910S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 246
| EXSHAW 985S | AB_985S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 247
| EYRE 558S | AB_558S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 248
| FEDPIPE JUDYCREEK 515S | AB_515S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 249
| FIBERGLASS | AB_XFIB_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 250
| FICKLE LAKE 406S | AB_406S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 251
| FIDLER 312S | AB_312S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2019. Travers Connection Assessment |  | 252
| FIELDGATE 824S | AB_824S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 253
| FINCASTLE 336S | AB_336S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2018. Fincastle Connection Assessment |  | 254
| FLAT LAKE 242S | AB_242S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 255
| FLATBUSH 500S | AB_500S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 256
| FLYING SHOT LAKE 749S | AB_749S_DSS |  |  |  | Alberta | T1 | 144 | 25 | 50 | 60 | 0.9 | 45 | 54 | AESO. 2016. Hughes Connection Assessment |  | 257
| FLYING SHOT LAKE 749S | AB_749S_DSS |  |  |  | Alberta | T2 | 144 | 25 | 50 | 60 | 0.9 | 45 | 54 | AESO. 2016. Hughes Connection Assessment |  | 258
| FOOTHILLS 237S | AB_237S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2016. Okotoks Connection Assessment |  | 259
| FOOTHILLS 237S | AB_237S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2016. Okotoks Connection Assessment |  | 260
| FORT ASSINIBOINE 234S | AB_234S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 262
| FORT HILLS 505S | AB_505S_GSS |  | 57.3954 | -111.5714 | Alberta |  | 240 | [8 empty] | 261
| FORT MACLEOD 15S | AB_15S_GSS |  | 49.7229 | -113.4044 | Alberta |  | 138 | [8 empty] | 263
| FORT SASK. 54S | AB_54S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2017. Heartland Connection Assessment |  | 265
| FORT SASK. 54S | AB_54S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2017. Heartland Connection Assessment |  | 266
| FORT SASK. CO-GEN 218S | AB_218S_GSS |  |  |  | Alberta |  | 144 | [8 empty] | 264
| FOSTER CREEK 1200S | AB_1200S_GSS |  | 55.0674 | -110.536 | Alberta |  | 144 | [8 empty] | 267
| FOX CREEK 741S | AB_741S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2017. Muir Connection Assessment |  | 268
| FOX CREEK 741S | AB_741S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2017. Muir Connection Assessment |  | 269
| FOX CREEK ALTALINK 347S | AB_347S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 270
| FREEMAN LAKE 742S | AB_742S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 271
| FRIEDENSTAL 800S | AB_800S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 272
| GAETZ 87S | AB_87S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 273
| GARDEN CITY 226S | AB_226S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 274
| GARNEAU | AB_XGAR_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 275
| GENESEE 330P | AB_330P_DSS |  |  |  | Alberta | T1 | 500 | 138 | 100 | 120 | 0.9 | 90 | 108 | AESO. 2016. Gainford Connection Assessment |  | 276
| GENESEE 330P | AB_330P_DSS |  |  |  | Alberta | T2 | 500 | 138 | 100 | 120 | 0.9 | 90 | 108 | AESO. 2016. Gainford Connection Assessment |  | 277
| GERMAIN 950S | AB_950S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 278
| GHOST 20S | AB_20S_GSS |  | 51.2188 | -114.7078 | Alberta |  | 138 | [8 empty] | 279
| GHOST PINE 114S | AB_114S_DSS |  | 51.8723 | -113.3181 | Alberta |  | 138 | [8 empty] | 280
| GLEICHEN 179S | AB_179S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 281
| GLENWOOD 229S | AB_229S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 282
| GOODFARE 815S | AB_815S_DSS |  |  |  | Alberta | T1 | 144 | 25 | 41.56 | 49.872 | 0.9 | 37.404 | 44.8848 | AESO. 2016. Hughes Connection Assessment |  | 283
| GOOSE LAKE 103S | AB_103S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2019. Mclaughlin Connection Assessment |  | 284
| GOOSE RIVER 725S | AB_725S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 285
| GRAND CENTRE 846S | AB_846S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 286
| GRANITE 342S | AB_342S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 287
| GRASSLAND 282S | AB_282S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 288
| GREEN STOCKING 925S | AB_925S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 289
| GREGOIRE 883S | AB_883S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 290
| GULF ROBB 414S | AB_414S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 291
| H.R. MILNER 740S | AB_740S_GSS |  | 54.0082 | -119.1022 | Alberta |  | 144 | [8 empty] | 292
| HAIG RIVER 748S | AB_748S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 293
| HALFWAY 2014S | AB_2014S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 294
| HALKIRK 615S | AB_615S_GSS |  | 52.2609 | -112.0271 | Alberta |  | 240 | [8 empty] | 295
| HAMBURG 855S | AB_855S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 296
| HANGINGSTONE 820S | AB_820S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 297
| HANNA 763S | AB_763S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 298
| HANSMAN LAKE 650S | AB_650S_DSS |  |  |  | Alberta | T2 | 240 | 34.5 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2016. Hughenden Connection Assessment |  | 300
| HANSMAN LAKE 650S | AB_650S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2017. Sharphills Connection Assessment |  | 299
| HANSMAN LAKE 650S | AB_650S_DSS |  |  |  | Alberta | T3 | 240 | 18 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2017. Sharphills Connection Assessment |  | 301
| HARDISTY | AB_XHAR_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 302
| HARDISTY 377S | AB_377S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 303
| HARMATTAN 256S | AB_256S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 304
| HARRY SMITH 367S | AB_367S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. Heartland Connection Assessment |  | 305
| HARRY SMITH 367S | AB_367S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. Heartland Connection Assessment |  | 306
| HARTELL 512S | AB_512S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 307
| HAYNES 482S | AB_482S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 308
| HAYS 421S | AB_421S_GSS |  |  |  | Alberta |  | 138 | [8 empty] | 309
| HAYTER 277S | AB_277S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 47 | 56.4 | 0.9 | 42.3 | 50.76 | AESO. 2016. Hughenden Connection Assessment |  | 310
| HAZELWOOD 287S | AB_287S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 311
| HEART LAKE 898S | AB_898S_DSS |  |  |  | Alberta | 902T | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2018. Kirby Connection Assessment |  | 312
| HEARTLAND 12S | AB_12S_DSS |  |  |  | Alberta | T1 | 500 | 240 | 1200 | 1440 | 0.9 | 1080 | 1296 | AESO. 2016. CPEEC Connection Assessment |  | 313
| HEATBURG 948S | AB_948S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 314
| HEATHFIELD 2029S | AB_2029S_DSS |  |  |  | Alberta |  | 500 | [8 empty] | 315
| HEISLER 764S | AB_764S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 316
| HIGH LEVEL 786S | AB_786S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 317
| HIGH PRAIRIE 787S | AB_787S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 318
| HIGH RIVER 65S | AB_65S_DSS |  |  |  | Alberta | T1 | 138 | 4.16 | 18.8 | 22.56 | 0.9 | 16.92 | 20.304 | AESO. 2016. Okotoks Connection Assessment |  | 319
| HIGH RIVER 65S | AB_65S_DSS |  |  |  | Alberta | T2 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Okotoks Connection Assessment |  | 320
| HIGH RIVER 65S | AB_65S_DSS |  |  |  | Alberta | T3 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Okotoks Connection Assessment |  | 321
| HILL 751S | AB_751S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 322
| HILLRIDGE 139S | AB_139S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 323
| HINES CREEK 724S | AB_724S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 324
| HORIZON MINING 838S | AB_838S_ISS |  |  |  | Alberta |  | 240 | [8 empty] | 325
| HORIZON UPGRADING 842S | AB_842S_GSS |  | 57.3393 | -111.7578 | Alberta |  | 240 | [8 empty] | 326
| HORSE CREEK T793S | AB_T793S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 327
| HORSE RIVER 917S | AB_917S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 328
| HORSESHOE 3S | AB_3S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 329
| HORSESHOE 737S | AB_737S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 330
| HOTCHKISS 788S | AB_788S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 331
| HRT EXPRESS 329S | AB_329S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 332
| HUGHENDEN 213S | AB_213S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2016. Hughenden Connection Assessment |  | 333
| HULL 257S | AB_257S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Fincastle Connection Assessment |  | 334
| HUSSAR 431S | AB_431S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 335
| IMPERIAL OIL CARSON LAKE 996S | AB_996S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 336
| IMPERIAL OIL EDMONTON 95S | AB_95S_ISS |  |  |  | Alberta |  | 138 | [8 empty] | 337
| INLAND CEMENT | AB_XINL_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 338
| INNISFAIL 214S | AB_214S_GSS |  | 52.0481 | -113.9768 | Alberta |  | 144 | [8 empty] | 339
| INTERLAKES 49S | AB_49S_GSS |  | 50.6335 | -115.1392 | Alberta |  | 144 | [8 empty] | 340
| IPIATIK 167S | AB_167S_DSS |  |  |  | Alberta | T2 | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2018. Kirby Connection Assessment |  | 341
| IRISH CREEK 706S | AB_706S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 342
| IRRICAN POWER 314S | AB_314S_GSS |  | 49.4526 | -112.7165 | Alberta |  | 138
| JACK PINE 920S | AB_920S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 343
| JACKFISH 698S | AB_698S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 344
| JANET 74S | AB_74S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. CEC Connection Assessment |  | 345
| JANET 74S | AB_74S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. CEC Connection Assessment |  | 346
| JARROW 252S | AB_252S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 347
| JASPER 805S | AB_805S_DSS |  |  |  | Alberta | T1 | 240 | 72 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2017. Clover Bar Connection Assessment |  | 348
| JENNER 275S | AB_275S_GSS |  | 50.7486 | -111.0489 | Alberta |  | 144 | [8 empty] | 349
| JOFFRE 535S | AB_535S_GSS |  | 52.3078 | -113.5468 | Alberta |  | 144 | [8 empty] | 350
| JOHNSON 281S | AB_281S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 351
| JOSEPHBURG 410S | AB_410S_DSS |  |  |  | Alberta | T1 | 250 | 144 | 336 | 403.2 | 0.9 | 302.4 | 362.88 | AESO. 2019. Abee 993S Connection Assessment |  | 352
| JOSEPHBURG 410S | AB_410S_DSS |  |  |  | Alberta | T2 | 250 | 144 | 336 | 403.2 | 0.9 | 302.4 | 362.88 | AESO. 2019. Abee 993S Connection Assessment |  | 353
| JOSLYN CREEK 849S | AB_849S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 354
| JUDY CREEK GAS PLANT 785S | AB_785S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 355
| JUMPING POUND 271S | AB_271S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 356
| JUMPING POUND JUNCTION 43S | AB_43S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 357
| KAKWA RIDGE 857S | AB_857S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 358
| KANANASKIS 2S | AB_2S_GSS |  | 51.0969 | -115.0582 | Alberta |  | 138 | [8 empty] | 359
| KAYBOB 346S | AB_346S_GSS |  | 54.099 | -116.6138 | Alberta |  | 144 | [8 empty] | 360
| KEARL 9900S | AB_9900S_GSS |  | 57.421 | -110.9264 | Alberta |  | 240 | [8 empty] | 361
| KEEPHILLS 320P | AB_320P_GSS |  | 53.3446 | -114.3049 | Alberta | T1 | 240 | 138 | 150 | 180 | 0.9 | 135 | 162 | AESO. 2016. Gainford Connection Assessment |  | 362
| KEEPHILLS 320P | AB_320P_GSS |  | 53.3446 | -114.3049 | Alberta | T6 | 500 | 240 | 1200 | 1440 | 0.9 | 1080 | 1296 | AESO. 2016. Gainford Connection Assessment |  | 363
| KEEPHILLS 320P | AB_320P_GSS |  | 53.3446 | -114.3049 | Alberta | PS | 240 | 240 | 600 | 720 | 0.9 | 540 | 648 | AESO. 2016. Gainford Connection Assessment |  | 364
| KEG RIVER 789S | AB_789S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 365
| KEMP RIVER 797S | AB_797S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 366
| KENNEDALE | AB_XKEN_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 367
| KETTLE RIVER 2049S | AB_2049S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 368
| KETTLE'S HILL 383S | AB_383S_GSS |  | 49.5159 | -113.8218 | Alberta |  | 144 | [8 empty] | 369
| KEYSTONE 384S | AB_384S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 370
| KIDNEY LAKE 878S | AB_878S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 371
| KILLARNEY LAKE 267S | AB_267S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Hughenden Connection Assessment |  | 372
| KINGMAN 299S | AB_299S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 373
| KINOSIS 856S | AB_856S_DSS |  |  |  | Alberta | 902T | 260 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 374
| KINOSIS 856S | AB_856S_DSS |  |  |  | Alberta | 903T | 260 | 144 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 375
| KINUSO 727S | AB_727S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 376
| KIRBY 651S | AB_651S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 377
| KITSCOTY 705S | AB_705S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 378
| KNIGHTSBRIDGE 216S | AB_216S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 379
| KSITUAN RIVER 754S | AB_754S_DSS |  |  |  | Alberta | 701T | 144 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Ksituan Connection Assessment |  | 380
| LAC LA BICHE 157S | AB_157S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 381
| LACOREY 721S | AB_721S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 382
| LAKE LOUISE 953S | AB_953S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 383
| LAKESEND 508S | AB_508S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 384
| LAKEVIEW 593S | AB_593S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 385
| LAMBTON | AB_XLAM_DSS |  |  |  | Alberta | T3 | 240 | 72 | 80 | 96 | 0.9 | 72 | 86.4 | AESO. 2017. Clover Bar Connection Assessment |  | 386
| LAMOUREUX 71S | AB_71S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 448 | 537.6 | 0.9 | 403.2 | 483.84 | AESO. 2018. Strathcona CG Connection Assessment |  | 387
| LAMOUREUX 71S | AB_71S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 448 | 537.6 | 0.9 | 403.2 | 483.84 | AESO. 2018. Strathcona CG Connection Assessment |  | 388
| LANFINE 959S | AB_959S_DSS |  |  |  | Alberta | 901T | 240 | 25 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Sharphills Connection Assessment |  | 389
| LANGDON 102S | AB_102S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 390
| LAURA LAKE 661S | AB_661S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 391
| LEDUC 325S | AB_325S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 392
| LEISMER 72S | AB_72S_DSS |  |  |  | Alberta | T1 | 240 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Kirby Connection Assessment |  | 393
| LEISMER 72S | AB_72S_DSS |  |  |  | Alberta | T2 | 240 | 144 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2018. Kirby Connection Assessment |  | 394
| LEMING LAKE 715S | AB_715S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 395
| LIMESTONE 304S | AB_304S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 396
| LINDBERGH 969S | AB_969S_GSS |  | 53.8753 | -110.6737 | Alberta |  | 144 | [8 empty] | 397
| LITTLE SMOKY 813S | AB_813S_DSS |  |  |  | Alberta | T1-H-Y | 144 | 25 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Muir Connection Assessment |  | 398
| LITTLE SMOKY 813S | AB_813S_DSS |  |  |  | Alberta | T2-H-Y | 144 | 25 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Muir Connection Assessment |  | 399
| LITTLE SMOKY 813S | AB_813S_DSS |  |  |  | Alberta | T1-H-X | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2017. Muir Connection Assessment |  | 400
| LITTLE SMOKY 813S | AB_813S_DSS |  |  |  | Alberta | T2-H-X | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2017. Muir Connection Assessment |  | 401
| LIVOCK 939S | AB_939S_DSS |  |  |  | Alberta | 901T | 240 | 144 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 402
| LLOYDMINSTER 716S | AB_716S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 403
| LODGEPOLE 61S | AB_61S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 404
| LONG LAKE 841S | AB_841S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 405
| LONG LAKE COGEN 864S | AB_864S_GSS |  |  |  | Alberta |  | 144 | [8 empty] | 406
| LOUISE CREEK 809S | AB_809S_DSS |  |  |  | Alberta | T1-H-Y | 144 | 25 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Muir Connection Assessment |  | 407
| LOUISE CREEK 809S | AB_809S_DSS |  |  |  | Alberta | T2-H-Y | 144 | 25 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Muir Connection Assessment |  | 408
| LOUISE CREEK 809S | AB_809S_DSS |  |  |  | Alberta | T1-H-X | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2017. Muir Connection Assessment |  | 409
| LOUISE CREEK 809S | AB_809S_DSS |  |  |  | Alberta | T2-H-X | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2017. Muir Connection Assessment |  | 410
| LOWE LAKE 944S | AB_944S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 411
| LOYALIST 903S | AB_903S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 412
| LUBICON 780S | AB_780S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 413
| LUNDBRECK 513S | AB_513S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 414
| MACDONALD 146S | AB_146S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 415
| MACKAY RIVER 874S | AB_874S_GSS |  | 57.0413 | -111.9055 | Alberta |  | 240 | [8 empty] | 416
| MADDEN 373S | AB_373S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 417
| MAGCAN 142S | AB_142S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 418
| MAGRATH 225S | AB_225S_GSS |  | 49.3859 | -112.9488 | Alberta | T1 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54 | AESO. 2019. Mclaughlin Connection Assessment |  | 419
| MAHIHKAN 837S | AB_837S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 420
| MAHKESES 889S | AB_889S_GSS |  | 54.5838 | -110.3934 | Alberta |  | 144 | [8 empty] | 421
| MAHNO 909S | AB_909S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 422
| MANNIX MINE 765S | AB_765S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 423
| MARGUERITE LAKE 826S | AB_826S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 424
| MARIANA 833S | AB_833S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 425
| MARION 21S | AB_21S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 426
| MARION LAKE 873S | AB_873S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 427
| MARLBORO 348S | AB_348S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 428
| MCBRIDE LAKE 240S | AB_240S_GSS |  | 49.6123 | -113.4815 | Alberta |  | 144 | [8 empty] | 429
| MCCLELLAND 957S | AB_957S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 430
| MCMILLAN 885S | AB_885S_DSS |  |  |  | Alberta | 902T | 260 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 431
| MCNEILL STATION 840S | AB_840S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 432
| MEADOW CREEK 2081S | AB_2081S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 433
| MEADOWLARK | AB_XMEA_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 434
| MEDICINE HAT 41S | AB_41S_GSS |  | 50.1004 | -110.7276 | Alberta | T1 | 138 | 13.8 | 56 | 67.2 | 0.9 | 50.4 | 60.48 | AESO. 2016. Bullshead Connection Assessment |  | 435
| MEDICINE HAT 41S | AB_41S_GSS |  | 50.1004 | -110.7276 | Alberta | T11 | 138 | 69 | 112 | 134.4 | 0.9 | 100.8 | 120.96 | AESO. 2016. Bullshead Connection Assessment |  | 436
| MEIKLE 905S | AB_905S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 437
| MELITO 890S | AB_890S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 438
| MERCER HILL 728S | AB_728S_DSS |  |  |  | Alberta | T1 | 144 | 25 | 41.6 | 49.92 | 0.9 | 37.44 | 44.928 | AESO. 2015. Eureka Connection Assessment |  | 439
| METISKOW 648S | AB_648S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2016. Hughenden Connection Assessment |  | 440
| METISKOW 648S | AB_648S_DSS |  |  |  | Alberta | T3 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2017. Sharphills Connection Assessment |  | 441
| MICHICHI CREEK 802S | AB_802S_DSS |  |  |  | Alberta | T1 | 144 | 72 | 33 | 39.6 | 0.9 | 29.7 | 35.64 | AESO. 2018. Wheatland Connection Assessment |  | 442
| MILDRED LAKE | AB_XMIL_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 443
| MILDRED LAKE MDLS | AB_XMDL_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 444
| MILLAR WESTERN 484S | AB_484S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 445
| MILO 356S | AB_356S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 446
| MITSUE 732S | AB_732S_DSS |  |  |  | Alberta | T1 | 240 | 25 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2014. Carmon Creek Connection Assessment |  | 447
| MITSUE 732S | AB_732S_DSS |  |  |  | Alberta | T2 | 240 | 25 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2014. Carmon Creek Connection Assessment |  | 448
| MOBIL OIL CARSON CREEK 887S | AB_887S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 449
| MONARCH 492S | AB_492S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 450
| MONITOR 774S | AB_774S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 451
| MOON LAKE 131S | AB_131S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 452
| MORSE RIVER 851S | AB_851S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 453
| MOUNTAIN COALBED 411S | AB_411S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 456
| MOWAT 2033S | AB_2033S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 457
| MT. ALLAN 115S | AB_115S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 6 | 7.2 | 0.9 | 5.4 | 6.48 | AESO. 2018. Mount Allan Connection Assessment |  | 454
| MT. ALLAN 115S | AB_115S_DSS |  |  |  | Alberta | T2 | 138 | 25 | 10 | 12 | 0.9 | 9 | 10.8 | AESO. 2018. Mount Allan Connection Assessment |  | 455
| MUIR 2018S | AB_2018S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 458
| MUSKEG RIVER 847S | AB_847S_GSS |  | 57.2537 | -111.5064 | Alberta |  | 240 | [8 empty] | 459
| N.E. LACOMBE 212S | AB_212S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 460
| N.W. CARDIFF 191S | AB_191S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 461
| NABIYE 942S | AB_942S_GSS |  | 54.7265 | -110.3441 | Alberta |  | 144 | [8 empty] | 462
| NAMAKA 428S | AB_428S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 463
| NAMAO | AB_XNAM_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 464
| NARROWS CREEK 858S | AB_858S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 465
| NELSON LAKE 429S | AB_429S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 466
| NEVIS 766S | AB_766S_DSS |  |  |  | Alberta | 901T | 240 | 144 | 100 | 120 | 0.9 | 90 | 108 | AESO. 2017. Sharphills Connection Assessment |  | 467
| NEVIS 766S | AB_766S_DSS |  |  |  | Alberta | 701T | 144 | 25 | 20 | 24 | 0.9 | 18 | 21.6 | AESO. 2017. Sharphills Connection Assessment |  | 468
| NEW ROSE VALLEY 635S | AB_635S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 469
| NEWELL 2075S | AB_2075S_DSS |  |  |  | Alberta |  | 500 | [8 empty] | 470
| NILREM 574S | AB_574S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. Sharphills Connection Assessment |  | 471
| NILREM 574S | AB_574S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. Sharphills Connection Assessment |  | 472
| NIPISI 796S | AB_796S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 473
| NISKU 149S | AB_149S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 474
| NORBERG 936S | AB_936S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 475
| NORCEN 812S | AB_812S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 476
| NORTH BARRHEAD 69S | AB_69S_DSS |  |  |  | Alberta | T4 | 240 | 138 | 179 | 214.8 | 0.9 | 161.1 | 193.32 | AESO. 2016. Plamondon Connection Assessment |  | 477
| NORTH CALDER 37S | AB_37S_DSS |  |  |  | Alberta | T6 | 240 | 138 | 286.8 | 344.16 | 0.9 | 258.12 | 309.744 | AESO. 2018. Strathcona CG Connection Assessment |  | 478
| NORTH HOLDEN 395S | AB_395S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 479
| NORTH LETHBRIDGE 370S | AB_370S_DSS |  |  |  | Alberta | T3 | 240 | 138 | 193.6 | 232.32 | 0.9 | 174.24 | 209.088 | AESO. 2019. Claresholm Connection Assessment |  | 480
| NORTH LETHBRIDGE 370S | AB_370S_DSS |  |  |  | Alberta | T5 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2019. Claresholm Connection Assessment |  | 481
| NORTH LETHBRIDGE 370S | AB_370S_DSS |  |  |  | Alberta | T6 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2019. Claresholm Connection Assessment |  | 482
| NORTH RED DEER 217S | AB_217S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 483
| NORTH ST. ALBERT 99S | AB_99S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 484
| NOSE CREEK 284S | AB_284S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 485
| OAKLAND 946S | AB_946S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 486
| OKOTOKS 678S | AB_678S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 487
| OLDMAN RIVER 806S | AB_806S_GSS |  | 49.561 | -113.896 | Alberta |  | 144 | [8 empty] | 488
| OLDS 55S | AB_55S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 489
| ONOWAY 352S | AB_352S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 490
| OPAL 439S | AB_439S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 491
| OTAUWAU 729S | AB_729S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 492
| OYEN 767S | AB_767S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 493
| P&G A808S | AB_A808S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 494
| PADDLE RIVER 106S | AB_106S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 495
| PAINTEARTH 863S | AB_863S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 496
| PARSONS CREEK 718S | AB_718S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 497
| PEACE BUTTE 404S | AB_404S_DSS |  |  |  | Alberta | T1 | 138 | 4.16 | 18.7 | 22.44 | 0.9 | 16.83 | 20.196 | AESO. 2015. Rothbauer Connection Assessment |  | 498
| PEACE BUTTE 404S | AB_404S_DSS |  |  |  | Alberta | T2 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2015. Rothbauer Connection Assessment |  | 499
| PEGASUS LAKE 659S | AB_659S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 500
| PEIGAN 59S | AB_59S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 179 | 214.8 | 0.9 | 161.1 | 193.32 | AESO. 2019. Mclaughlin Connection Assessment |  | 501
| PEMUKAN 932S | AB_932S_DSS |  |  |  | Alberta | 901T | 240 | 25 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Sharphills Connection Assessment |  | 502
| PETRO CANADA BRAZEAU RIVER 489S | AB_489S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 503
| PETRO CANADA EDMONTON 184S | AB_184S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 504
| PETROLIA | AB_XPET_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 505
| PICTURE BUTTE 120S | AB_120S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 506
| PIGEON LAKE 964S | AB_964S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 507
| PIKE 170S | AB_170S_DSS |  |  |  | Alberta | T1 | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2018. Kirby Connection Assessment |  | 508
| PIKE 170S | AB_170S_DSS |  |  |  | Alberta | T2 | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2018. Kirby Connection Assessment |  | 509
| PINCHER CREEK 396S | AB_396S_DSS |  |  |  | Alberta | T1 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54 | AESO. 2019. Mclaughlin Connection Assessment |  | 510
| PINEDALE 207S | AB_207S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 511
| PIPER CREEK 247S | AB_247S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 512
| PLAMONDON 353S | AB_353S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 513
| PLANT 30-2 UE-1 | AB_UE1S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 514
| POCATERRA 48S | AB_48S_GSS |  | 50.6993 | -115.1194 | Alberta |  | 144 | [8 empty] | 515
| PONOKA 331S | AB_331S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 516
| POPLAR HILL 790S | AB_790S_GSS |  | 57.008 | -111.4868 | Alberta | T1 | 144 | 25 | 33.3 | 39.96 | 0.9 | 29.97 | 35.964 | AESO. 2015. Eureka Connection Assessment |  | 517
| POPLAR HILL 790S | AB_790S_GSS |  | 57.008 | -111.4868 | Alberta | T2 | 144 | 25 | 33 | 39.6 | 0.9 | 29.7 | 35.64 | AESO. 2015. Eureka Connection Assessment |  | 518
| POUNDMAKER | AB_XPOU_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 519
| PRIMROSE 859S | AB_859S_GSS |  | 54.6963 | -110.7238 | Alberta |  | 144 | [8 empty] | 520
| PROVOST 545S | AB_545S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Hughenden Connection Assessment |  | 521
| QUEENSLAND 301S | AB_301S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 522
| QUEENSTOWN 504S | AB_504S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 523
| QUIGLEY 989S | AB_989S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 524
| RAINBOW COGEN 850S | AB_850S_GSS |  | 58.4471 | -119.2383 | Alberta |  | 144 | [8 empty] | 525
| RAINBOW LAKE 791S | AB_791S_GSS |  | 58.4471 | -119.2383 | Alberta |  | 144 | [8 empty] | 526
| RANGELAND YARROW 995S | AB_995S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 527
| RAVEN RIVER 634S | AB_634S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 528
| RAYMOND RESERVOIR 313S | AB_313S_GSS |  | 49.4071 | -112.6924 | Alberta |  | 72 | [8 empty] | 529
| RED DEER 63S | AB_63S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 530
| RED DEER DOWNTOWN RD15S | AB_RD15S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 531
| RED DEER NORTH RD14S | AB_RD14S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 532
| REDWATER 171S | AB_171S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 533
| RIBSTONE CREEK 892S | AB_892S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 534
| RICHDALE 776S | AB_776S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 535
| RICINUS 581S | AB_581S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 536
| RIMBEY 297S | AB_297S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 537
| RING CREEK 853S | AB_853S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 538
| RIVERBEND 618S | AB_618S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 539
| RIVERSIDE 388S | AB_388S_DSS |  | 53.8162 | -113.1263 | Alberta |  | 144 | [8 empty] | 540
| ROCKY MOUNTAIN HOUSE 262S | AB_262S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 541
| ROSS CREEK 906S | AB_906S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 542
| ROSSDALE | AB_XROS_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 543
| ROSYTH 296S | AB_296S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 544
| ROUND HILL 852S | AB_852S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 545
| ROWLEY 768S | AB_768S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 546
| RUNDLE 35S | AB_35S_GSS |  | 51.0887 | -115.3736 | Alberta |  | 138 | [8 empty] | 547
| RUSSELL 632S | AB_632S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 548
| RUTH LAKE 848S | AB_848S_DSS |  |  |  | Alberta | 901T | 260 | 72 | 100 | 120 | 0.9 | 90 | 108 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 549
| RUTH LAKE 848S | AB_848S_DSS |  |  |  | Alberta | 902T | 260 | 72 | 107.2 | 128.64 | 0.9 | 96.48 | 115.776 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 550
| RYCROFT 730S | AB_730S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 551
| SADDLE HILLS 865S | AB_865S_GSS |  | 55.6693 | -118.9178 | Alberta |  | 144 | [8 empty] | 552
| SAGITAWAH 77S | AB_77S_DSS |  |  |  | Alberta | T1 | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2014. Carmon Creek Connection Assessment |  | 553
| SAGITAWAH 77S | AB_77S_DSS |  |  |  | Alberta | T2 | 240 | 144 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2014. Carmon Creek Connection Assessment |  | 554
| SALT CREEK 977S | AB_977S_DSS |  |  |  | Alberta | 901T | 260 | 144 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 555
| SAND HILLS SUB 341S | AB_341S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 556
| SANDY POINT 204S | AB_204S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 557
| SARAH LAKE 743S | AB_743S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 558
| SARCEE 42S | AB_42S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. CEC Connection Assessment |  | 559
| SARCEE 42S | AB_42S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. CEC Connection Assessment |  | 560
| SAUNDERS LAKE 289S | AB_289S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 561
| SC1 266S | AB_266S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 562
| SCHRADER CREEK 531S | AB_531S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 563
| SCORIA 318S | AB_318S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 564
| SCOTFORD 409S | AB_409S_GSS |  | 53.7985 | -113.0943 | Alberta |  | 138 | [8 empty] | 565
| SCOTFORD UPGRADER 879S | AB_879S_ISS |  |  |  | Alberta |  | 138 | [8 empty] | 566
| SEAL LAKE 869S | AB_869S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 567
| SECORD 2005S | AB_2005S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 568
| SEDGEWICK 137S | AB_137S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 569
| SEEBE 245S | AB_245S_DSS |  |  |  | Alberta | T2 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2018. Mount Allan Connection Assessment |  | 570
| SHAMROCK 1018S | AB_1018S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 571
| SHEERNESS 807S | AB_807S_GSS |  | 51.4426 | -111.7919 | Alberta |  | 240 | [8 empty] | 572
| SHELL AOSP 402S | AB_402S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 573
| SHELL HARMATTAN 238S | AB_238S_GSS |  | 51.6584 | -114.1365 | Alberta |  | 144 | [8 empty] | 574
| SHELL WATERTON 502S | AB_502S_ISS |  |  |  | Alberta |  | 72 | [8 empty] | 575
| SHEPARD SS-25 | AB_SS25_GSS |  | 50.9713 | -113.8858 | Alberta |  | 240 | [8 empty] | 576
| SHERRITT GORDON 172S | AB_172S_GSS |  | 53.7198 | -113.1905 | Alberta |  | 144 | [8 empty] | 577
| SHERWOOD PARK 746S | AB_746S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Henday Connection Assessment |  | 578
| SHERWOOD PARK 746S | AB_746S_DSS |  |  |  | Alberta | T2 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Henday Connection Assessment |  | 579
| SIMONETTE 733S | AB_733S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 580
| SLAVE LAKE 745S | AB_745S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 581
| SODERGLEN 243S | AB_243S_GSS |  | 49.5385 | -113.5231 | Alberta |  | 144 | [8 empty] | 582
| SOUTH BEZANSON 862S | AB_862S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 583
| SOUTH MAYERTHORPE 443S | AB_443S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 584
| SOUTH RED DEER 194S | AB_194S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 585
| SPRAY 33S | AB_33S_GSS |  | 51.0745 | -115.4024 | Alberta |  | 138 | [8 empty] | 586
| SPRING COULEE 385S | AB_385S_GSS |  | 49.2871 | -113.1577 | Alberta |  | 69 | [8 empty] | 587
| SPRINGBANK 272S | AB_272S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 588
| SPRUCE GROVE 595S | AB_595S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 589
| SS-1 | AB_SS1_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 590
| SS-10 | AB_SS10_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 591
| SS-11 | AB_SS11_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 592
| SS-12 | AB_SS12_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 593
| SS-13 | AB_SS13_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 594
| SS-14 | AB_SS14_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 595
| SS-15 | AB_SS15_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 596
| SS-16 | AB_SS16_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 597
| SS-2 | AB_SS2_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 598
| SS-20 | AB_SS20_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 599
| SS-21 | AB_SS21_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 600
| SS-22 | AB_SS22_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 601
| SS-23 | AB_SS23_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 602
| SS-24 | AB_SS24_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 603
| SS-26 | AB_SS26_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 604
| SS-27 | AB_SS27_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 605
| SS-28 | AB_SS28_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 606
| SS-3 | AB_SS3_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 607
| SS-31 | AB_SS31_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 608
| SS-32 | AB_SS32_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 609
| SS-33 | AB_SS33_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 610
| SS-34 | AB_SS34_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 611
| SS-35 | AB_SS35_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 612
| SS-36 | AB_SS36_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 613
| SS-37 | AB_SS37_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 614
| SS-38 | AB_SS38_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 615
| SS-39 | AB_SS39_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 616
| SS-40 | AB_SS40_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 617
| SS-41 | AB_SS41_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 618
| SS-43 | AB_SS43_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 619
| SS-47 | AB_SS47_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 620
| SS-5 | AB_SS5_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 621
| SS-54 | AB_SS54_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 622
| SS-6 | AB_SS6_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 623
| SS-65 | AB_SS65_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. SS. 7 Connection Assessment |  | 624
| SS-65 | AB_SS65_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2017. SS. 7 Connection Assessment |  | 625
| SS-7 | AB_SS7_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 626
| SS-8 | AB_SS8_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 627
| SS-9 | AB_SS9_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 628
| ST. PAUL 707S | AB_707S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 629
| STAVELY 349S | AB_349S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 630
| STEEPBAK RIVER 836S | AB_836S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 631
| STELCO EDMONTON EAST 133S | AB_133S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 632
| STETTLER 769S | AB_769S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 633
| STIRLING 67S | AB_67S_GSS |  |  |  | Alberta | T2 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54 | AESO. 2019. Mclaughlin Connection Assessment |  | 634
| STONY PLAIN 434S | AB_434S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 635
| STRACHAN 263S | AB_263S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 636
| STRATHCONA | AB_XSTR_GSS |  | 53.5434 | -113.391 | Alberta |  | 72 | [8 empty] | 637
| STRATHMORE 151S | AB_151S_GSS |  | 51.0327 | -113.3767 | Alberta |  | 138 | [8 empty] | 638
| STROME 223S | AB_223S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 639
| STURGEON 2 881S | AB_881S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 640
| STURGEON 734S | AB_734S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 641
| SUFFIELD 895S | AB_895S_GSS |  | 50.2194 | -111.1597 | Alberta | T2 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2016. Bullshead Connection Assessment |  | 642
| SUFFIELD 895S | AB_895S_GSS |  | 50.2194 | -111.1597 | Alberta | T3 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2016. Bullshead Connection Assessment |  | 643
| SULLIVAN LAKE 775S | AB_775S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 644
| SULPHUR POINT 828S | AB_828S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 645
| SUMMERSIDE 657S | AB_657S_DSS |  |  |  | Alberta | T1 | 240 | 25 | 75 | 90 | 0.9 | 67.5 | 81 | AESO. 2020. Summerside Connection Assessment |  | 646
| SUMMERSIDE 657S | AB_657S_DSS |  |  |  | Alberta | T2 | 240 | 25 | 75 | 90 | 0.9 | 67.5 | 81 | AESO. 2020. Summerside Connection Assessment |  | 647
| SUMMERVIEW 354S | AB_354S_GSS |  | 49.5829 | -113.7931 | Alberta |  | 144 | [8 empty] | 648
| SUMMIT 653S | AB_653S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 649
| SUNDANCE 310P | AB_310P_GSS |  | 53.5075 | -114.5569 | Alberta | T1 | 240 | 138 | 168 | 201.6 | 0.9 | 151.2 | 181.44 | AESO. 2016. Gainford Connection Assessment |  | 650
| SUNDANCE 310P | AB_310P_GSS |  | 53.5075 | -114.5569 | Alberta | T4 | 240 | 69 | 44.8 | 53.76 | 0.9 | 40.32 | 48.384 | AESO. 2016. Gainford Connection Assessment |  | 651
| SUNDANCE BLOW-DOWN 867S | AB_867S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 652
| SUNDANCE SS 821S | AB_821S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 653
| SUNDAY CREEK 539S | AB_539S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 654
| SUNDRE 575S | AB_575S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 655
| SUNKEN LAKE 221S | AB_221S_DSS |  |  |  | Alberta | T1 | 138 | 4.16 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2016. Hughenden Connection Assessment |  | 656
| SUNKEN LAKE 221S | AB_221S_DSS |  |  |  | Alberta | T2 | 138 | 4.16 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2016. Hughenden Connection Assessment |  | 657
| SUNNYBROOK 510S | AB_510S_DSS |  |  |  | Alberta |  | 500 | [8 empty] | 658
| SUNSHINE VILLAGE 945S | AB_945S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 659
| SWAN RIVER 735S | AB_735S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 660
| SWANDIVE 854S | AB_854S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 661
| SWEETHEART LAKE 2032S | AB_2032S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 662
| SYLVAN LAKE 680S | AB_680S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 663
| SYNCRUDE P10 | AB_P10S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 664
| T.M.P.L. GAINFORD 165S | AB_165S_ISS |  |  |  | Alberta |  | 138 | [8 empty] | 665
| TABER 83S | AB_83S_DSS |  | 49.7822 | -112.1501 | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Fincastle Connection Assessment |  | 666
| TABER 83S | AB_83S_DSS |  | 49.7822 | -112.1501 | Alberta | T3 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Fincastle Connection Assessment |  | 667
| TABER WIND FARM 134S | AB_134S_GSS |  | 49.7184 | -111.9266 | Alberta |  | 144 | [8 empty] | 668
| THICKWOOD HILLS 951S | AB_951S_DSS |  |  |  | Alberta | 1201T | 525 | 258 | 1250 | 1500 | 0.9 | 1125 | 1350 | AESO. 2020. Suncor Base Plant Connection Assessment |  | 669
| THOMPSON 140S | AB_140S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 670
| THORNTON 2091S | AB_2091S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 671
| THREE HILLS 770S | AB_770S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 672
| THREE SISTERS 36S | AB_36S_GSS |  | 50.9985 | -115.3746 | Alberta |  | 144 | [8 empty] | 673
| TILLEY 498S | AB_498S_DSS |  | 50.5339 | -111.6702 | Alberta |  | 138 | [8 empty] | 674
| TINCHEBRAY 972S | AB_972S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 675
| TMPL NITON 228S | AB_228S_ISS |  |  |  | Alberta |  | 138 | [8 empty] | 676
| TOWER ROAD 933S | AB_933S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 677
| TRAVERS 554S | AB_554S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 678
| TRIANGLE 882S | AB_882S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 679
| TRUWELD GRATING 6500S | AB_6500S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 680
| TUCUMAN 478S | AB_478S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 681
| TURBO BALZAC 391S | AB_391S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 682
| UNDERWOOD 183S | AB_183S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 683
| UNION CARBIDE PRENTISS 276S | AB_276S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 684
| UPDIKE 886S | AB_886S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 685
| UPLANDS 241S | AB_241S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 686
| VALLEYVIEW 794S | AB_794S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 687
| VAUXHALL 158S | AB_158S_DSS |  | 50.1091 | -112.1421 | Alberta | T1 | 138 | 25 | 42 | 50.4 | 0.9 | 37.8 | 45.36 | AESO. 2018. Fincastle Connection Assessment |  | 688
| VEGREVILLE 709S | AB_709S_DSS |  | 53.6934 | -111.9786 | Alberta |  | 144 | [8 empty] | 689
| VERMILION 710S | AB_710S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 690
| VETERAN 771S | AB_771S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 691
| VICTORIA | AB_XVIC_DSS |  |  |  | Alberta | T1 | 72 | 14.4 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Clover Bar Connection Assessment |  | 692
| VICTORIA | AB_XVIC_DSS |  |  |  | Alberta | T2 | 72 | 14.4 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Clover Bar Connection Assessment |  | 693
| VICTORIA | AB_XVIC_DSS |  |  |  | Alberta | T3 | 72 | 14.4 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Clover Bar Connection Assessment |  | 694
| VICTORIA | AB_XVIC_DSS |  |  |  | Alberta | T4 | 72 | 14.4 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2017. Clover Bar Connection Assessment |  | 695
| VICTORIA | AB_XVIC_DSS |  |  |  | Alberta | T5 | 240 | 72 | 450 | 540 | 0.9 | 405 | 486 | AESO. 2017. Clover Bar Connection Assessment |  | 696
| VILNA 777S | AB_777S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 697
| VIOLET GROVE 283S | AB_283S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 698
| VIRGINIA HILLS 738S | AB_738S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 699
| VISCOUNT 92S | AB_92S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 700
| VISTA 1029S | AB_1029S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 701
| VULCAN 255S | AB_255S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 702
| WABAMUN 19S | AB_19S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 200 | 240 | 0.9 | 180 | 216 | AESO. 2016. Gainford Connection Assessment |  | 703
| WABAMUN 2739S | AB_2739S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 704
| WABASCA 720S | AB_720S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 705
| WADDEL 907S | AB_907S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 706
| WAINRIGHT 51S | AB_51S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 707
| WAP 1S | AB_1S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 708
| WAPITI 823S | AB_823S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 709
| WARDLOW 230S | AB_230S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 710
| WARE JUNCTION 132S | AB_132S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 711
| WARNER 344S | AB_344S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 712
| WATERTON 379S | AB_379S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 713
| WATSON CREEK 104S | AB_104S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 714
| WATT LAKE 956S | AB_956S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 715
| WAUPISOO 405S | AB_405S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 716
| WEASEL CREEK 947S | AB_947S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 717
| WESLEY CREEK 834S | AB_834S_DSS |  |  |  | Alberta | T1-H-Y | 144 | 25 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2016. Hughes Connection Assessment |  | 718
| WESLEY CREEK 834S | AB_834S_DSS |  |  |  | Alberta | T2-H-Y | 144 | 25 | 66.7 | 80.04 | 0.9 | 60.03 | 72.036 | AESO. 2016. Hughes Connection Assessment |  | 719
| WESLEY CREEK 834S | AB_834S_DSS |  |  |  | Alberta | T1-H-X | 240 | 144 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2016. Hughes Connection Assessment |  | 720
| WESLEY CREEK 834S | AB_834S_DSS |  |  |  | Alberta | T2-H-X | 240 | 144 | 300 | 360 | 0.9 | 270 | 324 | AESO. 2016. Hughes Connection Assessment |  | 721
| WEST BROOKS 28S | AB_28S_DSS |  |  |  | Alberta | T1 | 240 | 25 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2016. Bullshead Connection Assessment |  | 722
| WEST BROOKS 28S | AB_28S_DSS |  |  |  | Alberta | T2 | 240 | 25 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2016. Bullshead Connection Assessment |  | 723
| WEST CASCADE 177S | AB_177S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 724
| WEST CROSSFIELD 316S | AB_316S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 725
| WEST PEMBINA 359S | AB_359S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 726
| WEST PEMBINA 477S | AB_477S_GSS |  | 53.1032 | -115.3021 | Alberta |  | 144 | [8 empty] | 727
| WESTFIELD 107S | AB_107S_DSS |  |  |  | Alberta | T1 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 | AESO. 2018. Fincastle Connection Assessment |  | 728
| WESTLOCK 438S | AB_438S_GSS |  |  |  | Alberta |  | 138 | [8 empty] | 729
| WESTPEACE 793S | AB_793S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 730
| WESTWOOD 422S | AB_422S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 731
| WETASKIWIN 40S | AB_40S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 732
| WHEATLAND 609S | AB_609S_GSS |  | 51.2314 | -112.4079 | Alberta |  | 138 | [8 empty] | 733
| WHITBY LAKE 819S | AB_819S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 734
| WHITECOURT 268S | AB_268S_DSS |  |  |  | Alberta |  | 72 | [8 empty] | 735
| WHITECOURT INDUSTRIAL 364S | AB_364S_ISS |  |  |  | Alberta |  | 144 | [8 empty] | 736
| WHITECOURT POWER 323S | AB_323S_GSS |  |  |  | Alberta |  | 72 | [8 empty] | 737
| WHITEFISH LAKE 825S | AB_825S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 738
| WHITLA 251S | AB_251S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 739
| WILLESDENGREEN 68S | AB_68S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 740
| WILLOW LAKE 2009S | AB_2009S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 741
| WINDY FLATS 138S | AB_138S_DSS |  |  |  | Alberta | T1 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2019. Mclaughlin Connection Assessment |  | 742
| WINDY FLATS 138S | AB_138S_DSS |  |  |  | Alberta | T2 | 240 | 138 | 400 | 480 | 0.9 | 360 | 432 | AESO. 2019. Travers Connection Assessment |  | 743
| WINDY POINT 112S | AB_112S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 744
| WINEFRED 818S | AB_818S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 745
| WINTERING HILLS 804S | AB_804S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 746
| WOLF CREEK 288S | AB_288S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 747
| WOLF LAKE 822S | AB_822S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 748
| WOODCROFT | AB_XWOO_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 749
| YASA 286S | AB_286S_DSS |  |  |  | Alberta |  | 138 | [8 empty] | 750
| YEO 2015S | AB_2015S_DSS |  |  |  | Alberta |  | 240 | [8 empty] | 751
| YOUNGSTOWN 772S | AB_772S_DSS |  |  |  | Alberta |  | 69 | [8 empty] | 752
| ZAMA 795S | AB_795S_DSS |  |  |  | Alberta |  | 144 | [8 empty] | 753
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## System
AB | SYSTEM CHARACTERISTICS |  |  |  | System Characteristics
| Generator Type | Capacity Adjustment (ELCC) | Capacity Factor | Notes | Reserve Requirements | Transmission Losses
|  | (%) | (%) |  | (% installed MW) | (% across system)
| Coal | 90% | 55% |  | 15 | 3.61
| Natural Gas CC | 94% | 60% | DGC varies from 88 per cent to 100 per cent of installed capacity, so 94% used as an average
| Natural Gas CG | 94% | 30%
| Natural Gas CT | 94% | 30% | DGC varies from 88 per cent to 100 per cent of installed capacity, so 94% used as an average; BC Hydro presumes a minimum 18% capacity factor for its SCGTs
| Biomass / Biogas | 97% | 55%
| Hydro_daily | 100% | 24% | ELCC based on BC Hydro approach
| Hydro_run | 30% | 24% | ELCC based on BC Hydro approach
| Wind | 9% | 33% | See also: https://www.researchgate.net/publication/335777532_Assessing_Capacity_Value_of_Wind_in_Alberta
| Solar | 0% | 18% | Brooks was 17% capacity factor in 2019
Notes:
The reserve margin is "assumed" by the AESO pending final determination.
The transmission losses do not include distribution losses and are therefore not directly comparable to other jurisdictions.
ELCC is a dynamic value that changes as the wind penetration level changes, and is unique to each electricity system depending upon the capabilities of the other system generating units and the load shape.

## HGWh
AB | HISTORICAL ANNUAL ENERGY DEMAND | UNIT | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2009-2018
| Annual Energy Demand (after DSM) | GWh/year | 69914.294 | 71722.877 | 73600.053 | 75574.375 | 77450.544 | 79949.456 | 80256.902 | 79559.952 | 82572.427 | 85329.933 | Annual
| Annual Change in Energy Demand | GWh/year |  | 1808.583 | 1877.176 | 1974.322 | 1876.169 | 2498.912 | 307.446 | -696.95 | 3012.475 | 2757.506
| Percentage Change in Energy Demand | % |  | 2.587% | 2.617% | 2.683% | 2.483% | 3.226% | 0.3846% | -0.8684% | 3.786% | 3.339% | 2.239%
Notes:

## HMW
AB | HISTORICAL PEAK CAPACITY | UNIT | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2009-2018
| Annual Capacity Demand (after DSM) | MW | [10 empty] | Annual
| Annual Change in Capacity Demand | MW | [6 empty] | 0 | 0 | 0 | 0
| Percentage Change in Capacity Demand | % | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Notes:

## FGWh
AB | FORECAST ANNUAL ENERGY DEMAND | Unit | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | F2019 - F2030 | F2019-F2039 | Notes
| January | GWh | 7668.783 | 7961 | 8025 | 8110 | 8192 | 8286 | 8342 | 8392 | 8449 | 8503 | 8620 | 8703 | 8780 | 8835 | 8904 | 8983 | 9089 | 9148 | 9182 | 9228 | 9279
| February | GWh | 7183.101 | 7293 | 7144 | 7237 | 7320 | 7583 | 7372 | 7446 | 7518 | 7862 | 7612 | 7679 | 7759 | 8121 | 7938 | 8017 | 8024 | 8367 | 8140 | 8205 | 8270
| March | GWh | 7369.6718 | 7747 | 7843 | 7918 | 7985 | 8082 | 8137 | 8195 | 8263 | 8311 | 8436 | 8515 | 8587 | 8659 | 8731 | 8794 | 8916 | 8961 | 8997 | 9063 | 9104
| April | GWh | 6700.0667 | 6945 | 7029 | 7102 | 7168 | 7262 | 7299 | 7366 | 7436 | 7461 | 7566 | 7634 | 7711 | 7791 | 7844 | 7909 | 8005 | 8051 | 8105 | 8154 | 8197
| May | GWh | 6774.595 | 6929 | 7014 | 7110 | 7205 | 7259 | 7308 | 7363 | 7425 | 7502 | 7586 | 7664 | 7735 | 7793 | 7879 | 7970 | 8035 | 8078 | 8117 | 8165 | 8226
| June | GWh | 6685 | 6868 | 6957 | 7037 | 7108 | 7135 | 7214 | 7295 | 7355 | 7406 | 7460 | 7534 | 7629 | 7712 | 7783 | 7851 | 7896 | 7953 | 8026 | 8073 | 8119
| July | GWh | 7058 | 7474 | 7571 | 7661 | 7745 | 7782 | 7855 | 7932 | 7997 | 8062 | 8127 | 8217 | 8308 | 8376 | 8468 | 8553 | 8601 | 8661 | 8723 | 8774 | 8824
| August | GWh | 7025 | 7399 | 7497 | 7595 | 7674 | 7743 | 7780 | 7850 | 7922 | 7990 | 8096 | 8164 | 8232 | 8311 | 8401 | 8480 | 8569 | 8595 | 8639 | 8696 | 8755
| September | GWh | 6840 | 6983 | 7062 | 7142 | 7199 | 7285 | 7343 | 7403 | 7463 | 7506 | 7600 | 7684 | 7767 | 7827 | 7898 | 7956 | 8043 | 8109 | 8145 | 8193 | 8237
| October | GWh | 7207 | 7359 | 7448 | 7543 | 7628 | 7672 | 7743 | 7808 | 7868 | 7942 | 8017 | 8107 | 8198 | 8255 | 8349 | 8438 | 8495 | 8555 | 8606 | 8651 | 8707
| November | GWh | 7304 | 7462 | 7557 | 7649 | 7730 | 7761 | 7817 | 7906 | 7965 | 8038 | 8109 | 8176 | 8258 | 8340 | 8433 | 8521 | 8580 | 8616 | 8694 | 8742 | 8802
| December | GWh | 7980 | 8170 | 8282 | 8382 | 8453 | 8443 | 8547 | 8632 | 8710 | 8768 | 8788 | 8899 | 9013 | 9103 | 9210 | 9288 | 9284 | 9383 | 9462 | 9528 | 9594
| Reference Case (after "energy efficiency") | GWh/year | 85795.2176 | 88590 | 89429 | 90486 | 91407 | 92293 | 92757 | 93588 | 94371 | 95351 | 96017 | 96976 | 97977 | 99123 | 99838 | 100760 | 101537 | 102477 | 102836 | 103472 | 104114 | 2019-2030 Rate | 2019-2050 Rate | Assume extended to 2050
|  |  |  | 3.258% | 0.9471% | 1.182% | 1.018% | 0.9693% | 0.5027% | 0.8959% | 0.8366% | 1.038% | 0.6985% | 0.9988% | 1.032% | 1.17% | 0.7213% | 0.9235% | 0.7711% | 0.9258% | 0.3503% | 0.6185% | 0.6205% | 1.233% | 1.071% | Mid-load forecast for use in COPPER
| Low Growth Case (after "energy efficiency") | GWh/year | 85460 | 86634 | 86958 | 87054 | 87025 | 87189 | 86905 | 86875 | 86855 | 87084 | 86768 | 86710 | 86679 | 86903 | 86641 | 86610 | 86535 | 86738 | 86451 | 86426 | 86402 | 2019-2030 Rate | 2019-2050 Rate | Assume extended to 2050
|  |  |  | 1.374% | 0.374% | 0.1104% | -0.03331% | 0.1885% | -0.3257% | -0.03452% | -0.02302% | 0.2637% | -0.3629% | -0.06684% | -0.03575% | 0.2584% | -0.3015% | -0.03578% | -0.0866% | 0.2346% | -0.3309% | -0.02892% | -0.02777% | 0.1453% | 0.06784% | Low-load forecast for use in COPPER
| High Growth Case (after "energy efficiency") | GWh/year | 87345 | 90412 | 93117 | 95338 | 97571 | 99817 | 101347 | 103048 | 104771 | 106916 | 108258 | 110181 | 111898 | 113924 | 115359 | 117071 | 118751 | 120835 | 122281 | 124156 | 126101 | 2019-2030 Rate | 2019-2050 Rate | Assume extended to 2050
|  |  |  | 3.511% | 2.992% | 2.385% | 2.342% | 2.302% | 1.533% | 1.678% | 1.672% | 2.047% | 1.255% | 1.776% | 1.558% | 1.811% | 1.26% | 1.484% | 1.435% | 1.755% | 1.197% | 1.533% | 1.567% | 2.35% | 1.999% | High-load forecast for use in COPPER
Notes:
The 2019 LTO Reference Case accounts for anticipated energy efficiency impacts.

## FMW
AB | FORECAST PEAK DEMAND | Unit | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2019-2030 | 2019-2030 | Notes
| January | GWh | 11355 | 12087 | 12244 | 12380 | 12509 | 12505 | 12611 | 12721 | 12828 | 12929 | 12965 | 13083 | 13220 | 13345 | 13496 | 13629 | 13633 | 13727 | 13859 | 13970 | 14085
| February | GWh | 11471 | 11681 | 11802 | 11929 | 12062 | 12117 | 12190 | 12282 | 12369 | 12483 | 12572 | 12667 | 12789 | 12888 | 13012 | 13180 | 13237 | 13311 | 13393 | 13483 | 13588
| March | GWh | 11093.9998 | 11496 | 11994 | 12117 | 12233 | 11940 | 12070 | 12184 | 12593 | 12517 | 12461 | 12580 | 12703 | 12988 | 13271 | 13391 | 13163 | 13185 | 13347 | 13779 | 13877
| April | GWh | 9916.0784 | 10596 | 10757 | 10670 | 10821 | 11344 | 11131 | 11226 | 11335 | 11249 | 11323 | 11473 | 11724 | 11803 | 11709 | 11866 | 11967 | 12114 | 12271 | 12366 | 12298
| May | GWh | 10023 | 10419 | 10556 | 10685 | 10912 | 10810 | 10904 | 11037 | 11090 | 11171 | 11223 | 11325 | 11464 | 11586 | 11717 | 11948 | 11788 | 11852 | 12041 | 12027 | 12177
| June | GWh | 10471 | 11065 | 11190 | 11290 | 11389 | 11333 | 11602 | 11693 | 11730 | 11746 | 11746 | 11846 | 12172 | 12232 | 12301 | 12418 | 12321 | 12378 | 12716 | 12702 | 12747
| July | GWh | 10760 | 11604 | 11735 | 11858 | 11950 | 11791 | 12131 | 12201 | 12280 | 12358 | 12325 | 12490 | 12749 | 12758 | 12908 | 12981 | 12941 | 12964 | 13239 | 13267 | 13370
| August | GWh | 10822 | 11389 | 11366 | 11493 | 11593 | 11974 | 11716 | 11820 | 11918 | 12130 | 12475 | 12569 | 12299 | 12562 | 12532 | 12632 | 13105 | 13100 | 12826 | 12905 | 12976
| September | GWh | 10859 | 11004 | 11187 | 11303 | 11404 | 11446 | 11551 | 11650 | 11723 | 11728 | 11950 | 12004 | 12114 | 12165 | 12310 | 12406 | 12566 | 12462 | 12639 | 12703 | 12772
| October | GWh | 10546 | 10761 | 10872 | 10925 | 11025 | 11166 | 11305 | 11414 | 11444 | 11480 | 11702 | 11800 | 11921 | 11929 | 12041 | 12152 | 12351 | 12354 | 12488 | 12500 | 12577
| November | GWh | 11376 | 11683 | 11736 | 11857 | 11957 | 12129 | 12131 | 12219 | 12310 | 12470 | 12539 | 12645 | 12761 | 12931 | 12978 | 13092 | 13233 | 13371 | 13384 | 13464 | 13556
| December | GWh | 12024 | 12267 | 12414 | 12538 | 12640 | 12703 | 12803 | 12909 | 13002 | 13081 | 13200 | 13319 | 13449 | 13556 | 13688 | 13806 | 13908 | 13985 | 14094 | 14182 | 14274
| Reference Case (after "energy efficiency") | MAXIMUM | 12024 | 12267 | 12414 | 12538 | 12640 | 12703 | 12803 | 12909 | 13002 | 13081 | 13200 | 13319 | 13449 | 13556 | 13688 | 13806 | 13908 | 13985 | 14094 | 14182 | 14274 | 2019-2030 Rate | 2019-2050 Rate | Assume extended to 2050
|  |  |  | 2.021% | 1.198% | 0.9989% | 0.8135% | 0.4984% | 0.7872% | 0.8279% | 0.7204% | 0.6076% | 0.9097% | 0.9015% | 0.976% | 0.7956% | 0.9737% | 0.8621% | 0.7388% | 0.5536% | 0.7794% |  |  | 1.028% | 0.9069% | Mid-load forecast for use in COPPER
| Low Growth Case (after "energy efficiency") | GWh/year | 11925 | 12031 | 12116 | 12116 | 12116 | 12100 | 12111 | 12116 | 12116 | 12111 | 12111 | 12111 | 12111 | 12111 | 12116 | 12116 | 12111 | 12100 | 12116 | 12116 | 12116 | 2019-2030 Rate | 2019-2050 Rate | Assume extended to 2050
|  |  |  | 0.8889% | 0.7065% | 0% | 0% | -0.1321% | 0.09091% | 0.04128% | 0% | -0.04127% | 0% | 0% | 0% | 0% | 0.04128% | 0% | -0.04127% | -0.09083% | 0.1322% | 0% | 0% | 0.1549% | 0.09351% | Low-load forecast for use in COPPER
| High Growth Case (after "energy efficiency") | GWh/year | 12291 | 12674 | 12930 | 13193 | 13396 | 13621 | 13856 | 14063 | 14297 | 14487 | 14695 | 14949 | 15170 | 15382 | 15615 | 15846 | 16075 | 16309 | 16581 | 16865 | 17193 | 2019-2030 Rate | 2019-2050 Rate | Assume extended to 2050
|  |  |  | 3.116% | 2.02% | 2.034% | 1.539% | 1.68% | 1.725% | 1.494% | 1.664% | 1.329% | 1.436% | 1.728% | 1.478% | 1.397% | 1.515% | 1.479% | 1.445% | 1.456% | 1.668% | 1.713% | 1.945% | 1.977% | 1.777% | High-load forecast for use in COPPER
Notes:
The 2017 LTO Reference Case accounts for anticipated energy efficiency impacts.

## Hourly
AB | Hourly
See Hourly2018 file in the Hourly-2018 folder

## Inputs
AB | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance