## README
MB | LEGEND
| MB-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| Distribution | Characteristics of existing distribution substations
| System | Miscellaneous provincial system characteristics
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review or being gathered
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to sources
See the accompanying calculations file and raw data files for additional supporting information
See the related Gitlab issue for a summary of inventory status

## MB-Sources
MB | PRIMARY SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| Manitoba Hydro | 2015 | Interconnection Facilities Study for Keeyask Generating Station | https://www.oasis.oati.com/MHEB/index.html |  | Manitoba |  | 1
| Manitoba Hydro | 2015 | Manitoba - Minnesota Transmission Project EIS. Chapter 2 - Project Description | https://www.gov.mb.ca/sd/eal/registries/5750mbhydrombminnesota/index.html |  | Manitoba
| Manitoba Hydro | 2014 | St. Vital Complex Environmental Assessment Report. Chapter 3 Project Description | https://www.gov.mb.ca/sd/eal/registries/5750mbhydrombminnesota/index.html |  | Manitoba
| NPCC | 2017 | 2017 Québec Balancing Authority Area Comprehensive Review of Resource Adequacy | https://www.npcc.org/Library/Resource%20Adequacy/Forms/Public%20List.aspx |  | Québec
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" Column of the relevant tab
| Manitoba Hydro | 2011 | 2010/11 & 2011/12 General Rate Application Filing - Information Requests Round 1 RCM/TREE | https://www.hydro.mb.ca/regulatory_affairs/electric/gra_2010_2012/#rd1 |  | Manitoba
| Manitoba Hydro | 2019 | Manitoba Hydro Power Sale Arrangements | https://www.hydro.mb.ca/corporate/electricity_exports/power_sale_arrangements/ |  | Manitoba
| Manitoba Hydro | 2011 | Bipole III Environmental Impact Statement - Chapter 7 Maps | https://www.hydro.mb.ca/projects/bipoleIII/ |  | Manitoba
| Manitoba Hydro | 2007 | Kelsey Generating Station | https://www.oasis.oati.com/MHEB/index.html |  | Manitoba
| Manitoba Hydro | 2017 | Manitoba Hydro 2017/18 & 2018/19 General Rate Application COALITION/MH I-158a-Attachment | http://www.pubmanitoba.ca/v1/proceedings-decisions/appl-current/mh2017gra-irs.html |  | Manitoba
| Manitoba Hydro | 2013 | Bipole III Transmission Project - Index of Map Series | http://manitobawildlands.org/pdfs/bp3cec/HY-BP3-MBHY-ResponsetoCECIRsPackage4-Attach2-31Jul12.pdf |  | Manitoba
| Manitoba Hydro | 2010 | Manitoba Hydro 2010-2012 General Rate Application RCM/TREE/MH I-7 | http://www.pubmanitoba.ca/v1/proceedings-decisions/appl-previous/mhgra-index.html |  | Manitoba
| Manitoba Hydro | 2019 | Manitoba Hydro Generating Stations | https://www.hydro.mb.ca/corporate/facilities/generating_stations/ |  | Manitoba
| Manitoba Hydro | 2013 | Need for an Alternatives To (NFAT). Appendix 7.2 Range of Resource Options | http://www.pubmanitoba.ca/v1/proceedings-decisions/mh-nfat/application.html |  | Manitoba
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | National
| Manitoba Hydro | 2018 | Annual Reports [2013 through 2018 - See calculations] | https://www.hydro.mb.ca/corporate/ar/ |  | Manitoba
| Manitoba Hydro | 2016 | 2016/17 Resource Planning Assumptions & Analysis | https://www.hydro.mb.ca/regulatory_affairs/pdf/electric/general_rate_application_2017/07.3_appendix_7.3_mh_resource_planning_assumptions_and_analysis.pdf |  | Manitoba
| Manitoba Hydro | 2018 | 2018 Electric Load Forecast. Market Forecast & Load Research. | http://www.pubmanitoba.ca/v1/proceedings-decisions/appl-current/pubs/2019-mh-gra/2019-mh-application/appendix-15-2018-load-forecast.pdf |  | Manitoba
| MISO | 2020 | Manitoba Hydro Transmission Facilities Subject to MISO RC Responsibility | https://cdn.misoenergy.org/Manitoba%20Hydro%20Transmission%20Facilities%20Reliability%20Coordination%20MISO%202019390631.xlsx |  | Manitoba
| Manitoba Hydro | 2012 | Manitoba Hydro Available Transfer Capability Implementation Document (ATCID) | https://www.oasis.oati.com/MHEB/index.html |  | Manitoba
| The Water Power Act | 1988 | Water Power Regulation, Man Reg 25/88 R, s.6(5). | https://web2.gov.mb.ca/laws/regs/current/_pdf-regs.php?reg=25/88%20R |  | Manitoba
| Manitoba Hydro | 2014 | Pointe du Bois Transmission Project Environmental Assessment Report. Chapter 2 | https://www.gov.mb.ca/sd/eal/registries/5716mbhydropointedubois/ |  | Manitoba
| Manitoba Hydro | 2012 | Dorsey to Portage South 230 kV Transmission Line Environmental Assessment Report | https://www.manitoba.ca/sd/eal/registries/5611dorsey/index.html |  | Manitoba
| Manitoba Hydro | 2018 | Birtle Transmission Project Environmental Assessment Report | https://www.gov.mb.ca/sd/eal/registries/5950birtle/index.html |  | Manitoba
| NERC | 2020 | 2020 Summer Reliability Assessment | https://www.nerc.com/pa/RAPA/ra/Reliability%20Assessments%20DL/NERC_SRA_2020.pdf |  | Manitoba
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
MB | EXISTING GENERATION | [12 empty] | DESIGN | [7 empty] | OPERATIONS | [13 empty] | OPERATING COSTS
| Project Name | Gen Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Unit | # of units | Inc Heat Rate @ Max | Minimum Capacity | Maximum Capacity | Minimum Up Time | Minimum Down Time | Spin Up Ramp Rate | Spin Down Ramp Rate | Start Up Ramp Limit | Shut Down Ramp Limit | Must Run | Operating Reserve Fraction | Outage Duration | Forced Outage Rate | Maintenance Outage Rate | Start Up Costs | Fuel Costs | Shut Down Costs | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[16 empty] | (MW) |  | (MW) | (%) | (GWh/year) |  | (MMBtu/MWh) | (MW) | (MW) | (hours) | (hours) | (%/min) | (%/min) | [MW/hr p MWcap] | [MW/hr p MWcap] | (T/F) | (%) | (hours) | (%) | (days/y) | (S/MWcap) | ($/MWh) | (S/MWcap) | ($/year) | ($/MWh)
| Selkirk_01 | MB_SKK01_GEN | Manitoba Hydro | Selkirk | 50.1347 | -96.852 | Manitoba.a | Manitoba | Selkirk GS | MB_SKK_GSS | 115 | 1960 | 2100 | NG_CT | gasSC | 66 | 95.3% | 62.898 | 0.9351% | 5.4066 | 2
| Selkirk_02 | MB_SKK02_GEN | Manitoba Hydro | Selkirk | 50.1347 | -96.852 | Manitoba.a | Manitoba | Selkirk GS | MB_SKK_GSS | 115 | 1960 | 2100 | NG_CT | gasSC | 66 | 95.3% | 62.898 | 0.9351% | 5.4066 | 2
| Brandon_06 | MB_BDN06_GEN | Manitoba Hydro | Brandon | 49.8456 | -99.8901 | Manitoba.a | Manitoba | Brandon GS | MB_BDN_GSS | 115 | 2001 | 2100 | NG_CT | gasSC | 140 | 95.3% | 133.42 | 2.461% | 30.1814 | 2 | [20 empty] | Brandon also has a synchronous condenser
| Brandon_07 | MB_BDN07_GEN | Manitoba Hydro | Brandon | 49.8456 | -99.8901 | Manitoba.a | Manitoba | Brandon GS | MB_BDN_GSS | 115 | 2001 | 2100 | NG_CT | gasSC | 140 | 95.3% | 133.42 | 2.461% | 30.1814 | 2 | [20 empty] | Brandon also has a synchronous condenser
| Grand Rapids_01 | MB_GRP01_GEN | Manitoba Hydro | Saskatchewan River | 53.16 | -99.2863 | Manitoba.a | Manitoba | Grand Rapids GS | MB_GRP_GSS | 230 | 1968 | 2100 | Hydro_daily | hydro_daily | 120 | 98.1% | 117.72 | 36.98% | 388.75 | 4
| Grand Rapids_02 | MB_GRP02_GEN | Manitoba Hydro | Saskatchewan River | 53.16 | -99.2863 | Manitoba.a | Manitoba | Grand Rapids GS | MB_GRP_GSS | 230 | 1968 | 2100 | Hydro_daily | hydro_daily | 120 | 98.1% | 117.72 | 36.98% | 388.75 | 4
| Grand Rapids_03 | MB_GRP03_GEN | Manitoba Hydro | Saskatchewan River | 53.16 | -99.2863 | Manitoba.a | Manitoba | Grand Rapids GS | MB_GRP_GSS | 230 | 1968 | 2100 | Hydro_daily | hydro_daily | 120 | 98.1% | 117.72 | 36.98% | 388.75 | 4
| Grand Rapids_04 | MB_GRP04_GEN | Manitoba Hydro | Saskatchewan River | 53.16 | -99.2863 | Manitoba.a | Manitoba | Grand Rapids GS | MB_GRP_GSS | 230 | 1968 | 2100 | Hydro_daily | hydro_daily | 120 | 98.1% | 117.72 | 36.98% | 388.75 | 4
| Great Falls_01 | MB_GRF01_GEN | Manitoba Hydro | Winnipeg River | 50.4616 | -96.0095 | Manitoba.a | Manitoba | Great Falls GS | MB_GRF_GSS | 115 | 1928 | 2100 | Hydro_daily | hydro_daily | 21.5 | 98.1% | 21.0915 | 80.97% | 152.5 | 6
| Great Falls_02 | MB_GRF02_GEN | Manitoba Hydro | Winnipeg River | 50.4616 | -96.0095 | Manitoba.a | Manitoba | Great Falls GS | MB_GRF_GSS | 115 | 1928 | 2100 | Hydro_daily | hydro_daily | 21.5 | 98.1% | 21.0915 | 80.97% | 152.5 | 6
| Great Falls_03 | MB_GRF03_GEN | Manitoba Hydro | Winnipeg River | 50.4616 | -96.0095 | Manitoba.a | Manitoba | Great Falls GS | MB_GRF_GSS | 115 | 1928 | 2100 | Hydro_daily | hydro_daily | 21.5 | 98.1% | 21.0915 | 80.97% | 152.5 | 6
| Great Falls_04 | MB_GRF04_GEN | Manitoba Hydro | Winnipeg River | 50.4616 | -96.0095 | Manitoba.a | Manitoba | Great Falls GS | MB_GRF_GSS | 115 | 1928 | 2100 | Hydro_daily | hydro_daily | 21.5 | 98.1% | 21.0915 | 80.97% | 152.5 | 6
| Great Falls_05 | MB_GRF05_GEN | Manitoba Hydro | Winnipeg River | 50.4616 | -96.0095 | Manitoba.a | Manitoba | Great Falls GS | MB_GRF_GSS | 115 | 1928 | 2100 | Hydro_daily | hydro_daily | 21.5 | 98.1% | 21.0915 | 80.97% | 152.5 | 6
| Great Falls_06 | MB_GRF06_GEN | Manitoba Hydro | Winnipeg River | 50.4616 | -96.0095 | Manitoba.a | Manitoba | Great Falls GS | MB_GRF_GSS | 115 | 1928 | 2100 | Hydro_daily | hydro_daily | 21.5 | 98.1% | 21.0915 | 80.97% | 152.5 | 6
| Keeyask_01 | MB_KSK01_GEN | Manitoba Hydro JV | Nelson River | 56.3304 | -95.3421 | Manitoba.a | Manitoba | Keeyask GS | MB_KSK_GSS | 138 | 2021 | 2100 | Hydro_daily | hydro_daily | 99 | 98.1% | 97.119 | 72.99% | 633 | 7
| Keeyask_02 | MB_KSK02_GEN | Manitoba Hydro JV | Nelson River | 56.3304 | -95.3421 | Manitoba.a | Manitoba | Keeyask GS | MB_KSK_GSS | 138 | 2021 | 2100 | Hydro_daily | hydro_daily | 99 | 98.1% | 97.119 | 72.99% | 633 | 7
| Keeyask_03 | MB_KSK03_GEN | Manitoba Hydro JV | Nelson River | 56.3304 | -95.3421 | Manitoba.a | Manitoba | Keeyask GS | MB_KSK_GSS | 138 | 2021 | 2100 | Hydro_daily | hydro_daily | 99 | 98.1% | 97.119 | 72.99% | 633 | 7
| Keeyask_04 | MB_KSK04_GEN | Manitoba Hydro JV | Nelson River | 56.3304 | -95.3421 | Manitoba.a | Manitoba | Keeyask GS | MB_KSK_GSS | 138 | 2021 | 2100 | Hydro_daily | hydro_daily | 99 | 98.1% | 97.119 | 72.99% | 633 | 7
| Keeyask_05 | MB_KSK05_GEN | Manitoba Hydro JV | Nelson River | 56.3304 | -95.3421 | Manitoba.a | Manitoba | Keeyask GS | MB_KSK_GSS | 138 | 2021 | 2100 | Hydro_daily | hydro_daily | 99 | 98.1% | 97.119 | 72.99% | 633 | 7
| Keeyask_06 | MB_KSK06_GEN | Manitoba Hydro JV | Nelson River | 56.3304 | -95.3421 | Manitoba.a | Manitoba | Keeyask GS | MB_KSK_GSS | 138 | 2021 | 2100 | Hydro_daily | hydro_daily | 99 | 98.1% | 97.119 | 72.99% | 633 | 7
| Keeyask_07 | MB_KSK07_GEN | Manitoba Hydro JV | Nelson River | 56.3304 | -95.3421 | Manitoba.a | Manitoba | Keeyask GS | MB_KSK_GSS | 138 | 2021 | 2100 | Hydro_daily | hydro_daily | 99 | 98.1% | 97.119 | 72.99% | 633 | 7
| McArthur Falls_01 | MB_MCF01_GEN | Manitoba Hydro | Winnipeg River | 50.3981 | -95.9977 | Manitoba.a | Manitoba | McArthur Falls GS | MB_MCF_GSS | 115 | 1955 | 2100 | Hydro_daily | hydro_daily | 7 | 98.1% | 6.867 | 79.5% | 48.75 | 8
| McArthur Falls_02 | MB_MCF02_GEN | Manitoba Hydro | Winnipeg River | 50.3981 | -95.9977 | Manitoba.a | Manitoba | McArthur Falls GS | MB_MCF_GSS | 115 | 1955 | 2100 | Hydro_daily | hydro_daily | 7 | 98.1% | 6.867 | 79.5% | 48.75 | 8
| McArthur Falls_03 | MB_MCF03_GEN | Manitoba Hydro | Winnipeg River | 50.3981 | -95.9977 | Manitoba.a | Manitoba | McArthur Falls GS | MB_MCF_GSS | 115 | 1955 | 2100 | Hydro_daily | hydro_daily | 7 | 98.1% | 6.867 | 79.5% | 48.75 | 8
| McArthur Falls_04 | MB_MCF04_GEN | Manitoba Hydro | Winnipeg River | 50.3981 | -95.9977 | Manitoba.a | Manitoba | McArthur Falls GS | MB_MCF_GSS | 115 | 1955 | 2100 | Hydro_daily | hydro_daily | 7 | 98.1% | 6.867 | 79.5% | 48.75 | 8
| McArthur Falls_05 | MB_MCF05_GEN | Manitoba Hydro | Winnipeg River | 50.3981 | -95.9977 | Manitoba.a | Manitoba | McArthur Falls GS | MB_MCF_GSS | 115 | 1955 | 2100 | Hydro_daily | hydro_daily | 7 | 98.1% | 6.867 | 79.5% | 48.75 | 8
| McArthur Falls_06 | MB_MCF06_GEN | Manitoba Hydro | Winnipeg River | 50.3981 | -95.9977 | Manitoba.a | Manitoba | McArthur Falls GS | MB_MCF_GSS | 115 | 1955 | 2100 | Hydro_daily | hydro_daily | 7 | 98.1% | 6.867 | 79.5% | 48.75 | 8
| McArthur Falls_07 | MB_MCF07_GEN | Manitoba Hydro | Winnipeg River | 50.3981 | -95.9977 | Manitoba.a | Manitoba | McArthur Falls GS | MB_MCF_GSS | 115 | 1955 | 2100 | Hydro_daily | hydro_daily | 7 | 98.1% | 6.867 | 79.5% | 48.75 | 8
| McArthur Falls_08 | MB_MCF08_GEN | Manitoba Hydro | Winnipeg River | 50.3981 | -95.9977 | Manitoba.a | Manitoba | McArthur Falls GS | MB_MCF_GSS | 115 | 1955 | 2100 | Hydro_daily | hydro_daily | 7 | 98.1% | 6.867 | 79.5% | 48.75 | 8
| Pine Falls_01 | MB_PNF01_GEN | Manitoba Hydro | Winnipeg River | 50.5671 | -96.1783 | Manitoba.a | Manitoba | Pine Falls GS | MB_PNF_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 14 | 98.1% | 13.734 | 86.98% | 106.6667 | 6
| Pine Falls_02 | MB_PNF02_GEN | Manitoba Hydro | Winnipeg River | 50.5671 | -96.1783 | Manitoba.a | Manitoba | Pine Falls GS | MB_PNF_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 14 | 98.1% | 13.734 | 86.98% | 106.6667 | 6
| Pine Falls_03 | MB_PNF03_GEN | Manitoba Hydro | Winnipeg River | 50.5671 | -96.1783 | Manitoba.a | Manitoba | Pine Falls GS | MB_PNF_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 14 | 98.1% | 13.734 | 86.98% | 106.6667 | 6
| Pine Falls_04 | MB_PNF04_GEN | Manitoba Hydro | Winnipeg River | 50.5671 | -96.1783 | Manitoba.a | Manitoba | Pine Falls GS | MB_PNF_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 14 | 98.1% | 13.734 | 86.98% | 106.6667 | 6
| Pine Falls_05 | MB_PNF05_GEN | Manitoba Hydro | Winnipeg River | 50.5671 | -96.1783 | Manitoba.a | Manitoba | Pine Falls GS | MB_PNF_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 14 | 98.1% | 13.734 | 86.98% | 106.6667 | 6
| Pine Falls_06 | MB_PNF06_GEN | Manitoba Hydro | Winnipeg River | 50.5671 | -96.1783 | Manitoba.a | Manitoba | Pine Falls GS | MB_PNF_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 14 | 98.1% | 13.734 | 86.98% | 106.6667 | 6
| Pointe du Bois | MB_PDB00_GEN | Manitoba Hydro | Winnipeg River | 50.2981 | -95.5481 | Manitoba.a | Manitoba | Pointe Du Bois GS | MB_PDB_GSS | 115 | 1926 | 2100 | Hydro_daily | hydro_daily | 33 | 98.1% | 32.373 | 80.6% | 233 | 1 | [20 empty] | Capacity and energy values as of 2021 onwards
| CONTRACT - Basin Electric Power Cooperative | XX_MBUS05_GEN | Manitoba Hydro | MB-USA Border | 48.9994 | -99.5592 | Manitoba.a | Manitoba | INT Peace Gardens | XX_MBUS5_INT | 230 | 2023 | 2028 | Hydro_daily | hydro_daily | -80 | 98.1% | -78.48 | 90% | -630.72 | 1
| CONTRACT - MB-SK (PPA_01) | PP_MBSK01_GEN | Manitoba Hydro | MB-SK Border | 54.7947 | -101.8859 | Manitoba.a | Manitoba | IPB Island Falls | PP_MBSK1_IPT | 115 | 2015 | 2022 | Hydro_daily | hydro_daily | -25 | 98.1% | -24.525 | 90% | -197.1 | 1
| CONTRACT - MB-SK (PPA_01) | PP_MBSK02_GEN | Manitoba Hydro | MB-SK Border | 53.7227 | -101.7696 | Manitoba.a | Manitoba | IPB EB Campbell | PP_MBSK2_IPT | 230 | 2020 | 2040 | Hydro_daily | hydro_daily | -100 | 98.1% | -98.1 | 90% | -788.4 | 1
| CONTRACT - MB-SK (PPA_01) | PP_MBSK03_GEN | Manitoba Hydro | MB-SK Border | 50.5445 | -101.4747 | Manitoba.a | Manitoba | IPB Tantallon | PP_MBSK4_IPT | 230 | 2022 | 2038 | Hydro_daily | hydro_daily | -215 | 98.1% | -210.915 | 90% | -1695.06 | 1
| CONTRACT - Minnesota Power | XX_MBUS02_GEN | Manitoba Hydro | MB-USA Border | 49.0004 | -95.913 | Manitoba.a | Manitoba | INT Iron Range | XX_MBUS3_INT | 500 | 2020 | 2035 | Hydro_daily | hydro_daily | -250 | 98.1% | -245.25 | 90% | -1971 | 1
| CONTRACT - Wisconsin Public Service | XX_MBUS04_GEN | Manitoba Hydro | MB-USA Border | 49.0004 | -95.913 | Manitoba.a | Manitoba | INT Iron Range | XX_MBUS3_INT | 500 | 2021 | 2027 | Hydro_daily | hydro_daily | -100 | 98.1% | -98.1 | 90% | -788.4 | 1
| CONTRACT - Xcel Energy_01 | XX_MBUS01_GEN | Manitoba Hydro | MB-USA Border | 48.9993 | -95.5394 | Manitoba.a | Manitoba | INT Forbes | XX_MBUS2_INT | 500 | 2015 | 2025 | Hydro_daily | hydro_daily | -375 | 98.1% | -367.875 | 90% | -2956.5 | 1
| CONTRACT - Xcel Energy_02 | XX_MBUS03_GEN | Manitoba Hydro | MB-USA Border | 49.0004 | -95.913 | Manitoba.a | Manitoba | INT Iron Range | XX_MBUS3_INT | 500 | 2021 | 2025 | Hydro_daily | hydro_daily | -125 | 98.1% | -122.625 | 90% | -985.5 | 1
| Seven Sisters_01 | MB_SVS01_GEN | Manitoba Hydro | Winnipeg River | 50.1204 | -96.0177 | Manitoba.a | Manitoba | Seven Sisters GS | MB_SVS_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 27.5 | 98.1% | 26.9775 | 70.22% | 169.1667 | 6
| Seven Sisters_02 | MB_SVS02_GEN | Manitoba Hydro | Winnipeg River | 50.1204 | -96.0177 | Manitoba.a | Manitoba | Seven Sisters GS | MB_SVS_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 27.5 | 98.1% | 26.9775 | 70.22% | 169.1667 | 6
| Seven Sisters_03 | MB_SVS03_GEN | Manitoba Hydro | Winnipeg River | 50.1204 | -96.0177 | Manitoba.a | Manitoba | Seven Sisters GS | MB_SVS_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 27.5 | 98.1% | 26.9775 | 70.22% | 169.1667 | 6
| Seven Sisters_04 | MB_SVS04_GEN | Manitoba Hydro | Winnipeg River | 50.1204 | -96.0177 | Manitoba.a | Manitoba | Seven Sisters GS | MB_SVS_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 27.5 | 98.1% | 26.9775 | 70.22% | 169.1667 | 6
| Seven Sisters_05 | MB_SVS05_GEN | Manitoba Hydro | Winnipeg River | 50.1204 | -96.0177 | Manitoba.a | Manitoba | Seven Sisters GS | MB_SVS_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 27.5 | 98.1% | 26.9775 | 70.22% | 169.1667 | 6
| Seven Sisters_06 | MB_SVS06_GEN | Manitoba Hydro | Winnipeg River | 50.1204 | -96.0177 | Manitoba.a | Manitoba | Seven Sisters GS | MB_SVS_GSS | 115 | 1952 | 2100 | Hydro_daily | hydro_daily | 27.5 | 98.1% | 26.9775 | 70.22% | 169.1667 | 6
| Slave Falls_01 | MB_SLF01_GEN | Manitoba Hydro | Winnipeg River | 50.2221 | -95.5687 | Manitoba.a | Manitoba | Slave Falls GS | MB_SLF_GSS | 115 | 1948 | 2100 | Hydro_daily | hydro_daily | 8.5 | 98.1% | 8.3385 | 83.94% | 62.5 | 8
| Slave Falls_02 | MB_SLF02_GEN | Manitoba Hydro | Winnipeg River | 50.2221 | -95.5687 | Manitoba.a | Manitoba | Slave Falls GS | MB_SLF_GSS | 115 | 1948 | 2100 | Hydro_daily | hydro_daily | 8.5 | 98.1% | 8.3385 | 83.94% | 62.5 | 8
| Slave Falls_03 | MB_SLF03_GEN | Manitoba Hydro | Winnipeg River | 50.2221 | -95.5687 | Manitoba.a | Manitoba | Slave Falls GS | MB_SLF_GSS | 115 | 1948 | 2100 | Hydro_daily | hydro_daily | 8.5 | 98.1% | 8.3385 | 83.94% | 62.5 | 8
| Slave Falls_04 | MB_SLF04_GEN | Manitoba Hydro | Winnipeg River | 50.2221 | -95.5687 | Manitoba.a | Manitoba | Slave Falls GS | MB_SLF_GSS | 115 | 1948 | 2100 | Hydro_daily | hydro_daily | 8.5 | 98.1% | 8.3385 | 83.94% | 62.5 | 8
| Slave Falls_05 | MB_SLF05_GEN | Manitoba Hydro | Winnipeg River | 50.2221 | -95.5687 | Manitoba.a | Manitoba | Slave Falls GS | MB_SLF_GSS | 115 | 1948 | 2100 | Hydro_daily | hydro_daily | 8.5 | 98.1% | 8.3385 | 83.94% | 62.5 | 8
| Slave Falls_06 | MB_SLF06_GEN | Manitoba Hydro | Winnipeg River | 50.2221 | -95.5687 | Manitoba.a | Manitoba | Slave Falls GS | MB_SLF_GSS | 115 | 1948 | 2100 | Hydro_daily | hydro_daily | 8.5 | 98.1% | 8.3385 | 83.94% | 62.5 | 8
| Slave Falls_07 | MB_SLF07_GEN | Manitoba Hydro | Winnipeg River | 50.2221 | -95.5687 | Manitoba.a | Manitoba | Slave Falls GS | MB_SLF_GSS | 115 | 1948 | 2100 | Hydro_daily | hydro_daily | 8.5 | 98.1% | 8.3385 | 83.94% | 62.5 | 8
| Slave Falls_08 | MB_SLF08_GEN | Manitoba Hydro | Winnipeg River | 50.2221 | -95.5687 | Manitoba.a | Manitoba | Slave Falls GS | MB_SLF_GSS | 115 | 1948 | 2100 | Hydro_daily | hydro_daily | 8.5 | 98.1% | 8.3385 | 83.94% | 62.5 | 8
| Wuskwatim_01 | MB_WSK01_GEN | Manitoba Hydro JV | Burntwood River | 55.5383 | -98.4938 | Manitoba.a | Manitoba | Wuskwatim GS | MB_WSK_GSS | 230 | 2011 | 2100 | Hydro_daily | hydro_daily | 70 | 98.1% | 68.67 | 81.54% | 500 | 3
| Wuskwatim_02 | MB_WSK02_GEN | Manitoba Hydro JV | Burntwood River | 55.5383 | -98.4938 | Manitoba.a | Manitoba | Wuskwatim GS | MB_WSK_GSS | 230 | 2011 | 2100 | Hydro_daily | hydro_daily | 70 | 98.1% | 68.67 | 81.54% | 500 | 3
| Wuskwatim_03 | MB_WSK03_GEN | Manitoba Hydro JV | Burntwood River | 55.5383 | -98.4938 | Manitoba.a | Manitoba | Wuskwatim GS | MB_WSK_GSS | 230 | 2011 | 2100 | Hydro_daily | hydro_daily | 70 | 98.1% | 68.67 | 81.54% | 500 | 3
| Jenpeg_01 | MB_JPG01_GEN | Manitoba Hydro | Nelson River | 54.5432 | -98.0282 | Manitoba.a | Manitoba | Jenpeg GS | MB_JPG_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 19 | 98.1% | 18.639 | 92.63% | 154.1667 | 6
| Jenpeg_02 | MB_JPG02_GEN | Manitoba Hydro | Nelson River | 54.5432 | -98.0282 | Manitoba.a | Manitoba | Jenpeg GS | MB_JPG_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 19 | 98.1% | 18.639 | 92.63% | 154.1667 | 6
| Jenpeg_03 | MB_JPG03_GEN | Manitoba Hydro | Nelson River | 54.5432 | -98.0282 | Manitoba.a | Manitoba | Jenpeg GS | MB_JPG_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 19 | 98.1% | 18.639 | 92.63% | 154.1667 | 6
| Jenpeg_04 | MB_JPG04_GEN | Manitoba Hydro | Nelson River | 54.5432 | -98.0282 | Manitoba.a | Manitoba | Jenpeg GS | MB_JPG_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 19 | 98.1% | 18.639 | 92.63% | 154.1667 | 6
| Jenpeg_05 | MB_JPG05_GEN | Manitoba Hydro | Nelson River | 54.5432 | -98.0282 | Manitoba.a | Manitoba | Jenpeg GS | MB_JPG_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 19 | 98.1% | 18.639 | 92.63% | 154.1667 | 6
| Jenpeg_06 | MB_JPG06_GEN | Manitoba Hydro | Nelson River | 54.5432 | -98.0282 | Manitoba.a | Manitoba | Jenpeg GS | MB_JPG_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 19 | 98.1% | 18.639 | 92.63% | 154.1667 | 6
| Kelsey_01 | MB_KLS01_GEN | Manitoba Hydro | Nelson River | 56.0405 | -96.5379 | Manitoba.a | Manitoba | Kelsey GS | MB_KLS_GSS | 138 | 1961 | 2100 | Hydro_monthly | hydro_monthly | 41 | 98.1% | 40.221 | 71.99% | 258.5714 | 7
| Kelsey_02 | MB_KLS02_GEN | Manitoba Hydro | Nelson River | 56.0405 | -96.5379 | Manitoba.a | Manitoba | Kelsey GS | MB_KLS_GSS | 138 | 1961 | 2100 | Hydro_monthly | hydro_monthly | 41 | 98.1% | 40.221 | 71.99% | 258.5714 | 7
| Kelsey_03 | MB_KLS03_GEN | Manitoba Hydro | Nelson River | 56.0405 | -96.5379 | Manitoba.a | Manitoba | Kelsey GS | MB_KLS_GSS | 138 | 1961 | 2100 | Hydro_monthly | hydro_monthly | 41 | 98.1% | 40.221 | 71.99% | 258.5714 | 7
| Kelsey_04 | MB_KLS04_GEN | Manitoba Hydro | Nelson River | 56.0405 | -96.5379 | Manitoba.a | Manitoba | Kelsey GS | MB_KLS_GSS | 138 | 1961 | 2100 | Hydro_monthly | hydro_monthly | 41 | 98.1% | 40.221 | 71.99% | 258.5714 | 7
| Kelsey_05 | MB_KLS05_GEN | Manitoba Hydro | Nelson River | 56.0405 | -96.5379 | Manitoba.a | Manitoba | Kelsey GS | MB_KLS_GSS | 138 | 1961 | 2100 | Hydro_monthly | hydro_monthly | 41 | 98.1% | 40.221 | 71.99% | 258.5714 | 7
| Kelsey_06 | MB_KLS06_GEN | Manitoba Hydro | Nelson River | 56.0405 | -96.5379 | Manitoba.a | Manitoba | Kelsey GS | MB_KLS_GSS | 138 | 1961 | 2100 | Hydro_monthly | hydro_monthly | 41 | 98.1% | 40.221 | 71.99% | 258.5714 | 7
| Kelsey_07 | MB_KLS07_GEN | Manitoba Hydro | Nelson River | 56.0405 | -96.5379 | Manitoba.a | Manitoba | Kelsey GS | MB_KLS_GSS | 138 | 1961 | 2100 | Hydro_monthly | hydro_monthly | 41 | 98.1% | 40.221 | 71.99% | 258.5714 | 7
| Kettle_01 | MB_KTL01_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_02 | MB_KTL02_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_03 | MB_KTL03_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_04 | MB_KTL04_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_05 | MB_KTL05_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_06 | MB_KTL06_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_07 | MB_KTL07_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_08 | MB_KTL08_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_09 | MB_KTL09_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_10 | MB_KTL10_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_11 | MB_KTL11_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Kettle_12 | MB_KTL12_GEN | Manitoba Hydro | Nelson River | 56.3817 | -94.6346 | Manitoba.a | Manitoba | Radisson CS | MB_RDS_CSS | 138 | 1974 | 2100 | Hydro_monthly | hydro_monthly | 102 | 98.1% | 100.062 | 66.5% | 594.1667 | 12
| Limestone_01 | MB_LMS01_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_02 | MB_LMS02_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_03 | MB_LMS03_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_04 | MB_LMS04_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_05 | MB_LMS05_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_06 | MB_LMS06_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_07 | MB_LMS07_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_08 | MB_LMS08_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_09 | MB_LMS09_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Limestone_10 | MB_LMS10_GEN | Manitoba Hydro | Nelson River | 56.5075 | -94.1097 | Manitoba.a | Manitoba | Limestone GS | MB_LMS_GSS | 230 | 1990 | 2100 | Hydro_monthly | hydro_monthly | 135 | 98.1% | 132.435 | 64.52% | 763 | 10
| Long Spruce_01 | MB_LSP01_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_02 | MB_LSP02_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_03 | MB_LSP03_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_04 | MB_LSP04_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_05 | MB_LSP05_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_06 | MB_LSP06_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_07 | MB_LSP07_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_08 | MB_LSP08_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_09 | MB_LSP09_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Long Spruce_10 | MB_LSP10_GEN | Manitoba Hydro | Nelson River | 56.3978 | -94.3687 | Manitoba.a | Manitoba | Long Spruce GS | MB_LSP_GSS | 230 | 1979 | 2100 | Hydro_monthly | hydro_monthly | 98 | 98.1% | 96.138 | 70.82% | 608 | 10
| Laurie River 1 | MB_LRV01_GEN | Manitoba Hydro | Laurie River | 56.2508 | -101.1171 | Manitoba.a | Manitoba | Laurie River #1 TS | MB_LRV_TSS | 138 | 1952 | 2100 | Hydro_run | hydro_run | 5 | 65% | 3.25 | 68.49% | 30 | 2
| Laurie River 2 | MB_LRV02_GEN | Manitoba Hydro | Laurie River | 56.2251 | -101.0094 | Manitoba.a | Manitoba | Laurie River #1 TS | MB_LRV_TSS | 138 | 1958 | 2100 | Hydro_run | hydro_run | 5 | 65% | 3.25 | 68.49% | 30 | 2
| St. Joseph | MB_STJ00_GEN | Pattern Energy Group LP | Southern Manitoba | 49.1345 | -97.4205 | Manitoba.a | Manitoba | St Joseph GS | MB_STJ_GSS | 230 | 2012 | 2032 | Wind_Onshore | wind | 138 | 20% | 27.6 | 35% | 423.108
| St. Leon | MB_STL00_GEN | Algonquin Power | Southern Manitoba | 49.3472 | -98.6345 | Manitoba.a | Manitoba | St Leon GS | MB_STL_GSS | 230 | 2012 | 2032 | Wind_Onshore | wind | 120 | 20% | 24 | 35% | 367.92
Specific Notes:
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Unless noted otherwise, the wind generating stations are presumed to be connected to the nearest 69 kV substation
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit Hydro_run facilities treated as single-unit facilities
RH Additions, Comments and TODOs
Remote projects are not included in this list.
See calculations sheets for sources of values.
Sources

## Storage
MB | EXISTING STORAGE | [12 empty] | DESIGN | [7 empty] | OPERATIONS
| Project Name | Storage Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Technology | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Days | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | kV | [5 empty] | (MW) | (MWh) | (Hours) |  | ($M) | (hours) | (hours) | (%) | (days/y) | ($/year) | ($/MWh)
Specific Notes:

## HydroExisting
MB | EXISTING STORAGE HYDROELECTRIC | [24 empty] | RESERVOIR
| Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Average Annual Energy - Plant | # of units | Renewal Year | Dam Type | Penstock | Rated Head | Maximum Head | Minimum Head | Operating Flow (Facility) | Rated Discharge (Unit) | Rated Discharge (Facility) | Upstream Reservoir Area | Upstream Reservoir Storage | Turbine Type | Station Flow | Upper Storage Name | Upper Storage Level | Lower Storage Name | Lower Storage Level | Upper Storage Name | Minimum Level | Maximum Level | Initial Level | Low Reference Level | High Reference Level | Low Volume | High Volume | Live Storage | M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10 | M11 | M12 | Notes
|  |  | (MW) |  | (MW) |  | (GWh/year) |  |  |  | (m) | (m) | (m) | (m) | (m3/s) | (m3/s) | (m3/s) | (km2) | (hours) |  | (WSC#) |  | (WSC#) |  | (WSC#) |  | (m) | (m) | (m) | (m) | (m) | (m3) | (m3) | (m3) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s)
| Grand Rapids | Hydro_daily | 480 | 98.1% | 470.88 | 36.98% | 1555 | 4 | [12 empty] | 05KL001 | Cedar Lake | 05KL005 | Lake Winnipeg (West) | 05SG001 | Cedar Lake
| Great Falls | Hydro_daily | 129 | 98.1% | 126.549 | 80.97% | 915 | 6 | [12 empty] | 05PF048 | Great Falls |  | Pine Falls |  | Great Falls
| Keeyask | Hydro_daily | 693 | 98.1% | 679.833 | 72.99% | 4431 | 7 |  |  |  |  | 19.2 | 19.2 | 3125 |  |  | 93 |  |  |  | Split Lake | 05UF003 | Gull Lake |  | Split Lake
| McArthur Falls | Hydro_daily | 56 | 98.1% | 54.936 | 79.5% | 390 | 8 | [12 empty] | 05PF068 | McArthur Falls |  | Great Falls |  | McArthur Falls
| Pine Falls | Hydro_daily | 84 | 98.1% | 82.404 | 86.98% | 640 | 6 | [12 empty] | 05PF069 | Pine Falls |  | Lake Winnipeg (South) | 05SA003 | Pine Falls | [20 empty] | 05SA003 not directly below Pine Falls GS
| Pointe du Bois | Hydro_daily | 33 | 98.1% | 32.373 | 80.6% | 233 | 16
| Seven Sisters | Hydro_daily | 165 | 98.1% | 161.865 | 70.22% | 1015 | 6 | [13 empty] | Seven Sisters | 05PF057 | McArthur Falls |  | Seven Sisters
| Slave Falls | Hydro_daily | 68 | 98.1% | 66.708 | 87.3% | 520 | 8 | [12 empty] | 05PF063 | Slave Falls |  | Seven Sisters | 05PF057 | Slave Falls | [20 empty] | 05PF057 not directly below Slave Falls GS
| Wuskwatim | Hydro_daily | 211 | 98.1% | 206.991 | 81.15% | 1500 | 3 | [13 empty] | Wuskwatim Lake | 05TF006 |  |  | Wuskwatim Lake
| Jenpeg | Hydro_monthly | 114 | 98.1% | 111.834 | 92.63% | 925 | 6 | [12 empty] | 05UB009 | Lake Winnipeg (North) | 05RF001 | Cross Lake | 05UD001 | Lake Winnipeg (North)
| Kelsey | Hydro_monthly | 287 | 98.1% | 281.547 | 71.99% | 1810 | 7 | [12 empty] | 05UE005 | Kelsey |  | Split Lake | 05UF003 | Kelsey
| Kettle | Hydro_monthly | 1224 | 98.1% | 1200.744 | 66.5% | 7130 | 12 | [12 empty] | 05UF006 | Stephens Lake |  | Long Spruce |  | Stephens Lake
| Limestone | Hydro_monthly | 1350 | 98.1% | 1324.35 | 64.52% | 7630 | 10 | [13 empty] | Limestone |  | Hudson Bay |  | Limestone
| Long Spruce | Hydro_monthly | 980 | 98.1% | 961.38 | 70.82% | 6080 | 10 | [12 empty] | 05UF007 | Long Spruce |  | Limestone |  | Long Spruce
General Notes:
Hydroelectric generation type has been estimated based on available information concerning operations, reservoir size and operations, facility location and design flows.
The WSC# refers to the Water Survey of Canada Hydrometric station

## HydroRenewals
MB | HYDROELECTRIC RENEWAL |  | Existing Design | [5 empty] | Renewal Design | [14 empty] | Costs | 1.77% | 1.05 |  | 5% | 7% | 70
| Existing Project Name | Owner | Generation Type | Installed Capacity | Effective Capacity | Annual Average Energy Plant | Existing #units | Start Year | Renewal Project Name | Renewal Project Code | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Additional Annual Energy | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed Cost Existing Project | Fixed Cost Renewed Project | Fixed O&M | Variable Costs | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
|  |  |  | (MW) | (MW) | (GWh/year) | [5 empty] | dd.dddd | dd.dddd |  |  |  |  | (km) |  |  | (MW) | (MW) | (GWh/year) | ($2018M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M/year) | ($/kW-year) | ($/year) | ($/year) | ($2018M/year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
| Kelsey GS | Manitoba Hydro | Hydro_monthly | 286 | 286 | 2176 | 7 | 1961 | Kelsey Additional Units | RN_KEL | Nelson River | 56.0405 | -96.5379 | Manitoba.a | Kelsey GS | MB_KLS_GEN | 138 | 25 | Hydro_monthly | hydro_monthly | 178 | 178 | 0 | 300 | 5.31 | 40.1201 | 345.4301 | 50.2952 | 395.7253 | 27.9459 | 156.9996 | 6220888.1883 | 7764294.2795 | 8670.8207 | 1.9337 | 3.11 | 5.0437 |  |  | 4 | 6
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroGreenfield
MB | HYDROELECTRIC GREENFIELD | [10 empty] | DESIGN | [6 empty] | COSTS |  | 1.77% | 1.05 |  |  | 7% | 70
| Project Name | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Distance to Market Grid | Connecting Node Name | Connecting Node Code | Substation Voltage | Generation Type | Generation Type - COPPER | Installed Capacity | Effective Capacity | Average Annual Energy - Plant | Capacity Factor | # units | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implentation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed Cost | Fixed Cost | Fixed O&M | Variable Costs | Water Rentals | Variable O&M | Construction Time | Development Time | Notes
[8 empty] | (km) |  |  | (kV) |  |  | (MW) | (MW) | (GWh/year) |  |  | ($2012M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M/year) | ($/kW-year) | ($2012M/year) | ($2018M/year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | (years) | (years)
| Early Morning | GF_EMG | Manitoba Hydro | Burntwood River |  |  | Manitoba.a | 0 |  |  |  | hydro_daily | hydro_daily | 80 | 80 | 500 | 90% | 3 | 1409 | 1544.4585 | 27.3369 | 299.1673 | 1870.9627 | 158.2238 | 2029.1865 | 143.3002 | 1791.2524 | 6.0184 | 6.597 | 82462.4651 | 2.6267 | 3.11 | 5.7367 | 6 | 16
| Bonald | GF_BON | Manitoba Hydro | Churchill River |  |  | Manitoba.a | 0 |  |  |  | hydro_daily | hydro_daily | 110 | 110 | 600 | 65% | 4 | 2188 | 2398.35 | 42.4508 | 540.1523 | 2980.9532 | 217.0228 | 3197.976 | 225.8396 | 2053.0868 | 3.7268 | 4.0851 | 37137.1569 | 2.3251 | 3.11 | 5.4351 | 7 | 17
| Notigi | GF_NOT | Manitoba Hydro | Burntwood River |  |  | Manitoba.a | 0 |  |  |  | hydro_daily | hydro_daily | 120 | 120 | 830 | 85% | 2 | 935 | 1024.8891 | 18.1405 | 167.2838 | 1210.3134 | 117.7445 | 1328.0579 | 93.7868 | 781.5568 | 4.0656 | 4.4565 | 37137.1569 | 2.2489 | 3.11 | 5.3589 | 5 | 15
| Granville | GF_GRV | Manitoba Hydro | Churchill River |  |  | Manitoba.a | 0 |  |  |  | hydro_daily | hydro_daily | 120 | 120 | 700 | 65% | 4 | 1753 | 1921.53 | 34.0111 | 313.6347 | 2269.1758 | 180.3532 | 2449.5289 | 172.9846 | 1441.5381 | 4.0656 | 4.4565 | 37137.1569 | 2.2489 | 3.11 | 5.3589 | 5 | 15
| First Rapids | GF_FRP | Manitoba Hydro | Burntwood River |  |  | Manitoba.a | 0 |  |  |  | hydro_daily | hydro_daily | 210 | 210 | 1300 | 75% | 4 | 2053 | 2250.3714 | 39.8316 | 435.9052 | 2726.1082 | 204.2562 | 2930.3644 | 206.9409 | 985.4331 | 15.7983 | 17.3171 | 82462.4651 | 1.815 | 3.11 | 4.925 | 6 | 16
| Red Rock | GF_RRK | Manitoba Hydro | Upper Nelson River |  |  | Manitoba.a | 0 |  |  |  | hydro_monthly | hydro_monthly | 250 | 250 | 1280 | 65% | 6 | 2922 | 3202.9154 | 56.6916 | 522.7841 | 3782.3911 | 255.0701 | 4037.4612 | 285.1236 | 1140.4944 | 8.855 | 9.7063 | 38825.2095 | 1.6978 | 3.11 | 4.8078 | 5 | 15
| Manasan | GF_MSN | Manitoba Hydro | Burntwood River |  |  | Manitoba.a | 0 |  |  |  | hydro_daily | hydro_daily | 270 | 270 | 1600 | 65% | 4 | 2770 | 3036.3024 | 53.7426 | 588.1429 | 3678.1878 | 250.2816 | 3928.4694 | 277.4267 | 1027.5061 | 7.8759 | 8.6331 | 31974.3468 | 1.6485 | 3.11 | 4.7585 | 6 | 16
| Whitemud | GF_WMD | Manitoba Hydro | Upper Nelson River |  |  | Manitoba.a | 0 |  |  |  | hydro_monthly | hydro_monthly | 310 | 310 | 1620 | 65% | 6 | 3019 | 3309.2408 | 58.5736 | 641.0121 | 4008.8264 | 265.3321 | 4274.1585 | 301.839 | 973.6744 | 10.9802 | 12.0358 | 38825.2095 | 1.5635 | 3.11 | 4.6735 | 6 | 16
| Birthday Rapids | GF_BRP | Manitoba Hydro | Lower Nelson River |  |  | Manitoba.a | 0 |  |  |  | hydro_monthly | hydro_monthly | 380 | 380 | 1800 | 60% | 9 | 3684 | 4038.1726 | 71.4757 | 782.2088 | 4891.857 | 303.6979 | 5195.555 | 366.9076 | 965.5464 | 13.4596 | 14.7536 | 38825.2095 | 1.4462 | 3.11 | 4.5562 | 6 | 16
| Gillam Island | GF_GIS | Manitoba Hydro | Lower Nelson River |  |  | Manitoba.a | 0 |  |  |  | hydro_monthly | hydro_monthly | 1080 | 1080 | 4900 | 60% | 11 | 6863 | 7522.7954 | 133.1535 | 2455.0999 | 10111.0487 | 497.0002 | 10608.049 | 749.1354 | 693.6439 | 11.1024 | 12.1698 | 11268.2991 | 0.96938 | 3.11 | 4.0794 | 10 | 20
| Conawapa | GF_CON | Manitoba Hydro | Lower Nelson River |  |  | Manitoba.a | 0 |  |  |  | hydro_monthly | hydro_monthly | 1485 | 1485 | 7000 | 80% | 10 | 5513.5 | 6043.5571 | 106.971 | 1761.7112 | 7912.2392 | 420.8324 | 8333.0716 | 588.4776 | 396.2812 | 15.2658 | 16.7334 | 11268.2991 | 0.85807 | 3.11 | 3.9681 | 9 | 19
Specific Notes:
Transmission costs are included in Total Project cost, so distance to grid is taken as 0 km
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroPS
MB | HYDROELECTRIC PUIMPED STORAGE | [15 empty] | Existing Design | [8 empty] | Reservoir Design | [13 empty] | Costs | 1.77% | 1.06 |  |  | 7% | 70
| Pumped Storage Project | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Estimated Round Trip Efficiency | Existing Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Salt/Fresh | Reservoir Types | Reservoir Storage | Storage Requirement | Gross Head | Penstock | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping) | Turbine Type | Pump Type | Generation Duration at Peak Output | Efficient Pumping Capacity Duration | Total Footprint | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Cost of Capacity | Unit Cost of Stored Energy | Levelized Cost | Construction Time | Development Time | Notes
[5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) |  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) |  |  |  |  | (m3) | (MWh) | (m) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2018/MW) | ($2018/MWh) | ($2018/kW-year) | (years) | (years)
Specific Notes:
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## Transmission
MB | EXISTING TRANSMISSION
| Circuit ID | Owner | Operating Region | Number of Circuits | Current | Length | Length | Voltage | Reactance | Smax | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes | Count
[5 empty] | (ad/dc) | (km) | (miles) | (kV) | (ohm) |  | (A) | (A) | (MVA) | (MVA) |  | (MW) | (MW)
| ST6 | Manitoba Hydro | Manitoba | 1 | ac | 13.446 | 8.3 | 115 | 5.6089 | 3 | [5 empty] | 98.4491 | 108.4016 | Vivian | MB_VIV_DSS | Anola DSC | MB_ANO_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 207
| G1A | Manitoba Hydro | Manitoba | 1 | ac | 235.9044 | 145.62 | 230 | 113.2341 | 1.5875 | [5 empty] | 212.7288 | 230.1917 | Grand Rapids GS | MB_GRP_GSS | Ashern | MB_ASH_DSS |  |  | 60
| G2A | Manitoba Hydro | Manitoba | 1 | ac | 235.9044 | 145.62 | 230 | 113.2341 | 1.5875 | [5 empty] | 212.7288 | 230.1917 | Grand Rapids GS | MB_GRP_GSS | Ashern | MB_ASH_DSS |  |  | 61
| KY32 | Manitoba Hydro | Manitoba | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Laverendrye | MB_LAV_DSS | Augier | MB_AUG_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 122
| BP6 | Manitoba Hydro | Manitoba | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Carberry North | MB_CBY_DSS | Austin | MB_AUS_DSS |  |  | 18
| BP7 | Manitoba Hydro | Manitoba | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Carberry North | MB_CBY_DSS | Austin | MB_AUS_DSS |  |  | 22
| BE2 | Manitoba Hydro | Manitoba | 1 | ac | 1.8144 | 1.12 | 115 | 0.75686 | 3 | [5 empty] | 98.4491 | 108.4016 | Victoria Ave | MB_VCT_DSS | Brandon 65th St East | MB_B65_DSS |  | Assumed route of this line | 11
| K24B | Manitoba Hydro | Manitoba | 1 | ac | 98.658 | 60.9 | 230 | 47.3558 | 2.821 | [5 empty] | 378.0207 | 409.0522 | Kelsey TS | MB_KLT_TSS | Birchtree | MB_BCT_DSS |  |  | 95
| W76B | Manitoba Hydro | Manitoba | 1 | ac | 45.2952 | 27.96 | 230 | 21.7417 | 3 | [5 empty] | 402 | 435 | Wuskwatim GS | MB_WSK_GSS | Birchtree | MB_BCT_DSS |  |  | 245
| CB1 | Manitoba Hydro | Manitoba | 1 | ac | 0.2916 | 0.18 | 115 | 0.12164 | 3 | [5 empty] | 98.4491 | 108.4016 | Cornwallis | MB_CNW_DSS | Brandon GS | MB_BDN_GSS |  |  | 27
| CB3 | Manitoba Hydro | Manitoba | 1 | ac | 0.2916 | 0.18 | 115 | 0.12164 | 3 | [5 empty] | 98.4491 | 108.4016 | Cornwallis | MB_CNW_DSS | Brandon GS | MB_BDN_GSS |  |  | 28
| CB4 | Manitoba Hydro | Manitoba | 1 | ac | 0.2916 | 0.18 | 115 | 0.12164 | 3 | [5 empty] | 98.4491 | 108.4016 | Cornwallis | MB_CNW_DSS | Brandon GS | MB_BDN_GSS |  |  | 29
| CB42 | Manitoba Hydro | Manitoba | 1 | ac | 0.2916 | 0.18 | 115 | 0.12164 | 3 | [5 empty] | 98.4491 | 108.4016 | Cornwallis | MB_CNW_DSS | Brandon GS | MB_BDN_GSS |  |  | 30
| RF58 | Manitoba Hydro | Manitoba | 1 | ac | 1.1178 | 0.69 | 115 | 0.46628 | 3 | [5 empty] | 98.4491 | 108.4016 | Ross Lake | MB_RSL_DSS | Flin Flon Border | MB_BDR_DSS |  |  | 173
| GS21 | Manitoba Hydro | Manitoba | 1 | ac | 54.94 | 33.9136 | 115 | 22.9178 | 3 | [5 empty] | 98.4491 | 108.4016 | Great Falls GS | MB_GRF_GSS | Brokenhead | MB_BKH_DSS |  |  | 70
| SK1 | Manitoba Hydro | Manitoba | 1 | ac | 75 | 46.2963 | 115 | 31.2857 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | Brereton Lake | MB_BRT_DSS |  |  | 198
| SG12S | Manitoba Hydro | Manitoba | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Seddons Corner DSC | MB_SDC_DSS | Beausejour East | MB_BSJ_DSS |  |  | 197
| WB45 | Manitoba Hydro | Manitoba | 1 | ac | 4.2606 | 2.63 | 138 | 1.8473 | 3 | [5 empty] | 141 | 156 | Mystery Lake | MB_MYS_DSS | Burntwood | MB_BWD_DSS |  |  | 246
| P58C | Manitoba Hydro | Manitoba | 1 | ac | 90.67 | 55.9691 | 230 | 43.5216 | 2.9826 | [5 empty] | 399.6672 | 432.4757 | Ralls Island | MB_RLI_DSS | Cranberry Portage | MB_CBP_DSS |  |  | 154
| BP6 | Manitoba Hydro | Manitoba | 1 | ac | 50.78 | 31.3457 | 115 | 21.1825 | 3 | [5 empty] | 98.4491 | 108.4016 | Brandon GS | MB_BDN_GSS | Carberry North | MB_CBY_DSS |  |  | 17
| BP7 | Manitoba Hydro | Manitoba | 1 | ac | 50.78 | 31.3457 | 115 | 21.1825 | 3 | [5 empty] | 98.4491 | 108.4016 | Brandon GS | MB_BDN_GSS | Carberry North | MB_CBY_DSS |  |  | 21
| FC56 | Manitoba Hydro | Manitoba | 1 | ac | 3.6774 | 2.27 | 115 | 1.534 | 3 | [5 empty] | 98.4491 | 108.4016 | Flin Flon Border | MB_BDR_DSS | Cliff Lake | MB_CFL_DSS |  |  | 58
| H59C | Manitoba Hydro | Manitoba | 1 | ac | 134.784 | 83.2 | 230 | 64.6963 | 2.2964 | [5 empty] | 307.7155 | 332.9757 | Herblet Lake | MB_HBL_DSS | Cliff Lake | MB_CFL_DSS |  |  | 80
| P58C | Manitoba Hydro | Manitoba | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Cranberry Portage | MB_CBP_DSS | Cliff Lake | MB_CFL_DSS |  |  | 155
| RC57 | Manitoba Hydro | Manitoba | 1 | ac | 2.835 | 1.75 | 115 | 1.1826 | 3 | [5 empty] | 98.4491 | 108.4016 | Ross Lake | MB_RSL_DSS | Cliff Lake | MB_CFL_DSS |  |  | 171
| RC60 | Manitoba Hydro | Manitoba | 1 | ac | 270.702 | 167.1 | 138 | 117.3687 | 1.4498 | [5 empty] | 68.1414 | 75.3904 | Radisson CS | MB_RDS_CSS | Churchill South | MB_CHS_DSS |  |  | 172
| G37C | Manitoba Hydro | Manitoba | 1 | ac | 64.2492 | 39.66 | 230 | 30.8396 | 3 | [5 empty] | 402 | 435 | Glenboro South | MB_GBS_DSS | Cornwallis | MB_CNW_DSS |  |  | 63
| N56C | Manitoba Hydro | Manitoba | 1 | ac | 57.2022 | 35.31 | 230 | 27.4571 | 3 | [5 empty] | 402 | 435 | Neepawa | MB_NPW_DSS | Cornwallis | MB_CNW_DSS |  |  | 148
| P81C | Manitoba Hydro | Manitoba | 1 | ac | 125.469 | 77.45 | 230 | 60.2251 | 2.4074 | [5 empty] | 322.5975 | 349.0794 | Portage South | MB_PGS_DSS | Cornwallis | MB_CNW_DSS |  |  | 156
| BD52 | Manitoba Hydro | Manitoba | 1 | ac | 8.8128 | 5.44 | 115 | 3.6762 | 3 | [5 empty] | 98.4491 | 108.4016 | Brandon GS | MB_BDN_GSS | Crocus Plains | MB_CRP_DSS |  |  | 8
| RL2 | Manitoba Hydro | Manitoba | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | Court | MB_CRT_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 179
| VH1 | Manitoba Hydro | Manitoba | 1 | ac | 13.7538 | 8.49 | 115 | 5.7373 | 3 | [5 empty] | 98.4491 | 108.4016 | St Vital | MB_STV_DSS | Dakota | MB_DAK_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 235
| XV39 | Manitoba Hydro | Manitoba | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Mohawk | MB_MOH_DSS | Dakota | MB_DAK_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 254
| VG11-12-13 | Manitoba Hydro | Manitoba | 1 | dc | 895 | 552.4691 | 463.5 | [7 empty] | 927 | 927 | Radisson CS | MB_RDS_CSS | Dorsey CS | MB_DSY_CSS |  |  | 229
| VG21-22-23 | Manitoba Hydro | Manitoba | 1 | dc | 895 | 552.4691 | 463.5 | [7 empty] | 927 | 927 | Radisson CS | MB_RDS_CSS | Dorsey CS | MB_DSY_CSS |  |  | 230
| VG31-32 | Manitoba Hydro | Manitoba | 1 | dc | 937 | 578.3951 | 500 | [7 empty] | 1000 | 1000 | Henday CS | MB_HDY_CSS | Dorsey CS | MB_DSY_CSS |  |  | 231
| VG41-42 | Manitoba Hydro | Manitoba | 1 | dc | 937 | 578.3951 | 500 | [7 empty] | 1000 | 1000 | Henday CS | MB_HDY_CSS | Dorsey CS | MB_DSY_CSS |  |  | 232
| A4D | Manitoba Hydro | Manitoba | 1 | ac | 171.5256 | 105.88 | 230 | 82.3323 | 1.9588 | [5 empty] | 262.4858 | 284.0332 | Ashern | MB_ASH_DSS | Dorsey | MB_DSY_DSS |  |  | 2
| BK51 | Manitoba Hydro | Manitoba | 1 | ac | 0.2106 | 0.13 | 230 | 0.10109 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Dorsey | MB_DSY_DSS |  |  | 13
| BK52 | Manitoba Hydro | Manitoba | 1 | ac | 0.2106 | 0.13 | 230 | 0.10109 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Dorsey | MB_DSY_DSS |  |  | 14
| TS44 | Manitoba Hydro | Manitoba | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Tyndall DSC | MB_TYN_DSS | East Selkirk | MB_ESK_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 219
| DF54 | Manitoba Hydro | Manitoba | 1 | ac | 7.695 | 4.75 | 115 | 3.2099 | 3 | [5 empty] | 98.4491 | 108.4016 | Crocus Plains | MB_CRP_DSS | Fortier | MB_FRT_DSS |  |  | 53
| S53G | Manitoba Hydro | Manitoba | 1 | ac | 51.9858 | 32.09 | 230 | 24.9532 | 3 | [5 empty] | 402 | 435 | St Leon GS | MB_STL_GSS | Glenboro South | MB_GBS_DSS |  |  | 189
| GG64 | Manitoba Hydro | Manitoba | 1 | ac | 91.7082 | 56.61 | 138 | 39.7621 | 2.9603 | [5 empty] | 139.1332 | 153.9346 | Gods Lake Narrows | MB_GLN_DSS | Garden Hill | MB_GDH_DSS |  |  | 68
| TR5 | Manitoba Hydro | Manitoba | 1 | ac | 0.81 | 0.5 | 115 | 0.33789 | 3 | [5 empty] | 98.4491 | 108.4016 | Transcona | MB_TCA_DSS | Griffin Steel | MB_GFS_ISS |  |  | 216
| PC4 | Manitoba Hydro | Manitoba | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Pine Falls GS | MB_PNF_GSS | Gull Lake | MB_GLL_DSS |  |  | 159
| KN36 | Manitoba Hydro | Manitoba | 1 | ac | 85 | 52.4691 | 138 | 36.8536 | 3 | [5 empty] | 141 | 156 | Ilford | MB_ILF_DSS | Gillam | MB_GLM_DSS |  |  | 113
| HG61 | Manitoba Hydro | Manitoba | 1 | ac | 75.168 | 46.4 | 138 | 32.5907 | 3 | [5 empty] | 141 | 156 | Oxford House | MB_OXF_DSS | Gods Lake Narrows | MB_GLN_DSS |  |  | 82
| SG12 | Manitoba Hydro | Manitoba | 1 | ac | 25.8 | 15.9259 | 115 | 10.7623 | 3 | [5 empty] | 98.4491 | 108.4016 | Lac Du Bonnet | MB_LDB_DSS | Great Falls GS | MB_GRF_GSS |  |  | 194
| P18H | Manitoba Hydro | Manitoba | 1 | ac | 63.7146 | 39.33 | 230 | 30.583 | 3 | [5 empty] | 402 | 435 | Ponton | MB_PTN_DSS | Herblet Lake | MB_HBL_DSS |  |  | 150
| W73H | Manitoba Hydro | Manitoba | 1 | ac | 138.7854 | 85.67 | 230 | 66.617 | 2.2525 | [5 empty] | 301.8353 | 326.6129 | Wuskwatim GS | MB_WSK_GSS | Herblet Lake | MB_HBL_DSS |  |  | 243
| W74H | Manitoba Hydro | Manitoba | 1 | ac | 138.7854 | 85.67 | 230 | 66.617 | 2.2525 | [5 empty] | 301.8353 | 326.6129 | Wuskwatim GS | MB_WSK_GSS | Herblet Lake | MB_HBL_DSS |  |  | 244
| H1 | Manitoba Hydro | Manitoba | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Limestone GS | MB_LMS_GSS | Henday CS | MB_HDY_CSS |  |  | 75
| H2 | Manitoba Hydro | Manitoba | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Limestone GS | MB_LMS_GSS | Henday CS | MB_HDY_CSS |  |  | 76
| H3 | Manitoba Hydro | Manitoba | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Limestone GS | MB_LMS_GSS | Henday CS | MB_HDY_CSS |  |  | 77
| H4 | Manitoba Hydro | Manitoba | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Limestone GS | MB_LMS_GSS | Henday CS | MB_HDY_CSS |  |  | 78
| H5 | Manitoba Hydro | Manitoba | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Limestone GS | MB_LMS_GSS | Henday CS | MB_HDY_CSS |  |  | 79
| K61H | Manitoba Hydro | Manitoba | 1 | ac | 27 | 16.6667 | 230 | 12.96 | 3 | [5 empty] | 402 | 435 | Keewatinohk CS | MB_KWT_CSS | Henday CS | MB_HDY_CSS |  |  | 101
| K62H | Manitoba Hydro | Manitoba | 1 | ac | 27 | 16.6667 | 230 | 12.96 | 3 | [5 empty] | 402 | 435 | Keewatinohk CS | MB_KWT_CSS | Henday CS | MB_HDY_CSS |  |  | 102
| K63H | Manitoba Hydro | Manitoba | 1 | ac | 27 | 16.6667 | 230 | 12.96 | 3 | [5 empty] | 402 | 435 | Keewatinohk CS | MB_KWT_CSS | Henday CS | MB_HDY_CSS |  |  | 103
| K64H | Manitoba Hydro | Manitoba | 1 | ac | 27 | 16.6667 | 230 | 12.96 | 3 | [5 empty] | 402 | 435 | Keewatinohk CS | MB_KWT_CSS | Henday CS | MB_HDY_CSS |  |  | 104
| EH13 | Manitoba Hydro | Manitoba | 1 | ac | 6.4638 | 3.99 | 115 | 2.6963 | 3 | [5 empty] | 98.4491 | 108.4016 | Victoria Ave | MB_VCT_DSS | Highland Park | MB_HLP_DSS |  |  | 55
| FH53 | Manitoba Hydro | Manitoba | 1 | ac | 9.072 | 5.6 | 115 | 3.7843 | 3 | [5 empty] | 98.4491 | 108.4016 | Fortier | MB_FRT_DSS | Highland Park | MB_HLP_DSS |  |  | 59
| VJ50 | Manitoba Hydro | Manitoba | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Randolph | MB_RDP_DSS | Hanover | MB_HNV_DSS |  |  | 238
| VT63 | Manitoba Hydro | Manitoba | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Randolph | MB_RDP_DSS | Hanover | MB_HNV_DSS |  |  | 241
| VH1 | Manitoba Hydro | Manitoba | 1 | ac | 13.7538 | 8.49 | 115 | 5.7373 | 3 | [5 empty] | 98.4491 | 108.4016 | Dakota | MB_DAK_DSS | Harrow | MB_HRW_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 236
| XH46 | Manitoba Hydro | Manitoba | 1 | ac | 5.7024 | 3.52 | 115 | 2.3787 | 3 | [5 empty] | 98.4491 | 108.4016 | Mohawk | MB_MOH_DSS | Harrow | MB_HRW_DSS |  |  | 253
| KN36 | Manitoba Hydro | Manitoba | 1 | ac | 75 | 46.2963 | 138 | 32.5179 | 3 | [5 empty] | 141 | 156 | Kelsey GS | MB_KLS_GSS | Ilford | MB_ILF_DSS |  |  | 112
| BK9 | Manitoba Hydro | Manitoba | 1 | ac | 1.2636 | 0.78 | 138 | 0.54786 | 3 | [5 empty] | 141 | 156 | Mystery Lake | MB_MYS_DSS | Inco | MB_INC_ISS |  |  | 15
| KT1 | Manitoba Hydro | Manitoba | 1 | ac | 100.8774 | 62.27 | 138 | 43.7376 | 2.78 | [5 empty] | 130.6582 | 144.5581 | Kelsey GS | MB_KLS_GSS | Inco | MB_INC_ISS |  |  | 119
| KT2 | Manitoba Hydro | Manitoba | 1 | ac | 96.633 | 59.65 | 138 | 41.8973 | 2.8599 | [5 empty] | 134.4153 | 148.7148 | Kelsey GS | MB_KLS_GSS | Inco | MB_INC_ISS |  |  | 120
| RI8 | Manitoba Hydro | Manitoba | 1 | ac | 6.804 | 4.2 | 115 | 2.8382 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | Inkster | MB_INK_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 174
| RS51 | Manitoba Hydro | Manitoba | 1 | ac | 6.804 | 4.2 | 115 | 2.8382 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | Inkster | MB_INK_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 183
| RS52 | Manitoba Hydro | Manitoba | 1 | ac | 6.804 | 4.2 | 115 | 2.8382 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | Inkster | MB_INK_DSS |  |  | 185
| KY32 | Manitoba Hydro | Manitoba | 1 | ac | 1.86 | 1.1481 | 115 | 0.77589 | 3 | [5 empty] | 98.4491 | 108.4016 | Augier | MB_AUG_DSS | Kirkfield Park | MB_KFP_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 121
| RK6 | Manitoba Hydro | Manitoba | 1 | ac | 17.9982 | 11.11 | 115 | 7.5078 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | Kirkfield Park | MB_KFP_DSS |  |  | 176
| KK35 | Manitoba Hydro | Manitoba | 1 | ac | 0.486 | 0.3 | 138 | 0.21072 | 3 | [5 empty] | 141 | 156 | Kelsey GS | MB_KLS_GSS | Kelsey TS | MB_KLT_TSS |  |  | 111
| R26K | Manitoba Hydro | Manitoba | 1 | ac | 130.1994 | 80.37 | 230 | 62.4957 | 2.3494 | [5 empty] | 314.8192 | 340.6625 | Radisson CS | MB_RDS_CSS | Kelsey TS | MB_KLT_TSS |  |  | 166
| KE1 | Manitoba Hydro | Manitoba | 1 | ac | 3 | 1.8519 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Keeyask GS | MB_KSK_GSS | Keeyask SS | MB_KSS_SWS |  |  | 106
| KE2 | Manitoba Hydro | Manitoba | 1 | ac | 3 | 1.8519 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Keeyask GS | MB_KSK_GSS | Keeyask SS | MB_KSS_SWS |  |  | 107
| KE3 | Manitoba Hydro | Manitoba | 1 | ac | 3 | 1.8519 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Keeyask GS | MB_KSK_GSS | Keeyask SS | MB_KSS_SWS |  |  | 108
| KE4 | Manitoba Hydro | Manitoba | 1 | ac | 3 | 1.8519 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Keeyask GS | MB_KSK_GSS | Keeyask SS | MB_KSS_SWS |  |  | 109
| HS15 | Manitoba Hydro | Manitoba | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Snow Lake | MB_SNL_DSS | HBMS Lalor | MB_LAL_ISS |  |  | 84
| D11Y | Manitoba Hydro | Manitoba | 1 | ac | 27.0054 | 16.67 | 230 | 12.9626 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Laverendrye | MB_LAV_DSS |  |  | 39
| D15Y | Manitoba Hydro | Manitoba | 1 | ac | 27.0054 | 16.67 | 230 | 12.9626 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Laverendrye | MB_LAV_DSS |  |  | 43
| D55Y | Manitoba Hydro | Manitoba | 1 | ac | 27.0054 | 16.67 | 230 | 12.9626 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Laverendrye | MB_LAV_DSS |  |  | 47
| RY7 | Manitoba Hydro | Manitoba | 1 | ac | 29.8566 | 18.43 | 115 | 12.4545 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | Laverendrye | MB_LAV_DSS |  |  | 186
| SG13 | Manitoba Hydro | Manitoba | 1 | ac | 4.2 | 2.5926 | 115 | 1.752 | 3 | [5 empty] | 98.4491 | 108.4016 | Rutherford JCT | MB_RTH_JCT | Lac Du Bonnet | MB_LDB_DSS |  |  | 194
| YM31 | Manitoba Hydro | Manitoba | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Laverendrye | MB_LAV_DSS | Lowe Farm | MB_LFM_DSS |  |  | 259
| WL43 | Manitoba Hydro | Manitoba | 1 | ac | 100 | 61.7284 | 138 | 43.3571 | 2.796 | [5 empty] | 131.4132 | 145.3933 | Notigi | MB_NTG_DSS | Leaf Rapids | MB_LFR_DSS |  |  | 249
| PC3 | Manitoba Hydro | Manitoba | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Pine Falls GS | MB_PNF_GSS | Libau | MB_LIB_DSS |  |  | 157
| WL43 | Manitoba Hydro | Manitoba | 1 | ac | 90 | 55.5556 | 138 | 39.0214 | 2.9972 | [5 empty] | 140.8692 | 155.8552 | Leaf Rapids | MB_LFR_DSS | Laurie River #1 TS | MB_LRV_TSS |  |  | 250
| L1 | Manitoba Hydro | Manitoba | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Long Spruce GS | MB_LSP_GSS | Long Spruce SS | MB_LSP_SWS |  |  | 123
| L2 | Manitoba Hydro | Manitoba | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Long Spruce GS | MB_LSP_GSS | Long Spruce SS | MB_LSP_SWS |  |  | 124
| L3 | Manitoba Hydro | Manitoba | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Long Spruce GS | MB_LSP_GSS | Long Spruce SS | MB_LSP_SWS |  |  | 126
| L4 | Manitoba Hydro | Manitoba | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Long Spruce GS | MB_LSP_GSS | Long Spruce SS | MB_LSP_SWS |  |  | 127
| L41R | Manitoba Hydro | Manitoba | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Radisson CS | MB_RDS_CSS | Long Spruce SS | MB_LSP_SWS |  |  | 128
| L42R | Manitoba Hydro | Manitoba | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Radisson CS | MB_RDS_CSS | Long Spruce SS | MB_LSP_SWS |  |  | 129
| L43R | Manitoba Hydro | Manitoba | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Radisson CS | MB_RDS_CSS | Long Spruce SS | MB_LSP_SWS |  |  | 130
| L46H | Manitoba Hydro | Manitoba | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Henday CS | MB_HDY_CSS | Long Spruce SS | MB_LSP_SWS |  |  | 131
| L47H | Manitoba Hydro | Manitoba | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Henday CS | MB_HDY_CSS | Long Spruce SS | MB_LSP_SWS |  |  | 132
| L48H | Manitoba Hydro | Manitoba | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Henday CS | MB_HDY_CSS | Long Spruce SS | MB_LSP_SWS |  |  | 133
| L5 | Manitoba Hydro | Manitoba | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Long Spruce GS | MB_LSP_GSS | Long Spruce SS | MB_LSP_SWS |  |  | 134
| L8K | Manitoba Hydro | Manitoba | 1 | ac | 60 | 37.037 | 230 | 28.8 | 3 | [5 empty] | 402 | 435 | Keewatinohk CS | MB_KWT_CSS | Long Spruce SS | MB_LSP_SWS |  |  | 135
| E93L | Manitoba Hydro | Manitoba | 1 | ac | 102.708 | 63.4 | 230 | 49.2998 | 2.7472 | [5 empty] | 368.1229 | 398.3419 | Stanley | MB_STY_DSS | Letellier | MB_LTL_DSS |  |  | 54
| J89L | Manitoba Hydro | Manitoba | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | St Joseph GS | MB_STJ_GSS | Letellier | MB_LTL_DSS |  |  | 89
| Y51L | Manitoba Hydro | Manitoba | 1 | ac | 80.028 | 49.4 | 230 | 38.4134 | 3 | [5 empty] | 402 | 435 | Laverendrye | MB_LAV_DSS | Letellier | MB_LTL_DSS |  |  | 257
| RJ51 | Manitoba Hydro | Manitoba | 1 | ac | 12.9114 | 7.97 | 115 | 5.3859 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | Madison | MB_MAD_DSS |  |  | 175
| PR2 | Manitoba Hydro | Manitoba | 1 | ac | 28.4796 | 17.58 | 115 | 11.8801 | 3 | [5 empty] | 98.4491 | 108.4016 | Pine Falls GS | MB_PNF_GSS | McArthur Falls GS | MB_MCF_GSS |  |  | 162
| SR3 | Manitoba Hydro | Manitoba | 1 | ac | 37.6164 | 23.22 | 115 | 15.6914 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | McArthur Falls GS | MB_MCF_GSS |  |  | 203
| BP6 | Manitoba Hydro | Manitoba | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Austin | MB_AUS_DSS | Macgregor | MB_MCG_DSS |  |  | 19
| BP7 | Manitoba Hydro | Manitoba | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Austin | MB_AUS_DSS | Macgregor | MB_MCG_DSS |  |  | 23
| RL1 | Manitoba Hydro | Manitoba | 1 | ac | 7.614 | 4.7 | 115 | 3.1761 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | McPhillips | MB_MCP_DSS |  |  | 177
| RL2 | Manitoba Hydro | Manitoba | 1 | ac | 1.61 | 0.99383 | 115 | 0.6716 | 3 | [5 empty] | 98.4491 | 108.4016 | Court | MB_CRT_DSS | McPhillips | MB_MCP_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 178
| RL3 | Manitoba Hydro | Manitoba | 1 | ac | 7.614 | 4.7 | 115 | 3.1761 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | McPhillips | MB_MCP_DSS |  |  | 180
| RL4 | Manitoba Hydro | Manitoba | 1 | ac | 7.614 | 4.7 | 115 | 3.1761 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosser | MB_RSR_DSS | McPhillips | MB_MCP_DSS |  |  | 181
| MM30 | Manitoba Hydro | Manitoba | 1 | ac | 0.8 | 0.5 | 115 | 0.33371 | 3 | [5 empty] | 98.4491 | 108.4016 | Manitoba Rolling Mills | MB_MRM_DSS | Mercy Street | MB_MCY_DSS |  |  | 145
| MC28 | Manitoba Hydro | Manitoba | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Parkdale | MB_PKD_DSS | Mercy Street | MB_MCY_DSS |  |  | 146
| SM26 | Manitoba Hydro | Manitoba | 1 | ac | 4.9734 | 3.07 | 115 | 2.0746 | 3 | [5 empty] | 98.4491 | 108.4016 | Selkirk GS | MB_SKK_GSS | Mercy Street | MB_MCY_DSS |  |  | 202
| YM31 | Manitoba Hydro | Manitoba | 1 | ac | 50.4 | 31.1111 | 115 | 21.024 | 3 | [5 empty] | 98.4491 | 108.4016 | Lowe Farm | MB_LFM_DSS | Morden Corner | MB_MDC_DSS |  |  | 260
| MR11 | Manitoba Hydro | Manitoba | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Rapid City | MB_RPD_DSS | Minnedosa South | MB_MDS_DSS |  |  | 147
| NM10 | Manitoba Hydro | Manitoba | 1 | ac | 30.6342 | 18.91 | 115 | 12.7788 | 3 | [5 empty] | 98.4491 | 108.4016 | Neepawa South | MB_NPS_DSS | Minnedosa South | MB_MDS_DSS |  |  | 149
| PQ95 | Manitoba Hydro | Manitoba | 1 | ac | 115.992 | 71.6 | 115 | 48.3852 | 2.5354 | [5 empty] | 83.2035 | 91.6147 | Pine Falls GS | MB_PNF_GSS | Manigotagan Corner | MB_MGT_DSS |  |  | 161
| F10M | Manitoba Hydro | Manitoba | 1 | ac | 146.6043 | 90.4965 | 230 | 70.3701 | 2.1725 | [5 empty] | 291.12 | 315.0179 | Overflowing River | MB_OVL_DSS | Minitonas | MB_MIN_DSS |  |  | 56
| SV24 | Manitoba Hydro | Manitoba | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Selkirk GS | MB_SKK_GSS | Melrose DSC | MB_MLR_DSS |  |  | 209
| YX47 | Manitoba Hydro | Manitoba | 1 | ac | 19.116 | 11.8 | 115 | 7.9741 | 3 | [5 empty] | 98.4491 | 108.4016 | Laverendrye | MB_LAV_DSS | Mohawk | MB_MOH_DSS |  |  | 265
| YX48 | Manitoba Hydro | Manitoba | 1 | ac | 19.19 | 11.8457 | 115 | 8.005 | 3 | [5 empty] | 98.4491 | 108.4016 | Laverendrye | MB_LAV_DSS | Mohawk | MB_MOH_DSS |  |  | 266
| B77W | Manitoba Hydro | Manitoba | 1 | ac | 4.05 | 2.5 | 230 | 1.944 | 3 | [5 empty] | 402 | 435 | Birchtree | MB_BCT_DSS | Mystery Lake | MB_MYS_DSS |  |  | 7
| K24W | Manitoba Hydro | Manitoba | 1 | ac | 105 | 64.8148 | 230 | 50.4 | 2.7075 | [5 empty] | 362.8035 | 392.5859 | Kelsey TS | MB_KLT_TSS | Mystery Lake | MB_MYS_DSS |  |  | 96
| P19W | Manitoba Hydro | Manitoba | 1 | ac | 153.1872 | 94.56 | 230 | 73.5299 | 2.1105 | [5 empty] | 282.8079 | 306.0235 | Ponton | MB_PTN_DSS | Mystery Lake | MB_MYS_DSS |  |  | 151
| TW40 | Manitoba Hydro | Manitoba | 1 | ac | 1.2636 | 0.78 | 138 | 0.54786 | 3 | [5 empty] | 141 | 156 | Inco | MB_INC_ISS | Mystery Lake | MB_MYS_DSS |  |  | 223
| WL43 | Manitoba Hydro | Manitoba | 1 | ac | 75 | 46.2963 | 138 | 32.5179 | 3 | [5 empty] | 141 | 156 | Mystery Lake | MB_MYS_DSS | Nelson House | MB_NLH_DSS |  |  | 247
| BN5 | Manitoba Hydro | Manitoba | 1 | ac | 57.8988 | 35.74 | 115 | 24.1521 | 3 | [5 empty] | 98.4491 | 108.4016 | Brandon GS | MB_BDN_GSS | Neepawa South | MB_NPS_DSS |  |  | 16
| CN9 | Manitoba Hydro | Manitoba | 1 | ac | 140 | 86.4198 | 115 | 58.4 | 2.2396 | [5 empty] | 73.4954 | 80.9253 | Warren | MB_WRN_DSS | Neepawa South | MB_NPS_DSS |  |  | 33
| D54N | Manitoba Hydro | Manitoba | 1 | ac | 169.8894 | 104.87 | 230 | 81.5469 | 1.9713 | [5 empty] | 264.1503 | 285.8343 | Dorsey | MB_DSY_DSS | Neepawa | MB_NPW_DSS |  |  | 46
| WL43 | Manitoba Hydro | Manitoba | 1 | ac | 35 | 21.6049 | 138 | 15.175 | 3 | [5 empty] | 141 | 156 | Nelson House | MB_NLH_DSS | Notigi | MB_NTG_DSS |  |  | 248
| TS44 | Manitoba Hydro | Manitoba | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Transcona | MB_TCA_DSS | Oakbank | MB_OKB_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 217
| G9F | Manitoba Hydro | Manitoba | 1 | ac | 144.342 | 89.1 | 230 | 69.2842 | 2.1949 | [5 empty] | 294.1212 | 318.2655 | Grand Rapids GS | MB_GRP_GSS | Overflowing River | MB_OVL_DSS |  |  | 67
| KH38 | Manitoba Hydro | Manitoba | 1 | ac | 164.9484 | 101.82 | 138 | 71.5169 | 2.01 | [5 empty] | 94.4708 | 104.5209 | Kelsey GS | MB_KLS_GSS | Oxford House | MB_OXF_DSS |  |  | 110
| D12P | Manitoba Hydro | Manitoba | 1 | ac | 66.663 | 41.15 | 230 | 31.9982 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Portage South | MB_PGS_DSS |  |  | 40
| D83P | Manitoba Hydro | Manitoba | 1 | ac | 66 | 40.7407 | 230 | 31.68 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Portage South | MB_PGS_DSS |  |  | 52
| UP80 | Manitoba Hydro | Manitoba | 1 | ac | 92.7612 | 57.26 | 115 | 38.6947 | 2.9381 | [5 empty] | 96.417 | 106.1641 | Rockwood | MB_RKW_DSS | Portage South | MB_PGS_DSS |  | Assumed termination at Portage South | 225
| PC3 | Manitoba Hydro | Manitoba | 1 | ac | 34.5802 | 21.3458 | 115 | 14.4249 | 3 | [5 empty] | 98.4491 | 108.4016 | Libau | MB_LIB_DSS | Parkdale | MB_PKD_DSS |  |  | 158
| PC4 | Manitoba Hydro | Manitoba | 1 | ac | 54.58 | 33.6914 | 115 | 22.7677 | 3 | [5 empty] | 98.4491 | 108.4016 | Gull Lake | MB_GLL_DSS | Parkdale | MB_PKD_DSS |  |  | 160
| SC25 | Manitoba Hydro | Manitoba | 1 | ac | 21.3354 | 13.17 | 115 | 8.8999 | 3 | [5 empty] | 98.4491 | 108.4016 | Selkirk GS | MB_SKK_GSS | Parkdale | MB_PKD_DSS |  |  | 193
| TP65 | Manitoba Hydro | Manitoba | 1 | ac | 13.284 | 8.2 | 115 | 5.5413 | 3 | [5 empty] | 98.4491 | 108.4016 | Transcona | MB_TCA_DSS | Plessis | MB_PLS_DSS |  |  | 215
| VP35 | Manitoba Hydro | Manitoba | 1 | ac | 3.9204 | 2.42 | 115 | 1.6354 | 3 | [5 empty] | 98.4491 | 108.4016 | St Vital | MB_STV_DSS | Plessis | MB_PLS_DSS |  |  | 239
| GP1 | Manitoba Hydro | Manitoba | 1 | ac | 19.1484 | 11.82 | 115 | 7.9876 | 3 | [5 empty] | 98.4491 | 108.4016 | Great Falls GS | MB_GRF_GSS | Pine Falls GS | MB_PNF_GSS |  |  | 69
| G8P | Manitoba Hydro | Manitoba | 1 | ac | 100 | 61.7284 | 230 | 48 | 2.796 | [5 empty] | 374.6673 | 405.4236 | William River | MB_WLR_DSS | Ponton | MB_PTN_DSS |  |  | 66
| J30P | Manitoba Hydro | Manitoba | 1 | ac | 79.2828 | 48.94 | 230 | 38.0557 | 3 | [5 empty] | 402 | 435 | Jenpeg GS | MB_JPG_GSS | Ponton | MB_PTN_DSS |  |  | 88
| V57R | Manitoba Hydro | Manitoba | 1 | ac | 89.262 | 55.1 | 230 | 42.8458 | 3 | [5 empty] | 402 | 435 | Vermillion | MB_VML_DSS | Roblin South | MB_RBL_DSS |  |  | 227
| M88R | Manitoba Hydro | Manitoba | 1 | ac | 83.5758 | 51.59 | 230 | 40.1164 | 3 | [5 empty] | 402 | 435 | Riel | MB_RIL_DSS | Richer South | MB_RCH_DSS |  | Prior line R49R was divided into M49R and M88R | 143
| M88R | Manitoba Hydro | Manitoba | 1 | ac | 50 | 30.8642 | 230 | 24 | 3 | [5 empty] | 402 | 435 | Vivian | MB_VIV_DSS | Richer South | MB_RCH_DSS |  | Prior line R49R was divided into M49R and M88R | 144
| VJ50 | Manitoba Hydro | Manitoba | 1 | ac | 52 | 32.0988 | 115 | 21.6914 | 3 | [5 empty] | 98.4491 | 108.4016 | St Vital | MB_STV_DSS | Randolph | MB_RDP_DSS |  |  | 237
| VT63 | Manitoba Hydro | Manitoba | 1 | ac | 52 | 32.0988 | 115 | 21.6914 | 3 | [5 empty] | 98.4491 | 108.4016 | St Vital | MB_STV_DSS | Randolph | MB_RDP_DSS |  |  | 240
| K1 | Manitoba Hydro | Manitoba | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Kettle GS | MB_KTL_GSS | Radisson CS | MB_RDS_CSS |  |  | 91
| K2 | Manitoba Hydro | Manitoba | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Kettle GS | MB_KTL_GSS | Radisson CS | MB_RDS_CSS |  |  | 92
| K3 | Manitoba Hydro | Manitoba | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Kettle GS | MB_KTL_GSS | Radisson CS | MB_RDS_CSS |  |  | 97
| K4 | Manitoba Hydro | Manitoba | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Kettle GS | MB_KTL_GSS | Radisson CS | MB_RDS_CSS |  |  | 98
| K5 | Manitoba Hydro | Manitoba | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Kettle GS | MB_KTL_GSS | Radisson CS | MB_RDS_CSS |  |  | 99
| K6 | Manitoba Hydro | Manitoba | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Kettle GS | MB_KTL_GSS | Radisson CS | MB_RDS_CSS |  |  | 100
| K7 | Manitoba Hydro | Manitoba | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Kettle GS | MB_KTL_GSS | Radisson CS | MB_RDS_CSS |  |  | 105
| KN36 | Manitoba Hydro | Manitoba | 1 | ac | 5 | 3.0864 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Gillam | MB_GLM_DSS | Radisson CS | MB_RDS_CSS |  |  | 114
| KR1 | Manitoba Hydro | Manitoba | 1 | ac | 68 | 41.9753 | 138 | 29.4829 | 3 | [5 empty] | 141 | 156 | Keeyask SS | MB_KSS_SWS | Radisson CS | MB_RDS_CSS |  |  | 115
| KR2 | Manitoba Hydro | Manitoba | 1 | ac | 68 | 41.9753 | 138 | 29.4829 | 3 | [5 empty] | 141 | 156 | Keeyask SS | MB_KSS_SWS | Radisson CS | MB_RDS_CSS |  |  | 116
| KR3 | Manitoba Hydro | Manitoba | 1 | ac | 68 | 41.9753 | 138 | 29.4829 | 3 | [5 empty] | 141 | 156 | Keeyask SS | MB_KSS_SWS | Radisson CS | MB_RDS_CSS |  |  | 117
| D36R | Manitoba Hydro | Manitoba | 1 | ac | 32.8698 | 20.29 | 230 | 15.7775 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Ridgeway | MB_RGW_DSS |  |  | 45
| M32R | Manitoba Hydro | Manitoba | 1 | ac | 12.474 | 7.7 | 230 | 5.9875 | 3 | [5 empty] | 402 | 435 | Riel | MB_RIL_DSS | Ridgeway | MB_RGW_DSS |  |  | 136
| M33R | Manitoba Hydro | Manitoba | 1 | ac | 12.474 | 7.7 | 230 | 5.9875 | 3 | [5 empty] | 402 | 435 | Riel | MB_RIL_DSS | Ridgeway | MB_RGW_DSS |  |  | 137
| M49R | Manitoba Hydro | Manitoba | 1 | ac | 63.7146 | 39.33 | 230 | 30.583 | 3 | [5 empty] | 402 | 435 | Richer South | MB_RCH_DSS | Ridgeway | MB_RGW_DSS |  | Prior line R49R was divided into M49R and M88R | 139
| R23R | Manitoba Hydro | Manitoba | 1 | ac | 16.443 | 10.15 | 230 | 7.8926 | 3 | [5 empty] | 402 | 435 | Rosser | MB_RSR_DSS | Ridgeway | MB_RGW_DSS |  |  | 164
| VG51-52 | Manitoba Hydro | Manitoba | 1 | dc | 1376 | 849.3827 | 500 | [7 empty] | 1000 | 1000 | Keewatinohk CS | MB_KWT_CSS | Riel CS | MB_RIL_CSS |  |  | 233
| VG61-62 | Manitoba Hydro | Manitoba | 1 | dc | 1376 | 849.3827 | 500 | [7 empty] | 1000 | 1000 | Keewatinohk CS | MB_KWT_CSS | Riel CS | MB_RIL_CSS |  |  | 234
| D603M | Manitoba Hydro | Manitoba | 1 | ac | 50.0418 | 30.89 | 500 | 19.7665 | 3 | [5 empty] | 2550 | 3225 | Dorsey | MB_DSY_DSS | Riel | MB_RIL_DSS |  |  | 49
| CU81 | Manitoba Hydro | Manitoba | 1 | ac | 10.9512 | 6.76 | 115 | 4.5682 | 3 | [5 empty] | 98.4491 | 108.4016 | Parkdale | MB_PKD_DSS | Rockwood | MB_RKW_DSS |  |  | 38
| R92U | Manitoba Hydro | Manitoba | 1 | ac | 12.5226 | 7.73 | 230 | 6.0108 | 3 | [5 empty] | 402 | 435 | Rosser | MB_RSR_DSS | Rockwood | MB_RKW_DSS |  |  | 170
| U91A | Manitoba Hydro | Manitoba | 1 | ac | 233.7822 | 144.31 | 230 | 112.2155 | 1.597 | [5 empty] | 214.0004 | 231.5676 | Ashern | MB_ASH_DSS | Rockwood | MB_RKW_DSS |  |  | 224
| F27P | Manitoba Hydro | Manitoba | 1 | ac | 54.4158 | 33.59 | 230 | 26.1196 | 3 | [5 empty] | 402 | 435 | Overflowing River | MB_OVL_DSS | Ralls Island | MB_RLI_DSS |  |  | 57
| H75P | Manitoba Hydro | Manitoba | 1 | ac | 166.536 | 102.8 | 230 | 79.9373 | 1.9974 | [5 empty] | 267.6463 | 289.6172 | Herblet Lake | MB_HBL_DSS | Ralls Island | MB_RLI_DSS |  |  | 81
| MR11 | Manitoba Hydro | Manitoba | 1 | ac | 44 | 27.1605 | 115 | 18.3543 | 3 | [5 empty] | 98.4491 | 108.4016 | Brandon GS | MB_BDN_GSS | Rapid City | MB_RPD_DSS |  |  | 147
| YF11 | Manitoba Hydro | Manitoba | 1 | ac | 78.165 | 48.25 | 115 | 32.606 | 3 | [5 empty] | 98.4491 | 108.4016 | Laverendrye | MB_LAV_DSS | Rosenfeld | MB_RSF_DSS |  |  | 258
| A3R | Manitoba Hydro | Manitoba | 1 | ac | 170 | 104.9383 | 230 | 81.6 | 1.9704 | [5 empty] | 264.037 | 285.7116 | Ashern | MB_ASH_DSS | Rosser | MB_RSR_DSS |  |  | 1
| CR2 | Manitoba Hydro | Manitoba | 1 | ac | 15.39 | 9.5 | 115 | 6.4198 | 3 | [5 empty] | 98.4491 | 108.4016 | Parkdale | MB_PKD_DSS | Rosser | MB_RSR_DSS |  |  | 36
| CR4 | Manitoba Hydro | Manitoba | 1 | ac | 15.39 | 9.5 | 115 | 6.4198 | 3 | [5 empty] | 98.4491 | 108.4016 | Parkdale | MB_PKD_DSS | Rosser | MB_RSR_DSS |  |  | 37
| D13R | Manitoba Hydro | Manitoba | 1 | ac | 19.5858 | 12.09 | 230 | 9.4012 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Rosser | MB_RSR_DSS |  |  | 41
| D16R | Manitoba Hydro | Manitoba | 1 | ac | 19.5858 | 12.09 | 230 | 9.4012 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Rosser | MB_RSR_DSS |  |  | 44
| D5R | Manitoba Hydro | Manitoba | 1 | ac | 19.5858 | 12.09 | 230 | 9.4012 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | Rosser | MB_RSR_DSS |  |  | 48
| S65R | Manitoba Hydro | Manitoba | 1 | ac | 109.8522 | 67.81 | 230 | 52.7291 | 2.628 | [5 empty] | 352.1538 | 381.062 | Silver | MB_SLV_DSS | Rosser | MB_RSR_DSS |  |  | 190
| TR5 | Manitoba Hydro | Manitoba | 1 | ac | 30.213 | 18.65 | 115 | 12.6031 | 3 | [5 empty] | 98.4491 | 108.4016 | Griffin Steel | MB_GFS_ISS | Rosser | MB_RSR_DSS |  |  | 216
| C28R | Manitoba Hydro | Manitoba | 1 | ac | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Souris Enbridge East | MB_SEE_DSS | Reston | MB_RST_DSS |  |  | 26
| SG12 | Manitoba Hydro | Manitoba | 1 | ac | 13.43 | 8.2901 | 115 | 5.6022 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | Rutherford JCT | MB_RTH_JCT |  | Rutherford Junction is an assumed name | 194
| B69R | Manitoba Hydro | Manitoba | 1 | ac | 32.2866 | 19.93 | 230 | 15.4976 | 3 | [5 empty] | 402 | 435 | Birtle South | MB_BTS_DSS | Raven Lake | MB_RVL_DSS |  |  | 4
| MR11 | Manitoba Hydro | Manitoba | 1 | ac | 106.029 | 65.45 | 115 | 44.2292 | 2.6901 | [5 empty] | 88.2804 | 97.2049 | Minnedosa South | MB_MDS_DSS | Raven Lake | MB_RVL_DSS |  |  | 147
| V38R | Manitoba Hydro | Manitoba | 1 | ac | 100.278 | 61.9 | 230 | 48.1334 | 2.7909 | [5 empty] | 373.982 | 404.682 | Vermillion | MB_VML_DSS | Raven Lake | MB_RVL_DSS |  |  | 226
| JB14 | Manitoba Hydro | Manitoba | 1 | ac | 3.402 | 2.1 | 115 | 1.4191 | 3 | [5 empty] | 98.4491 | 108.4016 | Madison | MB_MAD_DSS | Sherbrook | MB_SBK_DSS |  |  | 90
| SB14 | Manitoba Hydro | Manitoba | 1 | ac | 3.402 | 2.1 | 115 | 1.4191 | 3 | [5 empty] | 98.4491 | 108.4016 | St James | MB_SJM_DSS | Sherbrook | MB_SBK_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 192
| VS27 | Manitoba Hydro | Manitoba | 1 | ac | 14.6448 | 9.04 | 115 | 6.109 | 3 | [5 empty] | 98.4491 | 108.4016 | St Vital | MB_STV_DSS | Scotland | MB_SCT_DSS |  |  | 242
| SG12N | Manitoba Hydro | Manitoba | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Rutherford JCT | MB_RTH_JCT | Seddons Corner DSC | MB_SDC_DSS |  |  | 196
| C28R | Manitoba Hydro | Manitoba | 1 | ac | 50.31 | 31.0556 | 230 | 24.1488 | 3 | [5 empty] | 402 | 435 | Cornwallis | MB_CNW_DSS | Souris Enbridge East | MB_SEE_DSS |  |  | 25
| HS15 | Manitoba Hydro | Manitoba | 1 | ac | 75 | 46.2963 | 115 | 31.2857 | 3 | [5 empty] | 98.4491 | 108.4016 | HBMS Lalor | MB_LAL_ISS | Sherridon | MB_SHD_DSS |  |  | 85
| RS51 | Manitoba Hydro | Manitoba | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Inkster | MB_INK_DSS | St James | MB_SJM_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 184
| YX48 | Manitoba Hydro | Manitoba | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Mohawk | MB_MOH_DSS | St James | MB_SJM_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 267
| BP6 | Manitoba Hydro | Manitoba | 1 | ac | 33 | 20.3704 | 115 | 13.7657 | 3 | [5 empty] | 98.4491 | 108.4016 | Macgregor | MB_MCG_DSS | Sask Ave | MB_SKA_DSS |  |  | 20
| BP7 | Manitoba Hydro | Manitoba | 1 | ac | 33 | 20.3704 | 115 | 13.7657 | 3 | [5 empty] | 98.4491 | 108.4016 | Macgregor | MB_MCG_DSS | Sask Ave | MB_SKA_DSS |  |  | 24
| CP17 | Manitoba Hydro | Manitoba | 1 | ac | 85 | 52.4691 | 115 | 35.4571 | 3 | [5 empty] | 98.4491 | 108.4016 | Stony Mountain West | MB_STM_DSS | Sask Ave | MB_SKA_DSS |  |  | 35
| RP16 | Manitoba Hydro | Manitoba | 1 | ac | 115.1982 | 71.11 | 115 | 48.0541 | 2.5469 | [5 empty] | 83.5811 | 92.0306 | Rosser | MB_RSR_DSS | Sask Ave | MB_SKA_DSS |  |  | 182
| GS21 | Manitoba Hydro | Manitoba | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Brokenhead | MB_BKH_DSS | Selkirk GS | MB_SKK_GSS |  |  | 71
| GS22 | Manitoba Hydro | Manitoba | 1 | ac | 74.9412 | 46.26 | 115 | 31.2612 | 3 | [5 empty] | 98.4491 | 108.4016 | Great Falls GS | MB_GRF_GSS | Selkirk GS | MB_SKK_GSS |  |  | 72
| TS44 | Manitoba Hydro | Manitoba | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | East Selkirk | MB_ESK_DSS | Selkirk GS | MB_SKK_GSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 220
| SK1 | Manitoba Hydro | Manitoba | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Brereton Lake | MB_BRT_DSS | Star Lake | MB_SLK_DSS |  |  | 200
| HS15 | Manitoba Hydro | Manitoba | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Herblet Lake | MB_HBL_DSS | Snow Lake | MB_SNL_DSS |  |  | 83
| KS37 | Manitoba Hydro | Manitoba | 1 | ac | 48.4542 | 29.91 | 138 | 21.0084 | 3 | [5 empty] | 141 | 156 | Kelsey GS | MB_KLS_GSS | Split Lake | MB_SPL_DSS |  |  | 118
| S1 | Manitoba Hydro | Manitoba | 1 | ac | 139.8384 | 86.32 | 115 | 58.3326 | 2.2413 | [5 empty] | 73.5514 | 80.9869 | Slave Falls GS | MB_SLF_GSS | Stafford | MB_STF_DSS |  |  | 187
| S2 | Manitoba Hydro | Manitoba | 1 | ac | 139.8384 | 86.32 | 115 | 58.3326 | 2.2413 | [5 empty] | 73.5514 | 80.9869 | Slave Falls GS | MB_SLF_GSS | Stafford | MB_STF_DSS |  |  | 188
| YS33 | Manitoba Hydro | Manitoba | 1 | ac | 20.5416 | 12.68 | 115 | 8.5688 | 3 | [5 empty] | 98.4491 | 108.4016 | Laverendrye | MB_LAV_DSS | Stafford | MB_STF_DSS |  |  | 261
| D14S | Manitoba Hydro | Manitoba | 1 | ac | 130.2642 | 80.41 | 230 | 62.5268 | 2.3486 | [5 empty] | 314.7159 | 340.5508 | Dorsey | MB_DSY_DSS | St Leon GS | MB_STL_GSS |  |  | 42
| CP17 | Manitoba Hydro | Manitoba | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Parkdale | MB_PKD_DSS | Stony Mountain West | MB_STM_DSS |  |  | 34
| D72V | Manitoba Hydro | Manitoba | 1 | ac | 53.9946 | 33.33 | 230 | 25.9174 | 3 | [5 empty] | 402 | 435 | Dorsey | MB_DSY_DSS | St Vital | MB_STV_DSS |  |  | 51
| M86V | Manitoba Hydro | Manitoba | 1 | ac | 7.614 | 4.7 | 230 | 3.6547 | 3 | [5 empty] | 402 | 435 | Riel | MB_RIL_DSS | St Vital | MB_STV_DSS |  |  | 141
| M87V | Manitoba Hydro | Manitoba | 1 | ac | 7.614 | 4.7 | 230 | 3.6547 | 3 | [5 empty] | 402 | 435 | Riel | MB_RIL_DSS | St Vital | MB_STV_DSS |  |  | 142
| SV24 | Manitoba Hydro | Manitoba | 1 | ac | 37.26 | 23 | 115 | 15.5427 | 3 | [5 empty] | 98.4491 | 108.4016 | Melrose DSC | MB_MLR_DSS | St Vital | MB_STV_DSS |  |  | 208
| TV1 | Manitoba Hydro | Manitoba | 1 | ac | 16.0542 | 9.91 | 115 | 6.6969 | 3 | [5 empty] | 98.4491 | 108.4016 | Transcona | MB_TCA_DSS | St Vital | MB_STV_DSS |  |  | 221
| TV2 | Manitoba Hydro | Manitoba | 1 | ac | 16.0542 | 9.91 | 115 | 6.6969 | 3 | [5 empty] | 98.4491 | 108.4016 | Transcona | MB_TCA_DSS | St Vital | MB_STV_DSS |  |  | 222
| V95L | Manitoba Hydro | Manitoba | 1 | ac | 119 | 73.4568 | 230 | 57.12 | 2.493 | [5 empty] | 334.0585 | 361.4813 | Letellier | MB_LTL_DSS | St Vital | MB_STV_DSS |  |  | 228
| XV39 | Manitoba Hydro | Manitoba | 1 | ac | 5.25 | 3.2407 | 115 | 2.19 | 3 | [5 empty] | 98.4491 | 108.4016 | Dakota | MB_DAK_DSS | St Vital | MB_STV_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 255
| Y36V | Manitoba Hydro | Manitoba | 1 | ac | 37 | 22.8395 | 230 | 17.76 | 3 | [5 empty] | 402 | 435 | Laverendrye | MB_LAV_DSS | St Vital | MB_STV_DSS |  |  | 256
| YV5 | Manitoba Hydro | Manitoba | 1 | ac | 23.57 | 14.5494 | 115 | 9.8321 | 3 | [5 empty] | 98.4491 | 108.4016 | Wilkes | MB_WLK_DSS | St Vital | MB_STV_DSS |  |  | 264
| CN9 | Manitoba Hydro | Manitoba | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Parkdale | MB_PKD_DSS | Stonewall | MB_STW_DSS |  |  | 31
| S94E | Manitoba Hydro | Manitoba | 1 | ac | 91.9026 | 56.73 | 230 | 44.1132 | 2.9561 | [5 empty] | 396.124 | 428.6416 | St Leon GS | MB_STL_GSS | Stanley | MB_STY_DSS |  |  | 191
| GT1 | Manitoba Hydro | Manitoba | 1 | ac | 55 | 33.9506 | 115 | 22.9429 | 3 | [5 empty] | 98.4491 | 108.4016 | Beausejour East | MB_BSJ_DSS | Transcona | MB_TCA_DSS |  |  | 73
| ST2 | Manitoba Hydro | Manitoba | 1 | ac | 55 | 33.9506 | 115 | 22.9429 | 3 | [5 empty] | 98.4491 | 108.4016 | Beausejour East | MB_BSJ_DSS | Transcona | MB_TCA_DSS |  |  | 204
| ST5 | Manitoba Hydro | Manitoba | 1 | ac | 78.246 | 48.3 | 115 | 32.6398 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | Transcona | MB_TCA_DSS |  |  | 205
| ST6 | Manitoba Hydro | Manitoba | 1 | ac | 24.3 | 15 | 115 | 10.1366 | 3 | [5 empty] | 98.4491 | 108.4016 | Anola DSC | MB_ANO_DSS | Transcona | MB_TCA_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 207
| WT34 | Manitoba Hydro | Manitoba | 1 | ac | 76.25 | 47.0679 | 115 | 31.8071 | 3 | [5 empty] | 98.4491 | 108.4016 | Whiteshell | MB_WSL_DSS | Transcona | MB_TCA_DSS |  |  | 251
| WT34A | Manitoba Hydro | Manitoba | 1 | ac | 76.2534 | 47.07 | 115 | 31.8086 | 3 | [5 empty] | 98.4491 | 108.4016 | Whiteshell | MB_WSL_DSS | Transcona | MB_TCA_DSS |  |  | 252
| YT10 | Manitoba Hydro | Manitoba | 1 | ac | 110 | 67.9012 | 115 | 45.8857 | 2.6257 | [5 empty] | 86.1655 | 94.8762 | Laverendrye | MB_LAV_DSS | Treherne | MB_TRH_DSS |  | Actual voltage is 110 kV | 262
| TS44 | Manitoba Hydro | Manitoba | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Oakbank | MB_OKB_DSS | Tyndall DSC | MB_TYN_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 218
| BE1 | Manitoba Hydro | Manitoba | 1 | ac | 1.8144 | 1.12 | 115 | 0.75686 | 3 | [5 empty] | 98.4491 | 108.4016 | Brandon GS | MB_BDN_GSS | Victoria Ave | MB_VCT_DSS |  |  | 9
| BE2 | Manitoba Hydro | Manitoba | 1 | ac | 1.8144 | 1.12 | 115 | 0.75686 | 3 | [5 empty] | 98.4491 | 108.4016 | Brandon GS | MB_BDN_GSS | Victoria Ave | MB_VCT_DSS |  |  | 10
| BE3 | Manitoba Hydro | Manitoba | 1 | ac | 1.8144 | 1.12 | 115 | 0.75686 | 3 | [5 empty] | 98.4491 | 108.4016 | Brandon GS | MB_BDN_GSS | Victoria Ave | MB_VCT_DSS |  |  | 12
| B70H | Manitoba Hydro | Manitoba | 1 | ac | 57.2994 | 35.37 | 230 | 27.5037 | 3 | [5 empty] | 402 | 435 | Birtle South | MB_BTS_DSS | Virden West | MB_VDW_DSS |  |  | 5
| R29H | Manitoba Hydro | Manitoba | 1 | ac | 48.0006 | 29.63 | 230 | 23.0403 | 3 | [5 empty] | 402 | 435 | Reston | MB_RST_DSS | Virden West | MB_VDW_DSS |  |  | 167
| ST6 | Manitoba Hydro | Manitoba | 1 | ac | 40.5 | 25 | 115 | 16.8943 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | Vivian | MB_VIV_DSS | Manitoba Hydro. 2020. Transmission Long-term Plan |  | 206
| A6V | Manitoba Hydro | Manitoba | 1 | ac | 130.572 | 80.6 | 230 | 62.6746 | 2.345 | [5 empty] | 314.2264 | 340.0211 | Ashern | MB_ASH_DSS | Vermillion | MB_VML_DSS |  |  | 3
| G31V | Manitoba Hydro | Manitoba | 1 | ac | 254.6964 | 157.22 | 230 | 122.2543 | 1.5093 | [5 empty] | 202.2431 | 218.8452 | Grand Rapids GS | MB_GRP_GSS | Vermillion | MB_VML_DSS |  |  | 62
| M39V | Manitoba Hydro | Manitoba | 1 | ac | 132.9948 | 82.0956 | 230 | 63.8375 | 2.3167 | [5 empty] | 310.4394 | 335.9232 | Minitonas | MB_MIN_DSS | Vermillion | MB_VML_DSS |  |  | 138
| YV5 | Manitoba Hydro | Manitoba | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Laverendrye | MB_LAV_DSS | Wilkes | MB_WLK_DSS |  |  | 263
| G8P | Manitoba Hydro | Manitoba | 1 | ac | 75 | 46.2963 | 230 | 36 | 3 | [5 empty] | 402 | 435 | Grand Rapids GS | MB_GRP_GSS | William River | MB_WLR_DSS |  |  | 65
| CN9 | Manitoba Hydro | Manitoba | 1 | ac | 18 | 11.1111 | 115 | 7.5086 | 3 | [5 empty] | 98.4491 | 108.4016 | Stonewall | MB_STW_DSS | Warren | MB_WRN_DSS |  |  | 32
| PW75 | Manitoba Hydro | Manitoba | 1 | ac | 46.5 | 28.7037 | 115 | 19.3971 | 3 | [5 empty] | 98.4491 | 108.4016 | Pointe Du Bois GS | MB_PDB_GSS | Whiteshell | MB_WSL_DSS |  |  | 163
| SW1 | Manitoba Hydro | Manitoba | 1 | ac | 2.3814 | 1.47 | 115 | 0.99338 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | Whiteshell | MB_WSL_DSS |  |  | 210
| SW2 | Manitoba Hydro | Manitoba | 1 | ac | 2.7702 | 1.71 | 115 | 1.1556 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | Whiteshell | MB_WSL_DSS |  |  | 211
| SW3 | Manitoba Hydro | Manitoba | 1 | ac | 2.7702 | 1.71 | 115 | 1.1556 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | Whiteshell | MB_WSL_DSS |  |  | 212
| SW4 | Manitoba Hydro | Manitoba | 1 | ac | 3.5964 | 2.22 | 115 | 1.5002 | 3 | [5 empty] | 98.4491 | 108.4016 | Seven Sisters GS | MB_SVS_GSS | Whiteshell | MB_WSL_DSS |  |  | 213
| GW62 | Manitoba Hydro | Manitoba | 1 | ac | 34.1334 | 21.07 | 138 | 14.7993 | 3 | [5 empty] | 141 | 156 | Garden Hill | MB_GDH_DSS | Wasagamack | MB_WSM_DSS |  |  | 74
| I1F | Manitoba Hydro | Manitoba | 1 | ac | 0.01 | 0.0061728 | 115 | 0.0041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Flin Flon Border | MB_BDR_DSS | IPT Island Falls | PP_MBSK1_IPT |  |  | 86
| I2F | Manitoba Hydro | Manitoba | 1 | ac | 0.01 | 0.0061728 | 115 | 0.0041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Flin Flon Border | MB_BDR_DSS | IPT Island Falls | PP_MBSK1_IPT |  |  | 87
| P52E | Manitoba Hydro | Manitoba | 1 | ac | 52.94 | 32.68 | 230 | 25.4112 | 3 | [5 empty] | 402 | 435 | Ralls Island | MB_RLI_DSS | IPT EB Campbell | PP_MBSK2_IPT |  |  | 152
| R7B | Manitoba Hydro | Manitoba | 1 | ac | 24.3 | 15 | 230 | 11.664 | 3 | [5 empty] | 402 | 435 | Reston | MB_RST_DSS | IPT Boundary Dam | PP_MBSK3_IPT |  |  | 169
| B71T | Manitoba Hydro | Manitoba | 1 | ac | 46.2 | 28.5185 | 230 | 22.176 | 3 | [5 empty] | 402 | 435 | Birtle South | MB_BTS_DSS | IPT Tantallon | PP_MBSK4_IPT |  |  | 6
| R25Y | Manitoba Hydro | Manitoba | 1 | ac | 15.39 | 9.5 | 230 | 7.3872 | 3 | [5 empty] | 402 | 435 | Roblin South | MB_RBL_DSS | IPT Yorkton | PP_MBSK5_IPT |  |  | 165
| SK1 | Manitoba Hydro | Manitoba | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Star Lake | MB_SLK_DSS | IPT Seven Sisters | PP_ONMB1_IPT |  |  | 201
| K21W | Manitoba Hydro | Manitoba | 1 | ac | 68.85 | 42.5 | 230 | 33.048 | 3 | [5 empty] | 402 | 435 | Whiteshell | MB_WSL_DSS | IPT Whiteshell | PP_ONMB2_IPT |  |  | 93
| K22W | Manitoba Hydro | Manitoba | 1 | ac | 68.85 | 42.5 | 230 | 33.048 | 3 | [5 empty] | 402 | 435 | Whiteshell | MB_WSL_DSS | IPT Whiteshell | PP_ONMB2_IPT |  |  | 94
| L20D | Manitoba Hydro | Manitoba | 1 | ac | 15.6006 | 9.63 | 230 | 7.4883 | 3 | [5 empty] | 100 | 100 | Letellier | MB_LTL_DSS | INT Drayton | XX_MBUS1_INT |  |  | 125
| M602F | Manitoba Hydro | Manitoba | 1 | ac | 194.5134 | 120.07 | 500 | 76.8328 | 1.8029 | [5 empty] | 500 | 500 | Riel | MB_RIL_DSS | INT Forbes | XX_MBUS2_INT |  |  | 140
| D604 | Manitoba Hydro | Manitoba | 1 | ac | 213 | 131.4815 | 500 | 84.135 | 1.6981 | [5 empty] | 883 | 883 | Dorsey | MB_DSY_DSS | INT Iron Range | XX_MBUS3_INT |  |  | 50
| R50M | Manitoba Hydro | Manitoba | 1 | ac | 100.0836 | 61.78 | 230 | 48.0401 | 2.7945 | [5 empty] | 175 | 175 | Richer South | MB_RCH_DSS | INT Moranville | XX_MBUS4_INT |  |  | 168
| G82P | Manitoba Hydro | Manitoba | 1 | ac | 80.8542 | 49.91 | 230 | 38.81 | 3 | [5 empty] | 700 | 700 | Glenboro South | MB_GBS_DSS | INT Peace Gardens | XX_MBUS5_INT |  |  | 64
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## Nodes
MB | EXISTING SUBSTATIONS
| Node Name | Node Code | Owner | Latitude | Longitude | Operating Region | Other References | Notes
| Anola DSC | MB_ANO_DSS | Manitoba Hydro | 49.9066 | -96.7042 | Manitoba
| Ashern | MB_ASH_DSS | Manitoba Hydro | 51.2039 | -98.4415 | Manitoba
| Augier | MB_AUG_DSS | Manitoba Hydro | 49.8764 | -97.3466 | Manitoba
| Austin | MB_AUS_DSS | Manitoba Hydro | 49.9459 | -98.9275 | Manitoba
| Beausejour East | MB_BSJ_DSS | Manitoba Hydro | 50.0734 | -96.4782 | Manitoba
| Birchtree | MB_BCT_DSS | Manitoba Hydro | 55.7018 | -97.9271 | Manitoba
| Birtle South | MB_BTS_DSS | Manitoba Hydro | 50.3721 | -101.0405 | Manitoba
| Brandon 65th St East | MB_B65_DSS | Manitoba Hydro | 49.8292 | -99.8496 | Manitoba
| Brandon GS | MB_BDN_GSS | Manitoba Hydro | 49.8456 | -99.8901 | Manitoba
| Brereton Lake | MB_BRT_DSS | Manitoba Hydro | 49.9446 | -95.5149 | Manitoba
| Brokenhead | MB_BKH_DSS | Manitoba Hydro | 50.2444 | -96.4901 | Manitoba
| Burntwood | MB_BWD_DSS | Manitoba Hydro | 55.7528 | -97.8194 | Manitoba
| Carberry North | MB_CBY_DSS | Manitoba Hydro | 49.9466 | -99.3409 | Manitoba
| Churchill South | MB_CHS_DSS | Manitoba Hydro | 58.7356 | -94.1109 | Manitoba
| Cliff Lake | MB_CFL_DSS | Manitoba Hydro | 54.7901 | -101.8444 | Manitoba
| Cornwallis | MB_CNW_DSS | Manitoba Hydro | 49.8451 | -99.896 | Manitoba
| Court | MB_CRT_DSS | Manitoba Hydro | 49.9577 | -97.1519 | Manitoba
| Cranberry Portage | MB_CBP_DSS | Manitoba Hydro | 54.6128 | -101.3472 | Manitoba
| Crocus Plains | MB_CRP_DSS | Manitoba Hydro | 49.8082 | -99.9383 | Manitoba
| Dakota | MB_DAK_DSS | Manitoba Hydro | 49.8336 | -97.1102 | Manitoba
| Dorsey | MB_DSY_DSS | Manitoba Hydro | 49.9919 | -97.4276 | Manitoba
| Dorsey CS | MB_DSY_CSS | Manitoba Hydro | 49.9919 | -97.4276 | Manitoba
| East Selkirk | MB_ESK_DSS | Manitoba Hydro | 50.1247 | -96.8522 | Manitoba
| Flin Flon Border | MB_BDR_DSS | Manitoba Hydro | 54.7769 | -101.8851 | Manitoba
| Fortier | MB_FRT_DSS | Manitoba Hydro | 49.8315 | -100.0057 | Manitoba
| Garden Hill | MB_GDH_DSS | Manitoba Hydro | 53.9093 | -94.6803 | Manitoba
| Gillam | MB_GLM_DSS | Manitoba Hydro | 56.3633 | -94.6164 | Manitoba
| Glenboro South | MB_GBS_DSS | Manitoba Hydro | 49.5403 | -99.2869 | Manitoba
| Gods Lake Narrows | MB_GLN_DSS | Manitoba Hydro | 54.5327 | -94.4385 | Manitoba
| Grand Rapids GS | MB_GRP_GSS | Manitoba Hydro | 53.16 | -99.2863 | Manitoba
| Great Falls GS | MB_GRF_GSS | Manitoba Hydro | 50.4616 | -96.0095 | Manitoba
| Griffin Steel | MB_GFS_ISS | Manitoba Hydro | 49.9142 | -96.9985 | Manitoba
| Gull Lake | MB_GLL_DSS | Manitoba Hydro | 50.3793 | -96.4949 | Manitoba
| Hanover | MB_HNV_DSS | Manitoba Hydro | 49.5378 | -96.7116 | Manitoba
| Harrow | MB_HRW_DSS | Manitoba Hydro | 49.8613 | -97.1573 | Manitoba
| HBMS Lalor | MB_LAL_ISS | Manitoba Hydro | 54.8613 | -100.0996 | Manitoba
| Henday CS | MB_HDY_CSS | Manitoba Hydro | 56.5036 | -94.1405 | Manitoba
| Herblet Lake | MB_HBL_DSS | Manitoba Hydro | 54.8868 | -99.9973 | Manitoba
| Highland Park | MB_HLP_DSS | Manitoba Hydro | 49.8752 | -99.9491 | Manitoba
| Ilford | MB_ILF_DSS | Manitoba Hydro | 56.1136 | -95.5547 | Manitoba
| Inco | MB_INC_ISS | Manitoba Hydro | 55.7291 | -97.8608 | Manitoba
| Inkster | MB_INK_DSS | Manitoba Hydro | 49.9438 | -97.2063 | Manitoba
| INT Drayton | XX_MBUS1_INT | MB-USA Border | 48.9997 | -97.2779 | Manitoba
| INT Forbes | XX_MBUS2_INT | MB-USA Border | 48.9993 | -95.5394 | Manitoba
| INT Iron Range | XX_MBUS3_INT | MB-USA Border | 49.0004 | -95.913 | Manitoba
| INT Moranville | XX_MBUS4_INT | MB-USA Border | 48.9992 | -95.5071 | Manitoba
| INT Peace Gardens | XX_MBUS5_INT | MB-USA Border | 48.9994 | -99.5592 | Manitoba
| IPT Boundary Dam | PP_MBSK3_IPT | MB-SK Border | 49.4953 | -101.3931 | Manitoba
| IPT EB Campbell | PP_MBSK2_IPT | MB-SK Border | 53.7227 | -101.7696 | Manitoba
| IPT Island Falls | PP_MBSK1_IPT | MB-SK Border | 54.7947 | -101.8859 | Manitoba
| IPT Seven Sisters | PP_ONMB1_IPT | ON-MB Border | 49.908 | -95.1529 | Manitoba
| IPT Tantallon | PP_MBSK4_IPT | MB-SK Border | 50.5445 | -101.4747 | Manitoba
| IPT Whiteshell | PP_ONMB2_IPT | ON-MB Border | 49.7886 | -95.152 | Manitoba
| IPT Yorkton | PP_MBSK5_IPT | MB-SK Border | 51.2025 | -101.5389 | Manitoba
| Jenpeg GS | MB_JPG_GSS | Manitoba Hydro | 54.5432 | -98.0282 | Manitoba
| Keewatinohk CS | MB_KWT_CSS | Manitoba Hydro | 56.662 | -93.8519 | Manitoba
| Keeyask GS | MB_KSK_GSS | Manitoba Hydro | 56.3304 | -95.3421 | Manitoba
| Keeyask SS | MB_KSS_SWS | Manitoba Hydro | 56.3304 | -95.3421 | Manitoba
| Kelsey GS | MB_KLS_GSS | Manitoba Hydro | 56.0405 | -96.5379 | Manitoba
| Kelsey TS | MB_KLT_TSS | Manitoba Hydro | 56.0405 | -96.5379 | Manitoba
| Kettle GS | MB_KTL_GSS | Manitoba Hydro | 56.3644 | -94.6183 | Manitoba
| Kirkfield Park | MB_KFP_DSS | Manitoba Hydro | 49.8996 | -97.3323 | Manitoba
| Lac Du Bonnet | MB_LDB_DSS | Manitoba Hydro | 50.2587 | -96.063 | Manitoba
| Laurie River #1 TS | MB_LRV_TSS | Manitoba Hydro | 56.2508 | -101.1171 | Manitoba
| Laverendrye | MB_LAV_DSS | Manitoba Hydro | 49.8043 | -97.3538 | Manitoba
| Leaf Rapids | MB_LFR_DSS | Manitoba Hydro | 56.4832 | -99.9886 | Manitoba
| Letellier | MB_LTL_DSS | Manitoba Hydro | 49.1338 | -97.3108 | Manitoba
| Libau | MB_LIB_DSS | Manitoba Hydro | 50.2637 | -96.7183 | Manitoba
| Limestone GS | MB_LMS_GSS | Manitoba Hydro | 56.5075 | -94.1097 | Manitoba
| Long Spruce GS | MB_LSP_GSS | Manitoba Hydro | 56.3978 | -94.3687 | Manitoba
| Long Spruce SS | MB_LSP_SWS | Manitoba Hydro | 56.3836 | -94.3608 | Manitoba
| Lowe Farm | MB_LFM_DSS | Manitoba Hydro | 49.3561 | -97.5733 | Manitoba
| Macgregor | MB_MCG_DSS | Manitoba Hydro | 49.945 | -98.7656 | Manitoba
| Madison | MB_MAD_DSS | Manitoba Hydro | 49.8929 | -97.2029 | Manitoba
| Manigotagan Corner | MB_MGT_DSS | Manitoba Hydro | 51.1149 | -96.3102 | Manitoba
| Manitoba Rolling Mills | MB_MRM_DSS | Manitoba Hydro | 50.13 | -96.8992 | Manitoba
| McArthur Falls GS | MB_MCF_GSS | Manitoba Hydro | 50.3981 | -95.9977 | Manitoba
| McPhillips | MB_MCP_DSS | Manitoba Hydro | 49.9229 | -97.1706 | Manitoba
| Melrose DSC | MB_MLR_DSS | Manitoba Hydro | 50.0339 | -96.8286 | Manitoba
| Mercy Street | MB_MCY_DSS | Manitoba Hydro | 50.1361 | -96.8906 | Manitoba
| Minitonas | MB_MIN_DSS | Manitoba Hydro | 52.1022 | -101.0642 | Manitoba
| Minnedosa South | MB_MDS_DSS | Manitoba Hydro | 50.24 | -99.8339 | Manitoba
| Mohawk | MB_MOH_DSS | Manitoba Hydro | 49.817 | -97.1633 | Manitoba
| Morden Corner | MB_MDC_DSS | Manitoba Hydro | 49.2007 | -97.9894 | Manitoba
| Mystery Lake | MB_MYS_DSS | Manitoba Hydro | 55.6937 | -97.8922 | Manitoba
| Neepawa | MB_NPW_DSS | Manitoba Hydro | 50.2252 | -99.4438 | Manitoba
| Neepawa South | MB_NPS_DSS | Manitoba Hydro | 50.2206 | -99.435 | Manitoba
| Nelson House | MB_NLH_DSS | Manitoba Hydro | 55.8841 | -98.823 | Manitoba
| Notigi | MB_NTG_DSS | Manitoba Hydro | 55.8745 | -99.3112 | Manitoba
| Oakbank | MB_OKB_DSS | Manitoba Hydro | 49.9605 | -96.8341 | Manitoba
| Overflowing River | MB_OVL_DSS | Manitoba Hydro | 53.1439 | -101.1003 | Manitoba
| Oxford House | MB_OXF_DSS | Manitoba Hydro | 54.9253 | -95.2448 | Manitoba
| Parkdale | MB_PKD_DSS | Manitoba Hydro | 50.0766 | -97.0501 | Manitoba
| Pine Falls GS | MB_PNF_GSS | Manitoba Hydro | 50.5671 | -96.1783 | Manitoba
| Plessis | MB_PLS_DSS | Manitoba Hydro | 49.8695 | -97.0307 | Manitoba
| Pointe Du Bois GS | MB_PDB_GSS | Manitoba Hydro | 50.2981 | -95.5481 | Manitoba
| Ponton | MB_PTN_DSS | Manitoba Hydro | 54.6649 | -99.1608 | Manitoba
| Portage South | MB_PGS_DSS | Manitoba Hydro | 49.931 | -98.2853 | Manitoba
| Radisson CS | MB_RDS_CSS | Manitoba Hydro | 56.3633 | -94.6164 | Manitoba
| Ralls Island | MB_RLI_DSS | Manitoba Hydro | 53.8311 | -101.2356 | Manitoba
| Randolph | MB_RDP_DSS | Manitoba Hydro | 49.5933 | -96.8221 | Manitoba
| Rapid City | MB_RPD_DSS | Manitoba Hydro | 50.124 | -99.9561 | Manitoba
| Raven Lake | MB_RVL_DSS | Manitoba Hydro | 50.3722 | -100.598 | Manitoba
| Reston | MB_RST_DSS | Manitoba Hydro | 49.5304 | -101.0969 | Manitoba
| Richer South | MB_RCH_DSS | Manitoba Hydro | 49.6198 | -96.4593 | Manitoba
| Ridgeway | MB_RGW_DSS | Manitoba Hydro | 49.9645 | -96.9925 | Manitoba
| Riel | MB_RIL_DSS | Manitoba Hydro | 49.8653 | -96.9391 | Manitoba
| Riel CS | MB_RIL_CSS | Manitoba Hydro | 49.8653 | -96.9391 | Manitoba
| Roblin South | MB_RBL_DSS | Manitoba Hydro | 51.2128 | -101.3273 | Manitoba
| Rockwood | MB_RKW_DSS | Manitoba Hydro | 50.0841 | -97.1632 | Manitoba
| Rosenfeld | MB_RSF_DSS | Manitoba Hydro | 49.1933 | -97.5765 | Manitoba
| Ross Lake | MB_RSL_DSS | Manitoba Hydro | 54.7751 | -101.8755 | Manitoba
| Rosser | MB_RSR_DSS | Manitoba Hydro | 49.9763 | -97.1618 | Manitoba
| Rutherford JCT | MB_RTH_JCT | Manitoba Hydro | 50.2236 | -96.0773 | Manitoba
| Sask Ave | MB_SKA_DSS | Manitoba Hydro | 49.9595 | -98.3909 | Manitoba
| Scotland | MB_SCT_DSS | Manitoba Hydro | 49.8624 | -97.1574 | Manitoba
| Seddons Corner DSC | MB_SDC_DSS | Manitoba Hydro | 50.0988 | -96.2883 | Manitoba
| Selkirk GS | MB_SKK_GSS | Manitoba Hydro | 50.1347 | -96.852 | Manitoba
| Seven Sisters GS | MB_SVS_GSS | Manitoba Hydro | 50.1204 | -96.0177 | Manitoba
| Sherbrook | MB_SBK_DSS | Manitoba Hydro | 49.8904 | -97.1586 | Manitoba
| Sherridon | MB_SHD_DSS | Manitoba Hydro | 55.1179 | -101.1106 | Manitoba
| Silver | MB_SLV_DSS | Manitoba Hydro | 50.8738 | -97.2187 | Manitoba
| Slave Falls GS | MB_SLF_GSS | Manitoba Hydro | 50.2221 | -95.5687 | Manitoba
| Snow Lake | MB_SNL_DSS | Manitoba Hydro | 54.8801 | -100.0161 | Manitoba
| Souris Enbridge East | MB_SEE_DSS | Manitoba Hydro | 49.6447 | -100.1407 | Manitoba
| Split Lake | MB_SPL_DSS | Manitoba Hydro | 56.2604 | -96.1559 | Manitoba
| St James | MB_SJM_DSS | Manitoba Hydro | 49.8807 | -97.202 | Manitoba
| St Joseph GS | MB_STJ_GSS | Manitoba Hydro | 49.1345 | -97.4205 | Manitoba
| St Leon GS | MB_STL_GSS | Manitoba Hydro | 49.3468 | -98.6341 | Manitoba
| St Vital | MB_STV_DSS | Manitoba Hydro | 49.844 | -97.0467 | Manitoba
| Stafford | MB_STF_DSS | Manitoba Hydro | 49.8613 | -97.1573 | Manitoba
| Stanley | MB_STY_DSS | Manitoba Hydro | 49.2655 | -97.9801 | Manitoba
| Star Lake | MB_SLK_DSS | Manitoba Hydro | 49.7425 | -95.2441 | Manitoba
| Stonewall | MB_STW_DSS | Manitoba Hydro | 50.1367 | -97.3091 | Manitoba
| Stony Mountain West | MB_STM_DSS | Manitoba Hydro | 50.0925 | -97.24 | Manitoba
| Transcona | MB_TCA_DSS | Manitoba Hydro | 49.909 | -97.0015 | Manitoba
| Transcona East | MB_TCE_DSS | Manitoba Hydro | 49.9092 | -96.9453 | Manitoba
| Treherne | MB_TRH_DSS | Manitoba Hydro | 49.6349 | -98.689 | Manitoba
| Tyndall DSC | MB_TYN_DSS | Manitoba Hydro | 50.0794 | -96.6829 | Manitoba
| Vermillion | MB_VML_DSS | Manitoba Hydro | 51.131 | -100.0887 | Manitoba
| Victoria Ave | MB_VCT_DSS | Manitoba Hydro | 49.8414 | -99.915 | Manitoba
| Virden West | MB_VDW_DSS | Manitoba Hydro | 49.8505 | -100.9621 | Manitoba
| Vivian | MB_VIV_DSS | Manitoba Hydro | 49.9467 | -96.5009 | Manitoba
| Warren | MB_WRN_DSS | Manitoba Hydro | 50.1222 | -97.5734 | Manitoba
| Wasagamack | MB_WSM_DSS | Manitoba Hydro | 53.8759 | -94.9808 | Manitoba
| Whiteshell | MB_WSL_DSS | Manitoba Hydro | 49.7425 | -95.2441 | Manitoba
| Wilkes | MB_WLK_DSS | Manitoba Hydro | 49.84 | -97.2772 | Manitoba
| William River | MB_WLR_DSS | Manitoba Hydro | 53.8872 | -99.2344 | Manitoba
| Wuskwatim GS | MB_WSK_GSS | Manitoba Hydro | 55.5383 | -98.4938 | Manitoba
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## Distribution
MB | EXISTING TRANSFORMERS
| Node Name | Node Code | Owner | Operating Region | Transformers | Primary Voltage | Secondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Other References | Notes
[6 empty] | (kV) | (kV) | (MVA) | (MVA) |  | (MW) | (MW)
| Anola DSC | MB_ANO_DSS | Manitoba Hydro | Manitoba |  | 115
| Ashern | MB_ASH_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 11.0833 | 13.3 | 0.9 | 9.975 | 11.97
| Augier | MB_AUG_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 61.876 | 78.75 | 0.9 | 55.6884 | 70.875
| Austin | MB_AUS_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 8.3833 | 10.06 | 0.9 | 7.545 | 9.054
| Beausejour East | MB_BSJ_DSS | Manitoba Hydro | Manitoba
| Birchtree | MB_BCT_DSS | Manitoba Hydro | Manitoba |  | 115
| Birtle South | MB_BTS_DSS | Manitoba Hydro | Manitoba |  | 230
| Brandon 65th St East | MB_B65_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 36.303 | 42.279 | 0.9 | 32.6727 | 38.0511
| Brandon GS | MB_BDN_GSS | Manitoba Hydro | Manitoba |  | 115
| Brereton Lake | MB_BRT_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 12.5 | 13.3 | 0.9 | 11.25 | 11.97
| Brokenhead | MB_BKH_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 3.51 | 4.212 | 0.9 | 3.159 | 3.7908
| Burntwood | MB_BWD_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 24.75 | 29.7 | 0.9 | 22.275 | 26.73
| Carberry North | MB_CBY_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 34.375 | 41.25 | 0.9 | 30.9375 | 37.125
| Churchill South | MB_CHS_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 32.55 | 39.06 | 0.9 | 29.295 | 35.154
| Cliff Lake | MB_CFL_DSS | Manitoba Hydro | Manitoba |  | 230 | 115
| Cornwallis | MB_CNW_DSS | Manitoba Hydro | Manitoba |  | 230
| Court | MB_CRT_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 133.1 | 171.1 | 0.9 | 119.79 | 153.99
| Cranberry Portage | MB_CBP_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 36.1667 | 43.4 | 0.9 | 32.55 | 39.06
| Crocus Plains | MB_CRP_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 36.1667 | 43.4 | 0.9 | 32.55 | 39.06
| Dakota | MB_DAK_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 78.84 | 123.4 | 0.9 | 70.956 | 111.06
| Dorsey | MB_DSY_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 12.5 | 13.3 | 0.9 | 11.25 | 11.97
| East Selkirk | MB_ESK_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 16.0017 | 19.202 | 0.9 | 14.4015 | 17.2818
| Flin Flon Border | MB_BDR_DSS | Manitoba Hydro | Manitoba |  | 115
| Fortier | MB_FRT_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 34.594 | 43.594 | 0.9 | 31.1346 | 39.2346
| Garden Hill | MB_GDH_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 32.55 | 39.06 | 0.9 | 29.295 | 35.154
| Gillam | MB_GLM_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 18.5625 | 22.275 | 0.9 | 16.7063 | 20.0475
| Glenboro South | MB_GBS_DSS | Manitoba Hydro | Manitoba |  | 138
| Gods Lake Narrows | MB_GLN_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 30.9375 | 37.125 | 0.9 | 27.8438 | 33.4125
| Grand Rapids GS | MB_GRP_GSS | Manitoba Hydro | Manitoba |  | 115 |  | 34.44 | 43.4 | 0.9 | 30.996 | 39.06
| Great Falls GS | MB_GRF_GSS | Manitoba Hydro | Manitoba |  | 115 |  | 2.34 | 2.808 | 0.9 | 2.106 | 2.5272
| Griffin Steel | MB_GFS_ISS | Manitoba Hydro | Manitoba |  | 115
| Gull Lake | MB_GLL_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 11.0833 | 13.3 | 0.9 | 9.975 | 11.97
| Hanover | MB_HNV_DSS | Manitoba Hydro | Manitoba |  | 115
| Harrow | MB_HRW_DSS | Manitoba Hydro | Manitoba |  | 115
| HBMS Lalor | MB_LAL_ISS | Manitoba Hydro | Manitoba |  | 115
| Henday CS | MB_HDY_CSS | Manitoba Hydro | Manitoba |  | 230
| Herblet Lake | MB_HBL_DSS | Manitoba Hydro | Manitoba |  | 115
| Highland Park | MB_HLP_DSS | Manitoba Hydro | Manitoba |  | 138
| Ilford | MB_ILF_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 5.85 | 7.74 | 0.9 | 5.265 | 6.966
| Inco | MB_INC_ISS | Manitoba Hydro | Manitoba |  | 115
| Inkster | MB_INK_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 58.8 | 75.6 | 0.9 | 52.92 | 68.04
| Jenpeg GS | MB_JPG_GSS | Manitoba Hydro | Manitoba |  | 138
| Keewatinohk CS | MB_KWT_CSS | Manitoba Hydro | Manitoba |  | 138
| Keeyask GS | MB_KSK_GSS | Manitoba Hydro | Manitoba |  | 138
| Keeyask SS | MB_KSS_SWS | Manitoba Hydro | Manitoba |  | 138
| Kelsey GS | MB_KLS_GSS | Manitoba Hydro | Manitoba |  | 138
| Kelsey TS | MB_KLT_TSS | Manitoba Hydro | Manitoba |  | 138
| Kettle GS | MB_KTL_GSS | Manitoba Hydro | Manitoba |  | 115 |  | 8.25 | 9.9 | 0.9 | 7.425 | 8.91
| Kirkfield Park | MB_KFP_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 40 | 40 | 0.9 | 36 | 36
| Lac Du Bonnet | MB_LDB_SUB | Manitoba Hydro |  |  | 138 |  | 22.7083 | 27.25 | 0.9 | 20.4375 | 24.525
| Laurie River #1 TS | MB_LRV_TSS | Manitoba Hydro | Manitoba |  | 230
| Laverendrye | MB_LAV_DSS | Manitoba Hydro | Manitoba |  | 138
| Leaf Rapids | MB_LFR_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 30.9375 | 37.125 | 0.9 | 27.8438 | 33.4125
| Letellier | MB_LTL_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 11.0833 | 13.3 | 0.9 | 9.975 | 11.97
| Libau | MB_LIB_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 11.0833 | 13.3 | 0.9 | 9.975 | 11.97
| Limestone GS | MB_LMS_GSS | Manitoba Hydro | Manitoba |  | 230 |  | 9.2817 | 11.138 | 0.9 | 8.3535 | 10.0242
| Long Spruce GS | MB_LSP_GSS | Manitoba Hydro | Manitoba |  | 115
| Lowe Farm | MB_LFM_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 11.0833 | 13.3 | 0.9 | 9.975 | 11.97
| Macgregor | MB_MCG_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 16.7758 | 20.131 | 0.9 | 15.0983 | 18.1179
| Madison | MB_MAD_DSS | Manitoba Hydro | Manitoba |  | 115
| Manigotagan Corner | MB_MGT_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 5.6625 | 6.795 | 0.9 | 5.0963 | 6.1155
| Manitoba Rolling Mills | MB_MRM_DSS | Manitoba Hydro | Manitoba |  | 115
| McArthur Falls GS | MB_MCF_GSS | Manitoba Hydro | Manitoba |  | 115
| McPhillips | MB_MCP_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 65.7 | 71.6 | 0.9 | 59.13 | 64.44
| Melrose DSC | MB_MLR_DSS | Manitoba Hydro | Manitoba |  | 115
| Mercy Street | MB_MCY_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 30.9375 | 37.125 | 0.9 | 27.8438 | 33.4125
| Minitonas | MB_MIN_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 6.2917 | 7.55 | 0.9 | 5.6625 | 6.795
| Minnedosa South | MB_MDS_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 18.3325 | 21.999 | 0.9 | 16.4992 | 19.7991
| Mohawk | MB_MOH_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 160 | 160 | 0.9 | 144 | 144
| Morden Corner | MB_MDC_DSS | Manitoba Hydro | Manitoba |  | 230 | 138
| Mystery Lake | MB_MYS_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 29.0625 | 34.875 | 0.9 | 26.1562 | 31.3875
| Neepawa | MB_NPW_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 22 | 26.5 | 0.9 | 19.8 | 23.85
| Neepawa South | MB_NPS_DSS | Manitoba Hydro | Manitoba |  | 138
| Nelson House | MB_NLH_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 9.2442 | 11.093 | 0.9 | 8.3198 | 9.9837
| Notigi | MB_NTG_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 1.29 | 1.548 | 0.9 | 1.161 | 1.3932
| Oakbank | MB_OKB_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 20.25 | 24.3 | 0.9 | 18.225 | 21.87
| Overflowing River | MB_OVL_DSS | Manitoba Hydro | Manitoba |  | 138
| Oxford House | MB_OXF_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 32.55 | 39.06 | 0.9 | 29.295 | 35.154
| Parkdale | MB_PKD_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 11.0833 | 13.3 | 0.9 | 9.975 | 11.97
| Pine Falls GS | MB_PNF_GSS | Manitoba Hydro | Manitoba |  | 115
| Plessis | MB_PLS_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 235.2 | 275.6 | 0.9 | 211.68 | 248.04
| Pointe Du Bois GS | MB_PDB_GSS | Manitoba Hydro | Manitoba |  | 230
| Ponton | MB_PTN_DSS | Manitoba Hydro | Manitoba |  | 230
| Portage South | MB_PGS_DSS | Manitoba Hydro | Manitoba |  | 138
| Radisson CS | MB_RDS_CSS | Manitoba Hydro | Manitoba |  | 230
| Ralls Island | MB_RLI_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 11.6667 | 14 | 0.9 | 10.5 | 12.6
| Ralls Island | MB_RLI_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 68.75 | 82.5 | 0.9 | 61.875 | 74.25
| Randolph | MB_RDP_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 17.28 | 22.275 | 0.9 | 15.552 | 20.0475
| Rapid City | MB_RPD_DSS | Manitoba Hydro | Manitoba |  | 230 | 115 | 11.1108 | 13.333 | 0.9 | 9.9998 | 11.9997
| Raven Lake | MB_RVL_DSS | Manitoba Hydro | Manitoba |  | 230
| Reston | MB_RST_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 8.3333 | 10 | 0.9 | 7.5 | 9
| Richer South | MB_RCH_DSS | Manitoba Hydro | Manitoba |  | 230
| Ridgeway | MB_RGW_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 25.82 | 37.75 | 0.9 | 23.238 | 33.975
| Riel | MB_RIL_DSS | Manitoba Hydro | Manitoba |  | 230
| Roblin South | MB_RBL_DSS | Manitoba Hydro | Manitoba |  | 230 | 115
| Rockwood | MB_RKW_DSS | Manitoba Hydro | Manitoba |  | 115
| Rosenfeld | MB_RSF_DSS | Manitoba Hydro | Manitoba |  | 115
| Ross Lake | MB_RSL_DSS | Manitoba Hydro | Manitoba |  | 230 | 115 | 68.75 | 82.5 | 0.9 | 61.875 | 74.25
| Rosser | MB_RSR_DSS | Manitoba Hydro | Manitoba |  | 115
| Sask Ave | MB_SKA_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 22.4083 | 26.89 | 0.9 | 20.1675 | 24.201
| Scotland | MB_SCT_DSS | Manitoba Hydro | Manitoba |  | 115 | 4 | 27.1 | 27.1 | 0.9 | 24.39 | 24.39
| Selkirk GS | MB_SKK_GSS | Manitoba Hydro | Manitoba |  | 115
| Seven Sisters GS | MB_SVS_GSS | Manitoba Hydro | Manitoba |  | 115
| Sherbrook | MB_SBK_DSS | Manitoba Hydro | Manitoba | TBD | 115 | 4 | 64.4 | 48.7 | 0.9 | 57.96 | 43.83
| Sherbrook | MB_SBK_DSS | Manitoba Hydro | Manitoba | TBD | 115 | 12 | 64.4 | 48.7 | 0.9 | 57.96 | 43.83
| Sherridon | MB_SHD_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 5.5 | 6.6 | 0.9 | 4.95 | 5.94
| Silver | MB_SLV_DSS | Manitoba Hydro | Manitoba |  | 124
| Slave Falls GS | MB_SLF_GSS | Manitoba Hydro | Manitoba |  | 115
| Snow Lake | MB_SNL_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 9.1667 | 11 | 0.9 | 8.25 | 9.9
| Souris Enbridge East | MB_SEE_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 35.8333 | 43 | 0.9 | 32.25 | 38.7
| Split Lake | MB_SPL_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 16.4592 | 19.751 | 0.9 | 14.8133 | 17.7759
| St James | MB_SJM_DSS | Manitoba Hydro | Manitoba | TBD | 115 | 4 | 18 | 18 | 0.9 | 16.2 | 16.2 | See 2016 MH LTT Plan
| St James | MB_SJM_DSS | Manitoba Hydro | Manitoba | TBD | 115 | 24 | 208 | 208 | 0.9 | 187.2 | 187.2 | See 2016 MH LTT Plan
| St Joseph GS | MB_STJ_GSS | Manitoba Hydro | Manitoba |  | 230
| St Leon GS | MB_STL_GSS | Manitoba Hydro | Manitoba |  | 230
| St Vital | MB_STV_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 91.6 | 121.3 | 0.9 | 82.44 | 109.17
| Stafford | MB_STF_DSS | Manitoba Hydro | Manitoba |  | 115
| Stanley | MB_STY_DSS | Manitoba Hydro | Manitoba |  | 230
| Star Lake | MB_SLK_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 11.52 | 14.85 | 0.9 | 10.368 | 13.365
| Stonewall | MB_STW_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 23.04 | 29.7 | 0.9 | 20.736 | 26.73
| Stony Mountain West | MB_STM_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 11.0833 | 13.3 | 0.9 | 9.975 | 11.97
| Transcona | MB_TCA_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 5 | 5 | 0.9 | 4.5 | 4.5
| Transcona | MB_TCE_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 8.33 | 11.7 | 0.9 | 7.497 | 10.53
| Treherne | MB_TRH_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 14.5317 | 17.438 | 0.9 | 13.0785 | 15.6942 |  | Actual primary voltage is 110 kV
| Tyndall DSC | MB_TYN_DSS | Manitoba Hydro | Manitoba |  | 115
| Vermillion | MB_VML_DSS | Manitoba Hydro | Manitoba |  | 230 |  | 8.3333 | 10 | 0.9 | 7.5 | 9
| Victoria Ave | MB_VCT_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 5.7333 | 6.88 | 0.9 | 5.16 | 6.192
| Virden West | MB_VDW_DSS | Manitoba Hydro | Manitoba |  | 230
| Vivian | MB_VIV_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 8.25 | 9.9 | 0.9 | 7.425 | 8.91
| Warren | MB_WRN_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 16.5 | 19.8 | 0.9 | 14.85 | 17.82
| Wasagamack | MB_WSM_DSS | Manitoba Hydro | Manitoba |  | 138 |  | 33.48 | 40.176 | 0.9 | 30.132 | 36.1584
| Whiteshell | MB_WSL_DSS | Manitoba Hydro | Manitoba |  | 230 | 115 | 14.9533 | 17.944 | 0.9 | 13.458 | 16.1496
| Wilkes | MB_WLK_DSS | Manitoba Hydro | Manitoba |  | 115 |  | 100 | 100 | 0.9 | 90 | 90
| William River | MB_WLR_DSS | Manitoba Hydro | Manitoba |  | 230
| Wuskwatim GS | MB_WSK_GSS | Manitoba Hydro | Manitoba |  | 230
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## System
MB | SYSTEM CHARACTERISTICS
| Generator Type | Capacity Adjustment (Winter) | Capacity Adjustment (Summer) | Capacity Adjustment (Average) | Capacity Factor | Notes | Reserve Requirements | Line Losses
|  | (%) | (%) | (%) | (%) |  | (% installed MW) | (% across system)
| Natural Gas CT | 95.3% | 95.3% | 95.3% | by facility |  | 12 | 9
| Hydro_run | 65% | 65% | 65% | by facility
| Hydro_daily | 98.1% | 98.1% | 98.1% | by facility
| Hydro_monthly | 98.1% | 98.1% | 98.1% | by facility
| Wind | 0.23 | 17% | 20% | 35%
Specific Notes:
Capacity adjustment numbers for Natural Gas and Hydro resources are for Quebec, and should be replaced with values for Manitoba
The winter wind capacity adjustment was derived based on reported values for the summer and average annual capacity adjustments
General Notes:

## HGWh
MB | HISTORICAL ANNUAL ENERGY DEMAND | UNIT | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2009-2018
| Annual Energy Demand (after DSM) | GWh/year | 23412 | 23892 | 23605 | 24750 | 25625 | 25505 | 24665 | 25227 | 25742 | 25935
| Annual Change in Energy Demand | GWh/year |  | 480 | -287 | 1145 | 875 | -120 | -840 | 562 | 515 | 193 | Average
| Percentage Change in Energy Demand | % |  | 2.05% | -1.201% | 4.851% | 3.535% | -0.4683% | -3.293% | 2.279% | 2.041% | 0.7497% | 1.144%
Notes:

## HMW
MB | HISTORICAL PEAK CAPACITY | UNIT | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2009-2018
| Annual Capacity Demand (after DSM) | MW | 4393 | 4286 | 4367 | 4559 | 4743 | 4713 | 4479 | 4822 | 4755 | 4815
| Annual Change in Capacity Demand | MW |  | -107 | 81 | 192 | 184 | -30 | -234 | 343 | -67 | 60 | Average
| Percentage Change in Capacity Demand | % |  | -2.436% | 1.89% | 4.397% | 4.036% | -0.6325% | -4.965% | 7.658% | -1.389% | 1.262% | 1.024%
Notes:

## FGWh
MB | ANNUAL ENERGY LOAD FORECAST | UNITS | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2018-2030 | 2018-2050 | Notes
| January | GWh | 1979 | 2002 | 2024 | 2041 | 2060 | 2086 | 2111 | 2135 | 2160 | 2183 | 2207 | 2233 | 2259 | 2286 | 2314 | 2342 | 2370 | 2399 | 2430 | 2465
| February | GWh | 1817 | 1838 | 1859 | 1875 | 1894 | 1917 | 1941 | 1962 | 1985 | 2006 | 2029 | 2052 | 2076 | 2101 | 2127 | 2152 | 2178 | 2205 | 2233 | 2265
| March | GWh | 1762 | 1783 | 1802 | 1818 | 1836 | 1859 | 1882 | 1903 | 1925 | 1946 | 1968 | 1991 | 2014 | 2038 | 2064 | 2088 | 2113 | 2139 | 2167 | 2198
| April | GWh | 1886 | 1910 | 1933 | 1950 | 1970 | 1995 | 2019 | 2042 | 2066 | 2088 | 2111 | 2136 | 2161 | 2187 | 2214 | 2240 | 2267 | 2295 | 2325 | 2358
| May | GWh | 1837 | 1861 | 1884 | 1901 | 1920 | 1944 | 1968 | 1990 | 2013 | 2034 | 2057 | 2081 | 2105 | 2131 | 2157 | 2183 | 2209 | 2236 | 2265 | 2297
| June | GWh | 1747 | 1768 | 1788 | 1803 | 1821 | 1844 | 1866 | 1887 | 1909 | 1929 | 1951 | 1974 | 1997 | 2021 | 2046 | 2070 | 2095 | 2120 | 2147 | 2178
| July | GWh | 1991 | 2014 | 2035 | 2053 | 2072 | 2098 | 2124 | 2147 | 2172 | 2195 | 2220 | 2245 | 2271 | 2299 | 2327 | 2355 | 2383 | 2412 | 2444 | 2479
| August | GWh | 2313 | 2339 | 2364 | 2385 | 2408 | 2439 | 2468 | 2496 | 2525 | 2552 | 2581 | 2611 | 2641 | 2674 | 2707 | 2740 | 2773 | 2808 | 2845 | 2886
| September | GWh | 2743 | 2773 | 2803 | 2828 | 2855 | 2891 | 2926 | 2959 | 2994 | 3025 | 3059 | 3095 | 3131 | 3170 | 3210 | 3249 | 3289 | 3331 | 3375 | 3424
| October | GWh | 2893 | 2925 | 2958 | 2984 | 3013 | 3052 | 3089 | 3124 | 3161 | 3194 | 3230 | 3268 | 3307 | 3348 | 3391 | 3433 | 3475 | 3519 | 3566 | 3618
| November | GWh | 2514 | 2542 | 2570 | 2592 | 2617 | 2650 | 2683 | 2713 | 2745 | 2774 | 2805 | 2838 | 2872 | 2907 | 2944 | 2980 | 3017 | 3055 | 3096 | 3141
| December | GWh | 2453 | 2480 | 2507 | 2527 | 2550 | 2582 | 2613 | 2642 | 2673 | 2701 | 2732 | 2764 | 2796 | 2830 | 2866 | 2900 | 2936 | 2972 | 3011 | 3055 | 2018-2030 Rate | 2019-2037 Rate
| Mid-load Forecast (before DSM) | GWh/year | 25935 | 26235 | 26527 | 26757 | 27016 | 27357 | 27690 | 28000 | 28328 | 28627 | 28950 | 29288 | 29630 | 29992 | 30367 | 30732 | 31105 | 31491 | 31904 | 32364 | 1.197% | 1.227%
| Cumulative DSM (Program based) | GWh/year | -285 | -541 | -861 | -1158 | -1341 | -1509 | -1666 | -1829 | -1998 | -2173 | -2345 | -2525 | -2697 | -2717 | -2742 | -2766 | -2791 | -2815 | -2839 | -2865
| Annual DSM (Program based) | GWh/year | -285 | -256 | -320 | -297 | -183 | -168 | -157 | -163 | -169 | -175 | -172 | -180 | -172 | -20 | -25 | -24 | -25 | -24 | -24 | -26
| Mid-load Forecast (after DSM) | GWh/year | 25650 | 25694 | 25666 | 25599 | 25675 | 25848 | 26024 | 26171 | 26330 | 26454 | 26605 | 26763 | 26933 | 27275 | 27625 | 27966 | 28314 | 28676 | 29065 | 29499 | 2018-2030 Rate | 2018-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 0.1715% | -0.109% | -0.261% | 0.2969% | 0.6738% | 0.6809% | 0.5649% | 0.6075% | 0.4709% | 0.5708% | 0.5939% | 0.6352% | 1.27% | 1.283% | 1.234% | 1.244% | 1.279% | 1.357% | 1.493% | 0.4447% | 0.7798% | Mid-load forecast for use in COPPER
| Low-load Forecast (before DSM) |  | 25554 | 25702 | 25876 | 26010 | 26184 | 26446 | 26710 | 26955 | 27222 | 27463 | 27733 | 28017 | 28311 | 28625 | 28955 | 29277 | 29608 | 29953 | 30325 | 30746
| Cumulative DSM (Program based) | GWh/year | -285 | -541 | -861 | -1158 | -1341 | -1509 | -1666 | -1829 | -1998 | -2173 | -2345 | -2525 | -2697 | -2717 | -2742 | -2766 | -2791 | -2815 | -2839 | -2865 |  |  | Assume same DSM program as under mid-load forecast
| Annual DSM (Program based) | GWh/year | -285 | -256 | -320 | -297 | -183 | -168 | -157 | -163 | -169 | -175 | -172 | -180 | -172 | -20 | -25 | -24 | -25 | -24 | -24 | -26
| Low-load Forecast (after DSM) | GWh/year | 25269 | 25161 | 25015 | 24852 | 24843 | 24937 | 25044 | 25126 | 25224 | 25290 | 25388 | 25492 | 25614 | 25908 | 26213 | 26511 | 26817 | 27138 | 27486 | 27881 | 2018-2030 Rate | 2018-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | -0.4274% | -0.5803% | -0.6516% | -0.03621% | 0.3784% | 0.4291% | 0.3274% | 0.39% | 0.2617% | 0.3875% | 0.4096% | 0.4786% | 1.148% | 1.177% | 1.137% | 1.154% | 1.197% | 1.282% | 1.437% | 0.1234% | 0.548% | Low-load forecast for use in COPPER
| High-load Forecast (before DSM) |  | 26317 | 26772 | 27179 | 27508 | 27852 | 28267 | 28672 | 29047 | 29436 | 29791 | 30170 | 30556 | 30949 | 31358 | 31779 | 32189 | 32604 | 33031 | 33482 | 33980
| Cumulative DSM (Program based) | GWh/year | -285 | -541 | -861 | -1158 | -1341 | -1509 | -1666 | -1829 | -1998 | -2173 | -2345 | -2525 | -2697 | -2717 | -2742 | -2766 | -2791 | -2815 | -2839 | -2865 |  |  | Assume same DSM program as under mid-load forecast
| Annual DSM (Program based) | GWh/year | -285 | -256 | -320 | -297 | -183 | -168 | -157 | -163 | -169 | -175 | -172 | -180 | -172 | -20 | -25 | -24 | -25 | -24 | -24 | -26
| High-load Forecast (after DSM) | GWh/year | 26032 | 26231 | 26318 | 26350 | 26511 | 26758 | 27006 | 27218 | 27438 | 27618 | 27825 | 28031 | 28252 | 28641 | 29037 | 29423 | 29813 | 30216 | 30643 | 31115 | 2018-2030 Rate | 2018-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 0.7644% | 0.3317% | 0.1216% | 0.611% | 0.9317% | 0.9268% | 0.785% | 0.8083% | 0.656% | 0.7495% | 0.7403% | 0.7884% | 1.377% | 1.383% | 1.329% | 1.325% | 1.352% | 1.413% | 1.54% | 0.7468% | 0.9958% | High-load forecast for use in COPPER
Notes:
Gross Firm Energy is the energy required to serve Manitoba Hydro’s customers on the Integrated System. It excludes exports, interruptible (non-firm) loads, Diesel Sales and Station Service for Keeyask and non-committed plants.

## FMW
MB | ANNUAL PEAK LOAD FORECAST | UNITS | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2018-2030 | 2018-2050 | Notes
| January | MW | 3511 | 3554 | 3592 | 3624 | 3660 | 3707 | 3753 | 3795 | 3841 | 3882 | 3927 | 3973 | 4020 | 4070 | 4121 | 4172 | 4223 | 4276 | 4333 | 4395
| February | MW | 3031 | 3069 | 3103 | 3132 | 3163 | 3204 | 3243 | 3280 | 3319 | 3355 | 3393 | 3433 | 3474 | 3517 | 3561 | 3604 | 3648 | 3694 | 3742 | 3796
| March | MW | 3193 | 3235 | 3270 | 3300 | 3335 | 3377 | 3419 | 3459 | 3500 | 3538 | 3579 | 3622 | 3665 | 3710 | 3758 | 3804 | 3851 | 3899 | 3951 | 4008
| April | MW | 3322 | 3367 | 3407 | 3439 | 3476 | 3521 | 3565 | 3606 | 3649 | 3688 | 3731 | 3775 | 3821 | 3868 | 3917 | 3965 | 4014 | 4065 | 4119 | 4178
| May | MW | 3368 | 3414 | 3455 | 3488 | 3526 | 3571 | 3616 | 3657 | 3702 | 3742 | 3785 | 3830 | 3876 | 3925 | 3975 | 4024 | 4074 | 4125 | 4180 | 4240
| June | MW | 3132 | 3171 | 3207 | 3236 | 3270 | 3312 | 3353 | 3391 | 3432 | 3469 | 3509 | 3550 | 3593 | 3637 | 3683 | 3728 | 3774 | 3821 | 3871 | 3927
| July | MW | 3391 | 3431 | 3468 | 3499 | 3534 | 3579 | 3623 | 3664 | 3708 | 3747 | 3790 | 3835 | 3880 | 3928 | 3978 | 4027 | 4076 | 4127 | 4182 | 4242
| August | MW | 4059 | 4107 | 4152 | 4189 | 4232 | 4285 | 4339 | 4388 | 4440 | 4488 | 4539 | 4593 | 4648 | 4706 | 4766 | 4825 | 4884 | 4946 | 5013 | 5085
| September | MW | 4554 | 4598 | 4650 | 4693 | 4740 | 4801 | 4861 | 4916 | 4975 | 5028 | 5085 | 5146 | 5207 | 5273 | 5340 | 5406 | 5474 | 5544 | 5619 | 5701
| October | MW | 4736 | 4783 | 4838 | 4884 | 4933 | 4996 | 5059 | 5117 | 5178 | 5233 | 5294 | 5356 | 5421 | 5489 | 5560 | 5629 | 5699 | 5772 | 5851 | 5936
| November | MW | 4644 | 4690 | 4743 | 4787 | 4834 | 4896 | 4957 | 5014 | 5075 | 5129 | 5188 | 5250 | 5313 | 5380 | 5449 | 5517 | 5586 | 5657 | 5734 | 5817
| December | MW | 4398 | 4450 | 4496 | 4535 | 4577 | 4636 | 4693 | 4747 | 4804 | 4855 | 4911 | 4970 | 5029 | 5092 | 5158 | 5222 | 5287 | 5354 | 5426 | 5505 | 2018-2030 Rate | 2018-2037 Rate
| Mid-load Forecast (before DSM) | MW | 4815 | 4863 | 4918 | 4965 | 5015 | 5079 | 5143 | 5202 | 5264 | 5320 | 5381 | 5445 | 5511 | 5580 | 5652 | 5722 | 5794 | 5869 | 5948 | 6035 | 1.226% | 1.255%
| Cumulative DSM (Program based) | MW | -53 | -99 | -169 | -238 | -283 | -319 | -352 | -386 | -421 | -455 | -487 | -521 | -552 | -557 | -561 | -566 | -571 | -576 | -580 | -585
| Annual DSM (Program based) | MW | -53 | -46 | -70 | -69 | -45 | -36 | -33 | -34 | -35 | -34 | -32 | -34 | -31 | -5 | -4 | -5 | -5 | -5 | -4 | -5
| Mid-load Forecast (after DSM) | MW | 4762 | 4764 | 4749 | 4727 | 4732 | 4760 | 4791 | 4816 | 4843 | 4865 | 4894 | 4924 | 4959 | 5023 | 5091 | 5156 | 5223 | 5293 | 5368 | 5450 | 2018-2030 Rate | 2018-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) | % | -1.101% | -0.9459% | -1.423% | -1.39% | -0.8973% | -0.7088% | -0.6416% | -0.6536% | -0.6649% | -0.6391% | -0.5947% | -0.6244% | -0.5625% | -0.08961% | -0.07077% | -0.08738% | -0.0863% | -0.08519% | -0.06725% | -0.08285% | 0.3692% | 0.7525% | Mid-load forecast for use in COPPER
| Low-load Forecast (before DSM) |  | 4723 | 4733 | 4760 | 4783 | 4812 | 4858 | 4905 | 4948 | 4996 | 5038 | 5086 | 5137 | 5191 | 5249 | 5310 | 5369 | 5431 | 5495 | 5565 | 5643
| Cumulative DSM (Program based) | MW | -53 | -99 | -169 | -238 | -283 | -319 | -352 | -386 | -421 | -455 | -487 | -521 | -552 | -557 | -561 | -566 | -571 | -576 | -580 | -585 |  |  | Assume same DSM program as under mid-load forecast
| Annual DSM (Program based) | MW | -53 | -46 | -70 | -69 | -45 | -36 | -33 | -34 | -35 | -34 | -32 | -34 | -31 | -5 | -4 | -5 | -5 | -5 | -4 | -5
| Low-load Forecast (after DSM) | MW | 4670 | 4634 | 4591 | 4545 | 4529 | 4539 | 4553 | 4562 | 4575 | 4583 | 4599 | 4616 | 4639 | 4692 | 4749 | 4803 | 4860 | 4919 | 4985 | 5058 | 2018-2030 Rate | 2018-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | -0.7709% | -0.9279% | -1.002% | -0.352% | 0.2208% | 0.3084% | 0.1977% | 0.285% | 0.1749% | 0.3491% | 0.3696% | 0.4983% | 1.142% | 1.215% | 1.137% | 1.187% | 1.214% | 1.342% | 1.464% | -0.06053% | 0.4444% | Low-load forecast for use in COPPER
| High-load Forecast (before DSM) |  | 26317 | 26772 | 27179 | 27508 | 27852 | 28267 | 28672 | 29047 | 29436 | 29791 | 30170 | 30556 | 30949 | 31358 | 31779 | 32189 | 32604 | 33031 | 33482 | 33980
| Cumulative DSM (Program based) | MW | -53 | -99 | -169 | -238 | -283 | -319 | -352 | -386 | -421 | -455 | -487 | -521 | -552 | -557 | -561 | -566 | -571 | -576 | -580 | -585 |  |  | Assume same DSM program as under mid-load forecast
| Annual DSM (Program based) | MW | -53 | -46 | -70 | -69 | -45 | -36 | -33 | -34 | -35 | -34 | -32 | -34 | -31 | -5 | -4 | -5 | -5 | -5 | -4 | -5
| High-load Forecast (after DSM) | MW | 26264 | 26673 | 27010 | 27270 | 27569 | 27948 | 28320 | 28661 | 29015 | 29336 | 29683 | 30035 | 30397 | 30801 | 31218 | 31623 | 32033 | 32455 | 32902 | 33395 | 2018-2030 Rate | 2018-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 1.557% | 1.263% | 0.9626% | 1.096% | 1.375% | 1.331% | 1.204% | 1.235% | 1.106% | 1.183% | 1.186% | 1.205% | 1.329% | 1.354% | 1.297% | 1.297% | 1.317% | 1.377% | 1.498% | 1.337% | 1.343% | High-load forecast for use in COPPER
Notes:
Hourly Gross Total Peak = Hourly Total Generation - Hourly Metered Exports + Hourly Metered Imports - Losses Associated with Exports + Gains Associated with Imports + Curtailments

## Hourly
MB | Hourly
Not yet available

## Inputs
MB | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance