## README
NB | LEGEND
| NB-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| Distribution | Characteristics of existing distribution substations
| System | Miscellaneous provincial system characteristics
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review or being gathered
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to sources
See the accompanying calculations file and raw data files for additional supporting information
See the related Gitlab issue for a summary of inventory status

## NB-Sources
NB | SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| Nova Scotia Power Inc. | 2020 | NS Power 2020 IRP Modeling Results Release | https://irp.nspower.ca/documents/modeling-results/ |  | Nova Scotia
| Energy and Environmental Economics | 2019 | Planning Reserve Margin and Capacity Value Study | https://irp.nspower.ca/documents/pre-irp-deliverables/ |  | Nova Scotia
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" column of the relevant tab
| NB Power | 2019 | 2018/2019 Annual Report [2011 through 2020] | https://www.nbpower.com/en/about-us/accountability-reports/annual-and-quarterly-reports/ |  | New Brunswick
| NB Power | 2020 | About Our Energy - Our Current Energy Mix | https://www.nbpower.com/en/about-us/our-energy |  | New Brunswick
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | National
| NB Power | 2018 | 2018-2027 Load Forecast Update | https://filemaker.nbeub.ca/fmi/webd/NBEUB%20ToolKit13 |  | New Brunswick
| NB Power | 2017 | NB Power 2017 Integrated Resource Plan Part A | https://www.nbpower.com/en/about-us/our-energy/integrated-resource-plan |  | New Brunswick
| NPCC | 2016 | 2016 Maritimes Area Comprehensive Review of Resource Adequacy | https://www.npcc.org/Library/Resource%20Adequacy/2016%20Maritimes%20Area%20CRRA%20for%20RCCpaf.pdf |  | New Brunswick
| Nova Scotia Power Inc. | 2018 | 10-Year System Outlook 2018 Report Revised | http://oasis.nspower.ca/en/home/oasis/forecasts-and-assessments.aspx |  | New Brunswick
| SNC-Lavalin T&D | 2009 | Transmission and System Operator Options for Nova Scotia. Prepared for Nova Scotia Department of Energy | https://energy.novascotia.ca/sites/default/files/Transmission%20and%20System%20Operator%20Options%20for%20Nova%20Scotia.pdf |  | Nova Scotia and New Brunswick
| NB Power | 2019 | Wind Energy | https://www.nbpower.com/en/about-us/our-energy/wind-energy |  | New Brunswick
| Ismail, S. | 2015 | Potential Hydro Energy: Review, Evaluation and Methodology | https://filemaker.nbeub.ca/fmi/webd/NBEUB%20ToolKit13 [Matter 336] | prepared for New Brunswick Power Corporation | New Brunswick
| Dunsky Energy Consulting | 2019 | City of Summerside Capacity Resource Plan | https://summerside.ca/residents/electricity/energy_capacity_resource_planning |  | New Brunswick
| Edmundston Energy | 2005 | Edmundston Energy Project - GHG Quantification Report | https://www.csaregistries.ca/files/projects/prj_5210_932.pdf |  | New Brunswick
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
NB | EXISTING GENERATION | [12 empty] | DESIGN | [7 empty] | OPERATIONS | [13 empty] | OPERATING COSTS
| Project Name | Gen Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Unit | # of units | Inc Heat Rate @ Max | Minimum Capacity | Maximum Capacity | Minimum Up Time | Minimum Down Time | Spin Up Ramp Rate | Spin Down Ramp Rate | Start Up Ramp Limit | Shut Down Ramp Limit | Must Run | Operating Reserve Fraction | Outage Duration | Forced Outage Rate | Maintenance Outage Rate | Start Up Costs | Fuel Costs | Shut Down Costs | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | (kV) |  |  |  |  | (MW) |  | (MW) | (%) | (GWh/year) |  | (MMBtu/MWh) | (MW) | (MW) | (hours) | (hours) | (%/min) | (%/min) | [MW/hr p MWcap] | [MW/hr p MWcap] | (T/F) | (%) | (hours) | (%) | (days/y) | (S/MWcap) | ($/MWh) | (S/MWcap) | ($/year) | ($/MWh)
| Atholville | NB_ATHO00_GEN | AV Group NB | Atholville | 47.9924 | -66.7212 | New Brunswick.a | New Brunswick | Frasers Atholville SS 5409 | NB_5409_DSS | 138 | 2010 | 2100 | Biomass | biomass | 21 | 95% | 19.95 | 45% | 82.782 | 1
| Nackawic | NB_NACK00_GEN | AV Group NB | Nackawic | 46.0042 | -67.2313 | New Brunswick.a | New Brunswick | St. Anne Nackawic SS 5116 | NB_5116_DSS | 138 | 2015 | 2100 | Biomass | biomass | 26 | 95% | 24.7 | 45% | 102.492 | 1
| Saint John | NB_STJO00_GEN | Irving Pulp & Paper Ltd | Saint John | 45.2589 | -66.0945 | New Brunswick.a | New Brunswick | Irving Pulp and Paper SS 5264 | NB_5264_ISS | 69 | 2010 | 2100 | Biomass | biomass | 33 | 95% | 31.35 | 45% | 130.086 | 1
| Twin Rivers | NB_TWNR00_GEN | Fraser Papers (Edmundston Pulp Mill) | Edmundston | 47.3702 | -68.3318 | New Brunswick.a | New Brunswick | Edmundston North SS 6397 | NB_6397_DSS | 69 | 1996 | 2100 | Biomass | biomass | 39 | 95% | 37.05 | 45% | 153.738 | 1 | [20 empty] | Presumed connected to Edmundston North Substation 6399
| Belledune | NB_BELL00_GEN | NB Power | Belledune | 47.8903 | -65.8727 | New Brunswick.a | New Brunswick | Belledune GS | NB_BELL_GSS | 138 | 1993 | 2041 | Coal | coal | 466 | 90% | 419.4 | 65% | 2653.404 | 1
| Millbank_01 | NB_MLBK01_GEN | NB Power | Millbank | 47.071 | -65.4541 | New Brunswick.a | New Brunswick | Millbank GS | NB_MLBK_GSS | 230 | 1991 | 2031 | Diesel_CT | diesel | 99 | 78% | 77.22 | 1% | 8.6724 | 4 | [20 empty] | Summer Capacity = 90 MW
| Millbank_02 | NB_MLBK02_GEN | NB Power | Millbank | 47.071 | -65.4541 | New Brunswick.a | New Brunswick | Millbank GS | NB_MLBK_GSS | 230 | 1991 | 2031 | Diesel_CT | diesel | 99 | 78% | 77.22 | 1% | 8.6724 | 4 | [20 empty] | Summer Capacity = 90 MW
| Millbank_03 | NB_MLBK03_GEN | NB Power | Millbank | 47.071 | -65.4541 | New Brunswick.a | New Brunswick | Millbank GS | NB_MLBK_GSS | 230 | 1991 | 2031 | Diesel_CT | diesel | 99 | 78% | 77.22 | 1% | 8.6724 | 4 | [20 empty] | Summer Capacity = 90 MW
| Millbank_04 | NB_MLBK04_GEN | NB Power | Millbank | 47.071 | -65.4541 | New Brunswick.a | New Brunswick | Millbank GS | NB_MLBK_GSS | 230 | 1991 | 2031 | Diesel_CT | diesel | 99 | 78% | 77.22 | 1% | 8.6724 | 4 | [20 empty] | Summer Capacity = 90 MW
| Point Lepreau Diesel | NB_PLPD00_GEN | NB Power | Point Lepreau | 45.0687 | -66.4543 | New Brunswick.a | New Brunswick | Point Lepreau GS | NB_PLPR_GSS | 345 | 1983 | 2100 | Diesel_CT | diesel | 5 | 78% | 3.9 | 1% | 0.438 | 1 | [20 empty] | Black start power
| Ste. Rose | NB_SROS00_GEN | NB Power | Ste. Rose | 47.6263 | -64.954 | New Brunswick.a | New Brunswick | Ste Rose GS | NB_SROS_GSS | 69 | 1991 | 2031 | Diesel_CT | diesel | 99 | 78% | 77.22 | 1% | 8.6724 | 1 | [20 empty] | Summer Capacity = 90 MW
| Beechwood_01 | NB_BCWD01_GEN | NB Power | Saint John River | 46.5428 | -67.6687 | New Brunswick.a | New Brunswick | Beechwood GS | NB_BCWD_GSS | 138 | 1957 | 2100 | Hydro_daily | hydro_daily | 36 | 95% | 34.2 | 46% | 145.0656 | 3
| Beechwood_02 | NB_BCWD02_GEN | NB Power | Saint John River | 46.5428 | -67.6687 | New Brunswick.a | New Brunswick | Beechwood GS | NB_BCWD_GSS | 138 | 1957 | 2100 | Hydro_daily | hydro_daily | 36 | 95% | 34.2 | 46% | 145.0656 | 3
| Beechwood_03 | NB_BCWD03_GEN | NB Power | Saint John River | 46.5428 | -67.6687 | New Brunswick.a | New Brunswick | Beechwood GS | NB_BCWD_GSS | 138 | 1957 | 2100 | Hydro_daily | hydro_daily | 41 | 95% | 38.95 | 46% | 165.2136 | 3
| Grand Falls_01 | NB_GRFS01_GEN | NB Power | Saint John River | 47.0429 | -67.7369 | New Brunswick.a | New Brunswick | Grand Falls GS | NB_GRFS_GSS | 138 | 1928 | 2100 | Hydro_daily | hydro_daily | 16 | 95% | 15.2 | 76% | 106.5216 | 4
| Grand Falls_02 | NB_GRFS02_GEN | NB Power | Saint John River | 47.0429 | -67.7369 | New Brunswick.a | New Brunswick | Grand Falls GS | NB_GRFS_GSS | 138 | 1928 | 2100 | Hydro_daily | hydro_daily | 16 | 95% | 15.2 | 76% | 106.5216 | 4
| Grand Falls_03 | NB_GRFS03_GEN | NB Power | Saint John River | 47.0429 | -67.7369 | New Brunswick.a | New Brunswick | Grand Falls GS | NB_GRFS_GSS | 138 | 1928 | 2100 | Hydro_daily | hydro_daily | 16 | 95% | 15.2 | 76% | 106.5216 | 4
| Grand Falls_04 | NB_GRFS04_GEN | NB Power | Saint John River | 47.0429 | -67.7369 | New Brunswick.a | New Brunswick | Grand Falls GS | NB_GRFS_GSS | 138 | 1928 | 2100 | Hydro_daily | hydro_daily | 16 | 95% | 15.2 | 79% | 110.7294 | 4
| Mactaquac_01 | NB_MTQC01_GEN | NB Power | Saint John River | 45.9551 | -66.8665 | New Brunswick.a | New Brunswick | Mactaquac GS | NB_MTQC_GSS | 345 | 1968 | 2100 | Hydro_daily | hydro_daily | 109 | 95% | 103.55 | 28% | 267.3552 | 6
| Mactaquac_02 | NB_MTQC02_GEN | NB Power | Saint John River | 45.9551 | -66.8665 | New Brunswick.a | New Brunswick | Mactaquac GS | NB_MTQC_GSS | 345 | 1968 | 2100 | Hydro_daily | hydro_daily | 109 | 95% | 103.55 | 28% | 267.3552 | 6
| Mactaquac_03 | NB_MTQC03_GEN | NB Power | Saint John River | 45.9551 | -66.8665 | New Brunswick.a | New Brunswick | Mactaquac GS | NB_MTQC_GSS | 345 | 1968 | 2100 | Hydro_daily | hydro_daily | 109 | 95% | 103.55 | 28% | 267.3552 | 6
| Mactaquac_04 | NB_MTQC04_GEN | NB Power | Saint John River | 45.9551 | -66.8665 | New Brunswick.a | New Brunswick | Mactaquac GS | NB_MTQC_GSS | 345 | 1968 | 2100 | Hydro_daily | hydro_daily | 115 | 95% | 109.25 | 28% | 282.072 | 6
| Mactaquac_05 | NB_MTQC05_GEN | NB Power | Saint John River | 45.9551 | -66.8665 | New Brunswick.a | New Brunswick | Mactaquac GS | NB_MTQC_GSS | 345 | 1968 | 2100 | Hydro_daily | hydro_daily | 112 | 95% | 106.4 | 28% | 274.7136 | 6
| Mactaquac_06 | NB_MTQC06_GEN | NB Power | Saint John River | 45.9551 | -66.8665 | New Brunswick.a | New Brunswick | Mactaquac GS | NB_MTQC_GSS | 345 | 1968 | 2100 | Hydro_daily | hydro_daily | 112 | 95% | 106.4 | 28% | 274.7136 | 6
| Tobique_01 | NB_TOBQ01_GEN | NB Power | Tobique River | 46.7801 | -67.6953 | New Brunswick.a | New Brunswick | Tobique GS | NB_TOBQ_GSS | 138 | 1953 | 2100 | Hydro_daily | hydro_daily | 10 | 95% | 9.5 | 55% | 48.18 | 2
| Tobique_02 | NB_TOBQ02_GEN | NB Power | Tobique River | 46.7801 | -67.6953 | New Brunswick.a | New Brunswick | Tobique GS | NB_TOBQ_GSS | 138 | 1953 | 2100 | Hydro_daily | hydro_daily | 10 | 95% | 9.5 | 55% | 48.18 | 2
| Madawaska | NB_MADA00_GEN | Edmundston Energy | Madawaska River | 47.3626 | -68.3236 | New Brunswick.a | New Brunswick | Edmundston North SS 6397 | NB_6397_DSS | 69 | 1917 | 2100 | Hydro_run | hydro_run | 3.8 | 95% | 3.61 | 60% | 19.9728 | 2 | [20 empty] | Presumed connected to Edmundston North Substation 6397
| Milltown | NB_MLTN00_GEN | NB Power | St. Croix River | 45.1755 | -67.2929 | New Brunswick.a | New Brunswick | Milltown GS | NB_MLTN_GSS | 69 | 1911 | 2100 | Hydro_run | hydro_run | 4 | 95% | 3.8 | 61% | 21.3744 | 1
| Nepisiguit Falls | NB_NPSG00_GEN | NB Power | Nepisiguit River | 47.4055 | -65.7918 | New Brunswick.a | New Brunswick | Nepisiguit Falls SS 6404 | NB_6404_DSS | 138 | 1921 | 2100 | Hydro_run | hydro_run | 11 | 95% | 10.45 | 58% | 55.8888 | 1
| Second Falls | NB_SFLS00_GEN | Edmundston Energy | Green River | 47.4684 | -68.2354 | New Brunswick.a | New Brunswick | Edmundston North SS 6397 | NB_6397_DSS | 69 | 1911 | 2100 | Hydro_run | hydro_run | 3 | 95% | 2.85 | 35% | 9.198 | 3 | [20 empty] | Presumed connected to Edmundston North Substation 6398
| Sisson | NB_SSON00_GEN | NB Power | Tobique River | 47.266 | -67.2434 | New Brunswick.a | New Brunswick | Sisson GS | NB_SSON_GSS | 69 | 1965 | 2100 | Hydro_run | hydro_run | 9 | 95% | 8.55 | 22% | 17.3448 | 1
| St. George | NB_SGRG00_GEN | St. George Power | Magaguadavic River | 45.1283 | -66.8279 | New Brunswick.a | New Brunswick | St. George GS | NB_SGRG_GSS | 69 | 1900 | 2100 | Hydro_run | hydro_run | 15 | 95% | 14.25 | 35% | 45.99 | 2 | [19 empty] | https://www.stgeorgepower.ca | Presumed connected to St. George Substation 6145
| Tinker | NB_TINK00_GEN | Algonquin Power | Aroostook River | 46.8097 | -67.7665 | New Brunswick.a | New Brunswick | Tinker GS | NB_TNK_GSS | 138 | 1923 | 2100 | Hydro_run | hydro_run | 35 | 95% | 33.25 | 35% | 107.31 | 5 | [20 empty] | Power is sold to town of Andover-Perth until 2031
| Bayside | NB_BAYS00_GEN | NB Power | Saint John | 47.9927 | -66.7225 | New Brunswick.a | New Brunswick | Bayside GS | NB_BAYS_GSS | 138 | 1999 | 2027 | NG_CC | gasCC | 290 | 73% | 211.7 | 20% | 508.08 | 1 | [20 empty] | Formerly called "Courtenay Bay"
| Grandview_01 | NB_GRDV01_GEN | TransCanada Energy | Saint John | 45.2842 | -66.0094 | New Brunswick.a | New Brunswick | Grandview GS | NB_GRDV_GSS | 138 | 2004 | 2025 | NG_CG | gasCC | 49 | 73% | 35.77 | 20% | 85.848 | 2 | [19 empty] | TransCanada Energy. (2019). Grandview Cogeneration Plant. | Summer Capacity = 43 MW; presumed connected at Irving Refinery 138 Terminal
| Grandview_02 | NB_GRDV02_GEN | TransCanada Energy | Saint John | 45.2842 | -66.0094 | New Brunswick.a | New Brunswick | Grandview GS | NB_GRDV_GSS | 138 | 2004 | 2025 | NG_CG | gasCC | 49 | 73% | 35.77 | 20% | 85.848 | 2 | [19 empty] | TransCanada Energy. (2019). Grandview Cogeneration Plant. | Summer Capacity = 43 MW; presumed connected at Irving Refinery 138 Terminal
| Grand Manan | NB_GMAN00_GEN | NB Power | Grand Manan | 44.7224 | -66.8239 | New Brunswick.a | New Brunswick | Grand Manan GS | NB_GMAN_GSS | 69 | 1989 | 2026 | NG_CT | gasSC | 28 | 78% | 21.84 | 1% | 2.4528 | 1
| CONTRACTED - NBPower-MECL | PP_NBPE100_GEN | NB Power | NB-PEI Border | 46.2051 | -63.7575 | New Brunswick.a | New Brunswick | IPT Richmond Cove | PP_NBPE1_IPT | 345 | 1983 | 2100 | Nuclear | nuclear | -30 | 90% | -27 | 90% | -236.52 | 1 | [20 empty] | 30 MW from the Point Lepreau Generating Station is committed to Maritime Electric Company Limited (MECL) until the end of 2024, and is presumed renewed beyond 2050.
| Point Lepreau Nuclear | NB_PLPR00_GEN | NB Power | Point Lepreau | 45.0687 | -66.4543 | New Brunswick.a | New Brunswick | Point Lepreau GS | NB_PLPR_GSS | 345 | 1983 | 2100 | Nuclear | nuclear | 660 | 90% | 594 | 90% | 5203.44 | 1
| Coleson Cove_01 | NB_CLCV01_GEN | NB Power | Saint John | 45.154 | -66.2019 | New Brunswick.a | New Brunswick | Coleson Cove GS | NB_CLCV_GSS | 345 | 1976 | 2041 | Oil_ST | diesel | 324 | 73% | 236.52 | 4% | 113.5296 | 3
| Coleson Cove_02 | NB_CLCV02_GEN | NB Power | Saint John | 45.154 | -66.2019 | New Brunswick.a | New Brunswick | Coleson Cove GS | NB_CLCV_GSS | 345 | 1976 | 2041 | Oil_ST | diesel | 324 | 73% | 236.52 | 4% | 113.5296 | 3
| Coleson Cove_03 | NB_CLCV03_GEN | NB Power | Saint John | 45.154 | -66.2019 | New Brunswick.a | New Brunswick | Coleson Cove GS | NB_CLCV_GSS | 345 | 1976 | 2041 | Oil_ST | diesel | 324 | 73% | 236.52 | 4% | 113.5296 | 3
| Caribou Mountain | NB_CRBO00_GEN | GDF Suez | Central NB | 47.5071 | -66.4135 | New Brunswick.a | New Brunswick | Caribou GS | NB_CRBO_GSS | 138 | 2009 | 2100 | Wind_Onshore | wind | 99 | 21% | 20.79 | 35.2% | 305.2685 | n/a
| Kent Hills | NB_KNTH00_GEN | Transalta | Riverside-Albert | 45.8194 | -64.8894 | New Brunswick.a | New Brunswick | Kent Hills Wind GS | NB_KNTH_GSS | 138 | 2010 | 2100 | Wind_Onshore | wind | 167 | 21% | 35.07 | 35.2% | 514.9478 | n/a
| Lamèque | NB_LMEQ00_GEN | Acciona | Lamèque Island | 47.8494 | -64.6187 | New Brunswick.a | New Brunswick | Lameque GS | NB_LMEQ_GSS | 69 | 2011 | 2100 | Wind_Onshore | wind | 45 | 21% | 9.45 | 35.2% | 138.7584 | n/a
| Wisokolamson | NB_WSKL00_GEN | Wisokolamson Energy | Riverside-Albert | 45.6747 | -64.831 | New Brunswick.a | New Brunswick | Kent Hills Wind GS | NB_KNTH_GSS | 138 | 2020 | 2100 | Wind_Onshore | wind | 18 | 21% | 3.78 | 35.2% | 55.5034 | n/a
Specific Notes:
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Unless noted otherwise, the wind generating stations are presumed to be connected to the nearest 69 kV substation
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit Hydro_run facilities treated as single-unit facilities
RH Additions, Comments and TODOs
Remote projects are not included in this list.
See calculations sheets for sources of values.
Sources

## Storage
NB | EXISTING STORAGE | [12 empty] | DESIGN | [7 empty] | OPERATIONS
| Project Name | Storage Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Technology | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Days | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | kV | [5 empty] | (MW) | (MWh) | (Hours) |  | ($M) | (hours) | (hours) | (%) | (days/y) | ($/year) | ($/MWh)
Specific Notes:

## HydroExisting
NB | EXISTING STORAGE HYDROELECTRIC | [24 empty] | RESERVOIR
| Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Renewal Year | Dam Type | Penstock | Rated Head | Maximum Head | Minimum Head | Operating Flow (Facility) | Rated Discharge (Unit) | Rated Discharge (Facility) | Upstream Reservoir Area | Upstream Reservoir Storage | Turbine Type | Station Flow | Upper Storage Name | Upper Storage Level | Lower Storage Name | Lower Storage Level | Upper Storage Name | Minimum Level | Maximum Level | Initial Level | Low Reference Level | High Reference Level | Low Volume | High Volume | Live Storage | M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10 | M11 | M12 | Other References | Notes
|  |  | (MW) |  | (MW) |  | (GWh/year) |  |  |  | (m) | (m) | (m) | (m) | (m3/s) | (m3/s) | (m3/s) | (km2) | (hours) |  | (WSC#) |  | (WSC#) |  | (WSC#) |  | (m) | (m) | (m) | (m) | (m) | (m3) | (m3) | (m3) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s)
| Mactaquac | Hydro_daily | 666 | 95% | 632.7 | 28% | 1633.5648 | 6 | [12 empty] | 01AK004/01AK010 | Saint John River |  | Saint John River
| Beechwood | Hydro_daily | 113 | 95% | 107.35 | 46% | 455.3448 | 3 | [12 empty] | 01AJ012 | Saint John River |  | Saint John River
| Grand Falls | Hydro_daily | 64 | 95% | 60.8 | 76% | 426.0864 | 4 | [12 empty] | 01AF002 | Saint John River | 01AD004 | Saint John River | 01AF002
| Tobique | Hydro_daily | 20 | 95% | 19 | 55% | 96.36 | 2 | [12 empty] | 01AH004 | Tobique River |  | Saint John River
General Notes:
Hydroelectric generation type has been estimated based on available information concerning operations, reservoir size and operations, facility location and design flows.
The WSC# refers to the Water Survey of Canada Hydrometric station

## HydroRenewals
NB | HYDROELECTRIC RENEWAL |  | Existing Design | [7 empty] | Renewal Design | [14 empty] | Costs | 1.77% | 1.05 |  |  |  | 7% | 70
| Existing Project Name | Owner | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Renewal Project Name | Renewal Project Code | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Additional Annual Energy | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed Cost Existing Project | Fixed Cost Renewed Project | Fixed O&M | Variable Costs | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
|  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) | [5 empty] | dd.dddd | dd.dddd |  |  |  |  | (km) |  |  | (MW) | (MW) | (GWh/year) | ($M) | ($M) | ($M) | ($2013M) | ($2018M) | ($M) | ($M) | ($M/year) | ($/kW-year) | ($/year) | ($/year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
| Grand Falls | NB Power | Hydro_daily | 64 | 95% | 60.8 | 76% | 426.0864 | 4 | 1931 | Grand Falls_05 | RN_GFL | St. John River | 47.0429 | -67.7369 | New Brunswick.a | Grand Falls GS | NB_GRFS_GEN | 138 | 0 | Hydro_daily | hydro_daily | 100 | 100 | 300 |  |  |  | 491.053 | 533.4403 | 13.5079 | 546.9482 | 38.6252 | 386.2522 | 3133770.446 | 4822089.1448 | 16883.187 | 2.4115 | 0 | 2.4115 |  |  | 3 | 5
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroGreenfield
NB | HYDROELECTRIC GREENFIELD | [10 empty] | DESIGN | [5 empty] | COSTS | 1.77% | 1.05 |  |  |  | 7% | 70
| Project Name | Project Short Name | Owner | Location | Latitude | Longitude | Balancing Area | Distance to Market Grid | Connecting Node Name | Connecting Node Code | Substation Voltage | Generation Type | Generation Type - CREST EMI | Installed Capacity | Dependable Capacity | Average Annual Energy | # of units | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed O&M | Variable Costs | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
[11 empty] | (kV) |  |  | (MW) | (MW) | (GWh/year) |  | ($2018M) | ($2018M) | ($2018M) | ($2013M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($M/MW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
| High Narrows | GF_HGN | NB Power | Bathurst | 47.365 | -65.8905 | New Brunswick.a | 25 | Nepisiguit Falls Substation 6404 | NB_6404_SUB | 138 | hydro_run | hydro_run | 40 | 40 | 148 |  |  |  |  | 301.446 | 327.4666 | 48.5056 | 375.9722 | 26.551 | 663.7745 | 63171.3615 | 3.4254 | 0 | 3.4254 |  |  | 4 | 6
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to didtance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume Hydro_daily and Hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroPS
NB | HYDROELECTRIC PUMPED STORAGE | [16 empty] | Existing Facility | [8 empty] | Reservoir Design | [14 empty] | Costs |  | 2% | 4% |  |  | 5% | 70
| Pumped Storage Project | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Installed Capacity | Dependable Capacity | Annual Generation | Annual Pumping | Existing Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Start Year | Water Type | Cycle Type | Storage Type | Reservoir Storage | Storage Requirement | Gross Head | Penstock | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping) | Turbine Type | Pump Type | Generation Duration to Empty Reservoir | Pumping Duration to Fill Reservoir | Total Footprint | Overnight Capital Cost | Overnight Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Annual Fixed O&M | Variable Cost | Water Rentals | Annualized Variable O&M | Levelized Cost of Capacity | Construction Time | Development Time | Notes
[5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) | (GWh/y) | (GWh/y) |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) | [5 empty] | (m3) | (MWh) | (m) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($M) | ($2021M) | ($2021M) | ($2021M) | ($2021M) | ($2021M) | ($2021M) | ($2021M/year) | ($/kW-year) | ($/kW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2021/kW-year) | (years) | (years)
| Grand Falls Pumped Storage | NB_GFL00_STO | NB Power | Saint John River | 47.043 | -67.7367 | New Brunswick.a | Grand Falls GS | NB_GRFS_GSS | 138 | 0 | hydro_pump | hydro_pump | 100 | 100 | 292 | 365 | Grand Falls | Hydro_daily | 64 | 95% | 60.8 | 76% | 426.0864 | 4 | 1931 | Fresh | Open | Reservoir to Reservoir | [12 empty] | 600 | 629.7638 | 12.5953 | 65.5462 | 707.9053 | 40.9163 | 748.8216 | 38.7134 | 387.1344 | 36.0201 | 2.4115 | 0 | 7.0417 | 430.1962 | 4 | 6 | $690M total in-service project cost in $2017
General Notes:
All projects assumed to be connected to the provincial or territorial transmission system
Assume installed capacity is all dependable capacity, though this should be verified with new studies.
Annual generation based on 8 hours per day generation, unless otherwise provided
Annual pumping estimated at 125% of annual generation, unless otherwise provided
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 2% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate of 1.77%
Assume IDC rate of 4% real
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume pumped storage facilities have an economic life of 70 years
Assume a discount rate of 5% real
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset
Water Rental assumed to be $0/MWh (i.e., not applied to pumped storage)

## Transmission
NB | EXISTING TRANSMISSION
| Circuit ID | Owner | Planning Region | Number of Circuits | Current | Length | Length | Voltage | Reactance | Smax | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes | Count
[5 empty] | (ad/dc) | (km) | (miles) | (kV) | (ohm) |  | (A) | (A) | (MVA) | (MVA) |  | (MW) | (MW)
| L0033 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Aberdeen St SS 6100 | NB_6100_DSS | Carleton St SS 6150 | NB_6150_DSS |  |  | 120
| L0012 | NB Power | New Brunswick | 1 | ac | 28 | 17 | 69 | 10.76 | 3 | [5 empty] | 36 | 39 | Allardville SS 6420 | NB_6420_DSS | Junction 0104 | NB_0104_JCT |  |  | 42
| L0012 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Allardville SWS | NB_ALDV_SWS | Allardville SS 6420 | NB_6420_DSS |  |  | 41
| L0013 | NB Power | New Brunswick | 1 | ac | 35 | 22 | 69 | 13.45 | 3 | [5 empty] | 36 | 39 | Allardville SWS | NB_ALDV_SWS | Hacheyville SS 6415 | NB_6415_DSS |  |  | 43
| L0003 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Allison SS 6520 | NB_6520_DSS | Junction 0015 | NB_0015_JCT |  |  | 6
| L0019 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Baig Blvd SS 6507 | NB_6507_DSS | Moncton TS | NB_MCTN_TSS |  |  | 74
| L0079 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 69 | 4.6114 | 3 | [5 empty] | 36 | 39 | Barkers Pt. SS 6125 | NB_6125_DSS | Doak SWS 4119 | NB_4119_SWS |  |  | 195
| L0012 | NB Power | New Brunswick | 1 | ac | 16 | 10 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Bathurst TS/SS 6432 | NB_6432_DSS | Allardville SWS | NB_ALDV_SWS |  |  | 40
| L1152 | NB Power | New Brunswick | 1 | ac | 56 | 35 | 138 | 24.28 | 3 | [5 empty] | 141 | 156 | Bathurst TS/SS 6432 | NB_6432_DSS | Caraquet TS | NB_CRQT_TSS |  |  | 325
| L2131 | NB Power | New Brunswick | 1 | ac | 64 | 40 | 230 | 30.72 | 3 | [5 empty] | 402 | 435 | Bathurst TS/SS 6432 | NB_6432_DSS | Highbank TS | NB_HBNK_TSS |  |  | 388
| L0062 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Bathurst TS/SS 6432 | NB_6432_DSS | Junction 0062 | NB_0062_JCT |  |  | 165
| L1137 | NB Power | New Brunswick | 1 | ac | 27 | 16 | 138 | 11.7064 | 3 | [5 empty] | 141 | 156 | Bathurst TS/SS 6432 | NB_6432_DSS | Junction 1195 | NB_1195_JCT |  |  | 303
| L1106 | NB Power | New Brunswick | 1 | ac | 73 | 45 | 138 | 31.6507 | 3 | [5 empty] | 141 | 156 | Bathurst TS/SS 6432 | NB_6432_DSS | Millbank GS | NB_MLBK_GSS |  |  | 268
| L3017 | NB Power | New Brunswick | 1 | ac | 225 | 139 | 345 | 99.8542 | 1.637 | [5 empty] | 532.0237 | 695.7233 | Bathurst TS/SS 6432 | NB_6432_DSS | Salisbury TS | NB_SLBY_TSS |  | Also called L3019 | 407
| L0063 | NB Power | New Brunswick | 1 | ac | 38 | 23 | 69 | 14.6029 | 3 | [5 empty] | 36 | 39 | Bathurst TS/SS 6432 | NB_6432_DSS | St. Leolin SS 6435 | NB_6435_DSS |  |  | 167
| L0025 | NB Power | New Brunswick | 1 | ac | 6 | 3 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Bathurst West SWS/SS 4400 | NB_4400_DSS | Junction 0126 | NB_0126_JCT |  |  | 106
| L0095 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Bathurst West SWS/SS 4401 | NB_4400_DSS | West Bathurst SS 6418 | NB_6418_DSS |  |  | 209
| L0105 | NB Power | New Brunswick | 1 | ac | 22 | 14 | 69 | 8.4543 | 3 | [5 empty] | 36 | 39 | Bay du Vin SS 6410 | NB_6410_DSS | Baie Ste. Anne SS 6429 | NB_6429_DSS |  |  | 216
| L0042 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 69 | 4.6114 | 3 | [5 empty] | 36 | 39 | Bayside Drive SS 5299 | NB_5299_DSS | Canaport SS 5204 | NB_5204_ISS |  |  | 142
| L0042 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 69 | 0.11529 | 3 | [5 empty] | 36 | 39 | Bayside GS | NB_BAYS_GSS | Bayside Drive SS 5299 | NB_5299_DSS |  |  | 141
| L1147 | NB Power | New Brunswick | 1 | ac | 45 | 28 | 138 | 19.5107 | 3 | [5 empty] | 141 | 156 | Bayside GS | NB_BAYS_GSS | Coleson Cove GS | NB_CLCV_GSS |  |  | 314
| L1165 | NB Power | New Brunswick | 1 | ac | 45 | 28 | 138 | 19.5107 | 3 | [5 empty] | 141 | 156 | Bayside GS | NB_BAYS_GSS | Coleson Cove GS | NB_CLCV_GSS |  |  | 346
| L0034 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Bayside GS | NB_BAYS_GSS | Cranston TS | NB_CRAN_TSS |  |  | 123
| L0052 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Bayside GS | NB_BAYS_GSS | Crown Street SS 5293 | NB_5293_DSS |  |  | 155
| L1109 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Bayside GS | NB_BAYS_GSS | Irving Refinery 138 TS | NB_IRV138_TSS |  |  | 271
| L0035 | NB Power | New Brunswick | 1 | ac | 4.5 | 2.8 | 69 | 1.7293 | 3 | [5 empty] | 36 | 39 | Bayside GS | NB_BAYS_GSS | Irving Refinery 69 TS | NB_IRV69_TSS |  |  | 124
| L1122 | NB Power | New Brunswick | 1 | ac | 1 | 0.6 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Bayside GS | NB_BAYS_GSS | Rothesay Paper SS 5295 | NB_5295_ISS |  |  | 291
| L0016 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 69 | 4.6114 | 3 | [5 empty] | 36 | 39 | Bayside SS 6222 | NB_6222_ISS | Oak Bay TS | NB_OKBY_TSS |  |  | 58
| L1176 | NB Power / Emera Maine | New Brunswick | 1 | ac | 11 | 7 | 138 | 4.7693 | 3 | [5 empty] | 75 | 75 | Beechwood GS | NB_BCWD_GSS | INT Beechwood | XX_NBUS4_INT |  |  | 357
| L1125 | NB Power | New Brunswick | 1 | ac | 65 | 40 | 138 | 28.1821 | 3 | [5 empty] | 141 | 156 | Beechwood GS | NB_BCWD_GSS | Junction 1172 | NB_1172_JCT |  |  | 293
| L1126 | NB Power | New Brunswick | 1 | ac | 37 | 23 | 138 | 16.0421 | 3 | [5 empty] | 141 | 156 | Beechwood GS | NB_BCWD_GSS | Junction 1205 | NB_1205_JCT |  |  | 295
| L0141 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 69 | 0.11529 | 3 | [5 empty] | 36 | 39 | Beechwood SS 6391 | NB_6391_DSS | Beechwood GS | NB_BCWD_GSS |  |  | 255
| L1213 | NB Power | New Brunswick | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Belledune Fert. SS 5406 | NB_5406_ISS | Belledune Smelter SS 5404 | NB_5404_ISS |  |  | 382
| L1213 | NB Power | New Brunswick | 1 | ac | 1 | 0.61728 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Belledune SS 6439 | NB_6439_DSS | Belledune Fert. SS 5406 | NB_5406_ISS |  |  | 404
| L1201 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Belledune SS 6439 | NB_6439_DSS | Belledune GS | NB_BELL_GSS |  |  | 378
| L3018 | NB Power | New Brunswick | 1 | ac | 49 | 30 | 345 | 21.746 | 3 | [5 empty] | 975 | 1275 | Belledune TS | NB_BELL_TSS | Bathurst TS/SS 6432 | NB_6432_DSS |  |  | 408
| L3022 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 345 | 4.438 | 3 | [5 empty] | 975 | 1275 | Belledune TS | NB_BELL_TSS | Belledune GS | NB_BELL_GSS |  |  | 409
| L0063 | NB Power | New Brunswick | 1 | ac | 11 | 7 | 69 | 4.2271 | 3 | [5 empty] | 36 | 39 | Bertrand SS 6421 | NB_6421_DSS | Caraquet SS 6401 | NB_6401_DSS |  |  | 169
| L0039 | NB Power | New Brunswick | 1 | ac | 24 | 15 | 69 | 9.2229 | 3 | [5 empty] | 36 | 39 | Boiestown SS 6117 | NB_6117_DSS | Doaktown SS 6419 | NB_6419_DSS |  |  | 135
| L0002 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Brookville TS/SS 5266 | NB_5266_DSS | Cranston TS | NB_CRAN_TSS |  |  | 2
| L0009 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Brown Rd. SWS | NB_BRWN_SWS | Nelson SS 6442 | NB_6442_DSS |  |  | 29
| L0076 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Brown Rd. SWS | NB_BRWN_SWS | Newcastle TS | NB_NWCS_TSS |  |  | 192
| L0018 | NB Power | New Brunswick | 1 | ac | 19 | 12 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Burpee Brook SS 6152 | NB_6152_DSS | Marysville TS | NB_MRYV_TSS |  |  | 70
| L0075 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Burton SS 6112 | NB_6112_DSS | Camp Gagetown SS 5191 | NB_5191_DSS |  |  | 189
| L1157 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 138 | 0.13007 | 3 | [5 empty] | 141 | 156 | Caledonia Park SS 6522 | NB_6522_DSS | Junction 1179 | NB_1179_JCT |  |  | 336
| L1156 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Caledonia Park SS 6522 | NB_6522_DSS | Ryan Rd SS 6525 | NB_6525_DSS |  |  | 332
| L0045 | NB Power | New Brunswick | 1 | ac | 32 | 20 | 69 | 12.2971 | 3 | [5 empty] | 36 | 39 | Campobello Island SS 6132 | NB_6132_DSS | Grand Manan - Grand Harbour SS 6131 | NB_6131_DSS |  |  | 148
| L0006 | NB Power | New Brunswick | 1 | ac | 26 | 16 | 69 | 9.9914 | 3 | [5 empty] | 36 | 39 | Canaan Forks SS 6202 | NB_6202_DSS | Coal Creek SS 6195 | NB_6195_DSS |  |  | 16
| L0111 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Caraquet TS | NB_CRQT_TSS | Caraquet SS 6401 | NB_6401_DSS |  |  | 221
| L0133 | NB Power | New Brunswick | 1 | ac | 18 | 11 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | Caraquet TS | NB_CRQT_TSS | Junction 0133 | NB_0133_JCT |  |  | 241
| L0136 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Caraquet TS | NB_CRQT_TSS | Lower Caraquet SS 6437 | NB_6437_DSS |  |  | 245
| L1158 | NB Power | New Brunswick | 1 | ac | 7 | 4 | 69 | 2.69 | 3 | [5 empty] | 36 | 39 | Caraquet TS | NB_CRQT_TSS | Ste Rose GS | NB_SROS_GSS |  |  | 339
| L1195 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Caribou Mining SS 5497 | NB_5497_ISS | Caribou GS | NB_CRBO_GSS |  |  | 372
| L0118 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | CBC Sackville SS 6541 | NB_6541_DSS | Aulac SS 6516 | NB_6516_DSS |  |  | 230
| L0010 | NB Power | New Brunswick | 1 | ac | 31 | 19 | 69 | 11.9129 | 3 | [5 empty] | 36 | 39 | Clairville SS 6544 | NB_6544_DSS | Lutz Mtn. SS 6510 | NB_6510_DSS |  |  | 38
| L0014 | NB Power | New Brunswick | 1 | ac | 22 | 13 | 69 | 8.4543 | 3 | [5 empty] | 36 | 39 | Clairville SS 6544 | NB_6544_DSS | St. Mary's SS 6505 | NB_6505_DSS |  |  | 48
| L0006 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 69 | 4.9957 | 3 | [5 empty] | 36 | 39 | Coal Creek SS 6195 | NB_6195_DSS | Grand Lake TS | NB_GRLK_TSS |  | Grand Lake GS decommissioned | 17
| L0008 | NB Power | New Brunswick | 1 | ac | 21 | 13 | 69 | 8.07 | 3 | [5 empty] | 36 | 39 | Coal Creek SS 6195 | NB_6195_DSS | Junction 0134 | NB_0134_JCT |  |  | 21
| L1156 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Cocagne SS 6521 | NB_6521_DSS | Scoudouc Ind. SS 6540 | NB_6540_ISS |  |  | 330
| L0008 | NB Power | New Brunswick | 1 | ac | 30 | 19 | 69 | 11.5286 | 3 | [5 empty] | 36 | 39 | Coles Island SS 6536 | NB_6536_DSS | Springfield SS 6200 | NB_6200_DSS |  |  | 23
| L1104 | NB Power | New Brunswick | 1 | ac | 72 | 44 | 138 | 31.2171 | 3 | [5 empty] | 141 | 156 | Coleson Cove GS | NB_CLCV_GSS | Junction 1121 | NB_1121_JCT |  |  | 260
| L1116 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 138 | 4.3357 | 3 | [5 empty] | 141 | 156 | Coleson Cove GS | NB_CLCV_GSS | Lancaster TS | NB_LNCT_TSS |  |  | 284
| L3002 | NB Power | New Brunswick | 1 | ac | 117 | 72 | 345 | 51.9242 | 2.5261 | [5 empty] | 820.9911 | 1073.6037 | Coleson Cove GS | NB_CLCV_GSS | Mactaquac GS | NB_MTQC_GSS |  |  | 392
| L1193 | NB Power | New Brunswick | 1 | ac | 65 | 40 | 138 | 28.1821 | 3 | [5 empty] | 141 | 156 | Coleson Cove GS | NB_CLCV_GSS | Pennfield TS | NB_PNFD_TSS |  |  | 371
| L3009 | NB Power | New Brunswick | 1 | ac | 29 | 18 | 345 | 12.8701 | 3 | [5 empty] | 975 | 1275 | Coleson Cove GS | NB_CLCV_GSS | Point Lepreau GS | NB_PLPR_GSS |  |  | 399
| L0029 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Commercial St SS 6503 | NB_6503_DSS | Moncton TS | NB_MCTN_TSS |  |  | 119
| L0038 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Connell St. SS 6199 | NB_6199_DSS | Woodstock South SS 6121 | NB_6121_DSS |  |  | 130
| L0002 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Cranston TS | NB_CRAN_TSS | Junction 0068 | NB_0068_JCT |  |  | 3
| L0052 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Crown Street SS 5293 | NB_5293_DSS | Union Street SS 5202 | NB_5202_DSS |  |  | 156
| L0060 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Darlington SS 6498 | NB_6498_DSS | Junction 0071 | NB_0071_JCT |  |  | 164
| L0025 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 69 | 7.6857 | 3 | [5 empty] | 36 | 39 | Darlington SS 6498 | NB_6498_DSS | Junction 0129 | NB_0129_JCT |  |  | 101
| L0045 | NB Power | New Brunswick | 1 | ac | 11 | 7 | 69 | 4.2271 | 3 | [5 empty] | 36 | 39 | Deer Island SS 6293 | NB_6293_DSS | Campobello Island SS 6132 | NB_6132_DSS |  |  | 147
| L0041 | NB Power | New Brunswick | 1 | ac | 11 | 7 | 69 | 4.2271 | 3 | [5 empty] | 36 | 39 | Dever Road SS 5263 | NB_5263_DSS | Millidgeville SS 5213 | NB_5213_DSS |  |  | 139
| L0075 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Doak SWS 4119 | NB_4119_SWS | Burton SS 6112 | NB_6112_DSS |  |  | 190
| L0074 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 69 | 4.6114 | 3 | [5 empty] | 36 | 39 | Doak SWS 4119 | NB_4119_SWS | Rusagonis SS 6141 | NB_6141_DSS |  |  | 187
| L0033 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 69 | 0.11529 | 3 | [5 empty] | 36 | 39 | Doak SWS 4119 | NB_4119_SWS | Vanier SS 6118 | NB_6118_DSS |  |  | 121
| L0029 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Drummond St SS 6596 | NB_6596_DSS | Junction 0103 | NB_0103_JCT |  |  | 117
| L0010 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | East Chatham SS 6440 | NB_6440_DSS | Junction 0105 | NB_0105_JCT |  |  | 34
| L0070 | NB Power | New Brunswick | 1 | ac | 15 | 9 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Edmundston North SS 6397 | NB_6397_DSS | Junction 0137 | NB_0137_JCT |  |  | 180
| L3113 | NB Power / HQT | New Brunswick | 1 | dc | 25 | 15 | 345 | 11.0949 | 3 | [5 empty] | 975 | 1275 | Edmundston TS | NB_EDMN_TSS | IPT Madawaska | PP_QBNB1_IPT |  |  | 410
| L3114 | NB Power / HQT | New Brunswick | 1 | dc | 25 | 15 | 345 | 11.0949 | 3 | [5 empty] | 975 | 1275 | Edmundston TS | NB_EDMN_TSS | IPT Madawaska | PP_QBNB1_IPT |  |  | 411
| L2103 | NB Power | New Brunswick | 1 | ac | 86 | 53 | 230 | 41.28 | 3 | [5 empty] | 402 | 435 | Eel River TS | NB_EELR_TSS | Bathurst TS/SS 6432 | NB_6432_DSS |  |  | 385
| L3008 | NB Power | New Brunswick | 1 | ac | 47 | 29 | 345 | 20.8584 | 3 | [5 empty] | 975 | 1275 | Eel River TS | NB_EELR_TSS | Belledune TS | NB_BELL_TSS |  |  | 398
| L0025 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Eel River TS | NB_EELR_TSS | Darlington SS 6498 | NB_6498_DSS |  |  | 100
| L0060 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Eel River TS | NB_EELR_TSS | Darlington SS 6498 | NB_6498_DSS |  |  | 163
| L2101 | NB Power / HQT | New Brunswick | 1 | dc | 38 | 23 | 230 | 18.24 | 3 | [5 empty] | 402 | 435 | Eel River TS | NB_EELR_TSS | IPT Matapédia | PP_QBNB2_IPT |  |  | 383
| L2102 | NB Power / HQT | New Brunswick | 1 | dc | 38 | 23 | 230 | 18.24 | 3 | [5 empty] | 402 | 435 | Eel River TS | NB_EELR_TSS | IPT Matapédia | PP_QBNB2_IPT |  |  | 384
| L0091 | NB Power | New Brunswick | 1 | ac | 19 | 12 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Eel River TS | NB_EELR_TSS | Junction 0092 | NB_0092_JCT |  |  | 203
| L1115 | NB Power | New Brunswick | 1 | ac | 47 | 29 | 138 | 20.3779 | 3 | [5 empty] | 141 | 156 | Eel River TS | NB_EELR_TSS | Junction 1128 | NB_1128_JCT |  |  | 281
| L0048 | NB Power | New Brunswick | 1 | ac | 33 | 20 | 69 | 12.6814 | 3 | [5 empty] | 36 | 39 | Florenceville SS 6114 | NB_6114_DSS | Juniper SS 6107 | NB_6107_DSS |  |  | 151
| L0076 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Gordon Road SS 6412 | NB_6412_DSS | Brown Rd. SWS | NB_BRWN_SWS |  |  | 191
| L0010 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Gordon Road SS 6412 | NB_6412_DSS | East Chatham SS 6440 | NB_6440_DSS |  | Assumed connected to Gorden Road when Chatham Plant closed | 33
| L0009 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Gordon Road SS 6412 | NB_6412_DSS | Junction 0099 | NB_0099_JCT |  |  | 27
| L0020 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Grafton SS 6105 | NB_6105_DSS | Junction 0038 | NB_0038_JCT |  |  | 79
| L0123 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Grand Bay SS 6528 | NB_6528_DSS | Westfield SS 6298 | NB_6298_DSS |  |  | 234
| L0058 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Grand Falls GS | NB_GRFS_GSS | Grand Falls South SS 6395 | NB_6395_DSS |  |  | 158
| L1175 | NB Power | New Brunswick | 1 | ac | 1 | 0.6 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Grand Falls GS | NB_GRFS_GSS | Junction 1162 | NB_1162_JCT |  |  | 355
| L1111 | NB Power | New Brunswick | 1 | ac | 9 | 5 | 138 | 3.9021 | 3 | [5 empty] | 141 | 156 | Grand Falls GS | NB_GRFS_GSS | Ortonville SWS | NB_ORTN_SWS |  |  | 274
| L0022 | NB Power | New Brunswick | 1 | ac | 0.1 | 0.1 | 69 | 0.038429 | 3 | [5 empty] | 36 | 39 | Grand Falls North SS 6333 | NB_6333_DSS | Junction 0138 | NB_0138_JCT |  |  | 88
| L0058 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Grand Falls South SS 6395 | NB_6395_DSS | Junction 0022 | NB_0022_JCT |  |  | 159
| L0018 | NB Power | New Brunswick | 1 | ac | 18 | 11 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | Grand Lake SS 6143 | NB_6143_DSS | Ripples SS 6142 | NB_6142_DSS |  |  | 68
| L0008 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 69 | 4.9957 | 3 | [5 empty] | 36 | 39 | Grand Lake TS | NB_GRLK_TSS | Coal Creek SS 6195 | NB_6195_DSS |  |  | 20
| L0018 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Grand Lake TS | NB_GRLK_TSS | Grand Lake SS 6143 | NB_6143_DSS |  |  | 67
| L1102 | NB Power | New Brunswick | 1 | ac | 35 | 22 | 138 | 15.175 | 3 | [5 empty] | 141 | 156 | Grand Lake TS | NB_GRLK_TSS | Marysville TS | NB_MRYV_TSS |  |  | 257
| L0007 | NB Power | New Brunswick | 1 | ac | 4 | 3 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Grand Lake TS | NB_GRLK_TSS | Minto SS 6120 | NB_6120_DSS |  |  | 18
| L0045E | NB Power | New Brunswick | 1 | ac | 4 | 3 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Grand Manan - Grand Harbour SS 6131 | NB_6131_DSS | Grand Manan GS | NB_GMAN_GSS |  |  | 149
| L0022 | NB Power | New Brunswick | 1 | ac | 22 | 14 | 69 | 8.4543 | 3 | [5 empty] | 36 | 39 | Green River SS 6144 | NB_6144_DSS | Junction 0115 | NB_0115_JCT |  |  | 85
| L0013 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 69 | 4.9957 | 3 | [5 empty] | 36 | 39 | Hacheyville SS 6415 | NB_6415_DSS | Six Roads SS 6425 | NB_6425_DSS |  |  | 44
| L0020 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 69 | 4.9957 | 3 | [5 empty] | 36 | 39 | Hainesville SS 6133 | NB_6133_DSS | Millville TS | NB_MIVL_TSS |  |  | 76
| L0003 | NB Power | New Brunswick | 1 | ac | 19 | 11 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Hampton 69 SS 6268 | NB_6268_DSS | Rothesay SS 6267 | NB_6267_DSS |  |  | 12
| L0008 | NB Power | New Brunswick | 1 | ac | 19 | 11 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Hampton 69 SS 6268 | NB_6268_DSS | Rothesay SS 6267 | NB_6267_DSS |  |  | 25
| L0010 | NB Power | New Brunswick | 1 | ac | 15 | 9 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Harcourt SS 6504 | NB_6504_DSS | Clairville SS 6544 | NB_6544_DSS |  |  | 37
| L1142 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Hardy Road SS 6514 | NB_6514_DSS | Murray Corner TS | NB_MCNR_TSS |  |  | 306
| L1143 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Hardy Road SS 6514 | NB_6514_DSS | Murray Corner TS | NB_MCNR_TSS |  |  | 309
| L2131 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Highbank TS | NB_HBNK_TSS | Newcastle TS | NB_NWCS_TSS |  |  | 389
| L0141 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 69 | 4.9957 | 3 | [5 empty] | 36 | 39 | Hunters Corner SS 6129 | NB_6129_DSS | Beechwood SS 6391 | NB_6391_DSS |  |  | 254
| L0048 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Hunters Corner SS 6129 | NB_6129_DSS | Florenceville SS 6114 | NB_6114_DSS |  |  | 150
| L1183 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Iroquois TS | NB_IROQ_TSS | Edmundston TS | NB_EDMN_TSS |  |  | 362
| L1184 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Iroquois TS | NB_IROQ_TSS | Edmundston TS | NB_EDMN_TSS |  |  | 363
| L0072 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Iroquois TS | NB_IROQ_TSS | Edmunston City SS 5398 | NB_5398_DSS |  |  | 183
| L0078 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Iroquois TS | NB_IROQ_TSS | Frasers Edmunston SS 5301 | NB_5301_ISS |  |  | 194
| L0073 | NB Power | New Brunswick | 1 | ac | 44 | 27 | 69 | 16.9086 | 3 | [5 empty] | 36 | 39 | Iroquois TS | NB_IROQ_TSS | Grand Falls GS | NB_GRFS_GSS |  |  | 184
| L1140 | NB Power | New Brunswick | 1 | ac | 44 | 27 | 138 | 19.0771 | 3 | [5 empty] | 141 | 156 | Iroquois TS | NB_IROQ_TSS | Grand Falls GS | NB_GRFS_GSS |  |  | 304
| L0088 | NB Power / MPS | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 40 | 40 | Iroquois TS | NB_IROQ_TSS | INT Madawaska | XX_NBUS1_INT |  |  | 200
| L0089 | NB Power / MPS | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 0 | 0 | Iroquois TS | NB_IROQ_TSS | INT Madawaska | XX_NBUS1_INT |  |  | 201
| L0022 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Iroquois TS | NB_IROQ_TSS | Junction 0107 | NB_0107_JCT |  |  | 82
| L0070 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Iroquois TS | NB_IROQ_TSS | Junction 0124 | NB_0124_JCT |  |  | 178
| L0073 | NB Power | New Brunswick | 1 | ac | 57 | 35 | 69 | 21.9043 | 3 | [5 empty] | 36 | 39 | Iroquois TS | NB_IROQ_TSS | McCains SS 5102 | NB_5102_DSS |  |  | 185
| L3012 | NB Power | New Brunswick | 1 | ac | 40 | 25 | 345 | 17.7519 | 3 | [5 empty] | 975 | 1275 | Iroquois TS | NB_IROQ_TSS | St. André TS | NB_SADR_TSS |  |  | 402
| L1149 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 138 | 0.13007 | 3 | [5 empty] | 141 | 156 | Irving Refinery 138 TS | NB_IRV138_TSS | Grandview GS | NB_GRDV_GSS | TransCanada Energy. 2019. Grandview Cogeneration Plant | Grandview GS is internal to the Irving Refinery | 323
| L0035 | NB Power | New Brunswick | 1 | ac | 0.5 | 0.3 | 69 | 0.19214 | 3 | [5 empty] | 36 | 39 | Irving Refinery 69 TS | NB_IRV69_TSS | Irving Refinery SS 5296 | NB_5296_ISS |  |  | 125
| L0036 | NB Power | New Brunswick | 1 | ac | 4.5 | 2.8 | 69 | 1.7293 | 3 | [5 empty] | 36 | 39 | Irving Refinery 69 TS | NB_IRV69_TSS | Millidgeville SS 5213 | NB_5213_DSS |  |  | 126
| L0036 | NB Power | New Brunswick | 1 | ac | 0.5 | 0.3 | 69 | 0.19214 | 3 | [5 empty] | 36 | 39 | Irving Refinery SS 5296 | NB_5296_ISS | Irving Refinery 69 TS | NB_IRV69_TSS |  |  | 127
| L0068 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Irving Tissue SS 5203 | NB_5203_ISS | Irving Pulp and Paper SS 5264 | NB_5264_ISS |  |  | 175
| L0003 | NB Power | New Brunswick | 1 | ac | 11 | 7 | 69 | 4.2271 | 3 | [5 empty] | 36 | 39 | Junction 0015 | NB_0015_JCT | Salisbury SS 6556 | NB_6556_DSS |  |  | 7
| L0015 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Junction 0015 | NB_0015_JCT | Turtle Creek SS 6517 | NB_6517_DSS |  |  | 49
| L0024 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0019 | NB_0019_JCT | Junction 0029 | NB_0029_JCT |  |  | 94
| L0019 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0019 | NB_0019_JCT | Wilber St SS 6555 | NB_6555_DSS |  |  | 71
| L0006 | NB Power | New Brunswick | 1 | ac | 23 | 14 | 69 | 8.8386 | 3 | [5 empty] | 36 | 39 | Junction 0021 | NB_0021_JCT | Canaan Forks SS 6202 | NB_6202_DSS |  |  | 15
| L0021 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Junction 0021 | NB_0021_JCT | Havelock SS 6519 | NB_6519_DSS |  |  | 81
| L0022 | NB Power | New Brunswick | 1 | ac | 9 | 5 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | Junction 0022 | NB_0022_JCT | Ortonville SWS | NB_ORTN_SWS |  |  | 90
| L0029 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0029 | NB_0029_JCT | Drummond St SS 6596 | NB_6596_DSS |  |  | 116
| L0024 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0029 | NB_0029_JCT | Lakeside SS 6545 | NB_6545_DSS |  |  | 95
| L0038 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Junction 0038 | NB_0038_JCT | Connell St. SS 6199 | NB_6199_DSS |  |  | 131
| L0020 | NB Power | New Brunswick | 1 | ac | 9 | 5 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | Junction 0038 | NB_0038_JCT | Woodstock TS | NB_WDSK_TSS |  |  | 80
| L0044E | NB Power | New Brunswick | 1 | ac | 19 | 12 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Junction 0044E | NB_0044E_JCT | Cape Pele SS 6506 | NB_6506_DSS |  |  | 145
| L0044 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0044E | NB_0044E_JCT | Shediac SS 6513 | NB_6513_DSS |  |  | 144
| L0045 | NB Power | New Brunswick | 1 | ac | 21 | 13 | 69 | 8.07 | 3 | [5 empty] | 36 | 39 | Junction 0045 | NB_0045_JCT | Deer Island SS 6293 | NB_6293_DSS |  |  | 146
| L0016 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0045 | NB_0045_JCT | St. George SS 6145 | NB_6145_DSS |  |  | 54
| L0050 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 69 | 0.11529 | 3 | [5 empty] | 36 | 39 | Junction 0050 | NB_0050_JCT | Mill Lane SS 6207 | NB_6207_DSS |  |  | 154
| L0017 | NB Power | New Brunswick | 1 | ac | 16 | 10 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Junction 0050 | NB_0050_JCT | Thomaston Corner SS 6193 | NB_6193_DSS |  |  | 61
| L0062 | NB Power | New Brunswick | 1 | ac | 15 | 9 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Junction 0062 | NB_0062_JCT | Junction 0112 | NB_0112_JCT |  |  | 166
| L0065 | NB Power | New Brunswick | 1 | ac | 28 | 17 | 69 | 10.76 | 3 | [5 empty] | 36 | 39 | Junction 0065 | NB_0065_JCT | Sisson GS | NB_SSON_GSS |  |  | 171
| L0028 | NB Power | New Brunswick | 1 | ac | 7 | 5 | 69 | 2.69 | 3 | [5 empty] | 36 | 39 | Junction 0065 | NB_0065_JCT | St. Quentin SS 6337 | NB_6337_DSS |  |  | 114
| L0067 | NB Power | New Brunswick | 1 | ac | 24 | 15 | 69 | 9.2229 | 3 | [5 empty] | 36 | 39 | Junction 0067 | NB_0067_JCT | Albert SS 6515 | NB_6515_DSS |  |  | 172
| L0015 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0067 | NB_0067_JCT | Hillsborough SS 6599 | NB_6599_DSS |  |  | 52
| L0002 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Junction 0068 | NB_0068_JCT | Lancaster TS | NB_LNCT_TSS |  |  | 4
| L0068 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0068 | NB_0068_JCT | Raynes Avenue SS 5214 | NB_5214_DSS |  |  | 173
| L0071 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Junction 0071 | NB_0071_JCT | Dalhousie SS 6492 | NB_6492_DSS |  | Dalhousie GS decommissioned. | 182
| L0081 | NB Power | New Brunswick | 1 | ac | 7 | 4 | 69 | 2.69 | 3 | [5 empty] | 36 | 39 | Junction 0081 | NB_0081_JCT | Hartland SS 6127 | NB_6127_DSS |  |  | 197
| L0141 | NB Power | New Brunswick | 1 | ac | 15 | 9 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Junction 0081 | NB_0081_JCT | Hunters Corner SS 6129 | NB_6129_DSS |  |  | 253
| L0016 | NB Power | New Brunswick | 1 | ac | 0.2 | 0.1 | 69 | 0.076857 | 3 | [5 empty] | 36 | 39 | Junction 0082 | NB_0082_JCT | Bayside SS 6222 | NB_6222_ISS |  |  | 57
| L0082 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Junction 0082 | NB_0082_JCT | St. Andrews SS 6296 | NB_6296_DSS |  |  | 198
| L0085 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Junction 0085 | NB_0085_JCT | Dorchester Cape SS 6539 | NB_6539_DSS |  |  | 199
| L0118 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Junction 0085 | NB_0085_JCT | Sackville SS 6511 | NB_6511_DSS |  |  | 228
| L0090 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Junction 0090 | NB_0090_JCT | Jacquet River SS 6413 | NB_6413_DSS |  |  | 202
| L0025 | NB Power | New Brunswick | 1 | ac | 24 | 15 | 69 | 9.2229 | 3 | [5 empty] | 36 | 39 | Junction 0090 | NB_0090_JCT | Petit Rocher SS 6491 | NB_6491_DSS |  |  | 103
| L0091 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0092 | NB_0092_JCT | Junction 0114 | NB_0114_JCT |  |  | 204
| L0092 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0092 | NB_0092_JCT | Sugar Loaf SS 6408 | NB_6408_DSS |  |  | 207
| L0028 | NB Power | New Brunswick | 1 | ac | 29 | 18 | 69 | 11.1443 | 3 | [5 empty] | 36 | 39 | Junction 0097 | NB_0097_JCT | Junction 0065 | NB_0065_JCT |  |  | 113
| L0097 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0097 | NB_0097_JCT | Veneer Siding SS 5312 | NB_5312_DSS |  |  | 210
| L0098 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 69 | 7.6857 | 3 | [5 empty] | 36 | 39 | Junction 0098 | NB_0098_JCT | Canterbury SS 6113 | NB_6113_DSS |  |  | 211
| L0017 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0098 | NB_0098_JCT | Nackawic SS 6108 | NB_6108_DSS |  |  | 65
| L0099 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0099 | NB_0099_JCT | Atlantic Waferboard SS 5407 | NB_5407_ISS |  |  | 212
| L0009 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0099 | NB_0099_JCT | Brown Rd. SWS | NB_BRWN_SWS |  |  | 28
| L0103 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0103 | NB_0103_JCT | Chartersville SS 6502 | NB_6502_DSS |  |  | 214
| L0029 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0103 | NB_0103_JCT | Commercial St SS 6503 | NB_6503_DSS |  |  | 118
| L0104 | NB Power | New Brunswick | 1 | ac | 23 | 14 | 69 | 8.8386 | 3 | [5 empty] | 36 | 39 | Junction 0104 | NB_0104_JCT | Neguac SS 6406 | NB_6406_DSS |  |  | 215
| L0105 | NB Power | New Brunswick | 1 | ac | 21 | 13 | 69 | 8.07 | 3 | [5 empty] | 36 | 39 | Junction 0105 | NB_0105_JCT | Bay du Vin SS 6410 | NB_6410_DSS |  |  | 217
| L0010 | NB Power | New Brunswick | 1 | ac | 29 | 18 | 69 | 11.1443 | 3 | [5 empty] | 36 | 39 | Junction 0105 | NB_0105_JCT | Rogersville SS 6411 | NB_6411_DSS |  |  | 35
| L0140 | NB Power | New Brunswick | 1 | ac | 16 | 10 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Junction 0106 | NB_0106_JCT | Lepreau SS 6205 | NB_6205_DSS |  | Musquash GS decommissioned. | 249
| L0106 | NB Power | New Brunswick | 1 | ac | 4.5 | 2.7778 | 69 | 1.7293 | 3 | [5 empty] | 36 | 39 | Junction 0106 | NB_0106_JCT | Musquash Pumping Station 5208 | NB_5208_SUB |  |  | 232
| L0107 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0107 | NB_0107_JCT | Frasers Iroquois SS 5105 | NB_5105_ISS |  |  | 218
| L0022 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0107 | NB_0107_JCT | St. Basile SS 6396 | NB_6396_DSS |  |  | 83
| L0025 | NB Power | New Brunswick | 1 | ac | 9 | 6 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | Junction 0109 | NB_0109_JCT | Bathurst West SWS/SS 4400 | NB_4400_DSS |  |  | 105
| L0109 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Junction 0109 | NB_0109_JCT | Beresford SS 6416 | NB_6416_DSS |  |  | 219
| L0110 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Junction 0110 | NB_0110_JCT | Flakeboard Co. SS 5209 | NB_5209_ISS |  |  | 220
| L0059 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Junction 0110 | NB_0110_JCT | Milltown GS | NB_MLTN_GSS |  |  | 161
| L0112 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Junction 0112 | NB_0112_JCT | Stone Con. Sawmill SS 6431 | NB_6431_ISS |  |  | 222
| L0114 | NB Power | New Brunswick | 1 | ac | 9 | 5 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | Junction 0114 | NB_0114_JCT | Christopher Brook SS 6422 | NB_6422_DSS |  |  | 223
| L0091 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0114 | NB_0114_JCT | Junction 0125 | NB_0125_JCT |  |  | 205
| L0115 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Junction 0115 | NB_0115_JCT | St. Leonard Sawmill SS 5107 | NB_5107_ISS |  |  | 224
| L0022 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0115 | NB_0115_JCT | St. Leonard SWS | NB_SLND_SWS |  |  | 86
| L0121 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0121 | NB_0121_JCT | Gayton SS 6527 | NB_6527_DSS |  |  | 231
| L0024 | NB Power | New Brunswick | 1 | ac | 7 | 5 | 69 | 2.69 | 3 | [5 empty] | 36 | 39 | Junction 0121 | NB_0121_JCT | Memramcook TS | NB_MRMK_TSS |  |  | 98
| L0122 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0122 | NB_0122_JCT | College Bridge SS 6526 | NB_6526_DSS |  |  | 233
| L0118 | NB Power | New Brunswick | 1 | ac | 7 | 4 | 69 | 2.69 | 3 | [5 empty] | 36 | 39 | Junction 0122 | NB_0122_JCT | Junction 0085 | NB_0085_JCT |  |  | 227
| L0124 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Junction 0124 | NB_0124_JCT | Edmundston East SS 6302 | NB_6302_DSS |  |  | 236
| L0070 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Junction 0124 | NB_0124_JCT | Edmundston North SS 6397 | NB_6397_DSS |  |  | 179
| L0091 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0125 | NB_0125_JCT | Atholville SS 6407 | NB_6407_DSS |  |  | 206
| L0125 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Junction 0125 | NB_0125_JCT | Campbellton SS 6426 | NB_6426_DSS |  |  | 237
| L0126 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Junction 0126 | NB_0126_JCT | Junction 0062 | NB_0062_JCT |  |  | 238
| L0025 | NB Power | New Brunswick | 1 | ac | 4 | 3 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Junction 0126 | NB_0126_JCT | South Bathurst SS 6449 | NB_6449_DSS |  |  | 107
| L0129 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Junction 0129 | NB_0129_JCT | Charlo SS 6430 | NB_6430_DSS |  |  | 239
| L0025 | NB Power | New Brunswick | 1 | ac | 25 | 15 | 69 | 9.6071 | 3 | [5 empty] | 36 | 39 | Junction 0129 | NB_0129_JCT | Junction 0090 | NB_0090_JCT |  |  | 102
| L0017 | NB Power | New Brunswick | 1 | ac | 17 | 10 | 69 | 6.5329 | 3 | [5 empty] | 36 | 39 | Junction 0130 | NB_0130_JCT | Junction 0098 | NB_0098_JCT |  |  | 64
| L0130 | NB Power | New Brunswick | 1 | ac | 11 | 7 | 69 | 4.2271 | 3 | [5 empty] | 36 | 39 | Junction 0130 | NB_0130_JCT | Lake George SS 6126 | NB_6126_DSS |  |  | 240
| L0013E | NB Power | New Brunswick | 1 | ac | 16 | 10 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Junction 0133 | NB_0133_JCT | Lameque SS 6417 | NB_6417_DSS |  |  | 46
| L0133 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0133 | NB_0133_JCT | Shippigan SS 6490 | NB_6490_DSS |  |  | 242
| L0008 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Junction 0134 | NB_0134_JCT | Coles Island SS 6536 | NB_6536_DSS |  |  | 22
| L0134 | NB Power | New Brunswick | 1 | ac | 31 | 19 | 69 | 11.9129 | 3 | [5 empty] | 36 | 39 | Junction 0134 | NB_0134_JCT | Jemseg SS 6153 | NB_6153_DSS |  |  | 243
| L0039 | NB Power | New Brunswick | 1 | ac | 30 | 18 | 69 | 11.5286 | 3 | [5 empty] | 36 | 39 | Junction 0135 | NB_0135_JCT | Boiestown SS 6117 | NB_6117_DSS |  |  | 134
| L0135 | NB Power | New Brunswick | 1 | ac | 30 | 18 | 69 | 11.5286 | 3 | [5 empty] | 36 | 39 | Junction 0135 | NB_0135_JCT | Cross Creek SS 6155 | NB_6155_DSS |  |  | 244
| L0137 | NB Power | New Brunswick | 1 | ac | 0.5 | 0.3 | 69 | 0.19214 | 3 | [5 empty] | 36 | 39 | Junction 0137 | NB_0137_JCT | Baker Brook SS 6304 | NB_6304_DSS |  |  | 246
| L0070 | NB Power | New Brunswick | 1 | ac | 12 | 8 | 69 | 4.6114 | 3 | [5 empty] | 36 | 39 | Junction 0137 | NB_0137_JCT | Clair SS 6311 | NB_6311_DSS |  |  | 181
| L0138 | NB Power | New Brunswick | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Junction 0138 | NB_0138_JCT | Grand Falls South SS 6395 | NB_6395_DSS |  |  | 247
| L0022 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Junction 0138 | NB_0138_JCT | Junction 0022 | NB_0022_JCT |  |  | 89
| L0139 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Junction 0139 | NB_0139_JCT | Harvey SS 6211 | NB_6211_DSS |  |  | 248
| L0017 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Junction 0139 | NB_0139_JCT | Junction 0130 | NB_0130_JCT |  |  | 63
| L1121 | NB Power | New Brunswick | 1 | ac | 36 | 22 | 138 | 15.6086 | 3 | [5 empty] | 141 | 156 | Junction 1121 | NB_1121_JCT | Junction 1129 | NB_1129_JCT |  |  | 289
| L1104 | NB Power | New Brunswick | 1 | ac | 18 | 11 | 138 | 7.8043 | 3 | [5 empty] | 141 | 156 | Junction 1121 | NB_1121_JCT | Waasis Road SWS SS 4103 | NB_4103_DSS |  |  | 261
| L1128 | NB Power | New Brunswick | 1 | ac | 7 | 4 | 138 | 3.035 | 3 | [5 empty] | 141 | 156 | Junction 1128 | NB_1128_JCT | Belledune SS 6439 | NB_6439_DSS |  |  | 297
| L1115 | NB Power | New Brunswick | 1 | ac | 27 | 16 | 138 | 11.7064 | 3 | [5 empty] | 141 | 156 | Junction 1128 | NB_1128_JCT | Tetagouche SS 6438 | NB_6438_DSS |  |  | 282
| L1129 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Junction 1129 | NB_1129_JCT | Mount Pleasant Mines SS 5216 | NB_5216_DSS |  |  | 298
| L1121 | NB Power | New Brunswick | 1 | ac | 30 | 19 | 138 | 13.0071 | 3 | [5 empty] | 141 | 156 | Junction 1129 | NB_1129_JCT | Oak Bay TS | NB_OKBY_TSS |  |  | 290
| L1110 | NB Power | New Brunswick | 1 | ac | 14 | 9 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Junction 1136 | NB_1136_JCT | Eel River TS | NB_EELR_TSS |  |  | 273
| L1136 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Junction 1136 | NB_1136_JCT | Frasers Atholville SS 5409 | NB_5409_DSS |  |  | 302
| L1144 | Algonquin Power | New Brunswick | 1 | ac | 5 | 3 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Junction 1144 | NB_1144_JCT | Tinker GS | NB_TNK_GSS |  |  | 311
| L1111 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Junction 1144 | NB_1144_JCT | Tobique GS | NB_TOBQ_GSS |  |  | 276
| L1105 | NB Power | New Brunswick | 1 | ac | 77 | 48 | 138 | 33.385 | 3 | [5 empty] | 141 | 156 | Junction 1153 | NB_1153_JCT | Grand Lake TS | NB_GRLK_TSS |  |  | 267
| L1153 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Junction 1153 | NB_1153_JCT | Howard SS 6441 | NB_6441_DSS |  | Howard Substation presumed to be 6441 | 326
| L1162 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Junction 1162 | NB_1162_JCT | Grand Falls East SS 6303 | NB_6303_DSS |  |  | 344
| L1175 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 138 | 5.6364 | 3 | [5 empty] | 141 | 156 | Junction 1162 | NB_1162_JCT | St. André TS | NB_SADR_TSS |  |  | 356
| L1163 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Junction 1163 | NB_1163_JCT | Gondola Point SS 6524 | NB_6524_DSS |  |  | 345
| L1149 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Junction 1163 | NB_1163_JCT | Junction 1208 | NB_1208_JCT |  |  | 319
| L1104 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 138 | 0.13007 | 3 | [5 empty] | 141 | 156 | Junction 1168 | NB_1168_JCT | Junction 1197 | NB_1197_JCT |  |  | 263
| L1168 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Junction 1168 | NB_1168_JCT | Oromocto Town SS 6140 | NB_6140_DSS |  |  | 348
| L1171 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Junction 1171 | NB_1171_JCT | Gunningsville SS 6531 | NB_6531_DSS |  |  | 349
| L1108 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Junction 1171 | NB_1171_JCT | Memramcook TS | NB_MRMK_TSS |  |  | 270
| L1125 | NB Power | New Brunswick | 1 | ac | 24 | 15 | 138 | 10.4057 | 3 | [5 empty] | 141 | 156 | Junction 1172 | NB_1172_JCT | Keswick TS | NB_KSWK_TSS |  |  | 294
| L1172 | NB Power | New Brunswick | 1 | ac | 7 | 4 | 138 | 3.035 | 3 | [5 empty] | 141 | 156 | Junction 1172 | NB_1172_JCT | Millville TS | NB_MIVL_TSS |  |  | 351
| L1173 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Junction 1173 | NB_1173_JCT | Hampton 138 SS 6534 | NB_6534_DSS |  |  | 352
| L1149 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Junction 1173 | NB_1173_JCT | Junction 1163 | NB_1163_JCT |  |  | 318
| L1104 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Junction 1174 | NB_1174_JCT | Marysville TS | NB_MRYV_TSS |  |  | 265
| L1174 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Junction 1174 | NB_1174_JCT | Vanier SS 6118 | NB_6118_DSS |  |  | 353
| L1199 | NB Power | New Brunswick | 1 | ac | 75 | 46 | 138 | 32.5179 | 3 | [5 empty] | 141 | 156 | Junction 1177 | NB_1177_JCT | Norton TS | NB_NRTN_TSS |  |  | 377
| L1177 | NB Power | New Brunswick | 1 | ac | 7 | 4 | 138 | 3.035 | 3 | [5 empty] | 141 | 156 | Junction 1177 | NB_1177_JCT | Sussex Corner SS 6537 | NB_6537_DSS |  |  | 358
| L1178 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 138 | 5.6364 | 3 | [5 empty] | 141 | 156 | Junction 1178 | NB_1178_JCT | Denison Potacan SS 5218 | NB_5218_DSS |  |  | 359
| L1149 | NB Power | New Brunswick | 1 | ac | 14 | 8 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Junction 1178 | NB_1178_JCT | Junction 1173 | NB_1173_JCT |  |  | 317
| L1179 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 138 | 0.13007 | 3 | [5 empty] | 141 | 156 | Junction 1179 | NB_1179_JCT | Canada Liquid Air SS 5501 | NB_5501_ISS |  |  | 360
| L1157 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Junction 1179 | NB_1179_JCT | Junction 1191 | NB_1191_JCT |  |  | 337
| L1199 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Junction 1181 | NB_1181_JCT | Junction 1177 | NB_1177_JCT |  |  | 376
| L1181 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Junction 1181 | NB_1181_JCT | Potash Co. SS 5217 | NB_5217_ISS |  |  | 361
| L1149 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 138 | 4.3357 | 3 | [5 empty] | 141 | 156 | Junction 1187 | NB_1187_JCT | Lakewood SS 5211 | NB_5211_DSS |  |  | 321
| L1187 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Junction 1187 | NB_1187_JCT | Loch Lomond SS 6204 | NB_6204_DSS |  |  | 365
| L1191 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Junction 1191 | NB_1191_JCT | Church St. SS 6543 | NB_6543_DSS |  |  | 369
| L1157 | NB Power | New Brunswick | 1 | ac | 1 | 0.6 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Junction 1191 | NB_1191_JCT | Dieppe Industrial SS 6530 | NB_6530_DSS |  |  | 338
| L1192 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Junction 1192 | NB_1192_JCT | Devon SS 6154 | NB_6154_DSS |  |  | 370
| L1112 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Junction 1192 | NB_1192_JCT | Marysville TS | NB_MRYV_TSS |  |  | 280
| L1195 | NB Power | New Brunswick | 1 | ac | 34 | 21 | 138 | 14.7414 | 3 | [5 empty] | 141 | 156 | Junction 1195 | NB_1195_JCT | Caribou Mining SS 5497 | NB_5497_ISS |  |  | 373
| L1104 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Junction 1197 | NB_1197_JCT | Junction 1174 | NB_1174_JCT |  |  | 264
| L1197 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Junction 1197 | NB_1197_JCT | New Maryland SS 6158 | NB_6158_DSS |  |  | 374
| L1126 | NB Power | New Brunswick | 1 | ac | 52 | 32 | 138 | 22.5457 | 3 | [5 empty] | 141 | 156 | Junction 1205 | NB_1205_JCT | Keswick TS | NB_KSWK_TSS |  |  | 296
| L1205 | NB Power | New Brunswick | 1 | ac | 21 | 13 | 138 | 9.105 | 3 | [5 empty] | 141 | 156 | Junction 1205 | NB_1205_JCT | Woodstock TS | NB_WDSK_TSS |  |  | 380
| L1208 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Junction 1208 | NB_1208_JCT | Fairvale SS 6226 | NB_6226_DSS |  |  | 381
| L1149 | NB Power | New Brunswick | 1 | ac | 0.3 | 0.2 | 138 | 0.13007 | 3 | [5 empty] | 141 | 156 | Junction 1208 | NB_1208_JCT | Junction 1187 | NB_1187_JCT |  |  | 320
| L0048 | NB Power | New Brunswick | 1 | ac | 16 | 10 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Juniper SS 6107 | NB_6107_DSS | Deersdale SS 5100 | NB_5100_DSS |  |  | 152
| L1189 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Keswick Ridge SS 6139 | NB_6139_DSS | Kingsclear SS 6109 | NB_6109_DSS |  |  | 367
| L3001 | NB Power / Emera Maine | New Brunswick | 1 | ac | 78 | 48 | 345 | 34.6161 | 3 | [5 empty] | 700 | 700 | Keswick TS | NB_KSWK_TSS | INT Keswick | XX_NBUS5_INT |  |  | 391
| L1103 | NB Power | New Brunswick | 1 | ac | 17 | 11 | 138 | 7.3707 | 3 | [5 empty] | 141 | 156 | Keswick TS | NB_KSWK_TSS | Nashwaaksis SS 6135 | NB_6135_DSS |  |  | 258
| L1112 | NB Power | New Brunswick | 1 | ac | 17 | 11 | 138 | 7.3707 | 3 | [5 empty] | 141 | 156 | Keswick TS | NB_KSWK_TSS | Nashwaaksis SS 6135 | NB_6135_DSS |  |  | 278
| L2130 | NB Power | New Brunswick | 1 | ac | 145 | 90 | 230 | 69.6 | 2.1804 | [5 empty] | 292.1781 | 316.1629 | Keswick TS | NB_KSWK_TSS | Newcastle TS | NB_NWCS_TSS |  |  | 387
| L0024 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Lakeside SS 6545 | NB_6545_DSS | Scoudouc SS 6595 | NB_6595_DSS |  |  | 96
| L0024 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Lakeside SS 6545 | NB_6545_DSS | Scoudouc SS 6595 | NB_6595_DSS |  |  | 99
| L1149 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 138 | 1.7343 | 3 | [5 empty] | 141 | 156 | Lakewood SS 5211 | NB_5211_DSS | Irving Refinery 138 TS | NB_IRV138_TSS |  |  | 322
| L0013E | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Lameque SS 6417 | NB_6417_DSS | Lameque GS | NB_LMEQ_GSS |  |  | 47
| L0123 | NB Power | New Brunswick | 1 | ac | 9 | 6 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | Lancaster TS | NB_LNCT_TSS | Grand Bay SS 6528 | NB_6528_DSS |  |  | 235
| L0001 | NB Power | New Brunswick | 1 | ac | 14 | 9 | 69 | 5.38 | 3 | [5 empty] | 36 | 39 | Lancaster TS | NB_LNCT_TSS | Junction 0106 | NB_0106_JCT |  |  | 1
| L0041 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Lancaster TS | NB_LNCT_TSS | Manawagonish Road SS 5219 | NB_5219_DSS |  |  | 137
| L0040 | NB Power | New Brunswick | 1 | ac | 16 | 10 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Lancaster TS | NB_LNCT_TSS | Westfield SS 6298 | NB_6298_DSS |  |  | 136
| L0140 | NB Power | New Brunswick | 1 | ac | 22 | 14 | 69 | 8.4543 | 3 | [5 empty] | 36 | 39 | Lepreau SS 6205 | NB_6205_DSS | Pennfield Ridge SS 6206 | NB_6206_DSS |  |  | 250
| L0010 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Lutz Mtn. SS 6510 | NB_6510_DSS | Moncton TS | NB_MCTN_TSS |  |  | 39
| L1189 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Mactaquac GS | NB_MTQC_GSS | Keswick Ridge SS 6139 | NB_6139_DSS |  |  | 366
| L1133 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Mactaquac GS | NB_MTQC_GSS | Keswick TS | NB_KSWK_TSS |  |  | 299
| L1134 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Mactaquac GS | NB_MTQC_GSS | Keswick TS | NB_KSWK_TSS |  |  | 300
| L3002 | NB Power | New Brunswick | 1 | ac | 14 | 9 | 345 | 6.2131 | 3 | [5 empty] | 975 | 1275 | Mactaquac GS | NB_MTQC_GSS | Keswick TS | NB_KSWK_TSS |  |  | 393
| L3003 | NB Power | New Brunswick | 1 | ac | 14 | 9 | 345 | 6.2131 | 3 | [5 empty] | 975 | 1275 | Mactaquac GS | NB_MTQC_GSS | Keswick TS | NB_KSWK_TSS |  |  | 394
| L1135 | NB Power | New Brunswick | 1 | ac | 16 | 10 | 138 | 6.9371 | 3 | [5 empty] | 141 | 156 | Mactaquac GS | NB_MTQC_GSS | Rainsford Lane SS 6137 | NB_6137_DSS |  |  | 301
| L0041 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Manawagonish Road SS 5219 | NB_5219_DSS | Dever Road SS 5263 | NB_5263_DSS |  |  | 138
| L0079 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Marysville TS | NB_MRYV_TSS | Barkers Pt. SS 6125 | NB_6125_DSS |  |  | 196
| L0023 | NB Power | New Brunswick | 1 | ac | 16 | 10 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Marysville TS | NB_MRYV_TSS | Doak SWS 4119 | NB_4119_SWS |  |  | 92
| L0020 | NB Power | New Brunswick | 1 | ac | 32 | 20 | 69 | 12.2971 | 3 | [5 empty] | 36 | 39 | Marysville TS | NB_MRYV_TSS | Hainesville SS 6133 | NB_6133_DSS |  |  | 75
| L0039 | NB Power | New Brunswick | 1 | ac | 31 | 19 | 69 | 11.9129 | 3 | [5 empty] | 36 | 39 | Marysville TS | NB_MRYV_TSS | Taymouth SS 6111 | NB_6111_DSS |  |  | 132
| L0017 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | McAdam SS 6225 | NB_6225_DSS | Junction 0050 | NB_0050_JCT |  |  | 60
| L0073 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | McCains SS 5102 | NB_5102_DSS | Grand Falls GS | NB_GRFS_GSS |  |  | 186
| L1142 | NB Power | New Brunswick | 1 | ac | 39 | 24 | 138 | 16.9093 | 3 | [5 empty] | 141 | 156 | Memramcook TS | NB_MRMK_TSS | Hardy Road SS 6514 | NB_6514_DSS |  |  | 305
| L1143 | NB Power | New Brunswick | 1 | ac | 39 | 24 | 138 | 16.9093 | 3 | [5 empty] | 141 | 156 | Memramcook TS | NB_MRMK_TSS | Hardy Road SS 6514 | NB_6514_DSS |  |  | 308
| L1160 | NB Power / NSPI | New Brunswick | 2 | ac | 15 | 9 | 138 | 6.5036 | 3 | [5 empty] | 141 | 156 | Memramcook TS | NB_MRMK_TSS | IPT Amherst | PP_NSNB2_IPT |  |  | 342
| L1159 | NB Power / NSPI | New Brunswick | 2 | ac | 20 | 12 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Memramcook TS | NB_MRMK_TSS | IPT Church St | PP_NSNB3_IPT |  |  | 341
| L0118 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Memramcook TS | NB_MRMK_TSS | Junction 0122 | NB_0122_JCT |  |  | 226
| L2111 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Millbank GS | NB_MLBK_GSS | Highbank TS | NB_HBNK_TSS |  |  | 386
| L1203 | NB Power | New Brunswick | 1 | ac | 16 | 10 | 138 | 6.9371 | 3 | [5 empty] | 141 | 156 | Millbank GS | NB_MLBK_GSS | Newcastle TS | NB_NWCS_TSS |  |  | 379
| L0041 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Millidgeville SS 5213 | NB_5213_DSS | Brookville TS/SS 5266 | NB_5266_DSS |  |  | 140
| L0059 | NB-EMEC | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 70 | 70 | Milltown GS | NB_MLTN_GSS | INT Milltown | XX_NBUS7_INT |  |  | 162
| L0020 | NB Power | New Brunswick | 1 | ac | 22 | 14 | 69 | 8.4543 | 3 | [5 empty] | 36 | 39 | Millville SS 6194 | NB_6194_DSS | Grafton SS 6105 | NB_6105_DSS |  |  | 78
| L0020 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Millville TS | NB_MIVL_TSS | Millville SS 6194 | NB_6194_DSS |  |  | 77
| L1172 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Millville TS | NB_MIVL_TSS | St. Anne Nackawic SS 5116 | NB_5116_DSS |  |  | 350
| L0007 | NB Power | New Brunswick | 1 | ac | 19 | 12 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Minto SS 6120 | NB_6120_DSS | Chipman SS 6106 | NB_6106_DSS |  |  | 19
| L1118 | NB Power | New Brunswick | 1 | ac | 46 | 28 | 138 | 19.9443 | 3 | [5 empty] | 141 | 156 | Miramichi P&P - South Nelson 5419 | NB_5419_ISS | St. Louis SS 6532 | NB_6532_DSS |  | St. Louis Substation presumed to be 6532. | 286
| L0003 | NB Power | New Brunswick | 1 | ac | 11 | 7 | 69 | 4.2271 | 3 | [5 empty] | 36 | 39 | Moncton TS | NB_MCTN_TSS | Allison SS 6520 | NB_6520_DSS |  |  | 5
| L1101 | NB Power | New Brunswick | 1 | ac | 100 | 62 | 138 | 43.3571 | 2.7879 | [5 empty] | 131.0332 | 144.9729 | Moncton TS | NB_MCTN_TSS | Grand Lake TS | NB_GRLK_TSS |  |  | 256
| L0024 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Moncton TS | NB_MCTN_TSS | Junction 0019 | NB_0019_JCT |  |  | 93
| L0006 | NB Power | New Brunswick | 1 | ac | 33 | 20 | 69 | 12.6814 | 3 | [5 empty] | 36 | 39 | Moncton TS | NB_MCTN_TSS | Junction 0021 | NB_0021_JCT |  |  | 14
| L1108 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 138 | 4.3357 | 3 | [5 empty] | 141 | 156 | Moncton TS | NB_MCTN_TSS | Junction 1171 | NB_1171_JCT |  |  | 269
| L1157 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Moncton TS | NB_MCTN_TSS | Ryan Rd SS 6525 | NB_6525_DSS |  |  | 334
| L1142 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Murray Corner TS | NB_MCNR_TSS | IPT Richmond Cove | PP_NBPE1_IPT |  |  | 307
| L1143 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Murray Corner TS | NB_MCNR_TSS | IPT Richmond Cove | PP_NBPE1_IPT |  |  | 310
| L0017 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 69 | 4.9957 | 3 | [5 empty] | 36 | 39 | Nackawic SS 6108 | NB_6108_DSS | Millville SS 6194 | NB_6194_DSS |  |  | 66
| L1112 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Nashwaaksis SS 6135 | NB_6135_DSS | Junction 1192 | NB_1192_JCT |  |  | 279
| L1103 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Nashwaaksis SS 6135 | NB_6135_DSS | Marysville TS | NB_MRYV_TSS |  |  | 259
| L0009 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Nelson SS 6442 | NB_6442_DSS | Newcastle Town SS 6443 | NB_6443_DSS |  |  | 30
| L0027 | NB Power | New Brunswick | 1 | ac | 19 | 12 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | New Denmark SS 6390 | NB_6390_DSS | Plaster Rock SS 6394 | NB_6394_DSS |  |  | 110
| L0009 | NB Power | New Brunswick | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Newcastle Town SS 6443 | NB_6443_DSS | Sweeny Lane SS 6409 | NB_6409_DSS |  |  | 31
| L1105 | NB Power | New Brunswick | 1 | ac | 39 | 24 | 138 | 16.9093 | 3 | [5 empty] | 141 | 156 | Newcastle TS | NB_NWCS_TSS | Junction 1153 | NB_1153_JCT |  |  | 266
| L1118 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Newcastle TS | NB_NWCS_TSS | Miramichi P&P - South Nelson 5419 | NB_5419_ISS |  | This is a simplification. See reference map. | 285
| L0116 | NB Power | New Brunswick | 1 | ac | 18 | 11 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | Newcastle TS | NB_NWCS_TSS | Red Bank SS 6424 | NB_6424_DSS |  |  | 225
| L3004 | NB Power | New Brunswick | 1 | ac | 96 | 59 | 345 | 42.6044 | 2.8806 | [5 empty] | 936.2079 | 1224.2719 | Norton TS | NB_NRTN_TSS | Coleson Cove GS | NB_CLCV_GSS |  |  | 396
| L1149 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Norton TS | NB_NRTN_TSS | Junction 1178 | NB_1178_JCT |  |  | 316
| L1155 | NB Power | New Brunswick | 1 | ac | 14 | 9 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Oak Bay TS | NB_OKBY_TSS | Flakeboard Co. SS 5209 | NB_5209_ISS |  |  | 327
| L0017 | NB Power | New Brunswick | 1 | ac | 46 | 28 | 69 | 17.6771 | 3 | [5 empty] | 36 | 39 | Oak Bay TS | NB_OKBY_TSS | McAdam SS 6225 | NB_6225_DSS |  |  | 59
| L0077 | NB Power | New Brunswick | 1 | ac | 9 | 6 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | Oak Bay TS | NB_OKBY_TSS | St. Stephen SS 6223 | NB_6223_DSS |  |  | 193
| L1111 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 138 | 5.6364 | 3 | [5 empty] | 141 | 156 | Ortonville SWS | NB_ORTN_SWS | Junction 1144 | NB_1144_JCT |  |  | 275
| L0027 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Ortonville SWS | NB_ORTN_SWS | New Denmark SS 6390 | NB_6390_DSS |  |  | 109
| L0022 | NB Power | New Brunswick | 1 | ac | 19 | 12 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Ortonville SWS | NB_ORTN_SWS | Tobique GS | NB_TOBQ_GSS |  |  | 91
| L0140 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Pennfield Ridge SS 6206 | NB_6206_DSS | Pennfield TS | NB_PNFD_TSS |  |  | 251
| L0049 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Pennfield TS | NB_PNFD_TSS | Blacks Harbour North SS 6209 | NB_6209_DSS |  |  | 153
| L0016 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Pennfield TS | NB_PNFD_TSS | Junction 0045 | NB_0045_JCT |  |  | 53
| L0100 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Pennfield TS | NB_PNFD_TSS | Lake Utopia Paper SS 5206 | NB_5206_ISS |  |  | 213
| L0025 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Petit Rocher SS 6491 | NB_6491_DSS | Junction 0109 | NB_0109_JCT |  |  | 104
| L0003 | NB Power | New Brunswick | 1 | ac | 45 | 28 | 69 | 17.2929 | 3 | [5 empty] | 36 | 39 | Petitcodiac SS 6558 | NB_6558_DSS | Sussex North SS 6297 | NB_6297_DSS |  |  | 9
| L0027 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Plaster Rock SS 6394 | NB_6394_DSS | Frasers Plaster Rock SS 5106 | NB_5106_ISS |  |  | 111
| L3016 | NB Power / Emera Maine | New Brunswick | 1 | ac | 90 | 56 | 345 | 39.9417 | 2.9815 | [5 empty] | 0 | 0 | Point Lepreau GS | NB_PLPR_GSS | INT Lepreau | XX_NBUS6_INT |  |  | 406
| L3003 | NB Power | New Brunswick | 1 | ac | 135 | 83 | 345 | 59.9125 | 2.3 | [5 empty] | 747.5104 | 977.5135 | Point Lepreau GS | NB_PLPR_GSS | Mactaquac GS | NB_MTQC_GSS |  |  | 395
| L1185 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Rainsford Lane SS 6137 | NB_6137_DSS | Priestman SS 6124 | NB_6124_DSS |  |  | 364
| L0068 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Raynes Avenue SS 5214 | NB_5214_DSS | Irving Tissue SS 5203 | NB_5203_ISS |  |  | 174
| L1156 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Rexton SS 6535 | NB_6535_DSS | West Buctouche SS 6508 | NB_6508_DSS |  |  | 328
| L1118 | NB Power | New Brunswick | 1 | ac | 6 | 4 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Richibucto SS 6533 | NB_6533_DSS | Rexton SS 6535 | NB_6535_DSS |  |  | 288
| L0018 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Ripples SS 6142 | NB_6142_DSS | Burpee Brook SS 6152 | NB_6152_DSS |  |  | 69
| L0010 | NB Power | New Brunswick | 1 | ac | 33 | 20 | 69 | 12.6814 | 3 | [5 empty] | 36 | 39 | Rogersville SS 6411 | NB_6411_DSS | Harcourt SS 6504 | NB_6504_DSS |  |  | 36
| L0003 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Rothesay SS 6267 | NB_6267_DSS | Brookville TS/SS 5266 | NB_5266_DSS |  |  | 13
| L0008 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Rothesay SS 6267 | NB_6267_DSS | Brookville TS/SS 5266 | NB_5266_DSS |  |  | 26
| L0074 | NB Power | New Brunswick | 1 | ac | 18 | 11 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | Rusagonis SS 6141 | NB_6141_DSS | Fredericton Junction SS 6116 | NB_6116_DSS |  |  | 188
| L1157 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Ryan Rd SS 6525 | NB_6525_DSS | Caledonia Park SS 6522 | NB_6522_DSS |  |  | 335
| L1156 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Ryan Rd SS 6525 | NB_6525_DSS | Moncton TS | NB_MCTN_TSS |  |  | 333
| L0118 | NB Power | New Brunswick | 1 | ac | 9 | 5 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | Sackville SS 6511 | NB_6511_DSS | CBC Sackville SS 6541 | NB_6541_DSS |  |  | 229
| L0003 | NB Power | New Brunswick | 1 | ac | 13 | 8 | 69 | 4.9957 | 3 | [5 empty] | 36 | 39 | Salisbury SS 6556 | NB_6556_DSS | Petitcodiac SS 6558 | NB_6558_DSS |  |  | 8
| L3006 | NB Power / NSPI | New Brunswick | 1 | ac | 55 | 34 | 345 | 24.4088 | 3 | [5 empty] | 975 | 1275 | Salisbury TS | NB_SLBY_TSS | IPT Onslow | PP_NSNB1_IPT |  |  | 397
| L1199 | NB Power | New Brunswick | 1 | ac | 50 | 31 | 138 | 21.6786 | 3 | [5 empty] | 141 | 156 | Salisbury TS | NB_SLBY_TSS | Junction 1181 | NB_1181_JCT |  |  | 375
| L1236 | NB Power | New Brunswick | 1 | ac | 29 | 18 | 138 | 12.5736 | 3 | [5 empty] | 141 | 156 | Salisbury TS | NB_SLBY_TSS | Kent Hills Wind GS | NB_KNTH_GSS |  |  | 405
| L2145 | NB Power | New Brunswick | 1 | ac | 147 | 91 | 230 | 70.56 | 2.1646 | [5 empty] | 290.0567 | 313.8673 | Salisbury TS | NB_SLBY_TSS | Keswick TS | NB_KSWK_TSS |  |  | 390
| L1190 | NB Power | New Brunswick | 1 | ac | 40 | 25 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | Salisbury TS | NB_SLBY_TSS | Memramcook TS | NB_MRMK_TSS |  |  | 368
| L1124 | NB Power | New Brunswick | 1 | ac | 30 | 19 | 138 | 13.0071 | 3 | [5 empty] | 141 | 156 | Salisbury TS | NB_SLBY_TSS | Moncton TS | NB_MCTN_TSS |  |  | 292
| L1148 | NB Power | New Brunswick | 1 | ac | 25 | 15 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Salisbury TS | NB_SLBY_TSS | Moncton TS | NB_MCTN_TSS |  |  | 315
| L1151 | NB Power | New Brunswick | 1 | ac | 25 | 15 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Salisbury TS | NB_SLBY_TSS | Moncton TS | NB_MCTN_TSS |  |  | 324
| L3013 | NB Power | New Brunswick | 1 | ac | 75 | 46 | 345 | 33.2847 | 3 | [5 empty] | 975 | 1275 | Salisbury TS | NB_SLBY_TSS | Norton TS | NB_NRTN_TSS |  |  | 403
| L1156 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Scoudouc Ind. SS 6540 | NB_6540_ISS | Caledonia Park SS 6522 | NB_6522_DSS |  |  | 331
| L1161 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Scoudouc Ind. SS 6540 | NB_6540_ISS | Coulter Manufacturing SS 5503 | NB_5503_DSS |  |  | 343
| L1166 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Scoudouc Ind. SS 6540 | NB_6540_ISS | Shediac Wst SS 6529 | NB_6529_DSS |  |  | 347
| L0044 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Scoudouc SS 6595 | NB_6595_DSS | Junction 0044E | NB_0044E_JCT |  |  | 143
| L0024 | NB Power | New Brunswick | 1 | ac | 11 | 7 | 69 | 4.2271 | 3 | [5 empty] | 36 | 39 | Scoudouc SS 6595 | NB_6595_DSS | Junction 0121 | NB_0121_JCT |  |  | 97
| L0013 | NB Power | New Brunswick | 1 | ac | 18 | 11 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | Six Roads SS 6425 | NB_6425_DSS | Junction 0133 | NB_0133_JCT |  |  | 45
| L0069 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 69 | 4.6114 | 3 | [5 empty] | 36 | 39 | Six Roads SS 6425 | NB_6425_DSS | Tracadie SS 6436 | NB_6436_DSS |  |  | 176
| L0025 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | South Bathurst SS 6449 | NB_6449_DSS | Bathurst TS/SS 6432 | NB_6432_DSS |  |  | 108
| L0008 | NB Power | New Brunswick | 1 | ac | 17 | 10 | 69 | 6.5329 | 3 | [5 empty] | 36 | 39 | Springfield SS 6200 | NB_6200_DSS | Hampton 69 SS 6268 | NB_6268_DSS |  |  | 24
| L3010 | NB Power | New Brunswick | 1 | ac | 141 | 87 | 345 | 62.5753 | 2.2297 | [5 empty] | 724.6633 | 947.6366 | St. André TS | NB_SADR_TSS | Eel River TS | NB_EELR_TSS |  |  | 400
| L1110 | NB Power | New Brunswick | 1 | ac | 127 | 78 | 138 | 55.0636 | 2.3962 | [5 empty] | 112.6231 | 124.6042 | St. André TS | NB_SADR_TSS | Junction 1136 | NB_1136_JCT |  |  | 272
| L3011 | NB Power | New Brunswick | 1 | ac | 160 | 99 | 345 | 71.0074 | 2.0476 | [5 empty] | 665.469 | 870.2286 | St. André TS | NB_SADR_TSS | Keswick TS | NB_KSWK_TSS |  |  | 401
| L0022 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | St. Basile SS 6396 | NB_6396_DSS | Green River SS 6144 | NB_6144_DSS |  |  | 84
| L0016 | NB Power | New Brunswick | 1 | ac | 27 | 17 | 69 | 10.3757 | 3 | [5 empty] | 36 | 39 | St. George SS 6145 | NB_6145_DSS | Junction 0082 | NB_0082_JCT |  |  | 56
| L0016 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | St. George SS 6145 | NB_6145_DSS | St. George GS | NB_SGRG_GSS |  | St. George GS presumed connected at St. George Substation 6145 | 55
| L0019 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | St. George St SS 6553 | NB_6553_DSS | Baig Blvd SS 6507 | NB_6507_DSS |  |  | 73
| L0063 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | St. Leolin SS 6435 | NB_6435_DSS | Bertrand SS 6421 | NB_6421_DSS |  |  | 168
| L0022 | NB Power | New Brunswick | 1 | ac | 15 | 9 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | St. Leonard SWS | NB_SLND_SWS | Grand Falls North SS 6333 | NB_6333_DSS |  |  | 87
| L0028 | NB Power | New Brunswick | 1 | ac | 20 | 12 | 69 | 7.6857 | 3 | [5 empty] | 36 | 39 | St. Leonard SWS | NB_SLND_SWS | Junction 0097 | NB_0097_JCT |  |  | 112
| L1118 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | St. Louis SS 6532 | NB_6532_DSS | Richibucto SS 6533 | NB_6533_DSS |  | St. Louis Substation presumed to be 6532. | 287
| L0028 | NB Power | New Brunswick | 1 | ac | 18 | 11 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | St. Quentin SS 6337 | NB_6337_DSS | Kedgwick SS 6301 | NB_6301_DSS |  |  | 115
| L0059 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | St. Stephen SS 6223 | NB_6223_DSS | Junction 0110 | NB_0110_JCT |  |  | 160
| L1158 | NB Power | New Brunswick | 1 | ac | 5 | 3 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Ste Rose GS | NB_SROS_GSS | Six Roads SS 6425 | NB_6425_DSS |  |  | 340
| L0112 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Stone Con. Sawmill SS 6431 | NB_6431_ISS | Nepisiguit Falls SS 6404 | NB_6404_DSS |  |  | 170
| L0003 | NB Power | New Brunswick | 1 | ac | 2 | 1 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Sussex North SS 6297 | NB_6297_DSS | Sussex W. SS 6203 | NB_6203_DSS |  |  | 10
| L0003 | NB Power | New Brunswick | 1 | ac | 33 | 20 | 69 | 12.6814 | 3 | [5 empty] | 36 | 39 | Sussex W. SS 6203 | NB_6203_DSS | Hampton 69 SS 6268 | NB_6268_DSS |  |  | 11
| L0009 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Sweeny Lane SS 6409 | NB_6409_DSS | Newcastle TS | NB_NWCS_TSS |  |  | 32
| L0039 | NB Power | New Brunswick | 1 | ac | 10 | 6 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Taymouth SS 6111 | NB_6111_DSS | Junction 0135 | NB_0135_JCT |  |  | 133
| L1115 | NB Power | New Brunswick | 1 | ac | 12 | 7 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Tetagouche SS 6438 | NB_6438_DSS | Bathurst TS/SS 6432 | NB_6432_DSS |  |  | 283
| L0017 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Thomaston Corner SS 6193 | NB_6193_DSS | Junction 0139 | NB_0139_JCT |  |  | 62
| L6904 | Algonquin Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 0 | 0 | Tinker GS | NB_TNK_GSS | INT Tinker North | XX_NBUS2_INT |  |  | 313
| L6901 | Algonquin Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 0 | 0 | Tinker GS | NB_TNK_GSS | INT Tinker South | XX_NBUS3_INT |  |  | 312
| L1111 | NB Power | New Brunswick | 1 | ac | 35 | 21 | 138 | 15.175 | 3 | [5 empty] | 141 | 156 | Tobique GS | NB_TOBQ_GSS | Beechwood GS | NB_BCWD_GSS |  |  | 277
| L0037 | NB Power | New Brunswick | 1 | ac | 1 | 1 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Tobique GS | NB_TOBQ_GSS | Tobique Narrows SS 6156 | NB_6156_DSS |  |  | 128
| L0037 | NB Power | New Brunswick | 1 | ac | 27 | 17 | 69 | 10.3757 | 3 | [5 empty] | 36 | 39 | Tobique Narrows SS 6156 | NB_6156_DSS | Beechwood GS | NB_BCWD_GSS |  |  | 129
| L0069 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Tracadie SS 6436 | NB_6436_DSS | Sheila SS 6405 | NB_6405_DSS |  |  | 177
| L0094 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Turtle Creek SS 6517 | NB_6517_DSS | Riverview SS 6518 | NB_6518_DSS |  |  | 208
| L0015 | NB Power | New Brunswick | 1 | ac | 19 | 12 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Turtle Creek SS 6517 | NB_6517_DSS | Weldon SS 6538 | NB_6538_DSS |  |  | 50
| L0052 | NB Power | New Brunswick | 1 | ac | 4 | 3 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Union Street SS 5202 | NB_5202_DSS | Cranston TS | NB_CRAN_TSS |  |  | 157
| L0033 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Vanier SS 6118 | NB_6118_DSS | Aberdeen St SS 6100 | NB_6100_DSS |  |  | 122
| L1174 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Vanier SS 6118 | NB_6118_DSS | Rainsford Lane SS 6137 | NB_6137_DSS |  |  | 354
| L1104 | NB Power | New Brunswick | 1 | ac | 8 | 5 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Waasis Road SWS SS 4103 | NB_4103_DSS | Junction 1168 | NB_1168_JCT |  |  | 262
| L0015 | NB Power | New Brunswick | 1 | ac | 4 | 2 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Weldon SS 6538 | NB_6538_DSS | Junction 0067 | NB_0067_JCT |  |  | 51
| L1156 | NB Power | New Brunswick | 1 | ac | 17 | 10 | 138 | 7.3707 | 3 | [5 empty] | 141 | 156 | West Buctouche SS 6508 | NB_6508_DSS | Cocagne SS 6521 | NB_6521_DSS |  |  | 329
| L0019 | NB Power | New Brunswick | 1 | ac | 3 | 2 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Wilber St SS 6555 | NB_6555_DSS | St. George St SS 6553 | NB_6553_DSS |  |  | 72
| L0141 | NB Power | New Brunswick | 1 | ac | 7 | 4 | 69 | 2.69 | 3 | [5 empty] | 36 | 39 | Woodstock TS | NB_WDSK_TSS | Junction 0081 | NB_0081_JCT |  |  | 252
Legend:
CGS = Customer Generating Station
CS = Converter Station
CTS = Customer Transformer Station
DSC = Distribution Supply Centre
GEN = Generating Station
GS = Generating Station
JCT = Junction
MTS = Municipal Transformer Station
SS = Substation
SWS = Switching Station
SUB = Substation, Switching Station or Terminal Station
TS = Terminal Station
Specific Notes:
General Notes:
Dual function generation/substation nodes are categorized as "GEN"
See inputs tab for assumptions regarding system parameters
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## Nodes
NB | EXISTING SSS
| Node Name | Node Code | Owner | Latitude | Longitude | Planning Region | Other References | Notes
| Aberdeen St SS 6100 | NB_6100_DSS | NB Power | 45.9571 | -66.6466 | New Brunswick
| Albert SS 6515 | NB_6515_DSS | NB Power | 45.7314 | -64.7585 | New Brunswick
| Allardville SS 6420 | NB_6420_DSS | NB Power | 47.4747 | -65.4961 | New Brunswick
| Allardville SWS | NB_ALDV_SWS | NB Power | 47.4736 | -65.4955 | New Brunswick
| Allison SS 6520 | NB_6520_DSS | NB Power | 46.0564 | -64.8815 | New Brunswick
| Atholville SS 6401 | NB_6407_DSS | NB Power | 47.9879 | -66.7284 | New Brunswick
| Atlantic Waferboard SS 5407 | NB_5407_ISS | NB Power | 47.0102 | -65.4977 | New Brunswick |  | Location approximate
| Aulac SS 6516 | NB_6516_DSS | NB Power | 45.8716 | -64.2682 | New Brunswick
| Baie Ste. Anne SS 6429 | NB_6429_DSS | NB Power | 47.0411 | -64.9772 | New Brunswick
| Baig Blvd SS 6507 | NB_6507_DSS | NB Power | 46.0756 | -64.8227 | New Brunswick
| Baker Brook SS 6304 | NB_6304_DSS | NB Power | 47.303 | -68.4856 | New Brunswick
| Barkers Pt. SS 6125 | NB_6125_DSS | NB Power | 45.959 | -66.5915 | New Brunswick
| Bathurst TS/SS 6432 | NB_6432_DSS | NB Power | 47.592 | -65.6128 | New Brunswick
| Bathurst West SWS/SS 4400 | NB_4400_DSS | NB Power | 47.6253 | -65.7062 | New Brunswick
| Bay du Vin SS 6410 | NB_6410_DSS | NB Power | 47.0373 | -65.1542 | New Brunswick
| Bayside Drive SS 5299 | NB_5299_DSS | NB Power | 45.2758 | -66.0286 | New Brunswick
| Bayside GS | NB_BAYS_GSS | NB Power | 45.2758 | -66.0286 | New Brunswick
| Bayside SS 6222 | NB_6222_ISS | NB Power | 45.1574 | -67.1325 | New Brunswick
| Beechwood GS | NB_BCWD_GSS | NB Power | 46.5428 | -67.6687 | New Brunswick
| Beechwood SS 6391 | NB_6391_DSS | NB Power | 46.5432 | -67.6666 | New Brunswick
| Belledune Fert. SS 5406 | NB_5406_ISS | NB Power | 47.894 | -65.8526 | New Brunswick |  | Closed December 2019
| Belledune GS | NB_BELL_GSS | NB Power | 47.8903 | -65.8727 | New Brunswick
| Belledune Smelter SS 5404 | NB_5404_ISS | NB Power | 47.905 | -65.8465 | New Brunswick |  | Closed December 2019
| Belledune SS 6439 | NB_6439_DSS | NB Power | 47.8986 | -65.8664 | New Brunswick
| Belledune TS | NB_BELL_TSS | NB Power | 47.8842 | -65.9285 | New Brunswick
| Beresford SS 6416 | NB_6416_DSS | NB Power | 47.7195 | -65.7101 | New Brunswick
| Bertrand SS 6421 | NB_6421_DSS | NB Power | 47.7494 | -65.07 | New Brunswick
| Blacks Harbour North SS 6209 | NB_6209_DSS | NB Power | 45.0493 | -66.7938 | New Brunswick
| Boiestown SS 6117 | NB_6117_DSS | NB Power | 46.47 | -66.3963 | New Brunswick
| Brookville TS/SS 5266 | NB_5266_DSS | NB Power | 45.3308 | -66.0281 | New Brunswick
| Brown Rd. SWS | NB_BRWN_SWS | NB Power | 46.9894 | -65.5311 | New Brunswick
| Burpee Brook SS 6152 | NB_6152_DSS | NB Power | 45.9913 | -66.3593 | New Brunswick
| Burton SS 6112 | NB_6112_DSS | NB Power | 45.8524 | -66.4664 | New Brunswick
| Caledonia Park SS 6522 | NB_6522_DSS | NB Power | 46.1344 | -64.7549 | New Brunswick
| Camp Gagetown SS 5191 | NB_5191_DSS | NB Power | 45.8499 | -66.4598 | New Brunswick
| Campbellton SS 6426 | NB_6426_DSS | NB Power | 47.9998 | -66.683 | New Brunswick
| Campobello Island SS 6132 | NB_6132_DSS | NB Power | 44.8945 | -66.9039 | New Brunswick
| Canaan Forks SS 6202 | NB_6202_DSS | NB Power | 46.0571 | -65.5383 | New Brunswick
| Canada Liquid Air SS 5501 | NB_5501_ISS | NB Power | 46.138 | -64.7487 | New Brunswick
| Canaport SS 5204 | NB_5204_ISS | NB Power | 45.2137 | -65.9787 | New Brunswick
| Canterbury SS 6113 | NB_6113_DSS | NB Power | 45.8916 | -67.4577 | New Brunswick
| Cape Pele SS 6506 | NB_6506_DSS | NB Power | 46.2083 | -64.2711 | New Brunswick
| Caraquet SS 6401 | NB_6401_DSS | NB Power | 47.7886 | -64.9353 | New Brunswick
| Caraquet TS | NB_CRQT_TSS | NB Power | 47.7459 | -64.9115 | New Brunswick
| Caribou GS | NB_CRBO_GSS | NB Power | 47.5071 | -66.4135 | New Brunswick
| Caribou Mining SS 5497 | NB_5497_ISS | NB Power | 47.5635 | -66.2891 | New Brunswick
| Carleton St SS 6150 | NB_6150_DSS | NB Power | 45.9602 | -66.6425 | New Brunswick
| CBC Sackville SS 6541 | NB_6541_DSS | NB Power | 45.8921 | -64.3685 | New Brunswick |  | Location approximate
| Charlo SS 6430 | NB_6430_DSS | NB Power | 47.9787 | -66.2873 | New Brunswick
| Chartersville SS 6502 | NB_6502_DSS | NB Power | 46.0871 | -64.7336 | New Brunswick |  | Location approximate
| Chipman SS 6106 | NB_6106_DSS | NB Power | 46.1736 | -65.9001 | New Brunswick
| Christopher Brook SS 6422 | NB_6422_DSS | NB Power | 47.942 | -66.7841 | New Brunswick
| Church St. SS 6543 | NB_6543_DSS | NB Power | 46.1 | -64.778 | New Brunswick
| Clair SS 6311 | NB_6311_DSS | NB Power | 47.2576 | -68.6101 | New Brunswick
| Clairville SS 6544 | NB_6544_DSS | NB Power | 46.3593 | -65.1287 | New Brunswick
| Coal Creek SS 6195 | NB_6195_DSS | NB Power | 46.1053 | -65.8834 | New Brunswick
| Cocagne SS 6521 | NB_6521_DSS | NB Power | 46.3306 | -64.6715 | New Brunswick
| Coles Island SS 6536 | NB_6536_DSS | NB Power | 45.9324 | -65.7941 | New Brunswick
| Coleson Cove GS | NB_CLCV_GSS | NB Power | 45.154 | -66.2019 | New Brunswick
| College Bridge SS 6526 | NB_6526_DSS | NB Power | 45.9772 | -64.5398 | New Brunswick
| Commercial St SS 6503 | NB_6503_DSS | NB Power | 46.1101 | -64.818 | New Brunswick
| Connell St. SS 6199 | NB_6199_DSS | NB Power | 46.1586 | -67.5877 | New Brunswick
| Coulter Manufacturing SS 5503 | NB_5503_DSS | NB Power | 46.1624 | -64.5893 | New Brunswick
| Cranston TS | NB_CRAN_TSS | NB Power | 45.2858 | -66.0733 | New Brunswick
| Cross Creek SS 6155 | NB_6155_DSS | NB Power | 46.3062 | -66.7205 | New Brunswick
| Crown Street SS 5293 | NB_5293_DSS | NB Power | 45.2763 | -66.0493 | New Brunswick
| Dalhousie SS 6492 | NB_6492_DSS | NB Power | 48.0539 | -66.3708 | New Brunswick
| Darlington SS 6498 | NB_6498_DSS | NB Power | 48.0438 | -66.3978 | New Brunswick
| Deer Island SS 6293 | NB_6293_DSS | NB Power | 44.9807 | -66.9736 | New Brunswick
| Deersdale SS 5100 | NB_5100_DSS | NB Power | 46.4963 | -67.0426 | New Brunswick
| Denison Potacan SS 5218 | NB_5218_DSS | NB Power | 45.5619 | -65.5757 | New Brunswick
| Dever Road SS 5263 | NB_5263_DSS | NB Power | 45.2539 | -66.1134 | New Brunswick
| Devon SS 6154 | NB_6154_DSS | NB Power | 45.9735 | -66.6298 | New Brunswick
| Dieppe Industrial SS 6530 | NB_6530_DSS | NB Power | 46.1057 | -64.7225 | New Brunswick
| Doak SWS 4119 | NB_4119_SWS | NB Power | 45.9076 | -66.6119 | New Brunswick
| Doaktown SS 6419 | NB_6419_DSS | NB Power | 46.5496 | -66.1176 | New Brunswick
| Dorchester Cape SS 6539 | NB_6539_DSS | NB Power | 45.8652 | -64.5373 | New Brunswick
| Drummond St SS 6596 | NB_6596_DSS | NB Power | 46.111 | -64.7538 | New Brunswick
| East Chatham SS 6440 | NB_6440_DSS | NB Power | 47.0393 | -65.4498 | New Brunswick
| Edmundston East SS 6302 | NB_6302_DSS | NB Power | 47.3875 | -68.3384 | New Brunswick
| Edmundston North SS 6397 | NB_6397_DSS | NB Power | 47.3932 | -68.3536 | New Brunswick
| Edmundston TS | NB_EDMN_TSS | NB Power | 47.4117 | -68.2452 | New Brunswick
| Edmunston City SS 5398 | NB_5398_DSS | NB Power | 47.3688 | -68.3269 | New Brunswick
| Eel River TS | NB_EELR_TSS | NB Power | 48.0161 | -66.4437 | New Brunswick
| Fairvale SS 6226 | NB_6226_DSS | NB Power | 45.3936 | -65.9731 | New Brunswick
| Flakeboard Co. SS 5209 | NB_5209_ISS | NB Power | 45.1873 | -67.3126 | New Brunswick
| Florenceville SS 6114 | NB_6114_DSS | NB Power | 46.4474 | -67.6132 | New Brunswick
| Frasers Atholville SS 5409 | NB_5409_DSS | NB Power | 47.9904 | -66.7235 | New Brunswick
| Frasers Edmunston SS 5301 | NB_5301_ISS | NB Power | 47.3709 | -68.3296 | New Brunswick
| Frasers Iroquois SS 5105 | NB_5105_ISS | NB Power | 47.3678 | -68.263 | New Brunswick
| Frasers Plaster Rock SS 5106 | NB_5106_ISS | NB Power | 46.9078 | -67.3905 | New Brunswick
| Fredericton Junction SS 6116 | NB_6116_DSS | NB Power | 45.651 | -66.5987 | New Brunswick
| Gayton SS 6527 | NB_6527_DSS | NB Power | 46.0555 | -64.5821 | New Brunswick
| Gondola Point SS 6524 | NB_6524_DSS | NB Power | 45.4463 | -65.963 | New Brunswick
| Gordon Road SS 6412 | NB_6412_DSS | NB Power | 47.0216 | -65.4614 | New Brunswick
| Grafton SS 6105 | NB_6105_DSS | NB Power | 46.1542 | -67.5347 | New Brunswick |  | Location approximate
| Grand Bay SS 6528 | NB_6528_DSS | NB Power | 45.2995 | -66.1966 | New Brunswick
| Grand Falls East SS 6303 | NB_6303_DSS | NB Power | 47.0505 | -67.7157 | New Brunswick
| Grand Falls GS | NB_GRFS_GSS | NB Power | 47.0429 | -67.7369 | New Brunswick
| Grand Falls North SS 6333 | NB_6333_DSS | NB Power | 47.0616 | -67.7591 | New Brunswick
| Grand Falls South SS 6395 | NB_6395_DSS | NB Power | 47.0358 | -67.7409 | New Brunswick
| Grand Lake SS 6143 | NB_6143_DSS | NB Power | 46.0435 | -66.0333 | New Brunswick
| Grand Lake TS | NB_GRLK_TSS | NB Power | 46.0596 | -66.0033 | New Brunswick
| Grand Manan - Grand Harbour SS 6131 | NB_6131_DSS | NB Power | 44.6858 | -66.7736 | New Brunswick
| Grand Manan GS | NB_GMAN_GSS | NB Power | 44.7224 | -66.8239 | New Brunswick
| Grandview GS | NB_GRDV_GSS | NB Power | 45.2842 | -66.0094 | New Brunswick
| Green River SS 6144 | NB_6144_DSS | NB Power | 47.3259 | -68.1396 | New Brunswick
| Gunningsville SS 6531 | NB_6531_DSS | NB Power | 46.0628 | -64.7658 | New Brunswick
| Hacheyville SS 6415 | NB_6415_DSS | NB Power | 47.5307 | -65.0744 | New Brunswick
| Hainesville SS 6133 | NB_6133_DSS | NB Power | 46.0681 | -67.0212 | New Brunswick
| Hampton 138 SS 6534 | NB_6534_DSS | NB Power | 45.5133 | -65.8297 | New Brunswick
| Hampton 69 SS 6268 | NB_6268_DSS | NB Power | 45.5133 | -65.8297 | New Brunswick
| Harcourt SS 6504 | NB_6504_DSS | NB Power | 46.4771 | -65.2281 | New Brunswick
| Hardy Road SS 6514 | NB_6514_DSS | NB Power | 46.086 | -64.0271 | New Brunswick
| Hartland SS 6127 | NB_6127_DSS | NB Power | 46.3126 | -67.5352 | New Brunswick
| Harvey SS 6211 | NB_6211_DSS | NB Power | 45.7083 | -67.0272 | New Brunswick
| Havelock SS 6519 | NB_6519_DSS | NB Power | 46.0039 | -65.3263 | New Brunswick
| Highbank TS | NB_HBNK_TSS | NB Power | 47.0972 | -65.6011 | New Brunswick
| Hillsborough SS 6599 | NB_6599_DSS | NB Power | 45.9216 | -64.6456 | New Brunswick
| Howard SS 6441 | NB_6441_DSS | NB Power | 46.7214 | -65.8289 | New Brunswick
| Hunters Corner SS 6129 | NB_6129_DSS | NB Power | 46.4397 | -67.6562 | New Brunswick
| INT Beechwood | XX_NBUS4_INT | NB-US Border | 46.6016 | -67.7888 | New Brunswick
| INT Lepreau | XX_NBUS6_INT | NB-US Border | 45.2098 | -67.4313 | New Brunswick
| INT Madawaska | XX_NBUS1_INT | NB-US Border | 47.3556 | -68.3017 | New Brunswick
| INT Keswick | XX_NBUS5_INT | NB-US Border | 45.8516 | -67.7895 | New Brunswick
| INT Milltown | XX_NBUS7_INT | NB-US Border | 45.1761 | -67.2936 | New Brunswick
| INT Tinker North | XX_NBUS2_INT | NB-US Border | 46.8252 | -67.7896 | New Brunswick
| INT Tinker South | XX_NBUS3_INT | NB-US Border | 46.7912 | -67.7896 | New Brunswick
| IPT Amherst | PP_NSNB2_IPT | NS-NB Border | 45.8638 | -64.2629 | New Brunswick
| IPT Church St | PP_NSNB3_IPT | NS-NB Border | 45.8975 | -64.2274 | New Brunswick
| IPT Madawaska | PP_QBNB1_IPT | QB-NB Border | 47.4588 | -68.5231 | New Brunswick
| IPT Matapédia | PP_QBNB2_IPT | QB-NB Border | 47.9926 | -66.8514 | New Brunswick
| IPT Onslow | PP_NSNB1_IPT | NS-NB Border | 45.8975 | -64.2274 | New Brunswick
| IPT Richmond Cove | PP_NBPE1_IPT | NB-PE Border | 46.2051 | -63.7575 | New Brunswick |  | Midway across Northumberland Strait
| Iroquois TS | NB_IROQ_TSS | NB Power | 47.3706 | -68.2784 | New Brunswick
| Irving Pulp and Paper SS 5264 | NB_5264_ISS | NB Power | 45.2616 | -66.0939 | New Brunswick
| Irving Refinery 138 TS | NB_IRV138_TSS | NB Power | 45.2768 | -66.0126 | New Brunswick
| Irving Refinery 69 TS | NB_IRV69_TSS | NB Power | 45.2777 | -66.0087 | New Brunswick
| Irving Refinery SS 5296 | NB_5296_ISS | NB Power | 45.28 | -66.0105 | New Brunswick
| Irving Tissue SS 5203 | NB_5203_ISS | NB Power | 45.2576 | -66.0958 | New Brunswick
| Jacquet River SS 6413 | NB_6413_DSS | NB Power | 47.9167 | -65.9787 | New Brunswick
| Jemseg SS 6153 | NB_6153_DSS | NB Power | 45.7809 | -66.1008 | New Brunswick
| Junction 0015 | NB_0015_JCT | NB Power | 46.0483 | -64.8986 | New Brunswick
| Junction 0019 | NB_0019_JCT | NB Power | 46.125 | -64.8172 | New Brunswick
| Junction 0021 | NB_0021_JCT | NB Power | 46.0308 | -65.2875 | New Brunswick
| Junction 0022 | NB_0022_JCT | NB Power | 47.0262 | -67.7457 | New Brunswick
| Junction 0029 | NB_0029_JCT | NB Power | 46.1337 | -64.7584 | New Brunswick
| Junction 0038 | NB_0038_JCT | NB Power | 46.1719 | -67.5895 | New Brunswick
| Junction 0044E | NB_0044E_JCT | NB Power | 46.2065 | -64.5079 | New Brunswick
| Junction 0045 | NB_0045_JCT | NB Power | 45.1211 | -66.8232 | New Brunswick
| Junction 0050 | NB_0050_JCT | NB Power | 45.5897 | -67.3159 | New Brunswick
| Junction 0062 | NB_0062_JCT | NB Power | 47.5721 | -65.6319 | New Brunswick
| Junction 0065 | NB_0065_JCT | NB Power | 47.4544 | -67.4421 | New Brunswick
| Junction 0067 | NB_0067_JCT | NB Power | 45.9272 | -64.6678 | New Brunswick
| Junction 0068 | NB_0068_JCT | NB Power | 45.2565 | -66.0935 | New Brunswick
| Junction 0071 | NB_0071_JCT | NB Power | 48.0583 | -66.3998 | New Brunswick
| Junction 0081 | NB_0081_JCT | NB Power | 46.3093 | -67.6223 | New Brunswick
| Junction 0082 | NB_0082_JCT | NB Power | 45.1574 | -67.1302 | New Brunswick
| Junction 0085 | NB_0085_JCT | NB Power | 45.9256 | -64.482 | New Brunswick
| Junction 0090 | NB_0090_JCT | NB Power | 47.882 | -65.9889 | New Brunswick
| Junction 0092 | NB_0092_JCT | NB Power | 47.9774 | -66.6753 | New Brunswick
| Junction 0097 | NB_0097_JCT | NB Power | 47.2879 | -67.7098 | New Brunswick
| Junction 0098 | NB_0098_JCT | NB Power | 45.968 | -67.2364 | New Brunswick
| Junction 0099 | NB_0099_JCT | NB Power | 47.002 | -65.5023 | New Brunswick
| Junction 0103 | NB_0103_JCT | NB Power | 46.0951 | -64.7505 | New Brunswick |  | Location approximate
| Junction 0104 | NB_0104_JCT | NB Power | 47.2198 | -65.3994 | New Brunswick
| Junction 0105 | NB_0105_JCT | NB Power | 46.9988 | -65.4101 | New Brunswick
| Junction 0106 | NB_0106_JCT | NB Power | 45.1976 | -66.2962 | New Brunswick
| Junction 0107 | NB_0107_JCT | NB Power | 47.37 | -68.2616 | New Brunswick
| Junction 0109 | NB_0109_JCT | NB Power | 47.7021 | -65.7519 | New Brunswick
| Junction 0110 | NB_0110_JCT | NB Power | 45.1878 | -67.299 | New Brunswick
| Junction 0112 | NB_0112_JCT | NB Power | 47.5172 | -65.8057 | New Brunswick
| Junction 0114 | NB_0114_JCT | NB Power | 47.9651 | -66.7746 | New Brunswick
| Junction 0115 | NB_0115_JCT | NB Power | 47.1963 | -67.9264 | New Brunswick
| Junction 0121 | NB_0121_JCT | NB Power | 46.0617 | -64.5562 | New Brunswick
| Junction 0122 | NB_0122_JCT | NB Power | 45.9806 | -64.5117 | New Brunswick
| Junction 0124 | NB_0124_JCT | NB Power | 47.394 | -68.3339 | New Brunswick
| Junction 0125 | NB_0125_JCT | NB Power | 47.9851 | -66.7194 | New Brunswick
| Junction 0126 | NB_0126_JCT | NB Power | 47.595 | -65.6679 | New Brunswick
| Junction 0129 | NB_0129_JCT | NB Power | 47.971 | -66.2925 | New Brunswick
| Junction 0130 | NB_0130_JCT | NB Power | 45.8363 | -67.1723 | New Brunswick
| Junction 0133 | NB_0133_JCT | NB Power | 47.7124 | -64.7403 | New Brunswick |  | Location approximate
| Junction 0134 | NB_0134_JCT | NB Power | 45.9391 | -65.7951 | New Brunswick
| Junction 0135 | NB_0135_JCT | NB Power | 46.2773 | -66.6027 | New Brunswick
| Junction 0137 | NB_0137_JCT | NB Power | 47.3058 | -68.4849 | New Brunswick
| Junction 0138 | NB_0138_JCT | NB Power | 47.0563 | -67.7633 | New Brunswick |  | Location approximate
| Junction 0139 | NB_0139_JCT | NB Power | 45.6953 | -67.1426 | New Brunswick
| Junction 1121 | NB_1121_JCT | NB Power | 45.6377 | -66.5961 | New Brunswick
| Junction 1128 | NB_1128_JCT | NB Power | 47.849 | -65.8935 | New Brunswick
| Junction 1129 | NB_1129_JCT | NB Power | 45.8363 | -67.1723 | New Brunswick
| Junction 1136 | NB_1136_JCT | NB Power | 47.9834 | -66.7263 | New Brunswick
| Junction 1144 | NB_1144_JCT | NB Power | 46.8404 | -67.7027 | New Brunswick
| Junction 1153 | NB_1153_JCT | NB Power | 46.7094 | -65.741 | New Brunswick
| Junction 1162 | NB_1162_JCT | NB Power | 47.0455 | -67.7326 | New Brunswick
| Junction 1163 | NB_1163_JCT | NB Power | 45.416 | -65.9051 | New Brunswick
| Junction 1168 | NB_1168_JCT | NB Power | 45.8558 | -66.6244 | New Brunswick
| Junction 1171 | NB_1171_JCT | NB Power | 46.0372 | -64.7886 | New Brunswick
| Junction 1172 | NB_1172_JCT | NB Power | 46.1303 | -67.1113 | New Brunswick
| Junction 1173 | NB_1173_JCT | NB Power | 45.5026 | -65.81 | New Brunswick
| Junction 1174 | NB_1174_JCT | NB Power | 45.9074 | -66.6121 | New Brunswick
| Junction 1177 | NB_1177_JCT | NB Power | 45.765 | -65.4715 | New Brunswick
| Junction 1178 | NB_1178_JCT | NB Power | 45.6118 | -65.7153 | New Brunswick
| Junction 1179 | NB_1179_JCT | NB Power | 46.136 | -64.7478 | New Brunswick
| Junction 1181 | NB_1181_JCT | NB Power | 45.7699 | -65.4391 | New Brunswick
| Junction 1187 | NB_1187_JCT | NB Power | 45.3748 | -65.9542 | New Brunswick
| Junction 1191 | NB_1191_JCT | NB Power | 46.1098 | -64.7202 | New Brunswick
| Junction 1192 | NB_1192_JCT | NB Power | 45.9832 | -66.6207 | New Brunswick
| Junction 1195 | NB_1195_JCT | NB Power | 47.4899 | -65.9076 | New Brunswick
| Junction 1197 | NB_1197_JCT | NB Power | 45.8562 | -66.6247 | New Brunswick
| Junction 1205 | NB_1205_JCT | NB Power | 46.3102 | -67.3666 | New Brunswick
| Junction 1208 | NB_1208_JCT | NB Power | 45.3761 | -65.953 | New Brunswick
| Juniper SS 6107 | NB_6107_DSS | NB Power | 46.5457 | -67.2213 | New Brunswick
| Kedgwick SS 6301 | NB_6301_DSS | NB Power | 47.6533 | -67.3429 | New Brunswick
| Kent Hills Wind GS | NB_KNTH_GSS | NB Power | 45.8194 | -64.8894 | New Brunswick
| Keswick Ridge SS 6139 | NB_6139_DSS | NB Power | 45.9632 | -66.8653 | New Brunswick
| Keswick TS | NB_KSWK_TSS | NB Power | 46.0572 | -66.8494 | New Brunswick
| Kingsclear SS 6109 | NB_6109_DSS | NB Power | 45.9368 | -66.7582 | New Brunswick
| Lake George SS 6126 | NB_6126_DSS | NB Power | 45.8482 | -67.0346 | New Brunswick
| Lake Utopia Paper SS 5206 | NB_5206_ISS | NB Power | 45.158 | -66.7704 | New Brunswick
| Lakeside SS 6545 | NB_6545_DSS | NB Power | 46.1539 | -64.6748 | New Brunswick
| Lakewood SS 5211 | NB_5211_DSS | NB Power | 45.3002 | -65.9912 | New Brunswick
| Lameque GS | NB_LMEQ_GSS | NB Power | 47.8494 | -64.6187 | New Brunswick
| Lameque SS 6417 | NB_6417_DSS | NB Power | 47.8358 | -64.6139 | New Brunswick
| Lancaster TS | NB_LNCT_TSS | NB Power | 45.2348 | -66.1368 | New Brunswick
| Lepreau SS 6205 | NB_6205_DSS | NB Power | 45.166 | -66.4789 | New Brunswick
| Loch Lomond SS 6204 | NB_6204_DSS | NB Power | 45.3399 | -65.8753 | New Brunswick
| Lower Caraquet SS 6437 | NB_6437_DSS | NB Power | 47.7936 | -64.8266 | New Brunswick
| Lutz Mtn. SS 6510 | NB_6510_DSS | NB Power | 46.1291 | -64.8861 | New Brunswick
| Mactaquac GS | NB_MTQC_GSS | NB Power | 45.9551 | -66.8665 | New Brunswick
| Manawagonish Road SS 5219 | NB_5219_DSS | NB Power | 45.2354 | -66.1374 | New Brunswick
| Marysville TS | NB_MRYV_TSS | NB Power | 45.967 | -66.597 | New Brunswick
| McAdam SS 6225 | NB_6225_DSS | NB Power | 45.5895 | -67.3179 | New Brunswick
| McCains SS 5102 | NB_5102_DSS | NB Power | 47.0642 | -67.7776 | New Brunswick
| Memramcook TS | NB_MRMK_TSS | NB Power | 46.0021 | -64.5106 | New Brunswick
| Mill Lane SS 6207 | NB_6207_DSS | NB Power | 45.5884 | -67.3156 | New Brunswick
| Millbank GS | NB_MLBK_GSS | NB Power | 47.071 | -65.4541 | New Brunswick
| Millidgeville SS 5213 | NB_5213_DSS | NB Power | 45.2895 | -66.0955 | New Brunswick
| Milltown GS | NB_MLTN_GSS | NB Power | 45.1755 | -67.2929 | New Brunswick
| Millville SS 6194 | NB_6194_DSS | NB Power | 46.0925 | -67.2204 | New Brunswick
| Millville TS | NB_MIVL_TSS | NB Power | 46.0836 | -67.1819 | New Brunswick
| Minto SS 6120 | NB_6120_DSS | NB Power | 46.0844 | -66.0341 | New Brunswick
| Miramichi P&P - South Nelson 5419 | NB_5419_ISS | NB Power | 46.9722 | -65.5539 | New Brunswick
| Moncton TS | NB_MCTN_TSS | NB Power | 46.0945 | -64.845 | New Brunswick
| Mount Pleasant Mines SS 5216 | NB_5216_DSS | NB Power | 45.4255 | -66.8195 | New Brunswick
| Murray Corner TS | NB_MCNR_TSS | NB Power | 46.1665 | -63.9562 | New Brunswick
| Musquash Pumping Station 5208 | NB_5208_SUB | NB Power | 45.2369 | -66.2906 | New Brunswick
| Nackawic SS 6108 | NB_6108_DSS | NB Power | 45.9967 | -67.2481 | New Brunswick
| Nashwaaksis SS 6135 | NB_6135_DSS | NB Power | 45.9942 | -66.6496 | New Brunswick
| Neguac SS 6406 | NB_6406_DSS | NB Power | 47.249 | -65.104 | New Brunswick
| Nelson SS 6442 | NB_6442_DSS | NB Power | 46.9966 | -65.5476 | New Brunswick
| Nepisiguit Falls SS 6404 | NB_6404_DSS | NB Power | 47.4055 | -65.7918 | New Brunswick
| New Denmark SS 6390 | NB_6390_DSS | NB Power | 47.0001 | -67.6114 | New Brunswick
| New Maryland SS 6158 | NB_6158_DSS | NB Power | 45.8852 | -66.6861 | New Brunswick
| Newcastle Town SS 6443 | NB_6443_DSS | NB Power | 46.9935 | -65.572 | New Brunswick
| Newcastle TS | NB_NWCS_TSS | NB Power | 47.0213 | -65.5963 | New Brunswick
| Norton TS | NB_NRTN_TSS | NB Power | 45.664 | -65.6512 | New Brunswick
| Oak Bay TS | NB_OKBY_TSS | NB Power | 45.2433 | -67.1957 | New Brunswick
| Oromocto Town SS 6140 | NB_6140_DSS | NB Power | 45.8385 | -66.5037 | New Brunswick
| Ortonville SWS | NB_ORTN_SWS | NB Power | 46.9507 | -67.7093 | New Brunswick
| Pennfield Ridge SS 6206 | NB_6206_DSS | NB Power | 45.1079 | -66.7406 | New Brunswick
| Pennfield TS | NB_PNFD_TSS | NB Power | 45.1095 | -66.7433 | New Brunswick
| Petit Rocher SS 6491 | NB_6491_DSS | NB Power | 47.8083 | -65.8063 | New Brunswick
| Petitcodiac SS 6558 | NB_6558_DSS | NB Power | 45.9252 | -65.1503 | New Brunswick
| Plaster Rock SS 6394 | NB_6394_DSS | NB Power | 46.9213 | -67.3989 | New Brunswick
| Point Lepreau GS | NB_PLPR_GSS | NB Power | 45.0687 | -66.4543 | New Brunswick
| Potash Co. SS 5217 | NB_5217_ISS | NB Power | 45.7524 | -65.4283 | New Brunswick
| Priestman SS 6124 | NB_6124_DSS | NB Power | 45.9379 | -66.6498 | New Brunswick
| Rainsford Lane SS 6137 | NB_6137_DSS | NB Power | 45.9453 | -66.7002 | New Brunswick
| Raynes Avenue SS 5214 | NB_5214_DSS | NB Power | 45.2552 | -66.0921 | New Brunswick
| Red Bank SS 6424 | NB_6424_DSS | NB Power | 46.9639 | -65.7458 | New Brunswick
| Rexton SS 6535 | NB_6535_DSS | NB Power | 46.6337 | -64.8748 | New Brunswick
| Richibucto SS 6533 | NB_6533_DSS | NB Power | 46.6791 | -64.8827 | New Brunswick
| Ripples SS 6142 | NB_6142_DSS | NB Power | 46.0132 | -66.2329 | New Brunswick
| Riverview SS 6518 | NB_6518_DSS | NB Power | 46.049 | -64.8131 | New Brunswick
| Rogersville SS 6411 | NB_6411_DSS | NB Power | 46.7434 | -65.4108 | New Brunswick
| Rothesay Paper SS 5295 | NB_5295_ISS | NB Power | 45.2799 | -66.0239 | New Brunswick
| Rothesay SS 6267 | NB_6267_DSS | NB Power | 45.3936 | -65.9731 | New Brunswick
| Rusagonis SS 6141 | NB_6141_DSS | NB Power | 45.805 | -66.6327 | New Brunswick
| Ryan Rd SS 6525 | NB_6525_DSS | NB Power | 46.1102 | -64.8487 | New Brunswick
| Sackville SS 6511 | NB_6511_DSS | NB Power | 45.9041 | -64.3816 | New Brunswick
| Salisbury SS 6556 | NB_6556_DSS | NB Power | 46.0078 | -65.0289 | New Brunswick
| Salisbury TS | NB_SLBY_TSS | NB Power | 46.021 | -64.9963 | New Brunswick
| Scoudouc Ind. SS 6540 | NB_6540_ISS | NB Power | 46.1764 | -64.5882 | New Brunswick
| Scoudouc SS 6595 | NB_6595_DSS | NB Power | 46.1576 | -64.5633 | New Brunswick
| Shediac SS 6513 | NB_6513_DSS | NB Power | 46.2235 | -64.4829 | New Brunswick
| Shediac Wst SS 6529 | NB_6529_DSS | NB Power | 46.21 | -64.5325 | New Brunswick
| Sheila SS 6405 | NB_6405_DSS | NB Power | 47.4884 | -64.9233 | New Brunswick
| Shippigan SS 6490 | NB_6490_DSS | NB Power | 47.7428 | -64.717 | New Brunswick
| Sisson GS | NB_SSON_GSS | NB Power | 47.266 | -67.2434 | New Brunswick
| Six Roads SS 6425 | NB_6425_DSS | NB Power | 47.6139 | -64.8921 | New Brunswick
| South Bathurst SS 6449 | NB_6449_DSS | NB Power | 47.6049 | -65.6458 | New Brunswick
| Springfield SS 6200 | NB_6200_DSS | NB Power | 45.6618 | -65.7877 | New Brunswick
| St. André TS | NB_SADR_TSS | NB Power | 47.1665 | -67.7305 | New Brunswick
| St. Andrews SS 6296 | NB_6296_DSS | NB Power | 45.0861 | -67.0661 | New Brunswick
| St. Anne Nackawic SS 5116 | NB_5116_DSS | NB Power | 46.0129 | -67.223 | New Brunswick
| St. Basile SS 6396 | NB_6396_DSS | NB Power | 47.3592 | -68.2207 | New Brunswick
| St. George GS | NB_SGRG_GSS | NB Power | 45.1283 | -66.8279 | New Brunswick
| St. George SS 6145 | NB_6145_DSS | NB Power | 45.1213 | -66.8244 | New Brunswick
| St. George St SS 6553 | NB_6553_DSS | NB Power | 46.0883 | -64.7966 | New Brunswick
| St. Leolin SS 6435 | NB_6435_DSS | NB Power | 47.7631 | -65.1974 | New Brunswick
| St. Leonard Sawmill SS 5107 | NB_5107_ISS | NB Power | 47.1927 | -67.9305 | New Brunswick
| St. Leonard SWS | NB_SLND_SWS | NB Power | 47.1732 | -67.9094 | New Brunswick
| St. Louis SS 6532 | NB_6532_DSS | NB Power | 46.7298 | -64.9794 | New Brunswick
| St. Mary's SS 6505 | NB_6505_DSS | NB Power | 46.412 | -64.8568 | New Brunswick
| St. Quentin SS 6337 | NB_6337_DSS | NB Power | 47.5135 | -67.4012 | New Brunswick
| St. Stephen SS 6223 | NB_6223_DSS | NB Power | 45.1993 | -67.2839 | New Brunswick
| Ste Rose GS | NB_SROS_GSS | NB Power | 47.6263 | -64.954 | New Brunswick
| Stone Con. Sawmill SS 6431 | NB_6431_ISS | NB Power | 47.474 | -65.7616 | New Brunswick
| Sugar Loaf SS 6408 | NB_6408_DSS | NB Power | 47.9921 | -66.6663 | New Brunswick
| Sussex Corner SS 6537 | NB_6537_DSS | NB Power | 45.7137 | -65.4703 | New Brunswick
| Sussex North SS 6297 | NB_6297_DSS | NB Power | 45.7334 | -65.5027 | New Brunswick
| Sussex W. SS 6203 | NB_6203_DSS | NB Power | 45.724 | -65.5247 | New Brunswick
| Sweeny Lane SS 6409 | NB_6409_DSS | NB Power | 46.995 | -65.579 | New Brunswick
| Taymouth SS 6111 | NB_6111_DSS | NB Power | 46.1832 | -66.6206 | New Brunswick
| Tetagouche SS 6438 | NB_6438_DSS | NB Power | 47.6488 | -65.7289 | New Brunswick
| Thomaston Corner SS 6193 | NB_6193_DSS | NB Power | 45.6567 | -67.1315 | New Brunswick
| Tinker GS | NB_TNK_GSS | NB Power | 46.8097 | -67.7665 | New Brunswick
| Tobique GS | NB_TOBQ_GSS | NB Power | 46.7801 | -67.6953 | New Brunswick
| Tobique Narrows SS 6156 | NB_6156_DSS | NB Power | 46.7788 | -67.6936 | New Brunswick
| Tracadie SS 6436 | NB_6436_DSS | NB Power | 47.5136 | -64.9342 | New Brunswick
| Turtle Creek SS 6517 | NB_6517_DSS | NB Power | 46.0234 | -64.8682 | New Brunswick
| Union Street SS 5202 | NB_5202_DSS | NB Power | 45.274 | -66.0665 | New Brunswick
| Vanier SS 6118 | NB_6118_DSS | NB Power | 45.9083 | -66.6126 | New Brunswick
| Veneer Siding SS 5312 | NB_5312_DSS | NB Power | 47.3142 | -67.7078 | New Brunswick
| Waasis Road SWS SS 4103 | NB_4103_DSS | NB Power | 45.8159 | -66.6324 | New Brunswick
| Weldon SS 6538 | NB_6538_DSS | NB Power | 45.9444 | -64.714 | New Brunswick
| West Bathurst SS 6418 | NB_6418_DSS | NB Power | 47.6285 | -65.6768 | New Brunswick
| West Buctouche SS 6508 | NB_6508_DSS | NB Power | 46.4685 | -64.737 | New Brunswick
| Westfield SS 6298 | NB_6298_DSS | NB Power | 45.359 | -66.2409 | New Brunswick
| Wilber St SS 6555 | NB_6555_DSS | NB Power | 46.0977 | -64.8048 | New Brunswick
| Woodstock South SS 6121 | NB_6121_DSS | NB Power | 46.1419 | -67.5811 | New Brunswick
| Woodstock TS | NB_WDSK_TSS | NB Power | 46.2491 | -67.6072 | New Brunswick
Legend:
CSS = Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
ISS = Industrial Customer Substation
JCT = Junction
SWS = Switching Station
TSS = Terminal Station

## Distribution
NB | EXISTING SSS
| Node Name | Node Code | Owner | Latitude | Longitude | Planning Region | Transformers | Primary Voltage | Secondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Other References | Notes
[8 empty] | (kV) | (kV) | (MVA) | (MVA) |  | (MW) | (MW)
| Aberdeen St SS 6100 | NB_6100_DSS | NB Power | 45.9571 | -66.6466 | New Brunswick
| Albert SS 6515 | NB_6515_DSS | NB Power | 45.7314 | -64.7585 | New Brunswick
| Allardville SS 6420 | NB_6420_DSS | NB Power | 47.4747 | -65.4961 | New Brunswick
| Allardville SWS | NB_ALDV_SWS | NB Power | 47.4736 | -65.4955 | New Brunswick
| Allison SS 6520 | NB_6520_DSS | NB Power | 46.0564 | -64.8815 | New Brunswick
| Atholville SS 6401 | NB_6407_DSS | NB Power | 47.9879 | -66.7284 | New Brunswick
| Atlantic Waferboard SS 5407 | NB_5407_ISS | NB Power | 47.0102 | -65.4977 | New Brunswick
| Aulac SS 6516 | NB_6516_DSS | NB Power | 45.8716 | -64.2682 | New Brunswick
| Baie Ste. Anne SS 6429 | NB_6429_DSS | NB Power | 47.0411 | -64.9772 | New Brunswick
| Baig Blvd SS 6507 | NB_6507_DSS | NB Power | 46.0756 | -64.8227 | New Brunswick
| Baker Brook SS 6304 | NB_6304_DSS | NB Power | 47.303 | -68.4856 | New Brunswick
| Barkers Pt. SS 6125 | NB_6125_DSS | NB Power | 45.959 | -66.5915 | New Brunswick
| Bathurst TS/SS 6432 | NB_6432_DSS | NB Power | 47.592 | -65.6128 | New Brunswick
| Bathurst West SWS/SS 4400 | NB_4400_DSS | NB Power | 47.6253 | -65.7062 | New Brunswick
| Bay du Vin SS 6410 | NB_6410_DSS | NB Power | 47.0373 | -65.1542 | New Brunswick
| Bayside Drive SS 5299 | NB_5299_DSS | NB Power | 45.2758 | -66.0286 | New Brunswick
| Bayside GS | NB_BAYS_GSS | NB Power | 45.2758 | -66.0286 | New Brunswick
| Bayside SS 6222 | NB_6222_ISS | NB Power | 45.1574 | -67.1325 | New Brunswick
| Beechwood GS | NB_BCWD_GSS | NB Power | 46.5428 | -67.6687 | New Brunswick
| Beechwood SS 6391 | NB_6391_DSS | NB Power | 46.5432 | -67.6666 | New Brunswick
| Belledune Fert. SS 5406 | NB_5406_ISS | NB Power | 47.894 | -65.8526 | New Brunswick
| Belledune GS | NB_BELL_GSS | NB Power | 47.8903 | -65.8727 | New Brunswick
| Belledune Smelter SS 5404 | NB_5404_ISS | NB Power | 47.905 | -65.8465 | New Brunswick
| Belledune SS 6439 | NB_6439_DSS | NB Power | 47.8986 | -65.8664 | New Brunswick
| Belledune TS | NB_BELL_TSS | NB Power | 47.8842 | -65.9285 | New Brunswick
| Beresford SS 6416 | NB_6416_DSS | NB Power | 47.7195 | -65.7101 | New Brunswick
| Bertrand SS 6421 | NB_6421_DSS | NB Power | 47.7494 | -65.07 | New Brunswick
| Blacks Harbour North SS 6209 | NB_6209_DSS | NB Power | 45.0493 | -66.7938 | New Brunswick
| Boiestown SS 6117 | NB_6117_DSS | NB Power | 46.47 | -66.3963 | New Brunswick
| Brookville TS/SS 5266 | NB_5266_DSS | NB Power | 45.3308 | -66.0281 | New Brunswick
| Brown Rd. SWS | NB_BRWN_SWS | NB Power | 46.9894 | -65.5311 | New Brunswick
| Burpee Brook SS 6152 | NB_6152_DSS | NB Power | 45.9913 | -66.3593 | New Brunswick
| Burton SS 6112 | NB_6112_DSS | NB Power | 45.8524 | -66.4664 | New Brunswick
| Caledonia Park SS 6522 | NB_6522_DSS | NB Power | 46.1344 | -64.7549 | New Brunswick
| Camp Gagetown SS 5191 | NB_5191_DSS | NB Power | 45.8499 | -66.4598 | New Brunswick
| Campbellton SS 6426 | NB_6426_DSS | NB Power | 47.9998 | -66.683 | New Brunswick
| Campobello Island SS 6132 | NB_6132_DSS | NB Power | 44.8945 | -66.9039 | New Brunswick
| Canaan Forks SS 6202 | NB_6202_DSS | NB Power | 46.0571 | -65.5383 | New Brunswick
| Canada Liquid Air SS 5501 | NB_5501_ISS | NB Power | 46.138 | -64.7487 | New Brunswick
| Canaport SS 5204 | NB_5204_ISS | NB Power | 45.2137 | -65.9787 | New Brunswick
| Canterbury SS 6113 | NB_6113_DSS | NB Power | 45.8916 | -67.4577 | New Brunswick
| Cape Pele SS 6506 | NB_6506_DSS | NB Power | 46.2083 | -64.2711 | New Brunswick
| Caraquet SS 6401 | NB_6401_DSS | NB Power | 47.7886 | -64.9353 | New Brunswick
| Caraquet TS | NB_CRQT_TSS | NB Power | 47.7459 | -64.9115 | New Brunswick
| Caribou GS | NB_CRBO_GSS | NB Power | 47.5071 | -66.4135 | New Brunswick
| Caribou Mining SS 5497 | NB_5497_ISS | NB Power | 47.5635 | -66.2891 | New Brunswick
| Carleton St SS 6150 | NB_6150_DSS | NB Power | 45.9602 | -66.6425 | New Brunswick
| CBC Sackville SS 6541 | NB_6541_DSS | NB Power | 45.8921 | -64.3685 | New Brunswick
| Charlo SS 6430 | NB_6430_DSS | NB Power | 47.9787 | -66.2873 | New Brunswick
| Chartersville SS 6502 | NB_6502_DSS | NB Power | 46.0871 | -64.7336 | New Brunswick
| Chipman SS 6106 | NB_6106_DSS | NB Power | 46.1736 | -65.9001 | New Brunswick
| Christopher Brook SS 6422 | NB_6422_DSS | NB Power | 47.942 | -66.7841 | New Brunswick
| Church St. SS 6543 | NB_6543_DSS | NB Power | 46.1 | -64.778 | New Brunswick
| Clair SS 6311 | NB_6311_DSS | NB Power | 47.2576 | -68.6101 | New Brunswick
| Clairville SS 6544 | NB_6544_DSS | NB Power | 46.3593 | -65.1287 | New Brunswick
| Coal Creek SS 6195 | NB_6195_DSS | NB Power | 46.1053 | -65.8834 | New Brunswick
| Cocagne SS 6521 | NB_6521_DSS | NB Power | 46.3306 | -64.6715 | New Brunswick
| Coles Island SS 6536 | NB_6536_DSS | NB Power | 45.9324 | -65.7941 | New Brunswick
| Coleson Cove GS | NB_CLCV_GSS | NB Power | 45.154 | -66.2019 | New Brunswick
| College Bridge SS 6526 | NB_6526_DSS | NB Power | 45.9772 | -64.5398 | New Brunswick
| Commercial St SS 6503 | NB_6503_DSS | NB Power | 46.1101 | -64.818 | New Brunswick
| Connell St. SS 6199 | NB_6199_DSS | NB Power | 46.1586 | -67.5877 | New Brunswick
| Coulter Manufacturing SS 5503 | NB_5503_DSS | NB Power | 46.1624 | -64.5893 | New Brunswick
| Cranston TS | NB_CRAN_TSS | NB Power | 45.2858 | -66.0733 | New Brunswick
| Cross Creek SS 6155 | NB_6155_DSS | NB Power | 46.3062 | -66.7205 | New Brunswick
| Crown Street SS 5293 | NB_5293_DSS | NB Power | 45.2763 | -66.0493 | New Brunswick
| Dalhousie SS 6492 | NB_6492_DSS | NB Power | 48.0539 | -66.3708 | New Brunswick
| Darlington SS 6498 | NB_6498_DSS | NB Power | 48.0438 | -66.3978 | New Brunswick
| Deer Island SS 6293 | NB_6293_DSS | NB Power | 44.9807 | -66.9736 | New Brunswick
| Deersdale SS 5100 | NB_5100_DSS | NB Power | 46.4963 | -67.0426 | New Brunswick
| Denison Potacan SS 5218 | NB_5218_DSS | NB Power | 45.5619 | -65.5757 | New Brunswick
| Dever Road SS 5263 | NB_5263_DSS | NB Power | 45.2539 | -66.1134 | New Brunswick
| Devon SS 6154 | NB_6154_DSS | NB Power | 45.9735 | -66.6298 | New Brunswick
| Dieppe Industrial SS 6530 | NB_6530_DSS | NB Power | 46.1057 | -64.7225 | New Brunswick
| Doak SWS 4119 | NB_4119_SWS | NB Power | 45.9076 | -66.6119 | New Brunswick
| Doaktown SS 6419 | NB_6419_DSS | NB Power | 46.5496 | -66.1176 | New Brunswick
| Dorchester Cape SS 6539 | NB_6539_DSS | NB Power | 45.8652 | -64.5373 | New Brunswick
| Drummond St SS 6596 | NB_6596_DSS | NB Power | 46.111 | -64.7538 | New Brunswick
| East Chatham SS 6440 | NB_6440_DSS | NB Power | 47.0393 | -65.4498 | New Brunswick
| Edmundston East SS 6302 | NB_6302_DSS | NB Power | 47.3875 | -68.3384 | New Brunswick
| Edmundston North SS 6397 | NB_6397_DSS | NB Power | 47.3932 | -68.3536 | New Brunswick
| Edmundston TS | NB_EDMN_TSS | NB Power | 47.4117 | -68.2452 | New Brunswick
| Edmunston City SS 5398 | NB_5398_DSS | NB Power | 47.3688 | -68.3269 | New Brunswick
| Eel River TS | NB_EELR_TSS | NB Power | 48.0161 | -66.4437 | New Brunswick
| Fairvale SS 6226 | NB_6226_DSS | NB Power | 45.3936 | -65.9731 | New Brunswick
| Flakeboard Co. SS 5209 | NB_5209_ISS | NB Power | 45.1873 | -67.3126 | New Brunswick
| Florenceville SS 6114 | NB_6114_DSS | NB Power | 46.4474 | -67.6132 | New Brunswick
| Frasers Atholville SS 5409 | NB_5409_DSS | NB Power | 47.9904 | -66.7235 | New Brunswick
| Frasers Edmunston SS 5301 | NB_5301_ISS | NB Power | 47.3709 | -68.3296 | New Brunswick
| Frasers Iroquois SS 5105 | NB_5105_ISS | NB Power | 47.3678 | -68.263 | New Brunswick
| Frasers Plaster Rock SS 5106 | NB_5106_ISS | NB Power | 46.9078 | -67.3905 | New Brunswick
| Fredericton Junction SS 6116 | NB_6116_DSS | NB Power | 45.651 | -66.5987 | New Brunswick
| Gayton SS 6527 | NB_6527_DSS | NB Power | 46.0555 | -64.5821 | New Brunswick
| Gondola Point SS 6524 | NB_6524_DSS | NB Power | 45.4463 | -65.963 | New Brunswick
| Gordon Road SS 6412 | NB_6412_DSS | NB Power | 47.0216 | -65.4614 | New Brunswick
| Grafton SS 6105 | NB_6105_DSS | NB Power | 46.1542 | -67.5347 | New Brunswick
| Grand Bay SS 6528 | NB_6528_DSS | NB Power | 45.2995 | -66.1966 | New Brunswick
| Grand Falls East SS 6303 | NB_6303_DSS | NB Power | 47.0505 | -67.7157 | New Brunswick
| Grand Falls GS | NB_GRFS_GSS | NB Power | 47.0429 | -67.7369 | New Brunswick
| Grand Falls North SS 6333 | NB_6333_DSS | NB Power | 47.0616 | -67.7591 | New Brunswick
| Grand Falls South SS 6395 | NB_6395_DSS | NB Power | 47.0358 | -67.7409 | New Brunswick
| Grand Lake SS 6143 | NB_6143_DSS | NB Power | 46.0435 | -66.0333 | New Brunswick
| Grand Lake TS | NB_GRLK_TSS | NB Power | 46.0596 | -66.0033 | New Brunswick
| Grand Manan - Grand Harbour SS 6131 | NB_6131_DSS | NB Power | 44.6858 | -66.7736 | New Brunswick
| Grand Manan GS | NB_GMAN_GSS | NB Power | 44.7224 | -66.8239 | New Brunswick
| Grandview GS | NB_GRDV_GSS | NB Power | 45.2842 | -66.0094 | New Brunswick
| Green River SS 6144 | NB_6144_DSS | NB Power | 47.3259 | -68.1396 | New Brunswick
| Gunningsville SS 6531 | NB_6531_DSS | NB Power | 46.0628 | -64.7658 | New Brunswick
| Hacheyville SS 6415 | NB_6415_DSS | NB Power | 47.5307 | -65.0744 | New Brunswick
| Hainesville SS 6133 | NB_6133_DSS | NB Power | 46.0681 | -67.0212 | New Brunswick
| Hampton 138 SS 6534 | NB_6534_DSS | NB Power | 45.5133 | -65.8297 | New Brunswick
| Hampton 69 SS 6268 | NB_6268_DSS | NB Power | 45.5133 | -65.8297 | New Brunswick
| Harcourt SS 6504 | NB_6504_DSS | NB Power | 46.4771 | -65.2281 | New Brunswick
| Hardy Road SS 6514 | NB_6514_DSS | NB Power | 46.086 | -64.0271 | New Brunswick
| Hartland SS 6127 | NB_6127_DSS | NB Power | 46.3126 | -67.5352 | New Brunswick
| Harvey SS 6211 | NB_6211_DSS | NB Power | 45.7083 | -67.0272 | New Brunswick
| Havelock SS 6519 | NB_6519_DSS | NB Power | 46.0039 | -65.3263 | New Brunswick
| Highbank TS | NB_HBNK_TSS | NB Power | 47.0972 | -65.6011 | New Brunswick
| Hillsborough SS 6599 | NB_6599_DSS | NB Power | 45.9216 | -64.6456 | New Brunswick
| Howard SS 6441 | NB_6441_DSS | NB Power | 46.7214 | -65.8289 | New Brunswick
| Hunters Corner SS 6129 | NB_6129_DSS | NB Power | 46.4397 | -67.6562 | New Brunswick
| INT Beechwood | XX_NBUS4_INT | NB Power | 46.6016 | -67.7888 | New Brunswick
| INT Lepreau | XX_NBUS6_INT | NB Power | 45.2098 | -67.4313 | New Brunswick
| INT Madawaska | XX_NBUS1_INT | NB Power | 47.3556 | -68.3017 | New Brunswick
| INT Keswick | XX_NBUS5_INT | NB Power | 45.8516 | -67.7895 | New Brunswick
| INT Milltown | XX_NBUS7_INT | NB Power | 45.1761 | -67.2936 | New Brunswick
| INT Tinker North | XX_NBUS2_INT | NB Power | 46.8252 | -67.7896 | New Brunswick
| INT Tinker South | XX_NBUS3_INT | NB Power | 46.7912 | -67.7896 | New Brunswick
| IPT Amherst | PP_NSNB2_IPT | NB Power | 45.8638 | -64.2629 | New Brunswick
| IPT Church St | PP_NSNB3_IPT | NB Power | 45.8975 | -64.2274 | New Brunswick
| IPT Madawaska | PP_QBNB1_IPT | NB Power | 47.4588 | -68.5231 | New Brunswick
| IPT Matapédia | PP_QBNB2_IPT | NB Power | 47.9926 | -66.8514 | New Brunswick
| IPT Onslow | PP_NSNB1_IPT | NB Power | 45.8975 | -64.2274 | New Brunswick
| IPT Richmond Cove | PP_NBPE1_IPT | NB Power | 46.2051 | -63.7575 | New Brunswick
| Iroquois TS | NB_IROQ_TSS | NB Power | 47.3706 | -68.2784 | New Brunswick
| Irving Pulp and Paper SS 5264 | NB_5264_ISS | NB Power | 45.2616 | -66.0939 | New Brunswick
| Irving Refinery 138 TS | NB_IRV138_TSS | NB Power | 45.2768 | -66.0126 | New Brunswick
| Irving Refinery 69 TS | NB_IRV69_TSS | NB Power | 45.2777 | -66.0087 | New Brunswick
| Irving Refinery SS 5296 | NB_5296_ISS | NB Power | 45.28 | -66.0105 | New Brunswick
| Irving Tissue SS 5203 | NB_5203_ISS | NB Power | 45.2576 | -66.0958 | New Brunswick
| Jacquet River SS 6413 | NB_6413_DSS | NB Power | 47.9167 | -65.9787 | New Brunswick
| Jemseg SS 6153 | NB_6153_DSS | NB Power | 45.7809 | -66.1008 | New Brunswick
| Junction 0015 | NB_0015_JCT | NB Power | 46.0483 | -64.8986 | New Brunswick
| Junction 0019 | NB_0019_JCT | NB Power | 46.125 | -64.8172 | New Brunswick
| Junction 0021 | NB_0021_JCT | NB Power | 46.0308 | -65.2875 | New Brunswick
| Junction 0022 | NB_0022_JCT | NB Power | 47.0262 | -67.7457 | New Brunswick
| Junction 0029 | NB_0029_JCT | NB Power | 46.1337 | -64.7584 | New Brunswick
| Junction 0038 | NB_0038_JCT | NB Power | 46.1719 | -67.5895 | New Brunswick
| Junction 0044E | NB_0044E_JCT | NB Power | 46.2065 | -64.5079 | New Brunswick
| Junction 0045 | NB_0045_JCT | NB Power | 45.1211 | -66.8232 | New Brunswick
| Junction 0050 | NB_0050_JCT | NB Power | 45.5897 | -67.3159 | New Brunswick
| Junction 0062 | NB_0062_JCT | NB Power | 47.5721 | -65.6319 | New Brunswick
| Junction 0065 | NB_0065_JCT | NB Power | 47.4544 | -67.4421 | New Brunswick
| Junction 0067 | NB_0067_JCT | NB Power | 45.9272 | -64.6678 | New Brunswick
| Junction 0068 | NB_0068_JCT | NB Power | 45.2565 | -66.0935 | New Brunswick
| Junction 0071 | NB_0071_JCT | NB Power | 48.0583 | -66.3998 | New Brunswick
| Junction 0081 | NB_0081_JCT | NB Power | 46.3093 | -67.6223 | New Brunswick
| Junction 0082 | NB_0082_JCT | NB Power | 45.1574 | -67.1302 | New Brunswick
| Junction 0085 | NB_0085_JCT | NB Power | 45.9256 | -64.482 | New Brunswick
| Junction 0090 | NB_0090_JCT | NB Power | 47.882 | -65.9889 | New Brunswick
| Junction 0092 | NB_0092_JCT | NB Power | 47.9774 | -66.6753 | New Brunswick
| Junction 0097 | NB_0097_JCT | NB Power | 47.2879 | -67.7098 | New Brunswick
| Junction 0098 | NB_0098_JCT | NB Power | 45.968 | -67.2364 | New Brunswick
| Junction 0099 | NB_0099_JCT | NB Power | 47.002 | -65.5023 | New Brunswick
| Junction 0103 | NB_0103_JCT | NB Power | 46.0951 | -64.7505 | New Brunswick
| Junction 0104 | NB_0104_JCT | NB Power | 47.2198 | -65.3994 | New Brunswick
| Junction 0105 | NB_0105_JCT | NB Power | 46.9988 | -65.4101 | New Brunswick
| Junction 0106 | NB_0106_JCT | NB Power | 45.1976 | -66.2962 | New Brunswick
| Junction 0107 | NB_0107_JCT | NB Power | 47.37 | -68.2616 | New Brunswick
| Junction 0109 | NB_0109_JCT | NB Power | 47.7021 | -65.7519 | New Brunswick
| Junction 0110 | NB_0110_JCT | NB Power | 45.1878 | -67.299 | New Brunswick
| Junction 0112 | NB_0112_JCT | NB Power | 47.5172 | -65.8057 | New Brunswick
| Junction 0114 | NB_0114_JCT | NB Power | 47.9651 | -66.7746 | New Brunswick
| Junction 0115 | NB_0115_JCT | NB Power | 47.1963 | -67.9264 | New Brunswick
| Junction 0121 | NB_0121_JCT | NB Power | 46.0617 | -64.5562 | New Brunswick
| Junction 0122 | NB_0122_JCT | NB Power | 45.9806 | -64.5117 | New Brunswick
| Junction 0124 | NB_0124_JCT | NB Power | 47.394 | -68.3339 | New Brunswick
| Junction 0125 | NB_0125_JCT | NB Power | 47.9851 | -66.7194 | New Brunswick
| Junction 0126 | NB_0126_JCT | NB Power | 47.595 | -65.6679 | New Brunswick
| Junction 0129 | NB_0129_JCT | NB Power | 47.971 | -66.2925 | New Brunswick
| Junction 0130 | NB_0130_JCT | NB Power | 45.8363 | -67.1723 | New Brunswick
| Junction 0133 | NB_0133_JCT | NB Power | 47.7124 | -64.7403 | New Brunswick
| Junction 0134 | NB_0134_JCT | NB Power | 45.9391 | -65.7951 | New Brunswick
| Junction 0135 | NB_0135_JCT | NB Power | 46.2773 | -66.6027 | New Brunswick
| Junction 0137 | NB_0137_JCT | NB Power | 47.3058 | -68.4849 | New Brunswick
| Junction 0138 | NB_0138_JCT | NB Power | 47.0563 | -67.7633 | New Brunswick
| Junction 0139 | NB_0139_JCT | NB Power | 45.6953 | -67.1426 | New Brunswick
| Junction 1121 | NB_1121_JCT | NB Power | 45.6377 | -66.5961 | New Brunswick
| Junction 1128 | NB_1128_JCT | NB Power | 47.849 | -65.8935 | New Brunswick
| Junction 1129 | NB_1129_JCT | NB Power | 45.8363 | -67.1723 | New Brunswick
| Junction 1136 | NB_1136_JCT | NB Power | 47.9834 | -66.7263 | New Brunswick
| Junction 1144 | NB_1144_JCT | NB Power | 46.8404 | -67.7027 | New Brunswick
| Junction 1153 | NB_1153_JCT | NB Power | 46.7094 | -65.741 | New Brunswick
| Junction 1162 | NB_1162_JCT | NB Power | 47.0455 | -67.7326 | New Brunswick
| Junction 1163 | NB_1163_JCT | NB Power | 45.416 | -65.9051 | New Brunswick
| Junction 1168 | NB_1168_JCT | NB Power | 45.8558 | -66.6244 | New Brunswick
| Junction 1171 | NB_1171_JCT | NB Power | 46.0372 | -64.7886 | New Brunswick
| Junction 1172 | NB_1172_JCT | NB Power | 46.1303 | -67.1113 | New Brunswick
| Junction 1173 | NB_1173_JCT | NB Power | 45.5026 | -65.81 | New Brunswick
| Junction 1174 | NB_1174_JCT | NB Power | 45.9074 | -66.6121 | New Brunswick
| Junction 1177 | NB_1177_JCT | NB Power | 45.765 | -65.4715 | New Brunswick
| Junction 1178 | NB_1178_JCT | NB Power | 45.6118 | -65.7153 | New Brunswick
| Junction 1179 | NB_1179_JCT | NB Power | 46.136 | -64.7478 | New Brunswick
| Junction 1181 | NB_1181_JCT | NB Power | 45.7699 | -65.4391 | New Brunswick
| Junction 1187 | NB_1187_JCT | NB Power | 45.3748 | -65.9542 | New Brunswick
| Junction 1191 | NB_1191_JCT | NB Power | 46.1098 | -64.7202 | New Brunswick
| Junction 1192 | NB_1192_JCT | NB Power | 45.9832 | -66.6207 | New Brunswick
| Junction 1195 | NB_1195_JCT | NB Power | 47.4899 | -65.9076 | New Brunswick
| Junction 1197 | NB_1197_JCT | NB Power | 45.8562 | -66.6247 | New Brunswick
| Junction 1205 | NB_1205_JCT | NB Power | 46.3102 | -67.3666 | New Brunswick
| Junction 1208 | NB_1208_JCT | NB Power | 45.3761 | -65.953 | New Brunswick
| Juniper SS 6107 | NB_6107_DSS | NB Power | 46.5457 | -67.2213 | New Brunswick
| Kedgwick SS 6301 | NB_6301_DSS | NB Power | 47.6533 | -67.3429 | New Brunswick
| Kent Hills Wind GS | NB_KNTH_GSS | NB Power | 45.8194 | -64.8894 | New Brunswick
| Keswick Ridge SS 6139 | NB_6139_DSS | NB Power | 45.9632 | -66.8653 | New Brunswick
| Keswick TS | NB_KSWK_TSS | NB Power | 46.0572 | -66.8494 | New Brunswick
| Kingsclear SS 6109 | NB_6109_DSS | NB Power | 45.9368 | -66.7582 | New Brunswick
| Lake George SS 6126 | NB_6126_DSS | NB Power | 45.8482 | -67.0346 | New Brunswick
| Lake Utopia Paper SS 5206 | NB_5206_ISS | NB Power | 45.158 | -66.7704 | New Brunswick
| Lakeside SS 6545 | NB_6545_DSS | NB Power | 46.1539 | -64.6748 | New Brunswick
| Lakewood SS 5211 | NB_5211_DSS | NB Power | 45.3002 | -65.9912 | New Brunswick
| Lameque GS | NB_LMEQ_GSS | NB Power | 47.8494 | -64.6187 | New Brunswick
| Lameque SS 6417 | NB_6417_DSS | NB Power | 47.8358 | -64.6139 | New Brunswick
| Lancaster TS | NB_LNCT_TSS | NB Power | 45.2348 | -66.1368 | New Brunswick
| Lepreau SS 6205 | NB_6205_DSS | NB Power | 45.166 | -66.4789 | New Brunswick
| Loch Lomond SS 6204 | NB_6204_DSS | NB Power | 45.3399 | -65.8753 | New Brunswick
| Lower Caraquet SS 6437 | NB_6437_DSS | NB Power | 47.7936 | -64.8266 | New Brunswick | [9 empty] | Closed December 2019
| Lutz Mtn. SS 6510 | NB_6510_DSS | NB Power | 46.1291 | -64.8861 | New Brunswick
| Mactaquac GS | NB_MTQC_GSS | NB Power | 45.9551 | -66.8665 | New Brunswick
| Manawagonish Road SS 5219 | NB_5219_DSS | NB Power | 45.2354 | -66.1374 | New Brunswick
| Marysville TS | NB_MRYV_TSS | NB Power | 45.967 | -66.597 | New Brunswick
| McAdam SS 6225 | NB_6225_DSS | NB Power | 45.5895 | -67.3179 | New Brunswick
| McCains SS 5102 | NB_5102_DSS | NB Power | 47.0642 | -67.7776 | New Brunswick
| Memramcook TS | NB_MRMK_TSS | NB Power | 46.0021 | -64.5106 | New Brunswick
| Mill Lane SS 6207 | NB_6207_DSS | NB Power | 45.5884 | -67.3156 | New Brunswick
| Millbank GS | NB_MLBK_GSS | NB Power | 47.071 | -65.4541 | New Brunswick
| Millidgeville SS 5213 | NB_5213_DSS | NB Power | 45.2895 | -66.0955 | New Brunswick
| Milltown GS | NB_MLTN_GSS | NB Power | 45.1755 | -67.2929 | New Brunswick | [9 empty] | Location approximate
| Millville SS 6194 | NB_6194_DSS | NB Power | 46.0925 | -67.2204 | New Brunswick | [9 empty] | Location approximate
| Millville TS | NB_MIVL_TSS | NB Power | 46.0836 | -67.1819 | New Brunswick
| Minto SS 6120 | NB_6120_DSS | NB Power | 46.0844 | -66.0341 | New Brunswick
| Miramichi P&P - South Nelson 5419 | NB_5419_ISS | NB Power | 46.9722 | -65.5539 | New Brunswick
| Moncton TS | NB_MCTN_TSS | NB Power | 46.0945 | -64.845 | New Brunswick
| Mount Pleasant Mines SS 5216 | NB_5216_DSS | NB Power | 45.4255 | -66.8195 | New Brunswick
| Murray Corner TS | NB_MCNR_TSS | NB Power | 46.1665 | -63.9562 | New Brunswick
| Musquash Pumping Station 5208 | NB_5208_SUB | NB Power | 45.2369 | -66.2906 | New Brunswick | [9 empty] | Location approximate
| Nackawic SS 6108 | NB_6108_DSS | NB Power | 45.9967 | -67.2481 | New Brunswick
| Nashwaaksis SS 6135 | NB_6135_DSS | NB Power | 45.9942 | -66.6496 | New Brunswick
Legend: | Neguac SS 6406 | NB_6406_DSS | NB Power | 47.249 | -65.104 | New Brunswick
CGS = Customer Generating Station | Nelson SS 6442 | NB_6442_DSS | NB Power | 46.9966 | -65.5476 | New Brunswick
CS = Converter Station | Nepisiguit Falls SS 6404 | NB_6404_DSS | NB Power | 47.4055 | -65.7918 | New Brunswick
CTS = Customer Transfofmer Station | New Denmark SS 6390 | NB_6390_DSS | NB Power | 47.0001 | -67.6114 | New Brunswick
DFL = Dual Function Line | New Maryland SS 6158 | NB_6158_DSS | NB Power | 45.8852 | -66.6861 | New Brunswick
DSC = Distribution Supply Centre | Newcastle Town SS 6443 | NB_6443_DSS | NB Power | 46.9935 | -65.572 | New Brunswick
GEN = Generating Station | Newcastle TS | NB_NWCS_TSS | NB Power | 47.0213 | -65.5963 | New Brunswick
GS = Generating Station | Norton TS | NB_NRTN_TSS | NB Power | 45.664 | -65.6512 | New Brunswick
JCT = Junction | Oak Bay TS | NB_OKBY_TSS | NB Power | 45.2433 | -67.1957 | New Brunswick
LC = Line Connection | Oromocto Town SS 6140 | NB_6140_DSS | NB Power | 45.8385 | -66.5037 | New Brunswick
MTS = Municipal Transformer Station | Ortonville SWS | NB_ORTN_SWS | NB Power | 46.9507 | -67.7093 | New Brunswick
N = Network | Pennfield Ridge SS 6206 | NB_6206_DSS | NB Power | 45.1079 | -66.7406 | New Brunswick
SS = Switching Station | Pennfield TS | NB_PNFD_TSS | NB Power | 45.1095 | -66.7433 | New Brunswick
SUB = Substation, Switching Station or Transformer Station | Petit Rocher SS 6491 | NB_6491_DSS | NB Power | 47.8083 | -65.8063 | New Brunswick
TS = Transformer Station | Petitcodiac SS 6558 | NB_6558_DSS | NB Power | 45.9252 | -65.1503 | New Brunswick
| Plaster Rock SS 6394 | NB_6394_DSS | NB Power | 46.9213 | -67.3989 | New Brunswick
Specific Notes: | Point Lepreau GS | NB_PLPR_GSS | NB Power | 45.0687 | -66.4543 | New Brunswick
| Potash Co. SS 5217 | NB_5217_ISS | NB Power | 45.7524 | -65.4283 | New Brunswick
| Priestman SS 6124 | NB_6124_DSS | NB Power | 45.9379 | -66.6498 | New Brunswick
| Rainsford Lane SS 6137 | NB_6137_DSS | NB Power | 45.9453 | -66.7002 | New Brunswick
General Notes: | Raynes Avenue SS 5214 | NB_5214_DSS | NB Power | 45.2552 | -66.0921 | New Brunswick
Dual function generation/substation nodes are categorized as "GEN" | Red Bank SS 6424 | NB_6424_DSS | NB Power | 46.9639 | -65.7458 | New Brunswick
See inputs tab for assumptions regarding system parameters | Rexton SS 6535 | NB_6535_DSS | NB Power | 46.6337 | -64.8748 | New Brunswick
| Richibucto SS 6533 | NB_6533_DSS | NB Power | 46.6791 | -64.8827 | New Brunswick
| Ripples SS 6142 | NB_6142_DSS | NB Power | 46.0132 | -66.2329 | New Brunswick
| Riverview SS 6518 | NB_6518_DSS | NB Power | 46.049 | -64.8131 | New Brunswick
| Rogersville SS 6411 | NB_6411_DSS | NB Power | 46.7434 | -65.4108 | New Brunswick
| Rothesay Paper SS 5295 | NB_5295_ISS | NB Power | 45.2799 | -66.0239 | New Brunswick
| Rothesay SS 6267 | NB_6267_DSS | NB Power | 45.3936 | -65.9731 | New Brunswick
| Rusagonis SS 6141 | NB_6141_DSS | NB Power | 45.805 | -66.6327 | New Brunswick
| Ryan Rd SS 6525 | NB_6525_DSS | NB Power | 46.1102 | -64.8487 | New Brunswick
| Sackville SS 6511 | NB_6511_DSS | NB Power | 45.9041 | -64.3816 | New Brunswick
| Salisbury SS 6556 | NB_6556_DSS | NB Power | 46.0078 | -65.0289 | New Brunswick
| Salisbury TS | NB_SLBY_TSS | NB Power | 46.021 | -64.9963 | New Brunswick
| Scoudouc Ind. SS 6540 | NB_6540_ISS | NB Power | 46.1764 | -64.5882 | New Brunswick
| Scoudouc SS 6595 | NB_6595_DSS | NB Power | 46.1576 | -64.5633 | New Brunswick
| Shediac SS 6513 | NB_6513_DSS | NB Power | 46.2235 | -64.4829 | New Brunswick
| Shediac Wst SS 6529 | NB_6529_DSS | NB Power | 46.21 | -64.5325 | New Brunswick
| Sheila SS 6405 | NB_6405_DSS | NB Power | 47.4884 | -64.9233 | New Brunswick
| Shippigan SS 6490 | NB_6490_DSS | NB Power | 47.7428 | -64.717 | New Brunswick
| Sisson GS | NB_SSON_GSS | NB Power | 47.266 | -67.2434 | New Brunswick
| Six Roads SS 6425 | NB_6425_DSS | NB Power | 47.6139 | -64.8921 | New Brunswick
| South Bathurst SS 6449 | NB_6449_DSS | NB Power | 47.6049 | -65.6458 | New Brunswick
| Springfield SS 6200 | NB_6200_DSS | NB Power | 45.6618 | -65.7877 | New Brunswick
| St. André TS | NB_SADR_TSS | NB Power | 47.1665 | -67.7305 | New Brunswick
| St. Andrews SS 6296 | NB_6296_DSS | NB Power | 45.0861 | -67.0661 | New Brunswick
| St. Anne Nackawic SS 5116 | NB_5116_DSS | NB Power | 46.0129 | -67.223 | New Brunswick
| St. Basile SS 6396 | NB_6396_DSS | NB Power | 47.3592 | -68.2207 | New Brunswick
| St. George GS | NB_SGRG_GSS | NB Power | 45.1283 | -66.8279 | New Brunswick
| St. George SS 6145 | NB_6145_DSS | NB Power | 45.1213 | -66.8244 | New Brunswick
| St. George St SS 6553 | NB_6553_DSS | NB Power | 46.0883 | -64.7966 | New Brunswick
| St. Leolin SS 6435 | NB_6435_DSS | NB Power | 47.7631 | -65.1974 | New Brunswick
| St. Leonard Sawmill SS 5107 | NB_5107_ISS | NB Power | 47.1927 | -67.9305 | New Brunswick
| St. Leonard SWS | NB_SLND_SWS | NB Power | 47.1732 | -67.9094 | New Brunswick
| St. Louis SS 6532 | NB_6532_DSS | NB Power | 46.7298 | -64.9794 | New Brunswick
| St. Mary's SS 6505 | NB_6505_DSS | NB Power | 46.412 | -64.8568 | New Brunswick
| St. Quentin SS 6337 | NB_6337_DSS | NB Power | 47.5135 | -67.4012 | New Brunswick
| St. Stephen SS 6223 | NB_6223_DSS | NB Power | 45.1993 | -67.2839 | New Brunswick
| Ste Rose GS | NB_SROS_GSS | NB Power | 47.6263 | -64.954 | New Brunswick
| Stone Con. Sawmill SS 6431 | NB_6431_ISS | NB Power | 47.474 | -65.7616 | New Brunswick
| Sugar Loaf SS 6408 | NB_6408_DSS | NB Power | 47.9921 | -66.6663 | New Brunswick
| Sussex Corner SS 6537 | NB_6537_DSS | NB Power | 45.7137 | -65.4703 | New Brunswick
| Sussex North SS 6297 | NB_6297_DSS | NB Power | 45.7334 | -65.5027 | New Brunswick
| Sussex W. SS 6203 | NB_6203_DSS | NB Power | 45.724 | -65.5247 | New Brunswick
| Sweeny Lane SS 6409 | NB_6409_DSS | NB Power | 46.995 | -65.579 | New Brunswick
| Taymouth SS 6111 | NB_6111_DSS | NB Power | 46.1832 | -66.6206 | New Brunswick
| Tetagouche SS 6438 | NB_6438_DSS | NB Power | 47.6488 | -65.7289 | New Brunswick
| Thomaston Corner SS 6193 | NB_6193_DSS | NB Power | 45.6567 | -67.1315 | New Brunswick
| Tinker GS | NB_TNK_GSS | NB Power | 46.8097 | -67.7665 | New Brunswick
| Tobique GS | NB_TOBQ_GSS | NB Power | 46.7801 | -67.6953 | New Brunswick
| Tobique Narrows SS 6156 | NB_6156_DSS | NB Power | 46.7788 | -67.6936 | New Brunswick
| Tracadie SS 6436 | NB_6436_DSS | NB Power | 47.5136 | -64.9342 | New Brunswick
| Turtle Creek SS 6517 | NB_6517_DSS | NB Power | 46.0234 | -64.8682 | New Brunswick
| Union Street SS 5202 | NB_5202_DSS | NB Power | 45.274 | -66.0665 | New Brunswick
| Vanier SS 6118 | NB_6118_DSS | NB Power | 45.9083 | -66.6126 | New Brunswick
| Veneer Siding SS 5312 | NB_5312_DSS | NB Power | 47.3142 | -67.7078 | New Brunswick
| Waasis Road SWS SS 4103 | NB_4103_DSS | NB Power | 45.8159 | -66.6324 | New Brunswick
| Weldon SS 6538 | NB_6538_DSS | NB Power | 45.9444 | -64.714 | New Brunswick
| West Bathurst SS 6418 | NB_6418_DSS | NB Power | 47.6285 | -65.6768 | New Brunswick
| West Buctouche SS 6508 | NB_6508_DSS | NB Power | 46.4685 | -64.737 | New Brunswick
| Westfield SS 6298 | NB_6298_DSS | NB Power | 45.359 | -66.2409 | New Brunswick
| Wilber St SS 6555 | NB_6555_DSS | NB Power | 46.0977 | -64.8048 | New Brunswick
| Woodstock South SS 6121 | NB_6121_DSS | NB Power | 46.1419 | -67.5811 | New Brunswick
| Woodstock TS | NB_WDSK_TSS | NB Power | 46.2491 | -67.6072 | New Brunswick

## System
NB | SYSTEM CHARACTERISTICS |  |  |  |  | System Characteristics
| Generator Type | Capacity Adjustment (ELCC) | Capacity Factor | Other References | Notes | Reserve Requirements | Line Losses
|  | (%) | (%) |  | (%) | (% installed MW) | (% across system)
| Coal | 90% | 65% | https://www.pembina.org/pub/out-with-coal | Based on 2560 GWh/year for Belledune | 20% | 5%
| Heavy Fuel Oil | 73% | 4% |  | Capacity factor based on reported 160 GWh/year for Grandview
| Light Fuel Oil CT | 78% | 1% |  | Capacity factor reflects operation only at peak or for contingencies
| Natural Gas CC | 73% | 20% | NBP03.03 [Matter 458] - NBP (NBEUB) - IR-06 | Capacity factor based on reported 160 GWh/year for Grandview
| Natural Gas CT | 93% | 1% |  | Capacity factor reflects operation only at peak or for contingencies
| Biomass / Biogas | 95% | 45% |  | Capacity factor based on reported 630 GWh/year from all biomass
| Nuclear | 90% | 90% |  | Capacity factor estimated from NB Power Annual Reports
| Hydro - NB Power | 95% | by facility
| Hydro - non NB Power | 95% | 35% |  | Capacity factor estimated from NB Power Annual Reports
| Wind | 21% | 35.2%
| Solar | 5% | 15%
Notes:
Line losses determined as ratio of (transmission losses + distribution losses)/(gross generation and purchases) for the last 5 years
Transmission losses determined to be 3.2% and distribution losses 1.8%

## HGWh
NB | HISTORICAL ANNUAL ENERGY DEMAND | UNIT | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2013-2018
| Annual Energy Demand (after DSM) | GWh/year | 12539 | 12073 | 12158 | 11907 | 10475 | 11194 | 11037 | 11099 | 10809 | 10873 | 10960
| Annual Change in Energy Demand | GWh/year |  | -466 | 85 | -251 | -1432 | 719 | -157 | 62 | -290 | 64 | 87 | Average
| Percentage Change in Energy Demand | % |  | -3.716% | 0.7041% | -2.064% | -12.03% | 6.864% | -1.403% | 0.5617% | -2.613% | 0.5921% | 0.8001% | -0.211%
Notes:

## HMW
NB | HISTORICAL PEAK CAPACITY | UNIT | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2013-2018
| Annual Capacity Demand (after DSM) | GWh/year
| Annual Change in Capacity Demand | GWh/year |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Average
| Percentage Change in Capacity Demand | % |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Notes:

## FGWh
NB | FORECASTED ANNUAL ENERGY DEMAND | UNIT | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2019 - 2030 | 2019-2050 | Notes
| January | GWh |  | 1625 | 1637 | 1650 | 1643 | 1637 | 1631 | 1628 | 1629 | 1630
| February | GWh |  | 1438 | 1451 | 1462 | 1458 | 1451 | 1447 | 1448 | 1447 | 1450
| March | GWh |  | 1387 | 1407 | 1410 | 1405 | 1410 | 1404 | 1395 | 1405 | 1404
| April | GWh |  | 1162 | 1152 | 1188 | 1177 | 1179 | 1167 | 1173 | 1169 | 1176
| May | GWh |  | 1022 | 1012 | 1050 | 1039 | 1038 | 1037 | 1036 | 1029 | 1037
| June | GWh |  | 913 | 910 | 941 | 935 | 932 | 928 | 928 | 929 | 932
| July | GWh |  | 921 | 919 | 948 | 945 | 939 | 937 | 936 | 937 | 939
| August | GWh |  | 937 | 934 | 966 | 964 | 957 | 954 | 955 | 954 | 958
| September | GWh |  | 913 | 911 | 941 | 938 | 932 | 929 | 931 | 932 | 934
| October | GWh |  | 1051 | 1063 | 1078 | 1074 | 1069 | 1065 | 1065 | 1067 | 1069
| November | GWh |  | 1223 | 1235 | 1249 | 1245 | 1239 | 1234 | 1236 | 1236 | 1238
| December | GWh |  | 1510 | 1520 | 1533 | 1525 | 1520 | 1515 | 1515 | 1513 | 1515
| Mid-load (after DSM) | GWh/year | 14127 | 14102 | 14151 | 14416 | 14348 | 14303 | 14248 | 14246 | 14247 | 14282 | 2019-2027 Rate | 2019-2027 Rate | Assume extended to 2050
| Incremental annual load growth After DSM | % |  | -0.177% | 0.3475% | 1.873% | -0.4717% | -0.3136% | -0.3845% | -0.01404% | 0.00702% | 0.2457% | 0.1213% | 0.1213% | Mid-load forecast for use in COPPER
Notes:
The above load forecast includes demand met by the Large Industrial Renewable Energy Purchase Program (LIREPP).
NB Power has a regulatory target of 40% in-province electricity demand from renewable sources by 2020.

## FMW
NB | FORECASTED PEAK CAPACITY | UNIT | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2019 - 2030 | 2019-2050 | Notes
| January | MW |  | 3060 | 3060 | 3050 | 3020 | 2970 | 2920 | 2890 | 2870 | 2860
| February | MW |  | 3020 | 3020 | 3020 | 2980 | 2940 | 2890 | 2870 | 2840 | 2840
| March | MW |  | 2610 | 2630 | 2610 | 2590 | 2560 | 2520 | 2490 | 2480 | 2470
| April | MW |  | 2170 | 2150 | 2180 | 2150 | 2140 | 2100 | 2080 | 2070 | 2070
| May | MW |  | 1840 | 1820 | 1860 | 1830 | 1820 | 1790 | 1770 | 1750 | 1760
| June | MW |  | 1590 | 1590 | 1610 | 1590 | 1580 | 1550 | 1540 | 1530 | 1530
| July | MW |  | 1530 | 1520 | 1550 | 1530 | 1510 | 1490 | 1470 | 1470 | 1470
| August | MW |  | 1550 | 1540 | 1570 | 1550 | 1530 | 1510 | 1490 | 1490 | 1490
| September | MW |  | 1690 | 1680 | 1710 | 1690 | 1670 | 1650 | 1630 | 1630 | 1620
| October | MW |  | 1950 | 1960 | 1970 | 1950 | 1930 | 1900 | 1880 | 1870 | 1870
| November | MW |  | 2350 | 2360 | 2370 | 2350 | 2320 | 2290 | 2270 | 2260 | 2250
| December | MW |  | 2780 | 2780 | 2770 | 2740 | 2710 | 2660 | 2640 | 2620 | 2610
| Mid-load (after DSM) | MW | 3090 | 3060 | 3060 | 3050 | 3020 | 2970 | 2920 | 2890 | 2870 | 2860 | 2019-2027 Rate | 2019-2027 Rate | Assume extended to 2050
| Incremental annual load growth After DSM | % |  | -0.9709% | 0% | -0.3268% | -0.9836% | -1.656% | -1.684% | -1.027% | -0.692% | -0.3484% | -0.8558% | -0.8558% | Mid-load forecast for use in COPPER
Notes:
The above load forecast includes demand met by the Large Industrial Renewable Energy Purchase Program (LIREPP)
The above is coincident peak demand

## Hourly
NB | Hourly
See Hourly2018 file in the Hourly-2018 folder

## Inputs
NB | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance