## README
NL | LEGEND
| NL-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| Distribution | Characteristics of existing distribution substations
| System | Miscellaneous provincial system characteristics
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to references
See the accompanying calculations file and raw data files for additional supporting information

## NL-Sources
NL | SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| Newfoundland Power | 2013 | 2013-2014 General Rate Application. Response to Requests for Information CA-NP-036 Attachment A. | http://www.pub.nf.ca/applications/NP2013GRA/index.htm |  | Newfoundland and Labrador
| Newfoundland and Labrador Hydro | 2013 | 2013 Amended General Rate Application | http://www.pub.nf.ca/applications/NLH2013GRA/files/application/NLH-2013-GRA-Application-Volume-2-AMENDED-2014-11-10.pdf |  | Newfoundland and Labrador
| Newfoundland and Labrador Hydro | 2012 | Generation Planning Issues. System Planning Department. | https://nlhydro.com/wp-content/uploads/2014/11/Generation-Planning-Issues-Report-November-2012-FINAL.pdf |  | Newfoundland and Labrador
| Nalcor Energy | 2019 | Reference to Board on Rate Mitigation Options and Impacts. Nalcor Response to Information Request PUB-Nalcor-129 Attachment 1 Maps | http://www.pub.nf.ca/2018ratemitigation/responses.php |  | Newfoundland and Labrador
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" column of the relevant tab
| Newfoundland and Labrador Hydro | 2014 | Newfoundland and Labrador Hydro GT Inspection Assessment | http://www.pub.nl.ca/applications/nlh2014capital/NLHCBSUPP2014/100MWTurbine/files/rfi/GT-DD-NLH-002.pdf |  | Newfoundland and Labrador
| Newfoundland and Labrador Hydro | 2016 | Island Interconnection System Supply Issues and Power Outages. PUB-NLH-324 | http://www.pub.nf.ca/applications/IslandInterconnectedSystem/ResponsestoRFIs.htm |  | Newfoundland and Labrador
| Nalcor Energy | 2011 | Nalcor's Submission to the Board of Commissioners of Public Utilities with respect to the Reference from the Lieutenant-Governor in Council on the Muskrat Falls Project | https://nalcorenergy.com/wp-content/uploads/2016/12/Final_Submission_to_PUB_for_Muskrat_Falls_Review_2011_11_10_all_Volumes3.pdf |  | Newfoundland and Labrador
| Newfoundland Power | 2014 | Investigation and Hearing into Supply Issues and Power Outages on the Island Interconnected System Responses to Information Requests PUB-NP-274 | http://www.pub.nf.ca/applications/IslandInterconnectedSystem/ResponsestoRFIs.htm |  | Newfoundland and Labrador
| Newfoundland Power | 2014 | Investigation and Hearing into Supply Issues and Power Outages on the Island Interconnected System Responses to Information Requests PUB-NP-177 | http://www.pub.nf.ca/applications/IslandInterconnectedSystem/ResponsestoRFIs.htm |  | Newfoundland and Labrador
| Newfoundland Power | 2014 | Investigation and Hearing into Supply Issues and Power Outages on the Island Interconnected System Responses to Information Requests PUB-NP-275 | http://www.pub.nf.ca/applications/IslandInterconnectedSystem/ResponsestoRFIs.htm |  | Newfoundland and Labrador
| Newfoundland and Labrador Hydro | 2014 | Investigation and Hearing into Supply Issues and Power Outages on the Island Interconnected System Responses to Information Requests PUB-NLH-148 | http://www.pub.nf.ca/applications/IslandInterconnectedSystem/ResponsestoRFIs.htm |  | Newfoundland and Labrador
| Nalcor Energy | 2019 | Operations | https://nlhydro.com/operations/ |  | Newfoundland and Labrador
| Nalcor Energy | 2009 | Lower Churchill Hydroelectric Generation Project Environmental Impact Statement | https://ceaa.gc.ca/052/details-eng.cfm?pid=26178 |  | Newfoundland and Labrador
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | Canada
| Newfoundland Power | 2019 | Response to IR PUB-NP-037. Rate Mitigation Options and Impacts Reference | http://www.pub.nf.ca/2018ratemitigation/responses/PUB-NP-037.PDF |  | Newfoundland and Labrador
| Power Advisory LLC | 2015 | Review of Newfoundland and Labrador Electricity System | https://www.nr.gov.nl.ca/nr/publications/energy/review_of_nl_electricty_system.pdf |  | Newfoundland and Labrador
| Nova Scotia Power Inc. | 2019 | Nova Scotia Power Final Pre-IRP Report | https://irp.nspower.ca/documents/pre-irp-deliverables/ |  | Newfoundland and Labrador
| Nalcor Energy | 2019 | Reference to Board on Rate Mitigation Options and Impacts. Nalcor Response to Information Request PUB-Nalcor-057 Attachment 1 Load Forecasts | http://www.pub.nf.ca/2018ratemitigation/responses.php |  | Newfoundland and Labrador
| Newfoundland and Labrador Hydro | 2019 | Reliability and Resource Adequacy Study | https://nalcorenergy.com/wp-content/uploads/2019/01/R-Final-Response-PB-947-2018-with-Appendix-1-Reliability-and-Supply-Adequacy-Study-2018-11-16-Low-1.pdf |  | Newfoundland and Labrador
| Newfoundland Power | 2019 | 2019 Capital Budget Application | http://www.pub.nf.ca/applications/NP2019Capital/applications/NP%20-%202019%20Capital%20Budget%20Application%20-%202018-07-13.PDF |  | Newfoundland and Labrador
| Newfoundland Power | 2019 | 2019/2020 General Rate Application. Volume 2: Supporting Materials | http://www.pub.nf.ca/applications/NP2019GRA/index.htm |  | Newfoundland and Labrador
| Newfoundland Power | 2005 | 2006 Capital Budget Application Electrical System Handbook | http://www.pub.nf.ca/np2006cap/files/applic/NP2006ApplicationHandbook.pdf |  | Newfoundland and Labrador
| Churchill Fall (Labrador) Corporation | 1991 | An Energy Giant: The Churchill Falls Power Development | https://www.muskratfallsinquiry.ca/files/P-00017.pdf |  | Newfoundland and Labrador
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
NL | EXISTING GENERATION | [12 empty] | DESIGN | DESIGN | [6 empty] | OPERATIONS | [13 empty] | OPERATING COSTS
| Project Name | Gen Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy | # of units | Inc Heat Rate @ Max | Minimum Capacity | Maximum Capacity | Minimum Up Time | Minimum Down Time | Spin Up Ramp Rate | Spin Down Ramp Rate | Start Up Ramp Limit | Shut Down Ramp Limit | Must Run | Operating Reserve Fraction | Outage Duration | Forced Outage Rate | Maintenance Outage Rate | Start Up Costs | Fuel Costs | Shut Down Costs | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | (kV) |  |  |  |  | (MW) |  | (MW) | (%) | (GWh/year) |  | (MMBtu/MWh) | (MW) | (MW) | (hours) | (hours) | (%/min) | (%/min) | [MW/hr p MWcap] | [MW/hr p MWcap] | (T/F) | (%) | (hours) | (%) | (days/y) | (S/MWcap) | ($/MWh) | (S/MWcap) | ($/year) | ($/MWh)
| Cornerbrook | NL_CNB00_GEN | Kruger Energy | Cornerbrook | 48.9561 | -57.9496 | Newfoundland and Labrador.a | Newfoundland | Deer Lake (DLK) | NL_DLK_DFS | 66 | 2002 | 2023 | Biomass | biomass | 15.3 | 52% | 7.956 | 49.99% | 67 | 1
| Happy Valley North Side Diesel | NL_HVD00_GEN | Nalcor Energy | Happy Valley - Goose Bay, Labrador | 53.2986 | -60.3798 | Newfoundland and Labrador.b | Labrador | Happy Valley (HVY) | NL_HVY_DFS | 138 | 2000 | 2100 | Diesel_CT | diesel | 11.7 | 100% | 11.7 | 1% | 1.0249 | 1 | 10.97 | [19 empty] | Back up facility
| Hawkes Bay | NL_HBY00_GEN | Nalcor Energy | Hawke's Bay | 50.6095 | -57.1691 | Newfoundland and Labrador.a | Newfoundland | Hawkes Bay (HBY) | NL_HBY_GSS | 66 | 1971 | 2100 | Diesel_CT | diesel | 5 | 100% | 5 | 1% | 0.438 | 1 | 10.97 | [19 empty] | Back up facility
| Holyrood Diesel | NL_HLD00_GEN | Nalcor Energy | Conception Bay South | 47.3858 | -53.1277 | Newfoundland and Labrador.a | Newfoundland | Holyrood GS (HOL) | NL_HOL_GSS | 138 | 2015 | 2100 | Diesel_CT | diesel | 12 | 70% | 8.4 | 1% | 1.0512 | 1 | 10.97 | [19 empty] | Black start diesel facility
| Vale Capacity Assistance | NL_VCA00_GEN | Vale | Long Harbour | 47.4668 | -53.7412 | Newfoundland and Labrador.a | Newfoundland | Long Harbour (LHB) | NL_LHB_ISS | 230 | 2015 | 2100 | Diesel_CT | diesel | 11 | 100% | 11 | 0% | 0 | 1 | 10.97 | [19 empty] | Back up facility
| Port Aux Basques | NL_PAB00_GEN | Newfoundland Power | Port Aux Basques | 47.5743 | -59.137 | Newfoundland and Labrador.a | Newfoundland | Port Aux Basques (PAB) | NL_PAB_DFS | 66 | 1969 | 2100 | Diesel_CT | diesel | 2.5 | 100% | 2.5 | 0.3% | 0.0657 | 1
| St. Anthony | NL_SOP00_GEN | Nalcor Energy | St. Anthony | 51.371 | -55.5986 | Newfoundland and Labrador.a | Newfoundland | St Anthony (SOP) | NL_SOP_GSS | 66 | 1982 | 2100 | Diesel_CT | diesel | 9.7 | 100% | 9.7 | 1% | 0.84972 | 1 | 10.97 | [19 empty] | Back up facility
| Greenhill | NL_GRH00_GEN | Newfoundland Power | Burin | 47.1019 | -55.7601 | Newfoundland and Labrador.a | Newfoundland | Greenhill (GRH) | NL_GRH_DFS | 66 | 1975 | 2100 | Gas_CT | diesel | 20 | 100% | 20 | 0.24% | 0.42048 | 1 | 12.26 | [19 empty] | Back up facility
| Happy Valley Gas | NL_HVG00_GEN | Nalcor Energy | Happy Valley - Goose Bay, Labrador | 53.2986 | -60.3798 | Newfoundland and Labrador.b | Labrador | Happy Valley (HVY) | NL_HVY_DFS | 138 | 2000 | 2100 | Gas_CT | diesel | 25 | 100% | 25 | 1% | 2.19 | 1 | 12.26
| Hardwoods | NL_HWD00_GEN | Nalcor Energy | St. John's | 47.5882 | -52.7823 | Newfoundland and Labrador.a | Newfoundland | Hardwoods (HWD) | NL_HWD_DFS | 66 | 1976 | 2100 | Gas_CT | diesel | 50 | 100% | 50 | 1% | 4.38 | 1 | 12.26 | [19 empty] | Primarily operates in synchronous condense mode
| Holyrood_04 | NL_HOL04_GEN | Nalcor Energy | Conception Bay South | 47.3858 | -53.1277 | Newfoundland and Labrador.a | Newfoundland | Holyrood GS (HOL) | NL_HOL_GSS | 230 | 2014 | 2100 | Gas_CT | diesel | 123.5 | 100% | 123.5 | 0% | 0 | 4 | 10.289 | 5 | 123.5
| Stephenville | NL_STV00_GEN | Nalcor Energy | Stephenville | 48.5485 | -58.579 | Newfoundland and Labrador.a | Newfoundland | Stephenville (STV) | NL_STV_GSS | 230 | 1975 | 2100 | Gas_CT | diesel | 50 | 100% | 50 | 1% | 4.38 | 1 | 12.26 | [19 empty] | Primarily operates in synchronous condense mode
| Wesleyville | NL_WES00_GEN | Newfoundland Power | Wesleyville | 49.1218 | -53.5993 | Newfoundland and Labrador.a | Newfoundland | Wesleyville (WES) | NL_WES_DFS | 66 | 1969 | 2100 | Gas_CT | diesel | 8 | 100% | 8 | 0.28% | 0.19622 | 1 | 12.26 | [19 empty] | Back up facility
| Bishops Falls_01 | NL_BFS01_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 3 | 67% | 2.01 | 70.05% | 18.4091 | 9
| Bishops Falls_02 | NL_BFS02_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 3 | 67% | 2.01 | 70.05% | 18.4091 | 9
| Bishops Falls_03 | NL_BFS03_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 3 | 67% | 2.01 | 70.05% | 18.4091 | 9
| Bishops Falls_04 | NL_BFS04_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 3 | 67% | 2.01 | 70.05% | 18.4091 | 9
| Bishops Falls_05 | NL_BFS05_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 3 | 67% | 2.01 | 70.05% | 18.4091 | 9
| Bishops Falls_06 | NL_BFS06_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 3 | 67% | 2.01 | 70.05% | 18.4091 | 9
| Bishops Falls_07 | NL_BFS07_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 2 | 67% | 1.34 | 70.05% | 12.2727 | 9
| Bishops Falls_08 | NL_BFS08_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 1 | 67% | 0.67 | 70.05% | 6.1364 | 9
| Bishops Falls_09 | NL_BFS09_GEN | Nalcor Energy | Exploits River | 49.0154 | -55.4722 | Newfoundland and Labrador.a | Newfoundland | Bishops Falls (BFS) | NL_BFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 1 | 67% | 0.67 | 70.05% | 6.1364 | 9
| Cat Arm_01 | NL_CAM01_GEN | Nalcor Energy | Northern Peninsula | 50.0258 | -56.765 | Newfoundland and Labrador.a | Newfoundland | Cat Arm (CAM) | NL_CAM_GSS | 230 | 1985 | 2100 | Hydro_daily | hydro_daily | 68.5 | 98% | 67.13 | 62.91% | 377.5 | 2
| Cat Arm_02 | NL_CAM02_GEN | Nalcor Energy | Northern Peninsula | 50.0258 | -56.765 | Newfoundland and Labrador.a | Newfoundland | Cat Arm (CAM) | NL_CAM_GSS | 230 | 1985 | 2100 | Hydro_daily | hydro_daily | 68.5 | 98% | 67.13 | 62.91% | 377.5 | 2
| Watsons Brook | NL_WBK00_GEN | Kruger Energy | Deer Lake | 48.9415 | -57.9282 | Newfoundland and Labrador.a | Newfoundland | Deer Lake (DLK) | NL_DLK_DFS | 66 | 1925 | 2100 | Hydro_daily | hydro_daily | 9 | 100% | 9 | 82.45% | 65 | 1
| Deer Lake_01 | NL_DLP01_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 67 | 1925 | 2100 | Hydro_daily | hydro_daily | 11.5 | 100% | 11.5 | 93.31% | 94 | 9 | [20 empty] | Capacities for 60 Hz units assumed equivalent
| Deer Lake_02 | NL_DLP02_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 68 | 1925 | 2100 | Hydro_daily | hydro_daily | 11.5 | 100% | 11.5 | 93.31% | 94 | 9 | [20 empty] | Capacities for 60 Hz units assumed equivalent
| Deer Lake_03 | NL_DLP03_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 69 | 1925 | 2100 | Hydro_daily | hydro_daily | 11.5 | 100% | 11.5 | 93.31% | 94 | 9 | [20 empty] | Capacities for 60 Hz units assumed equivalent
| Deer Lake_04 | NL_DLP04_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 70 | 1925 | 2100 | Hydro_daily | hydro_daily | 11.5 | 100% | 11.5 | 93.31% | 94 | 9 | [20 empty] | Capacities for 60 Hz units assumed equivalent
| Deer Lake_05 | NL_DLP05_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 71 | 1925 | 2100 | Hydro_daily | hydro_daily | 11.5 | 100% | 11.5 | 93.31% | 94 | 9 | [20 empty] | Capacities for 60 Hz units assumed equivalent
| Deer Lake_06 | NL_DLP06_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 72 | 1925 | 2100 | Hydro_daily | hydro_daily | 11.5 | 100% | 11.5 | 93.31% | 94 | 9 | [20 empty] | Capacities for 60 Hz units assumed equivalent
| Deer Lake_07 | NL_DLP07_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 73 | 1925 | 2100 | Hydro_daily | hydro_daily | 11.5 | 100% | 11.5 | 93.31% | 94 | 9 | [20 empty] | Capacities for 60 Hz units assumed equivalent
| Deer Lake_08 | NL_DLP08_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 74 | 1925 | 2100 | Hydro_daily | hydro_daily | 22.5 | 40% | 9 | 32.98% | 65 | 9 | [20 empty] | Generates at 50 Hz so effective capacity reduced
| Deer Lake_09 | NL_DLP09_GEN | Kruger Energy | Deer Lake | 49.1699 | -57.4363 | Newfoundland and Labrador.a | Newfoundland | Deer Lake GS (DLP) | NL_DLP_GSS | 75 | 1925 | 2100 | Hydro_daily | hydro_daily | 22.5 | 40% | 9 | 32.98% | 65 | 9 | [20 empty] | Generates at 50 Hz so effective capacity reduced
| Grand Falls_04 | NL_GFS04_GEN | Nalcor Energy | Exploits River | 48.9254 | -55.6678 | Newfoundland and Labrador.a | Newfoundland | Grand Falls (GFS) | NL_GFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 29 | 83% | 24.07 | 73.06% | 185.6 | 6
| Grand Falls_05 | NL_GFS05_GEN | Nalcor Energy | Exploits River | 48.9254 | -55.6678 | Newfoundland and Labrador.a | Newfoundland | Grand Falls (GFS) | NL_GFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 4 | 62.5% | 2.5 | 73.06% | 25.6 | 6
| Grand Falls_06 | NL_GFS06_GEN | Nalcor Energy | Exploits River | 48.9254 | -55.6678 | Newfoundland and Labrador.a | Newfoundland | Grand Falls (GFS) | NL_GFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 4 | 62.5% | 2.5 | 73.06% | 25.6 | 6
| Grand Falls_07 | NL_GFS07_GEN | Nalcor Energy | Exploits River | 48.9254 | -55.6678 | Newfoundland and Labrador.a | Newfoundland | Grand Falls (GFS) | NL_GFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 4 | 62.5% | 2.5 | 73.06% | 25.6 | 6
| Grand Falls_08 | NL_GFS08_GEN | Nalcor Energy | Exploits River | 48.9254 | -55.6678 | Newfoundland and Labrador.a | Newfoundland | Grand Falls (GFS) | NL_GFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 4 | 62.5% | 2.5 | 73.06% | 25.6 | 6
| Grand Falls_09 | NL_GFS09_GEN | Nalcor Energy | Exploits River | 48.9254 | -55.6678 | Newfoundland and Labrador.a | Newfoundland | Grand Falls (GFS) | NL_GFS_DFS | 230 | 1905 | 2100 | Hydro_daily | hydro_daily | 30 | 80% | 24 | 73.06% | 192 | 6
| Hinds Lake | NL_HLK00_GEN | Nalcor Energy | Grand Lake | 49.0825 | -57.2014 | Newfoundland and Labrador.a | Newfoundland | Hinds Lake (HLK) | NL_HLK_GSS | 138 | 1980 | 2100 | Hydro_daily | hydro_daily | 75 | 100% | 75 | 53.88% | 354 | 1
| Paradise River | NL_PRV00_GEN | Nalcor Energy | Paradise River | 47.6182 | -54.4315 | Newfoundland and Labrador.a | Newfoundland | Paradise River (PRV) | NL_PRV_DFS | 138 | 1989 | 2100 | Hydro_daily | hydro_daily | 8 | 100% | 8 | 49.94% | 35 | 1
| Rattle Brook | NL_RTK00_GEN | Algonquin Power | Northern Peninsula | 49.8876 | -56.8359 | Newfoundland and Labrador.a | Newfoundland | Rattle Brook (RTK) | NL_RTK_GSS | 66 | 1998 | 2023 | Hydro_daily | hydro_daily | 4 | 0% | 0 | 42.81% | 15 | 1
| Star Lake | NL_SLK00_GEN | Nalcor Energy | Deer Lake | 48.5523 | -57.2057 | Newfoundland and Labrador.a | Newfoundland | Star Lake (SLK) | NL_SLK_GSS | 66 | 1998 | 2100 | Hydro_daily | hydro_daily | 18 | 100% | 18 | 89.42% | 141 | 1
| Bay Despoir_01 | NL_BDE01_GEN | Nalcor Energy | Bay Despoir | 47.9901 | -55.7997 | Newfoundland and Labrador.a | Newfoundland | Bay Despoir (BDE) | NL_BDE_GSS | 230 | 1967 | 2100 | Hydro_monthly | hydro_monthly | 76.5 | 100% | 76.5 | 49.39% | 331 | 7
| Bay Despoir_02 | NL_BDE02_GEN | Nalcor Energy | Bay Despoir | 47.9901 | -55.7997 | Newfoundland and Labrador.a | Newfoundland | Bay Despoir (BDE) | NL_BDE_GSS | 230 | 1967 | 2100 | Hydro_monthly | hydro_monthly | 76.5 | 100% | 76.5 | 49.39% | 331 | 7
| Bay Despoir_03 | NL_BDE03_GEN | Nalcor Energy | Bay Despoir | 47.9901 | -55.7997 | Newfoundland and Labrador.a | Newfoundland | Bay Despoir (BDE) | NL_BDE_GSS | 230 | 1967 | 2100 | Hydro_monthly | hydro_monthly | 76.5 | 100% | 76.5 | 49.39% | 331 | 7
| Bay Despoir_04 | NL_BDE04_GEN | Nalcor Energy | Bay Despoir | 47.9901 | -55.7997 | Newfoundland and Labrador.a | Newfoundland | Bay Despoir (BDE) | NL_BDE_GSS | 230 | 1968 | 2100 | Hydro_monthly | hydro_monthly | 76.5 | 100% | 76.5 | 49.39% | 331 | 7
| Bay Despoir_05 | NL_BDE05_GEN | Nalcor Energy | Bay Despoir | 47.9901 | -55.7997 | Newfoundland and Labrador.a | Newfoundland | Bay Despoir (BDE) | NL_BDE_GSS | 230 | 1970 | 2100 | Hydro_monthly | hydro_monthly | 76.5 | 100% | 76.5 | 49.39% | 331 | 7
| Bay Despoir_06 | NL_BDE06_GEN | Nalcor Energy | Bay Despoir | 47.9901 | -55.7997 | Newfoundland and Labrador.a | Newfoundland | Bay Despoir (BDE) | NL_BDE_GSS | 230 | 1970 | 2100 | Hydro_monthly | hydro_monthly | 76.5 | 100% | 76.5 | 49.39% | 331 | 7
| Bay Despoir_07 | NL_BDE07_GEN | Nalcor Energy | Bay Despoir | 47.9901 | -55.7997 | Newfoundland and Labrador.a | Newfoundland | Bay Despoir (BDE) | NL_BDE_GSS | 230 | 1977 | 2100 | Hydro_monthly | hydro_monthly | 154.4 | 100% | 154.4 | 49.02% | 663 | 7
| Churchill Falls_01 | NL_CFP01_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_02 | NL_CFP02_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_03 | NL_CFP03_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_04 | NL_CFP04_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_05 | NL_CFP05_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_06 | NL_CFP06_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_07 | NL_CFP07_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_08 | NL_CFP08_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_09 | NL_CFP09_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_10 | NL_CFP10_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Churchill Falls_11 | NL_CFP11_GEN | Churchill Fall (Labrador Corporation) | Churchill Falls, Labrador | 53.5294 | -63.9651 | Newfoundland and Labrador.b | Labrador | Churchill Falls (CFP) | NL_CFP_GSS | 230 | 1969 | 2100 | Hydro_monthly | hydro_monthly | 493.45 | 98.1% | 484.0744 | 69.4% | 3000 | 11
| Granite Canal | NL_GCL00_GEN | Nalcor Energy | Bay D'Espoir System | 48.1966 | -56.8152 | Newfoundland and Labrador.a | Newfoundland | Granite Canal (GCL) | NL_GCL_GSS | 230 | 2003 | 2100 | Hydro_monthly | hydro_monthly | 40 | 100% | 40 | 70.21% | 246 | 1
| CONTRACTED - QB-NL | NL_QBNL100_GEN | Churchill Fall (Labrador) Corporation | QB-NL Border | 52.1021 | -65.6932 | Newfoundland and Labrador.b | Labrador | IPT Montagnais | PP_QBNL1_IPT | 735 | 1969 | 2041 | Hydro_monthly | hydro_monthly | -4903 | 100% | -4903 | 66.74% | -28665 | [21 empty] | 1969 CFLCo Contract + Guaranteed Winter Availability Contract (GWAC)
| CONTRACTED - NS-NL | NL_NSNL100_GEN | Nalcor Energy | NS-NL Border | 46.9965 | -59.44 | Newfoundland and Labrador.a | Newfoundland | IPT Woodbine | PP_NSNL1_IPT | 230 | 2020 | 2055 | Hydro_monthly | hydro_monthly | -170 | 100% | -170 | 65.81% | -980 | 1 | [20 empty] | Average Annual Energy based on 16 hours per day, or 66.67%
| Muskrat Falls_01 | NL_MSF01_GEN | Nalcor Energy | Churchill River, Labrador | 53.2476 | -60.7728 | Newfoundland and Labrador.b | Labrador | Muskrat Falls (TS2) | NL_TS2_CSS | 315 | 2020 | 2070 | Hydro_monthly | hydro_monthly | 206 | 96% | 197.76 | 68.02% | 1227.5 | 4
| Muskrat Falls_02 | NL_MSF02_GEN | Nalcor Energy | Churchill River, Labrador | 53.2476 | -60.7728 | Newfoundland and Labrador.b | Labrador | Muskrat Falls (TS2) | NL_TS2_CSS | 315 | 2020 | 2070 | Hydro_monthly | hydro_monthly | 206 | 96% | 197.76 | 68.02% | 1227.5 | 4
| Muskrat Falls_03 | NL_MSF03_GEN | Nalcor Energy | Churchill River, Labrador | 53.2476 | -60.7728 | Newfoundland and Labrador.b | Labrador | Muskrat Falls (TS2) | NL_TS2_CSS | 315 | 2020 | 2070 | Hydro_monthly | hydro_monthly | 206 | 96% | 197.76 | 68.02% | 1227.5 | 4
| Muskrat Falls_04 | NL_MSF04_GEN | Nalcor Energy | Churchill River, Labrador | 53.2476 | -60.7728 | Newfoundland and Labrador.b | Labrador | Muskrat Falls (TS2) | NL_TS2_CSS | 315 | 2020 | 2070 | Hydro_monthly | hydro_monthly | 206 | 96% | 197.76 | 68.02% | 1227.5 | 4
| Upper Salmon | NL_USL00_GEN | Nalcor Energy | Bay D'Espoir System | 48.1835 | -56.1725 | Newfoundland and Labrador.a | Newfoundland | Upper Salmon (USL) | NL_USL_GSS | 230 | 1983 | 2100 | Hydro_monthly | hydro_monthly | 84 | 100% | 84 | 75.56% | 556 | 1
| Buchans | NL_BUC00_GEN | Nalcor Energy | Exploits River | 48.822 | -56.8314 | Newfoundland and Labrador.a | Newfoundland | Buchans (BUC) | NL_BUC_DFS | 230 | 1987 | 2100 | Hydro_run | hydro_run | 2 | 75% | 1.5 | 70.05% | 12.2727 | 1
| Cape Broyle | NL_CAB00_GEN | Newfoundland Power | Cape Broyle | 47.0959 | -52.9372 | Newfoundland and Labrador.a | Newfoundland | Cape Broyle (CAB) | NL_CAB_DFS | 66 | 1953 | 2100 | Hydro_run | hydro_run | 6.26 | 75% | 4.695 | 57.64% | 31.6084 | 1
| Topsail | NL_TOP00_GEN | Newfoundland Power | St. John's | 47.5395 | -52.9191 | Newfoundland and Labrador.a | Newfoundland | Chamberlains (CHA) | NL_CHA_DFS | 66 | 1932 | 2100 | Hydro_run | hydro_run | 2.55 | 75% | 1.9125 | 52.08% | 11.6336 | 1
| Hearts Content | NL_HCT00_GEN | Newfoundland Power | Avalon | 47.8628 | -53.3758 | Newfoundland and Labrador.a | Newfoundland | Hearts Content (HCT) | NL_HCT_DFS | 66 | 1960 | 2100 | Hydro_run | hydro_run | 2.37 | 75% | 1.7775 | 39.88% | 8.2796 | 1
| Horsechops | NL_HCP00_GEN | Newfoundland Power | St. John's | 47.132 | -52.9816 | Newfoundland and Labrador.a | Newfoundland | Horsechops (HCP) | NL_HCP_GSS | 66 | 1953 | 2100 | Hydro_run | hydro_run | 8.3 | 75% | 6.225 | 55% | 39.9894 | 1
| Lockston | NL_LOK00_GEN | Newfoundland Power | Clarenville | 48.4008 | -53.3786 | Newfoundland and Labrador.a | Newfoundland | Lockston (LOK) | NL_LOK_DFS | 66 | 1956 | 2100 | Hydro_run | hydro_run | 3.38 | 75% | 2.535 | 37.22% | 11.0204 | 2
| Rose Blanche | NL_RBH00_GEN | Newfoundland Power | Stephenville | 47.6519 | -58.713 | Newfoundland and Labrador.a | Newfoundland | Long Lake (LGL) | NL_LGL_DFS | 69 | 1998 | 2100 | Hydro_run | hydro_run | 5.96 | 75% | 4.47 | 52.5% | 27.41 | 1
| Lookout Brook | NL_LBK00_GEN | Newfoundland Power | Stephenville | 48.3662 | -58.2939 | Newfoundland and Labrador.a | Newfoundland | Lookout Brook (LBK) | NL_LBK_DFS | 69 | 1945 | 2100 | Hydro_run | hydro_run | 6.15 | 75% | 4.6125 | 57.06% | 30.7405 | 2
| Mobile | NL_MOB00_GEN | Newfoundland Power | Mobile | 47.2479 | -52.8418 | Newfoundland and Labrador.a | Newfoundland | Mobile (MOB) | NL_MOB_DFS | 66 | 1950 | 2100 | Hydro_run | hydro_run | 11.97 | 75% | 8.9775 | 45.88% | 48.1085 | 1
| Morris | NL_MRP00_GEN | Newfoundland Power | St. John's | 47.2537 | -52.9358 | Newfoundland and Labrador.a | Newfoundland | Morris (MRP) | NL_MRP_GSS | 66 | 1983 | 2100 | Hydro_run | hydro_run | 1.14 | 75% | 0.855 | 52.52% | 5.2449 | 1
| New Chelsea | NL_NCH00_GEN | Newfoundland Power | Avalon | 48.0292 | -53.2104 | Newfoundland and Labrador.a | Newfoundland | New Chelsea (NCH) | NL_NCH_DFS | 66 | 1956 | 2100 | Hydro_run | hydro_run | 3.7 | 75% | 2.775 | 44.78% | 14.5141 | 1
| Petty Harbour | NL_PHR00_GEN | Newfoundland Power | St. John's | 47.4654 | -52.7123 | Newfoundland and Labrador.a | Newfoundland | Petty Harbour (PHR) | NL_PHR_DFS | 66 | 1900 | 2100 | Hydro_run | hydro_run | 5.31 | 75% | 3.9825 | 33.3% | 15.4897 | 3
| Pierres Brook | NL_PBK00_GEN | Newfoundland Power | St. John's | 47.2884 | -52.821 | Newfoundland and Labrador.a | Newfoundland | Pierres Brook (PBK) | NL_PBK_GSS | 66 | 1931 | 2100 | Hydro_run | hydro_run | 4.3 | 75% | 3.225 | 69.86% | 26.3149 | 1
| Rattling Brook | NL_RBK00_GEN | Newfoundland Power | Grand Falls | 49.0675 | -55.298 | Newfoundland and Labrador.a | Newfoundland | Rattling Brook (RBK) | NL_RBK_DFS | 66 | 1958 | 2100 | Hydro_run | hydro_run | 11.1 | 75% | 8.325 | 65.02% | 63.2228 | 2
| Rocky Pond | NL_ROP00_GEN | Newfoundland Power | St. John's | 47.2104 | -52.895 | Newfoundland and Labrador.a | Newfoundland | Rocky Pond (ROP) | NL_ROP_DFS | 66 | 1943 | 2100 | Hydro_run | hydro_run | 3.25 | 75% | 2.4375 | 42.16% | 12.003 | 1
| Sandy Brook | NL_SBK00_GEN | Newfoundland Power | Grand Falls | 48.891 | -55.8228 | Newfoundland and Labrador.a | Newfoundland | Sandy Brook (SBK) | NL_SBK_GSS | 66 | 1963 | 2100 | Hydro_run | hydro_run | 5.53 | 75% | 4.1475 | 54.94% | 26.6145 | 1
| Seal Cove | NL_SCV00_GEN | Newfoundland Power | St. John's | 47.4574 | -53.0678 | Newfoundland and Labrador.a | Newfoundland | Seal Cove (SCV) | NL_SCV_DFS | 66 | 1924 | 2100 | Hydro_run | hydro_run | 3.5 | 75% | 2.625 | 29.32% | 8.9895 | 2
| Tors Cove | NL_TCV00_GEN | Newfoundland Power | Tors Cove | 47.2107 | -52.8483 | Newfoundland and Labrador.a | Newfoundland | Tors Cove (TCV) | NL_TCV_GSS | 66 | 1942 | 2100 | Hydro_run | hydro_run | 6.5 | 75% | 4.875 | 43.34% | 24.6778 | 3
| Holyrood_01 | NL_HOL01_GEN | Nalcor Energy | Conception Bay South | 47.3858 | -53.1277 | Newfoundland and Labrador.a | Newfoundland | Holyrood GS (HOL) | NL_HOL_GSS | 230 | 1970 | 2020 | Oil_ST | diesel | 170 | 100% | 170 | 25% | 372.3 | 4 | 10.39 | [11 empty] | 10% | 8
| Holyrood_02 | NL_HOL02_GEN | Nalcor Energy | Conception Bay South | 47.3858 | -53.1277 | Newfoundland and Labrador.a | Newfoundland | Holyrood GS (HOL) | NL_HOL_GSS | 230 | 1971 | 2020 | Oil_ST | diesel | 170 | 100% | 170 | 25% | 372.3 | 4 | 10.39 | [11 empty] | 5% | 8
| Holyrood_03 | NL_HOL03_GEN | Nalcor Energy | Conception Bay South | 47.3858 | -53.1277 | Newfoundland and Labrador.a | Newfoundland | Holyrood GS (HOL) | NL_HOL_GSS | 230 | 1980 | 2020 | Oil_ST | diesel | 150 | 100% | 150 | 25% | 328.5 | 4 | 10.39 | [11 empty] | 7% | 8
| Fermeuse | NL_FER00_GEN | Elemental Energy | Fermeuse | 46.9699 | -52.97 | Newfoundland and Labrador.a | Newfoundland | Fermeuse (FER) | NL_FER_DFS | 66 | 2008 | 2028 | Wind_Onshore | wind | 27 | 22% | 5.94 | 35.51% | 84
| St Lawrence | NL_STL00_GEN | Enel North America Inc. | St. Lawrence | 46.95 | -55.4293 | Newfoundland and Labrador.a | Newfoundland | Webbers Cove (WBC) | NL_WBC_DFS | 66 | 2008 | 2028 | Wind_Onshore | wind | 27 | 22% | 5.94 | 44.39% | 105
Specific Notes:
Total installed capacity at Churchill Falls is 5428 MW; 300 MW at 90% capacity factor and an additional 225 MW (1,970 GWh/y) under the TwinCo block is available to Nalcor; the remainder is sold to Hydro Quebec under the 1969 Power Contract
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Unless noted otherwise, the wind generating stations are presumed to be connected to the nearest 69 kV substation
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit Hydro_run facilities treated as single-unit facilities
RH Additions, Comments and TODOs
Remote projects are not included in this list.
See calculations sheets for sources of values.
Sources

## Storage
NL | EXISTING STORAGE | [12 empty] | DESIGN | [7 empty] | OPERATIONS
| Project Name | Storage Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Technology | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Days | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | kV | [5 empty] | (MW) | (MWh) | (Hours) |  | ($M) | (hours) | (hours) | (%) | (days/y) | ($/year) | ($/MWh)
NONE
Specific Notes:

## HydroExisting
NL | EXISTING STORAGE HYDROELECTRIC | [24 empty] | RESERVOIR
| Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Renewal Year | Dam Type | Penstock | Rated Head | Maximum Head | Minimum Head | Operating Flow (Facility) | Rated Discharge (Unit) | Rated Discharge (Facility) | Upstream Reservoir Area | Upstream Reservoir Storage | Turbine Type | Station Flow | Upper Storage Name | Upper Storage Level | Lower Storage Name | Lower Storage Level | Upper Storage Name | Minimum Level | Maximum Level | Initial Level | Low Reference Level | High Reference Level | Low Volume | High Volume | Live Storage | M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10 | M11 | M12 | Other References | Notes
|  |  | (MW) |  | (MW) |  | (GWh/year) |  |  |  | (m) | (m) | (m) | (m) | (m3/s) | (m3/s) | (m3/s) | (km2) | (hours) |  | (WSC#) |  | (WSC#) |  | (WSC#) |  | (m) | (m) | (m) | (m) | (m) | (m3) | (m3) | (m3) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s)
| Bay Despoir | Hydro_monthly | 613.4 | 100% | 613.4 | 49.3% | 2649 | 7 |  |  |  | 176 |  |  |  |  | 320 |  |  |  | 02ZE003 | Jeddore Lake |  | Bay Despoir
| Bishops Falls | Hydro_monthly | 22 | 67% | 14.5 | 70.05% | 135 | 9 | [13 empty] | Exploits River |  | Exploits River | [23 empty] | Monthly storage but at reduced dependable capacity, so daily
| Cat Arm | Hydro_daily | 137 | 78% | 134 | 31.25% | 375 | 2 |  |  |  | 386 |  |  |  |  | 40 |  |  |  | 02YF001 | Cat Arm Reservoir |  | White Bay
| Churchill Falls Recall Power | Hydro_monthly | 300 | 98.1% | 300 | 90% | 2362 | 11 |  |  |  | 312.4 |  |  |  |  | 1388 |  |  |  | 03OD005 | East Forebay |  | Churchill River | [23 empty] | Churchill Falls split into three parts
| Churchill Falls Contracted | Hydro_monthly | 4903 | 98.1% | 4809.843 | 66.74% | 28665 | 11 |  |  |  | 312.4 |  |  |  |  | 1388 |  |  |  | 03OD005 | East Forebay |  | Churchill River | [23 empty] | Churchill Falls split into three parts
| Churchill Falls TwinCo | Hydro_monthly | 225 | 98.1% | 225 | 100% | 1971 | 11 |  |  |  | 312.4 |  |  |  |  | 1388 |  |  |  | 03OD005 | East Forebay |  | Churchill River | [23 empty] | Churchill Falls split into three parts
| Deer Lake | Hydro_hourly | 125.5 | 78.49% | 98.5 | 71.68% | 788 | 9 | [12 empty] | 02YK001 | Grand Lake |  | Deer Lake | 02YL007
| Grand Falls | Hydro_monthly | 75 | 64% | 48 | 73.06% | 480 | 6 | [12 empty] | 02YO001 | Red Indian Reservoir |  | Exploits River | [23 empty] | Monthly storage but at reduced dependable capacity, so daily
| Granite Canal | Hydro_monthly | 40 | 100% | 40 | 70.21% | 246 | 1 |  |  |  | 37 |  |  |  |  | 122 |  |  |  |  | Granite Lake | 02ZC004 |  | 02ZD003
| Hinds Lake | Hydro_monthly | 75 | 100% | 75 | 53.27% | 350 | 1 |  |  |  | 214 |  |  |  |  | 40 |  |  |  | 02YO016 | Red Indian Lake | 02YO017 | Exploits River | 02YO016
| Muskrat Falls | Hydro_monthly | 824 | 95.87% | 790 | 68.02% | 4910 | 4 |  |  |  | 36 |  |  |  |  | 1840 |  |  |  | 03OE001 | Churchill River | 03OE001 | Churchill River | 03OE014 | [22 empty] | 03OE001 prior to full reservoir inundation
| Paradise | Hydro_hourly | 8 | 100% | 8 | 49.94% | 35 | 1 |  |  |  | 43 |  |  |  |  | 25
| Rattle Brook | Hydro_hourly | 4 | 100% | 4 | 42.81% | 15 | 1
| Star Lake | Hydro_monthly | 18 | 100% | 18 | 89.42% | 141 | 1 | [13 empty] | Star Lake |  | Red Indian Reservoir
| Upper Salmon | Hydro_monthly | 84 | 100% | 84 | 77.46% | 570 | 1 |  |  |  | 51 |  |  |  |  | 190 |  |  |  |  | Meelpaeg |  | Jeddore Lake
| Watsons Brook | Hydro_hourly | 9 | 100% | 9 | 82.45% | 65 | 1
General Notes:
Hydroelectric generation type has been estimated based on available information concerning operations, reservoir size and operations, facility location and design flows.
The WSC# refers to the Water Survey of Canada Hydrometric station

## HydroRenewals
NL | HYDROELECTRIC RENEWAL |  | Existing Design | [7 empty] | Renewal Design | [14 empty] | Costs | 1.77% | 1.05 |  |  | 7% | 70
| Existing Project Name | Owner | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Renewal Project Name | Renewal Project Code | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Additional Annual Energy | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed Cost Existing Project | Fixed Cost Renewed Project | Fixed O&M | Variable Costs | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
|  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) | [5 empty] | dd.dddd | dd.dddd |  |  |  |  | (km) |  |  | (MW) | (MW) | (GWh/year) | ($2018M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M/year) | ($/kW-year) | ($/year) | ($/year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
| Bay Despoir | Nalcor Energy | Hydro_monthly | 613.4 | 100% | 613.4 | 49.3% | 2649 | 7 | 1967 | Bay Despoir_08 | RN_BD8 | Bay Despoir |  |  | Newfoundland and Labrador.a | Bay Despoir (BDE) | NL_BDE_GEN | 230 | 25 | Hydro_monthly | hydro_monthly | 154 | 154 | 0 |  |  |  | 393.7 | 10.9924 | 404.6924 | 28.5792 | 185.5791 | 8823144.6612 | 9776349.8479 | 6189.6441 | 5.7 | 3.24 | 8.94 |  |  | 4 | 6
| Cat Arm | Nalcor Energy | Hydro_daily | 137 | 78% | 134 | 31.25% | 375 | 2 | 1985 | Cat Arm_03 | RN_CAT | Northern Peninsula |  |  | Newfoundland and Labrador.a | Cat Arm (CAM) | NL_CAM_GEN | 230 | 150 | Hydro_daily | hydro_daily | 68.2 | 68.2 | 25 | 667 | 11.8059 | -117.0728 | 561.7331 | 13.9899 | 575.723 | 40.6573 | 596.1479 | 4440734.1274 | 5343354.4219 | 13234.9017 | 5.7 | 3.24 | 8.94 |  |  | 4 | 6 | Transmission must be developed to DLK - Deer Lake
General Notes:
Distance to grid is 0 km in all instances but 25 km is used to account for potential grid interconnection and upgrade costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume Hydro_daily and Hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroGreenfield
NL | HYDROELECTRIC GREENFIELD | [10 empty] | DESIGN | [6 empty] | COSTS |  |  | 1.77% | 1.05 |  |  | 7% | 70
| Project Name | Project Code | Owner | Location (River) | Latitude | Longitude | COPPER Balancing Area | Distance to Market Grid | Connecting Node Name | Connecting Node Code | Connecting Voltage | Generation Type | Generation Type - COPPER | Installed Capacity | Effective Capacity | Average Annual Energy - Plant | Capacity Factor | # of units | Total Capital Cost | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Construction Time | Development Time | Notes
[11 empty] | (kV) |  |  | (MW) | (MW) | (GWh/year) | (%) |  | ($1977M) | ($2008M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($M/MW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | (years) | (years)
| Badger Chute | GF_BDC | Nalcor Energy | Exploits River | 48.9391 | -55.9759 | Newfoundland and Labrador.a | 25 | Buchans (BUC) | NL_BUC_SUB | 69 | hydro_daily | hydro_daily | 24 | 24 | 154 | 73.25% | 3 |  |  | 227.6 | 4.0285 | 23.9446 | 255.5731 | 40.9979 | 296.571 | 20.9437 | 0.87265 | 83322.4937 | 5.7 | 3.24 | 8.94 | 3 | 5
| Gull Island | GF_GIP | Nalcor Energy | Churchill River, Labrador | 52.9743 | -61.4484 | Newfoundland and Labrador.b | 1500 | Muskrat Falls (TS2) | NL_TS2_SUB | 735 | hydro_monthly | hydro_monthly | 2250 | 2250 | 11900 | 60.38% | 5 |  | 4300 | 5027.3444 | 88.984 | 1465.4828 | 6581.8112 | 371.4226 | 6953.2338 | 491.0341 | 0.21824 | 7111.379 | 0.73183 | 3.24 | 4.24 | 9 | 17 | Capital cost includes transmission to Churchill Falls; Presumes that Gull Island_230 substation is also built
| Island Pond | GF_ISP | Nalcor Energy | Bay D'Espoir System | 48.3798 | -56.3788 | Newfoundland and Labrador.a | 25 | Granite Canal Tap (GCL) | NL_GRC_SUB | 230 | hydro_run | hydro_run | 36 | 36 | 186 | 58.98% | 1 |  |  | 377.9 | 6.6888 | 39.7569 | 424.3457 | 57.8293 | 482.175 | 34.051 | 0.94586 | 66883.778 | 5.7 | 3.24 | 8.94 | 3 | 5
| Portland Creek | GF_POC | Nalcor Energy | Daniels Harbour | 50.1631 | -57.6195 | Newfoundland and Labrador.a | 50 | Peters Barren (PBN) | NL_PBN_SUB | 69 | hydro_run | hydro_run | 23 | 23 | 142 | 70.48% | 2 |  |  | 237.7 | 4.2073 | 25.0072 | 266.9145 | 42.2234 | 309.1379 | 21.8312 | 0.94918 | 85266.859 | 5.7 | 3.24 | 8.94 | 3 | 5
| Red Indian Falls | GF_RIF | Nalcor Energy | Exploits River | 48.8672 | -56.2251 | Newfoundland and Labrador.a | 75 | Buchans (BUC) | NL_BUC_SUB | 69 | hydro_daily | hydro_daily | 42 | 42 | 268 | 72.84% | 2 |  |  | 359.3 | 6.3596 | 37.8001 | 403.4597 | 55.8827 | 459.3424 | 32.4385 | 0.77235 | 61522.7355 | 5.7 | 3.24 | 8.94 | 3 | 5
| Round Pond | GF_ROP | Nalcor Energy | Bay D'Espoir System | 48.201 | -55.994 | Newfoundland and Labrador.a | 75 | Bay Despoir (BDE) | NL_BDE_GEN | 230 | hydro_run | hydro_run | 18 | 18 | 139 | 88.15% | 1 |  |  | 224.1 | 3.9666 | 23.5764 | 251.643 | 40.5691 | 292.212 | 20.6359 | 1.1464 | 97382.0818 | 5.7 | 3.24 | 8.94 | 3 | 5
General Notes:
Distance to grid is 0 km in all instances but 25 km is used to account for potential grid interconnection and upgrade costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume Hydro_daily and Hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroPS
NL | HYDROELECTRIC PUIMPED STORAGE | [15 empty] | Existing Design | [8 empty] | Reservoir Design | [13 empty] | Costs | 1.77% | 1.06 |  |  | 7% | 70
| Pumped Storage Project | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Estimated Round Trip Efficiency | Existing Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Salt/Fresh | Reservoir Types | Reservoir Storage | Storage Requirement | Gross Head | Penstock | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping) | Turbine Type | Pump Type | Generation Duration at Peak Output | Efficient Pumping Capacity Duration | Total Footprint | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Cost of Capacity | Unit Cost of Stored Energy | Levelized Cost | Construction Time | Development Time | Notes
[5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) |  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) |  |  |  |  | (m3) | (MWh) | (m) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2018/MW) | ($2018/MWh) | ($2018/kW-year) | (years) | (years)
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume Hydro_daily and Hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## Transmission
NL | EXISTING TRANSMISSION
| Circuit ID | Owner | Operating Region | Number of Circuits | Current | Length | Length | Voltage | Reactance | Smax | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes
[5 empty] | (ac/dc) | (km) | (miles) | (kV) | (ohm) |  | (A) | (A) | (MVA) | (MVA) |  | (MW) | (MW)
| 410L | Newfoundland Power | Newfoundland | 1 | ac | 20 | 12.3 | 66 | 7.6429 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Abraham's Cove (ABC) | NL_ABC_DSS | Lower Cove Mine (LCV) | NL_LCV_DSS
| 124L | Newfoundland Power | Newfoundland | 1 | ac | 35 | 21.6 | 138 | 15.175 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Alexander Bay (ALX) | NL_ALX_JCT | Gambo (GAM) | NL_GAM_DSS
| 121L | Newfoundland Power | Newfoundland | 1 | ac | 17.6 | 10.9 | 138 | 7.6309 |  |  | 550.4 |  | 131.6 | 0.9 | 98.7 | 118.44 | Alexander Bay (ALX) | NL_ALX_JCT | Glovertown (GLV) | NL_GLV_DSS
| 363L | Newfoundland Power | Newfoundland | 1 | ac | 41.2 | 25.4 | 138 | 17.8631 |  |  | 550.4 |  | 131.6 | 0.9 | 98.7 | 118.44 | Baie Verte Junction (BVJ) | NL_BVJ_DSS | Seal Cove Road (SCR) | NL_SCR_DSS |  | Bay Verte Junction also called Indian River
| TL223 | Nalcor Energy | Newfoundland | 1 | ac | 23.3 | 14.4 | 138 | 10.1022 |  |  |  |  | 92.7 | 0.9 | 69.525 | 83.43 | Baie Verte Junction (BVJ) | NL_BVJ_DSS | Springdale (SPR) | NL_SPR_DSS
| TL220 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 66 | 13.3368 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Bay Despoir (BDE) | NL_BDE_GSS | Conne River (CRV) | NL_CRV_DSS
| TL202 | Nalcor Energy | Newfoundland | 1 | ac | 139.5 | 86.1 | 230 | 66.96 |  |  |  |  | 369.5 | 0.9 | 277.125 | 332.55 | Bay Despoir (BDE) | NL_BDE_GSS | Sunnyside (SUN) | NL_SUN_TSS
| TL206 | Nalcor Energy | Newfoundland | 1 | ac | 139.5 | 86.1 | 230 | 66.96 |  |  |  |  | 369.5 | 0.9 | 277.125 | 332.55 | Bay Despoir (BDE) | NL_BDE_GSS | Sunnyside (SUN) | NL_SUN_TSS
| TL234 | Nalcor Energy | Newfoundland | 1 | ac | 64 | 39.5 | 230 | 30.72 |  |  |  |  | 469.6 | 0.9 | 352.2 | 422.64 | Bay Despoir (BDE) | NL_BDE_GSS | Upper Salmon (USL) | NL_USL_GSS
| TL267 | Nalcor Energy | Newfoundland | 1 | ac | 135 | 83.3 | 230 | 64.8 | 2.2946 |  |  |  |  | 0.9 | 307.4718 | 332.712 | Bay Despoir (BDE) | NL_BDE_GSS | Western Avalon (WAV) | NL_WAV_DSS
| TL212 | Nalcor Energy | Newfoundland | 1 | ac | 58.1 | 35.9 | 138 | 25.1905 |  |  |  |  | 112.4 | 0.9 | 84.3 | 101.16 | Bay Largent (BLA) | NL_BLA_DSS | Linton Lake (LLK) | NL_LLK_DSS
| 048L | Newfoundland Power | Newfoundland | 1 | ac | 29.4 | 18.2 | 66 | 11.235 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Bay Roberts (BRB) | NL_BRB_DSS | Blaketown (BLK) | NL_BLK_DSS
| 056L | Newfoundland Power | Newfoundland | 1 | ac | 32.4 | 20 | 66 | 12.3814 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Bay Roberts (BRB) | NL_BRB_DSS | Carbonear (CAR) | NL_CAR_DSS
| 057L | Newfoundland Power | Newfoundland | 1 | ac | 11 | 6.8 | 66 | 4.2036 |  |  | 471.5 |  | 53.9 | 0.9 | 40.425 | 48.51 | Bay Roberts (BRB) | NL_BRB_DSS | Upper Island Cove (ILC) | NL_ILC_DSS
| 358L | Newfoundland Power | Newfoundland | 1 | ac | 14.7 | 9.1 | 66 | 5.6175 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Bayview (BVS) | NL_BVS_DSS | Gillams (GIL) | NL_GIL_DSS
| TL244 | Nalcor Energy | Newfoundland | 1 | ac | 29.1 | 17.9 | 138 | 12.6169 |  |  |  |  | 112.6 | 0.9 | 84.45 | 101.34 | Bear Cove (BRV) | NL_BRV_DSS | Plum Point (PPT) | NL_PPT_DSS
| 410L | Newfoundland Power | Newfoundland | 1 | ac | 24 | 14.8 | 66 | 9.1714 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Berry Head (BHD) | NL_BHD_DSS | Abraham's Cove (ABC) | NL_ABC_DSS
| TL239 | Nalcor Energy | Newfoundland | 1 | ac | 75.6 | 46.7 | 138 | 32.778 |  |  |  |  | 161.7 | 0.9 | 121.275 | 145.53 | Berry Hill (BHL) | NL_BHL_DSS | Deer Lake (DLK) | NL_DLK_DFS
| TL259 | Nalcor Energy | Newfoundland | 1 | ac | 81.4 | 50.2 | 138 | 35.2927 |  |  |  |  | 161.7 | 0.9 | 121.275 | 145.53 | Berry Hill (BHL) | NL_BHL_DSS | Peters Barren (PBN) | NL_PBN_DSS
| TL227 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 66 | 4.4329 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Berry Hill (BHL) | NL_BHL_DSS | Sallys Cove (SCV) | NL_SCV_DSS
| 024L | Newfoundland Power | Newfoundland | 1 | ac | 10.5 | 6.5 | 66 | 4.0125 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Big Pond (BIG) | NL_BIG_DSS | Mobile (MOB) | NL_MOB_DFS
| 134L | Newfoundland Power | Newfoundland | 1 | ac | 14.7 | 9.1 | 66 | 5.6175 |  |  | 550.4 |  | 131.6 | 0.9 | 98.7 | 118.44 | Bishops Falls (BFS) | NL_BFS_DFS | Botwood (BOT) | NL_BOT_DSS
| 080L | Newfoundland Power | Newfoundland | 1 | ac | 25 | 15.4 | 66 | 9.5536 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Blaketown (BLK) | NL_BLK_DSS | New Harbour (NHR) | NL_NHR_DSS
| 055L | Newfoundland Power | Newfoundland | 1 | ac | 15 | 9.3 | 66 | 5.7321 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Blaketown (BLK) | NL_BLK_DSS | Placentia Junction (PJN) | NL_PJN_DSS
| 094L | Newfoundland Power | Newfoundland | 1 | ac | 27 | 16.7 | 66 | 10.3179 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Blaketown (BLK) | NL_BLK_DSS | St Catherines (SCT) | NL_SCT_DSS
| 064L | Newfoundland Power | Newfoundland | 1 | ac | 17.6 | 10.9 | 66 | 6.7257 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Blaketown (BLK) | NL_BLK_DSS | Western Avalon (WAV) | NL_WAV_DSS
| TL233 | Nalcor Energy | Newfoundland | 1 | ac | 139.5 | 86.1 | 230 | 66.96 |  |  |  |  | 369.5 | 0.9 | 277.125 | 332.55 | Bottom Brook (BBK) | NL_BBK_TSS | Buchans (BUC) | NL_BUC_DFS
| TL214 | Newfoundland Power | Newfoundland | 1 | ac | 116.3 | 71.8 | 138 | 50.4244 |  |  |  |  | 112.4 | 0.9 | 84.3 | 101.16 | Bottom Brook (BBK) | NL_BBK_TSS | Doyles (DOY) | NL_DOY_DSS
| TL250 | Nalcor Energy | Newfoundland | 1 | ac | 110.5 | 68.2 | 138 | 47.9096 |  |  |  |  | 161.7 | 0.9 | 121.275 | 145.53 | Bottom Brook (BBK) | NL_BBK_TSS | Grandy Brook (GBK) | NL_GBK_DSS
| TL269 | Emera | Newfoundland | 1 | ac | 155 | 95.7 | 230 | 74.4 | 2.0939 |  |  |  |  | 0.9 | 280.5816 | 303.6144 | Bottom Brook (BBK) | NL_BBK_TSS | Granite Canal TS (GCL) | NL_GCL_TSS
| L2001 | Emera | Newfoundland | 1 | dc | 190 | 117.3 | 200 | [7 empty] | 250 | 250 | Bottom Brook (BBK) | NL_BBK_TSS | IPT Woodbine | PP_NSNL1_IPT |  | Length to midpoint across Cabot Strait
| L2002 | Emera | Newfoundland | 1 | dc | 190 | 117.3 | 200 | [7 empty] | 250 | 250 | Bottom Brook (BBK) | NL_BBK_TSS | IPT Woodbine | PP_NSNL1_IPT |  | Length to midpoint across Cabot Strait
| TL209 | Nalcor Energy | Newfoundland | 1 | ac | 29.1 | 17.9 | 230 | 13.968 |  |  |  |  | 369.5 | 0.9 | 277.125 | 332.55 | Bottom Brook (BBK) | NL_BBK_TSS | Stephenville (STV) | NL_STV_GSS
| 400L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Bottom Brook (BBK) | NL_BBK_TSS | Wheelers (WHE) | NL_WHE_DSS
| TL254 | Nalcor Energy | Newfoundland | 1 | ac | 17.4 | 10.8 | 66 | 6.6493 |  |  |  |  | 80.8 | 0.9 | 60.6 | 72.72 | Boyds Cove (BOY) | NL_BOY_DSS | Farewell Head (FHD) | NL_FHD_DSS
| 114L | Newfoundland Power | Newfoundland | 1 | ac | 16 | 9.9 | 66 | 6.1143 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Boyds Cove (BOY) | NL_BOY_DSS | Summerford (SUM) | NL_SUM_DSS
| TL264 | Teck Resources | Newfoundland | 1 | ac | 45 | 27.8 | 66 | 17.1964 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Buchans (BUC) | NL_BUC_DFS | Duck Pond (DKP) | NL_DKP_DSS
| TL280 | Nalcor Energy | Newfoundland | 1 | ac | 45 | 27.8 | 66 | 17.1964 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Buchans (BUC) | NL_BUC_DFS | Star Lake (SLK) | NL_SLK_GSS
| TL205 | Nalcor Energy | Newfoundland | 1 | ac | 81.4 | 50.2 | 230 | 39.072 |  |  |  |  | 322.2 | 0.9 | 241.65 | 289.98 | Buchans (BUC) | NL_BUC_DFS | Stony Brook (STY) | NL_STY_TSS
| TL232 | Nalcor Energy | Newfoundland | 1 | ac | 81.4 | 50.2 | 230 | 39.072 |  |  |  |  | 469.6 | 0.9 | 352.2 | 422.64 | Buchans (BUC) | NL_BUC_DFS | Stony Brook (STY) | NL_STY_TSS
| 066L | Newfoundland Power | Newfoundland | 1 | ac | 17.6 | 10.9 | 66 | 6.7257 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Cape Broyle (CAB) | NL_CAB_DFS | Fermeuse (FER) | NL_FER_DFS
| 041L | Newfoundland Power | Newfoundland | 1 | ac | 14.7 | 9.1 | 66 | 5.6175 |  |  | 471.5 |  | 53.9 | 0.9 | 40.425 | 48.51 | Carbonear (CAR) | NL_CAR_DSS | Hearts Content (HCT) | NL_HCT_DFS
| 040L | Newfoundland Power | Newfoundland | 1 | ac | 8.8 | 5.4 | 66 | 3.3629 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Carbonear (CAR) | NL_CAR_DSS | Victoria (VIC) | NL_VIC_DSS
| 117L | Newfoundland Power | Newfoundland | 1 | ac | 14.7 | 9.1 | 138 | 6.3735 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Catalina (CAT) | NL_CAT_DSS | Bonavista (BVA) | NL_BVA_DSS
| 051L | Newfoundland Power | Newfoundland | 1 | ac | 10.5 | 6.5 | 66 | 4.0125 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Chamberlains (CHA) | NL_CHA_DFS | Kelligrews (KEL) | NL_KEL_DSS
| L1301 | Nalcor Energy | Labrador | 1 | ac | 240 | 148.1 | 138 | 104.0571 | 1.5699 |  |  |  |  | 0.9 | 73.7875 | 81.6372 | Churchill Falls (CFP) | NL_CFP_GSS | Churchill River (TS1) | NL_TS1_TSS
| L7051 | Nalcor Energy | Labrador | 1 | ac | 170 | 104.9 | 735 | 64.6 | 1.9709 |  |  |  |  | 0.9 | 3943.4409 | 4258.9162 | Churchill Falls (CFP) | NL_CFP_GSS | IPT Montagnais | PP_QBNL1_IPT
| L7052 | Nalcor Energy | Labrador | 1 | ac | 170 | 104.9 | 735 | 64.6 | 1.9709 |  |  |  |  | 0.9 | 3943.4409 | 4258.9162 | Churchill Falls (CFP) | NL_CFP_GSS | IPT Montagnais | PP_QBNL1_IPT
| L7053 | Nalcor Energy | Labrador | 1 | ac | 170 | 104.9 | 735 | 64.6 | 1.9709 |  |  |  |  | 0.9 | 3943.4409 | 4258.9162 | Churchill Falls (CFP) | NL_CFP_GSS | IPT Montagnais | PP_QBNL1_IPT
| L3101 | Nalcor Energy | Labrador | 1 | ac | 250 | 154.3 | 315 | 113.3102 | 1.5281 |  |  |  |  | 0.9 | 404.3229 | 489.1003 | Churchill Falls (CFP) | NL_CFP_GSS | Muskrat Falls (TS2) | NL_TS2_CSS
| L3102 | Nalcor Energy | Labrador | 1 | ac | 250 | 154.3 | 315 | 113.3102 | 1.5281 |  |  |  |  | 0.9 | 404.3229 | 489.1003 | Churchill Falls (CFP) | NL_CFP_GSS | Muskrat Falls (TS2) | NL_TS2_CSS
| L2303 | Nalcor Energy | Labrador | 1 | ac | 245 | 151.2 | 230 | 117.6 | 1.5486 |  |  |  |  | 0.9 | 207.5182 | 224.5533 | Churchill Falls (CFP) | NL_CFP_GSS | Wabush (WTS) | NL_WTS_DSS
| L2304 | Nalcor Energy | Labrador | 1 | ac | 245 | 151.2 | 230 | 117.6 | 1.5486 |  |  |  |  | 0.9 | 207.5182 | 224.5533 | Churchill Falls (CFP) | NL_CFP_GSS | Wabush (WTS) | NL_WTS_DSS
| L1301 | Nalcor Energy | Labrador | 1 | ac | 16 | 9.9 | 138 | 6.9371 | 3 |  |  |  |  | 0.9 | 141 | 156 | Churchill River (TS1) | NL_TS1_TSS | Churchill River (TS3) | NL_TS3_TSS
| L1302 | Nalcor Energy | Labrador | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 |  |  |  |  | 0.9 | 141 | 156 | Churchill River (TS3) | NL_TS3_TSS | Happy Valley (HVY) | NL_HVY_DFS
| 110L | Newfoundland Power | Newfoundland | 1 | ac | 6 | 3.7 | 138 | 2.6014 |  |  | 350.4 |  | 40.1 | 0.9 | 30.075 | 36.09 | Clarenville (CLV) | NL_CLV_DSS | Milton (MIL) | NL_MIL_DSS
| 124L | Newfoundland Power | Newfoundland | 1 | ac | 18 | 11.1 | 138 | 7.8043 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Clarenville (CLV) | NL_CLV_DSS | Port Blandford (PBD) | NL_PBD_DSS
| 123L | Newfoundland Power | Newfoundland | 1 | ac | 85.3 | 52.7 | 138 | 36.9836 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Clarenville (CLV) | NL_CLV_DSS | Princeton Pond (PRC) | NL_PRC_DSS
| 114L | Newfoundland Power | Newfoundland | 1 | ac | 12 | 7.4 | 66 | 4.5857 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Clarke's Head (CKH) | NL_CKH_DSS | Boyds Cove (BOY) | NL_BOY_DSS
| 136L | Newfoundland Power | Newfoundland | 1 | ac | 41.2 | 25.4 | 66 | 15.7443 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Cobbs Pond (COB) | NL_COB_DSS | Bishops Falls (BFS) | NL_BFS_DFS
| 142L | Newfoundland Power | Newfoundland | 1 | ac | 35 | 21.6 | 66 | 13.375 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Cobbs Pond (COB) | NL_COB_DSS | Clarke's Head (CKH) | NL_CKH_DSS
| 144L | Newfoundland Power | Newfoundland | 1 | ac | 8.8 | 5.4 | 138 | 3.8154 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Cobbs Pond (COB) | NL_COB_DSS | Gander (GAN) | NL_GAN_DSS
| TL210 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 138 | 5.0294 |  |  |  |  | 144.1 | 0.9 | 108.075 | 129.69 | Cobbs Pond (COB) | NL_COB_DSS | Gander (GAN) | NL_GAN_DSS
| 039L | Newfoundland Power | Newfoundland | 1 | ac | 9 | 5.6 | 66 | 3.4393 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Colliers (COL) | NL_COL_DSS | Springfield (SPF) | NL_SPF_DSS
| TL237 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 230 | 16.752 |  |  |  |  | 459.6 | 0.9 | 344.7 | 413.64 | Come by Chance (CBC) | NL_CBC_ISS | Western Avalon (WAV) | NL_WAV_DSS
| TL220 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 66 | 13.3368 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Conne River (CRV) | NL_CRV_DSS | English HR. West (EHW) | NL_EHW_DSS
| TL227 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 66 | 4.4329 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Cow Head (CHD) | NL_CHD_DSS | Parsons Pond (PPD) | NL_PPD_DSS
| TL247 | Nalcor Energy | Newfoundland | 1 | ac | 122.1 | 75.4 | 230 | 58.608 |  |  |  |  | 466.6 | 0.9 | 349.95 | 419.94 | Deer Lake (DLK) | NL_DLK_DFS | Cat Arm (CAM) | NL_CAM_GSS
| TL225 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 66 | 4.4329 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Deer Lake (DLK) | NL_DLK_DFS | Deer Lake GS (DLP) | NL_DLP_GSS
| TL245 | Nalcor Energy | Newfoundland | 1 | ac | 29.1 | 17.9 | 138 | 12.6169 |  |  |  |  | 112.6 | 0.9 | 84.45 | 101.34 | Deer Lake (DLK) | NL_DLK_DFS | Howley (HOW) | NL_HOW_DSS
| TL248 | Nalcor Energy | Newfoundland | 1 | ac | 52.3 | 32.3 | 230 | 25.104 |  |  |  |  | 466.6 | 0.9 | 349.95 | 419.94 | Deer Lake (DLK) | NL_DLK_DFS | Massey Drive (MAS) | NL_MAS_TSS
| TL226 | Nalcor Energy | Newfoundland | 1 | ac | 40.7 | 25.1 | 66 | 15.5532 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Deer Lake (DLK) | NL_DLK_DFS | Wiltondale (WDL) | NL_WDL_DSS
| TL215 | Newfoundland Power | Newfoundland | 1 | ac | 29.1 | 17.9 | 66 | 11.1204 |  |  |  |  | 46 | 0.9 | 34.5 | 41.4 | Doyles (DOY) | NL_DOY_DSS | Grand Bay (GBS) | NL_GBS_DSS
| 039L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Duffs (DUF) | NL_DUF_DSS | Holyrood (HOL) | NL_HOL_DSS
| 038L | Newfoundland Power | Newfoundland | 1 | ac | 7 | 4.3 | 66 | 2.675 |  |  | 1003.9 |  | 114.8 | 0.9 | 86.1 | 103.32 | Duffs (DUF) | NL_DUF_DSS | Seal Cove (SCV) | NL_SCV_DFS
| 055L | Newfoundland Power | Newfoundland | 1 | ac | 8 | 4.9 | 66 | 3.0571 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Dunville (DUN) | NL_DUN_DSS | Clarkes Pond (CLK) | NL_CLK_DSS
| TL220 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 66 | 13.3368 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | English HR. West (EHW) | NL_EHW_DSS | Barachoix (BCX) | NL_BCX_DSS
| 402L | Newfoundland Power | Newfoundland | 1 | ac | 8.8 | 5.4 | 66 | 3.3629 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Gallant (GAL) | NL_GAL_DSS | Berry Head (BHD) | NL_BHD_DSS
| 115L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Gambo (GAM) | NL_GAM_DSS | Hare Bay (HBS) | NL_HBS_DSS
| 146L | Newfoundland Power | Newfoundland | 1 | ac | 35.3 | 21.8 | 138 | 15.3051 |  |  | 563.8 |  | 134.8 | 0.9 | 101.1 | 121.32 | Gander (GAN) | NL_GAN_DSS | Gambo (GAM) | NL_GAM_DSS
| 108L | Newfoundland Power | Newfoundland | 1 | ac | 20 | 12.3 | 66 | 7.6429 |  |  | 350.1 |  | 40.1 | 0.9 | 30.075 | 36.09 | Gander (GAN) | NL_GAN_DSS | Jonathan's Pond (JON) | NL_JON_DSS
| 102L | Newfoundland Power | Newfoundland | 1 | ac | 28 | 17.3 | 66 | 10.7 |  |  | 350.4 |  | 40.1 | 0.9 | 30.075 | 36.09 | Gander (GAN) | NL_GAN_DSS | Roycefield Mine Tap (RFD) | NL_RFD_JCT
| 114L | Newfoundland Power | Newfoundland | 1 | ac | 4 | 2.5 | 66 | 1.5286 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Gander Bay (GBY) | NL_GBY_DSS | Clarke's Head (CKH) | NL_CKH_DSS
| 301L | Newfoundland Power | Newfoundland | 1 | ac | 13 | 8 | 66 | 4.9679 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Garnish (GAR) | NL_GAR_DSS | Salt Pond (SPO) | NL_SPO_DSS
| TL229 | Nalcor Energy | Newfoundland | 1 | ac | 23.3 | 14.4 | 66 | 8.9039 |  |  |  |  | 53.4 | 0.9 | 40.05 | 48.06 | Glenburnie (GLB) | NL_GLB_DSS | Wiltondale (WDL) | NL_WDL_DSS
| TL210 | Nalcor Energy | Newfoundland | 1 | ac | 23.3 | 14.4 | 138 | 10.1022 |  |  |  |  | 144.1 | 0.9 | 108.075 | 129.69 | Glenwood (GLN) | NL_GLN_DSS | Cobbs Pond (COB) | NL_COB_DSS
| 017L | Newfoundland Power | Newfoundland | 1 | ac | 11.6 | 7.1 | 66 | 4.4329 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Goulds (GOU) | NL_GOU_DSS | Big Pond (BIG) | NL_BIG_DSS
| 018L | Newfoundland Power | Newfoundland | 1 | ac | 7.4 | 4.5 | 66 | 2.8279 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Goulds (GOU) | NL_GOU_DSS | Glendale (GDL) | NL_GDL_DSS
| 003L | Newfoundland Power | Newfoundland | 1 | ac | 5.3 | 3.2 | 66 | 2.0254 |  |  | 474.3 |  | 27.1 | 0.9 | 20.325 | 24.39 | Goulds (GOU) | NL_GOU_DSS | Petty Harbour (PHR) | NL_PHR_DFS
| 004L | Newfoundland Power | Newfoundland | 1 | ac | 14.7 | 9.1 | 66 | 5.6175 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Goulds (GOU) | NL_GOU_DSS | St Johns Main (SJM) | NL_SJM_DSS
| 025L | Newfoundland Power | Newfoundland | 1 | ac | 14.7 | 9.1 | 66 | 5.6175 |  |  | 800.5 |  | 91.5 | 0.9 | 68.625 | 82.35 | Goulds (GOU) | NL_GOU_DSS | St Johns Main (SJM) | NL_SJM_DSS
| 416L | Newfoundland Power | Newfoundland | 1 | ac | 29.4 | 18.2 | 66 | 11.235 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Grand Bay (GBS) | NL_GBS_DSS | Long Lake (LGL) | NL_LGL_DFS
| 417L | Newfoundland Power | Newfoundland | 1 | ac | 14.7 | 9.1 | 66 | 5.6175 |  |  | 471.5 |  | 53.9 | 0.9 | 40.425 | 48.51 | Grand Bay (GBS) | NL_GBS_DSS | Port Aux Basques (PAB) | NL_PAB_DFS
| 301L | Newfoundland Power | Newfoundland | 1 | ac | 17 | 10.5 | 66 | 6.4964 |  |  | 574.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Grand Beach (GBE) | NL_GBE_DSS | Garnish (GAR) | NL_GAR_DSS
| 101L | Newfoundland Power | Newfoundland | 1 | ac | 2 | 1.2 | 66 | 0.76429 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Grand Falls (GFS) | NL_GFS_DFS | New Grand Falls (NGF) | NL_NGF_DSS
| 105L | Newfoundland Power | Newfoundland | 1 | ac | 32.4 | 20 | 66 | 12.3814 |  |  | 350.4 |  | 40.1 | 0.9 | 30.075 | 36.09 | Grand Falls (GFS) | NL_GFS_DFS | Sandy Brook (SBK) | NL_SBK_GSS
| TL270 | Nalcor Energy | Newfoundland | 1 | ac | 10 | 6.2 | 230 | 4.8 | 3 |  |  |  |  | 0.9 | 402 | 435 | Granite Canal TS (GCL) | NL_GCL_TSS | Granite Canal (GCL) | NL_GCL_GSS
| 301L | Newfoundland Power | Newfoundland | 1 | ac | 17 | 10.5 | 66 | 6.4964 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Greenhill (GRH) | NL_GRH_DFS | Grand Beach (GBE) | NL_GBE_DSS
| 116L | Newfoundland Power | Newfoundland | 1 | ac | 20 | 12.3 | 66 | 7.6429 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Greenspond (GPD) | NL_GPD_DSS | Wesleyville (WES) | NL_WES_DFS
| TL251 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 66 | 4.4329 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Hampden Tap (HDT) | NL_HDT_DSS | Hampden (HDN) | NL_HDN_DSS
| TL252 | Nalcor Energy | Newfoundland | 1 | ac | 40.7 | 25.1 | 66 | 15.5532 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Hampden Tap (HDT) | NL_HDT_DSS | Jacksons Arm Tap (JAT) | NL_JAT_DSS
| 068L | Newfoundland Power | Newfoundland | 1 | ac | 8.8 | 5.4 | 66 | 3.3629 |  |  | 471.5 |  | 53.9 | 0.9 | 40.425 | 48.51 | Harbour Grace (HGR) | NL_HGR_DSS | Carbonear (CAR) | NL_CAR_DSS
| 005L | Newfoundland Power | Newfoundland | 1 | ac | 13.7 | 8.4 | 66 | 5.2354 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Hardwoods (HWD) | NL_HWD_DFS | Broad Cove (BCV) | NL_BCV_DSS
| 049L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 639.9 |  | 73.2 | 0.9 | 54.9 | 65.88 | Hardwoods (HWD) | NL_HWD_DFS | Chamberlains (CHA) | NL_CHA_DFS
| 079L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Hardwoods (HWD) | NL_HWD_DFS | Chamberlains (CHA) | NL_CHA_DFS
| 073L | Newfoundland Power | Newfoundland | 1 | ac | 7.4 | 4.5 | 66 | 2.8279 |  |  | 1003.9 |  | 114.8 | 0.9 | 86.1 | 103.32 | Hardwoods (HWD) | NL_HWD_DFS | Glendale (GDL) | NL_GDL_DSS
| 072L | Newfoundland Power | Newfoundland | 1 | ac | 15.8 | 9.7 | 66 | 6.0379 |  |  | 1003.9 |  | 114.8 | 0.9 | 86.1 | 103.32 | Hardwoods (HWD) | NL_HWD_DFS | Goulds (GOU) | NL_GOU_DSS
| 019L | Newfoundland Power | Newfoundland | 1 | ac | 16.8 | 10.4 | 66 | 6.42 |  |  | 779.9 |  | 73.2 | 0.9 | 54.9 | 65.88 | Hardwoods (HWD) | NL_HWD_DFS | Molloys Lane (MOL) | NL_MOL_DSS
| 116L | Newfoundland Power | Newfoundland | 1 | ac | 20 | 12.3 | 66 | 7.6429 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Hare Bay (HBS) | NL_HBS_DSS | Trinity (TRN) | NL_TRN_DSS
| 406L | Newfoundland Power | Newfoundland | 1 | ac | 8.8 | 5.4 | 66 | 3.3629 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Harmon (HAR) | NL_HAR_DSS | Gallant (GAL) | NL_GAL_DSS
| 405L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Harmon (HAR) | NL_HAR_DSS | Stephenville (STV) | NL_STV_GSS
| 043L | Newfoundland Power | Newfoundland | 1 | ac | 20.6 | 12.7 | 66 | 7.8721 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Hearts Content (HCT) | NL_HCT_DFS | New Chelsea (NCH) | NL_NCH_DFS
| 039L | Newfoundland Power | Labrador | 1 | ac | 9 | 5.6 | 66 | 3.4393 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Holyrood (HOL) | NL_HOL_DSS | Colliers (COL) | NL_COL_DSS
| TL218 | Nalcor Energy | Labrador | 1 | ac | 34.9 | 21.5 | 230 | 16.752 |  |  |  |  | 369.5 | 0.9 | 277.125 | 332.55 | Holyrood GS (HOL) | NL_HOL_GSS | Oxen Pond (OXP) | NL_OXP_DSS
| 020L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 875.6 |  | 100.1 | 0.9 | 75.075 | 90.09 | Horsechops Tap (HCP) | NL_HCP_JCT | Cape Broyle (CAB) | NL_CAB_DFS
| 021L | Newfoundland Power | Newfoundland | 1 | ac | 14.7 | 9.1 | 66 | 5.6175 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Horsechops Tap (HCP) | NL_HCP_JCT | Horsechops (HCP) | NL_HCP_GSS
| TL224 | Nalcor Energy | Newfoundland | 1 | ac | 58.1 | 35.9 | 138 | 25.1905 |  |  |  |  | 92.7 | 0.9 | 69.525 | 83.43 | Howley (HOW) | NL_HOW_DSS | Baie Verte Junction (BVJ) | NL_BVJ_DSS |  | Bay Verte Junction also called Indian River
| TL251 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 66 | 13.3368 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Howley (HOW) | NL_HOW_DSS | Hampden Tap (HDT) | NL_HDT_DSS
| TL243 | Nalcor Energy | Newfoundland | 1 | ac | 17.4 | 10.8 | 138 | 7.5441 |  |  |  |  | 161.7 | 0.9 | 121.275 | 145.53 | Howley (HOW) | NL_HOW_DSS | Hinds Lake (HLK) | NL_HLK_GSS
| 359L | Newfoundland Power | Newfoundland | 1 | ac | 26.5 | 16.3 | 66 | 10.1268 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Humber (HUM) | NL_HUM_DSS | Bayview (BVS) | NL_BVS_DSS
| 080L | Newfoundland Power | Newfoundland | 1 | ac | 19 | 11.7 | 66 | 7.2607 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Islington (ISL) | NL_ISL_DSS | Hearts Content (HCT) | NL_HCT_DFS
| TL252 | Nalcor Energy | Newfoundland | 1 | ac | 17.4 | 10.8 | 66 | 6.6493 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Jacksons Arm Tap (JAT) | NL_JAT_DSS | Jacksons Arm (JAM) | NL_JAM_DSS
| TL253 | Nalcor Energy | Newfoundland | 1 | ac | 15 | 9.3 | 66 | 5.7321 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Jacksons Arm Tap (JAT) | NL_JAT_DSS | Rattle Brook (RTK) | NL_RTK_GSS |  | RTK is used so as not to be confused with Rattling Brook
| 108L | Newfoundland Power | Newfoundland | 1 | ac | 15 | 9.3 | 66 | 5.7321 |  |  | 350.4 |  | 40.1 | 0.9 | 30.075 | 36.09 | Jonathan's Pond (JON) | NL_JON_DSS | Gander Bay (GBY) | NL_GBY_DSS
| 052L | Newfoundland Power | Newfoundland | 1 | ac | 8.4 | 5.2 | 66 | 3.21 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Kelligrews (KEL) | NL_KEL_DSS | Seal Cove (SCV) | NL_SCV_DFS
| 054L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 1003.9 |  | 114.8 | 0.9 | 86.1 | 103.32 | Kenmount (KEN) | NL_KEN_DSS | Hardwoods (HWD) | NL_HWD_DFS
| 069L | Newfoundland Power | Newfoundland | 1 | ac | 10.5 | 6.5 | 66 | 4.0125 |  |  | 550.4 |  | 52.9 | 0.9 | 39.675 | 47.61 | Kenmount (KEN) | NL_KEN_DSS | Stamps Lane (SLA) | NL_SLA_DSS
| 012L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 379.3 |  | 43.4 | 0.9 | 32.55 | 39.06 | Kings Bridge (KBR) | NL_KBR_DSS | Memorial (MUN) | NL_MUN_DSS
| 016L | Newfoundland Power | Newfoundland | 1 | ac | 5.3 | 3.2 | 66 | 2.0254 |  |  | 379.3 |  | 43.4 | 0.9 | 32.55 | 39.06 | Kings Bridge (KBR) | NL_KBR_DSS | Pepperrell (PEP) | NL_PEP_DSS
| 305L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Laurentian (LAU) | NL_LAU_DSS | Webbers Cove (WBC) | NL_WBC_DFS
| 110L | Newfoundland Power | Newfoundland | 1 | ac | 15 | 9.3 | 138 | 6.5036 |  |  | 302.3 |  | 34.6 | 0.9 | 25.95 | 31.14 | Lethbridge (LET) | NL_LET_DSS | Summerville (SMV) | NL_SMV_DSS
| 300L | Newfoundland Power | Newfoundland | 1 | ac | 8.8 | 5.4 | 66 | 3.3629 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Linton Lake (LLK) | NL_LLK_DSS | Marystown (MSY) | NL_MSY_DSS
| TL212 | Nalcor Energy | Newfoundland | 1 | ac | 16 | 9.9 | 138 | 6.9371 |  |  |  |  | 112.4 | 0.9 | 84.3 | 101.16 | Linton Lake (LLK) | NL_LLK_DSS | Salt Pond (SPO) | NL_SPO_DSS
| 111L | Newfoundland Power | Newfoundland | 1 | ac | 16 | 9.9 | 66 | 6.1143 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Lockston (LOK) | NL_LOK_DFS | Port Union (PUN) | NL_PUN_DSS
| TL257B | Nalcor Energy | Newfoundland | 1 | ac | 29.1 | 17.9 | 66 | 11.1204 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Main Brook (MBK) | NL_MBK_DSS | Roddickton (RCK) | NL_RCK_DSS
| L1 | Newfoundland Power | Newfoundland | 1 | ac | 13 | 8 | 66 | 4.9679 | 3 |  |  |  |  | 0.9 | 32.67 | 35.7049 | Marble Mountain (MMT) | NL_MMT_DSS | Pasadena (PAS) | NL_PAS_DSS
| 308L | Newfoundland Power | Newfoundland | 1 | ac | 8.8 | 5.4 | 66 | 3.3629 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Marystown (MSY) | NL_MSY_DSS | Salt Pond (SPO) | NL_SPO_DSS
| 357L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Massey Drive (MAS) | NL_MAS_TSS | Bayview (BVS) | NL_BVS_DSS
| TL211 | Nalcor Energy | Newfoundland | 1 | ac | 58.1 | 35.9 | 230 | 27.888 |  |  |  |  | 322.2 | 0.9 | 241.65 | 289.98 | Massey Drive (MAS) | NL_MAS_TSS | Bottom Brook (BBK) | NL_BBK_TSS
| TL228 | Nalcor Energy | Newfoundland | 1 | ac | 110.5 | 68.2 | 230 | 53.04 |  |  |  |  | 282.3 | 0.9 | 211.725 | 254.07 | Massey Drive (MAS) | NL_MAS_TSS | Buchans (BUC) | NL_BUC_DFS
| 356L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 816.4 |  | 93.3 | 0.9 | 69.975 | 83.97 | Massey Drive (MAS) | NL_MAS_TSS | Humber (HUM) | NL_HUM_DSS
| L1 | Newfoundland Power | Newfoundland | 1 | ac | 17 | 10.5 | 66 | 6.4964 | 3 |  |  |  |  | 0.9 | 32.67 | 35.7049 | Massey Drive (MAS) | NL_MAS_TSS | Marble Mountain (MMT) | NL_MMT_DSS
| 351L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Massey Drive (MAS) | NL_MAS_TSS | Walbournes (WAL) | NL_WAL_DSS
| 352L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Massey Drive (MAS) | NL_MAS_TSS | Walbournes (WAL) | NL_WAL_DSS
| 014L | Newfoundland Power | Newfoundland | 1 | ac | 4.2 | 2.6 | 66 | 1.605 |  |  | 608 |  | 69.5 | 0.9 | 52.125 | 62.55 | Memorial (MUN) | NL_MUN_DSS | Stamps Lane (SLA) | NL_SLA_DSS
| 110L | Newfoundland Power | Newfoundland | 1 | ac | 15 | 9.3 | 138 | 6.5036 |  |  | 302.3 |  | 34.6 | 0.9 | 25.95 | 31.14 | Milton (MIL) | NL_MIL_DSS | Lethbridge (LET) | NL_LET_DSS
| 020L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 875.6 |  | 100.1 | 0.9 | 75.075 | 90.09 | Mobile (MOB) | NL_MOB_DFS | Morris Tap (MRP) | NL_MRP_JCT
| 023L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 518.4 |  | 29.6 | 0.9 | 22.2 | 26.64 | Mobile (MOB) | NL_MOB_DFS | Pierres Brook (PBK) | NL_PBK_GSS
| 011L | Newfoundland Power | Newfoundland | 1 | ac | 8.8 | 5.4 | 66 | 3.3629 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Mobile (MOB) | NL_MOB_DFS | Tors Cove (TCV) | NL_TCV_GSS
| TL212 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 138 | 15.1316 |  |  |  |  | 112.4 | 0.9 | 84.3 | 101.16 | Monkstown (MKS) | NL_MKS_TSS | Bay Largent (BLA) | NL_BLA_DSS
| TL258 | Nalcor Energy | Newfoundland | 1 | ac | 81.4 | 50.2 | 138 | 35.2927 | 3 |  |  |  |  | 0.9 | 141 | 156 | Monkstown (MKS) | NL_MKS_TSS | Paradise River (PRV) | NL_PRV_DFS
| 020L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 875.6 |  | 100.1 | 0.9 | 75.075 | 90.09 | Morris Tap (MRP) | NL_MRP_JCT | Horsechops Tap (HCP) | NL_HCP_JCT
| 022L | Newfoundland Power | Newfoundland | 1 | ac | 17.6 | 10.9 | 66 | 6.7257 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Morris Tap (MRP) | NL_MRP_JCT | Morris (MRP) | NL_MRP_GSS
| 020L | Newfoundland Power | Newfoundland | 1 | ac | 8 | 4.9 | 66 | 3.0571 |  |  | 875.6 |  | 100.1 | 0.9 | 75.075 | 90.09 | Morris Tap (MRP) | NL_MRP_JCT | Rocky Pond Tap (ROP) | NL_ROP_JCT
| L3501 | Nalcor Energy | Labrador | 1 | dc | 400 | 246.9 | 350 | [7 empty] | 450 | 450 | Muskrat Falls (TS2) | NL_TS2_CSS | Strait of Belle Isle (SBI) | NL_SBI_JCT
| L3502 | Nalcor Energy | Labrador | 1 | dc | 400 | 246.9 | 350 | [7 empty] | 450 | 450 | Muskrat Falls (TS2) | NL_TS2_CSS | Strait of Belle Isle (SBI) | NL_SBI_JCT
| 065L | Newfoundland Power | Newfoundland | 1 | ac | 17.6 | 10.9 | 66 | 6.7257 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | New Chelsea (NCH) | NL_NCH_DFS | Old Perlican (OPL) | NL_OPL_DSS
| 132L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 138 | 10.1889 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | New Grand Falls (NGF) | NL_NGF_DSS | Bishops Falls (BFS) | NL_BFS_DFS
| 101L | Newfoundland Power | Newfoundland | 1 | ac | 42.1 | 26 | 66 | 16.0882 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | New Grand Falls (NGF) | NL_NGF_DSS | Rattling Brook (RBK) | NL_RBK_DFS
| 130L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 138 | 10.1889 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | New Grand Falls (NGF) | NL_NGF_DSS | Stony Brook (STY) | NL_STY_TSS
| 080L | Newfoundland Power | Newfoundland | 1 | ac | 15 | 9.3 | 66 | 5.7321 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | New Harbour (NHR) | NL_NHR_DSS | Islington (ISL) | NL_ISL_DSS
| 109L | Newfoundland Power | Newfoundland | 1 | ac | 20 | 12.3 | 138 | 8.6714 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Northwest Brook (NWB) | NL_NWB_DSS | Clarenville (CLV) | NL_CLV_DSS
| 103L | Newfoundland Power | Newfoundland | 1 | ac | 11.8 | 7.3 | 66 | 4.5093 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Notre Dame Junction (NDJ) | NL_NDJ_DSS | Lewisporte (LEW) | NL_LEW_DSS
| 102L | Newfoundland Power | Newfoundland | 1 | ac | 14 | 8.6 | 66 | 5.35 |  |  | 350.4 |  | 40.1 | 0.9 | 30.075 | 36.09 | Notre Dame Junction (NDJ) | NL_NDJ_DSS | Rattling Brook (RBK) | NL_RBK_DFS
| TL236 | Nalcor Energy | Newfoundland | 1 | ac | 17.4 | 10.8 | 230 | 8.352 |  |  |  |  | 459.6 | 0.9 | 344.7 | 413.64 | Oxen Pond (OXP) | NL_OXP_DSS | Hardwoods (HWD) | NL_HWD_DFS
| 035L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 471.5 |  | 53.9 | 0.9 | 40.425 | 48.51 | Oxen Pond (OXP) | NL_OXP_DSS | Kenmount (KEN) | NL_KEN_DSS
| 032L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Oxen Pond (OXP) | NL_OXP_DSS | Ridge Road (RRD) | NL_RRD_DSS
| 067L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Oxen Pond (OXP) | NL_OXP_DSS | Ridge Road (RRD) | NL_RRD_DSS
| 031L | Newfoundland Power | Newfoundland | 1 | ac | 7.4 | 4.5 | 66 | 2.8279 |  |  | 1003.9 |  | 114.4 | 0.9 | 85.8 | 102.96 | Oxen Pond (OXP) | NL_OXP_DSS | Stamps Lane (SLA) | NL_SLA_DSS
| 070L | Newfoundland Power | Newfoundland | 1 | ac | 7.4 | 4.5 | 66 | 2.8279 |  |  | 1003.9 |  | 114.8 | 0.9 | 86.1 | 103.32 | Oxen Pond (OXP) | NL_OXP_DSS | Stamps Lane (SLA) | NL_SLA_DSS
| 034L | Newfoundland Power | Newfoundland | 1 | ac | 13.7 | 8.4 | 66 | 5.2354 |  |  | 1003.9 |  | 114.4 | 0.9 | 85.8 | 102.96 | Oxen Pond (OXP) | NL_OXP_DSS | Virginia Waters (VIR) | NL_VIR_DSS
| 058L | Newfoundland Power | Newfoundland | 1 | ac | 12.6 | 7.8 | 66 | 4.815 |  |  | 1003.9 |  | 114.8 | 0.9 | 86.1 | 103.32 | Oxen Pond (OXP) | NL_OXP_DSS | Virginia Waters (VIR) | NL_VIR_DSS
| TL227 | Nalcor Energy | Newfoundland | 1 | ac | 29.1 | 17.9 | 66 | 11.1204 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Parsons Pond (PPD) | NL_PPD_DSS | Daniels Harbour (DHR) | NL_DHR_DSS
| L1 | Newfoundland Power | Newfoundland | 1 | ac | 15 | 9.3 | 66 | 5.7321 | 3 |  |  |  |  | 0.9 | 32.67 | 35.7049 | Pasadena (PAS) | NL_PAS_DSS | Deer Lake GS (DLP) | NL_DLP_GSS
| TL262 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 66 | 4.4329 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Peters Barren (PBN) | NL_PBN_DSS | Daniels Harbour (DHR) | NL_DHR_DSS
| TL221 | Nalcor Energy | Newfoundland | 1 | ac | 60 | 37 | 66 | 22.9286 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Peters Barren (PBN) | NL_PBN_DSS | Hawkes Bay (HBY) | NL_HBY_GSS
| 055L | Newfoundland Power | Newfoundland | 1 | ac | 15 | 9.3 | 66 | 5.7321 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Placentia Junction (PJN) | NL_PJN_DSS | Quartz (QTZ) | NL_QTZ_ISS
| TL241 | Nalcor Energy | Newfoundland | 1 | ac | 110.5 | 68.2 | 138 | 47.9096 |  |  |  |  | 160.8 | 0.9 | 120.6 | 144.72 | Plum Point (PPT) | NL_PPT_DSS | Peters Barren (PBN) | NL_PBN_DSS
| 124L | Newfoundland Power | Newfoundland | 1 | ac | 14 | 8.6 | 138 | 6.07 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Port Blandford (PBD) | NL_PBD_DSS | Terra Nova (TNS) | NL_TNS_DSS
| 111L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Port Union (PUN) | NL_PUN_DSS | Catalina (CAT) | NL_CAT_DSS
| 123L | Newfoundland Power | Newfoundland | 1 | ac | 85.3 | 52.7 | 138 | 36.9836 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Princeton Pond (PRC) | NL_PRC_DSS | Catalina (CAT) | NL_CAT_DSS
| 110L | Newfoundland Power | Newfoundland | 1 | ac | 5 | 3.1 | 138 | 2.1679 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Princeton Pond (PRC) | NL_PRC_DSS | Lockston (LOK) | NL_LOK_DFS
| 055L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Quartz (QTZ) | NL_QTZ_ISS | Dunville (DUN) | NL_DUN_DSS
| TL253 | Nalcor Energy | Newfoundland | 1 | ac | 8 | 4.9 | 66 | 3.0571 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | Rattle Brook (RTK) | NL_RTK_GSS | Coney Arm (CAM) | NL_CAM_DSS
| 030L | Newfoundland Power | Newfoundland | 1 | ac | 8.4 | 5.2 | 66 | 3.21 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Ridge Road (RRD) | NL_RRD_DSS | Kings Bridge (KBR) | NL_KBR_DSS
| 095L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Riverhead (RVH) | NL_RVH_DSS | Trepassey (TRP) | NL_TRP_DSS
| 403L | Newfoundland Power | Newfoundland | 1 | ac | 9 | 5.6 | 66 | 3.4393 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Robinsons Tap (ROB) | NL_ROB_JCT | Lookout Brook (LBK) | NL_LBK_DFS
| 403L | Newfoundland Power | Newfoundland | 1 | ac | 15 | 9.3 | 66 | 5.7321 |  |  | 302.3 |  | 34.6 | 0.9 | 25.95 | 31.14 | Robinsons Tap (ROB) | NL_ROB_JCT | Robinsons (ROB) | NL_ROB_DSS
| TL226 | Nalcor Energy | Newfoundland | 1 | ac | 5 | 3.1 | 66 | 1.9107 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Rocky Harbour (RHR) | NL_RHR_DSS | Berry Hill (BHL) | NL_BHL_DSS
| 020L | Newfoundland Power | Newfoundland | 1 | ac | 3 | 1.9 | 66 | 1.1464 |  |  | 875.6 |  | 100.1 | 0.9 | 75.075 | 90.09 | Rocky Pond Tap (ROP) | NL_ROP_JCT | Rocky Pond (ROP) | NL_ROP_DFS
| 102L | Newfoundland Power | Newfoundland | 1 | ac | 14 | 8.6 | 66 | 5.35 |  |  | 350.4 |  | 40.1 | 0.9 | 30.075 | 36.09 | Roycefield Mine Tap (RFD) | NL_RFD_JCT | Notre Dame Junction (NDJ) | NL_NDJ_DSS
| 104L | Newfoundland Power | Newfoundland | 1 | ac | 35.3 | 21.8 | 66 | 13.4896 |  |  | 303.3 |  | 34.7 | 0.9 | 26.025 | 31.23 | Roycefield Mine Tap (RFD) | NL_RFD_JCT | Roycefield Mine (RFD) | NL_RFD_ISS
| TL227 | Nalcor Energy | Newfoundland | 1 | ac | 23.3 | 14.4 | 66 | 8.9039 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Sallys Cove (SCV) | NL_SCV_DSS | Cow Head (CHD) | NL_CHD_DSS
| 302L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 352.1 |  | 40.2 | 0.9 | 30.15 | 36.18 | Salt Pond (SPO) | NL_SPO_DSS | Laurentian (LAU) | NL_LAU_DSS
| TL260 | Nalcor Energy | Newfoundland | 1 | ac | 29.1 | 17.9 | 138 | 12.6169 |  |  |  |  | 161.7 | 0.9 | 121.275 | 145.53 | Seal Cove Road (SCR) | NL_SCR_DSS | Bottom Waters (BWT) | NL_BWT_DSS
| TL266 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 230 | 16.752 | 3 |  |  |  |  | 0.9 | 402 | 435 | Soldiers Pond (SOL) | NL_SOL_CSS | Hardwoods (HWD) | NL_HWD_DFS
| TL242 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 230 | 16.752 |  |  |  |  | 459.6 | 0.9 | 344.7 | 413.64 | Soldiers Pond (SOL) | NL_SOL_CSS | Hardwoods (HWD) | NL_HWD_DFS
| TL265 | Nalcor Energy | Newfoundland | 1 | ac | 5.8 | 3.6 | 230 | 2.784 | 3 |  |  |  |  | 0.9 | 402 | 435 | Soldiers Pond (SOL) | NL_SOL_CSS | Holyrood GS (HOL) | NL_HOL_GSS
| TL268 | Nalcor Energy | Newfoundland | 1 | ac | 5.8 | 3.6 | 230 | 2.784 | 3 |  |  |  |  | 0.9 | 402 | 435 | Soldiers Pond (SOL) | NL_SOL_CSS | Holyrood GS (HOL) | NL_HOL_GSS
| TL222 | Nalcor Energy | Newfoundland | 1 | ac | 70 | 43.2 | 138 | 30.35 |  |  |  |  | 112.4 | 0.9 | 84.3 | 101.16 | South Brook (SOK) | NL_SOK_DSS | Stony Brook (STY) | NL_STY_TSS
| TL222 | Nalcor Energy | Newfoundland | 1 | ac | 17 | 10.5 | 138 | 7.3707 |  |  |  |  | 112.4 | 0.9 | 84.3 | 101.16 | Springdale (SPR) | NL_SPR_DSS | South Brook (SOK) | NL_SOK_DSS
| 039L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Springfield (SPF) | NL_SPF_DSS | Bay Roberts (BRB) | NL_BRB_DSS
| TL256 | Nalcor Energy | Newfoundland | 1 | ac | 40.7 | 25.1 | 138 | 17.6464 |  |  |  |  | 160.8 | 0.9 | 120.6 | 144.72 | St Anthony Airport (STA) | NL_STA_DSS | Bear Cove (BRV) | NL_BRV_DSS
| TL257A | Nalcor Energy | Newfoundland | 1 | ac | 29.1 | 17.9 | 66 | 11.1204 |  |  |  |  | 56.2 | 0.9 | 42.15 | 50.58 | St Anthony Airport (STA) | NL_STA_DSS | Main Brook (MBK) | NL_MBK_DSS
| TL261 | Nalcor Energy | Newfoundland | 1 | ac | 34.9 | 21.5 | 66 | 13.3368 |  |  |  |  | 76.9 | 0.9 | 57.675 | 69.21 | St Anthony Airport (STA) | NL_STA_DSS | St Anthony (SOP) | NL_SOP_GSS
| 094L | Newfoundland Power | Newfoundland | 1 | ac | 17 | 10.5 | 66 | 6.4964 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | St Catherines (SCT) | NL_SCT_DSS | Riverhead (RVH) | NL_RVH_DSS
| 013L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | St Johns Main (SJM) | NL_SJM_DSS | Stamps Lane (SLA) | NL_SLA_DSS
| 015L | Newfoundland Power | Newfoundland | 1 | ac | 5.3 | 3.2 | 66 | 2.0254 |  |  | 550.4 |  | 51.6 | 0.9 | 38.7 | 46.44 | Stamps Lane (SLA) | NL_SLA_DSS | Molloys Lane (MOL) | NL_MOL_DSS
| 403L | Newfoundland Power | Newfoundland | 1 | ac | 35 | 21.6 | 66 | 13.375 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Stephenville (STV) | NL_STV_GSS | Robinsons Tap (ROB) | NL_ROB_JCT
| TL238 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 230 | 5.568 | 3 |  |  |  |  | 0.9 | 402 | 435 | Stephenville (STV) | NL_STV_GSS | Stephenville Crossing (STX) | NL_STX_DSS
| 407L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Stephenville (STV) | NL_STV_GSS | Stephenville Crossing (STX) | NL_STX_DSS
| 401L | Newfoundland Power | Newfoundland | 1 | ac | 4 | 2.5 | 66 | 1.5286 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Stephenville (STV) | NL_STV_GSS | Wheelers Tap (WHE) | NL_WHE_JCT
| 407L | Newfoundland Power | Newfoundland | 1 | ac | 14 | 8.6 | 66 | 5.35 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Stephenville Crossing (STX) | NL_STX_DSS | St Georges (STG) | NL_STG_DSS
| TL204 | Nalcor Energy | Newfoundland | 1 | ac | 104.7 | 64.6 | 230 | 50.256 |  |  |  |  | 469.6 | 0.9 | 352.2 | 422.64 | Stony Brook (STY) | NL_STY_TSS | Bay Despoir (BDE) | NL_BDE_GSS
| TL231 | Nalcor Energy | Newfoundland | 1 | ac | 104.7 | 64.6 | 230 | 50.256 |  |  |  |  | 469.6 | 0.9 | 352.2 | 422.64 | Stony Brook (STY) | NL_STY_TSS | Bay Despoir (BDE) | NL_BDE_GSS
| 133L | Newfoundland Power | Newfoundland | 1 | ac | 20.6 | 12.7 | 138 | 8.9316 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Stony Brook (STY) | NL_STY_TSS | Bishops Falls (BFS) | NL_BFS_DFS
| TL210 | Nalcor Energy | Newfoundland | 1 | ac | 58.1 | 35.9 | 138 | 25.1905 |  |  |  |  | 144.1 | 0.9 | 108.075 | 129.69 | Stony Brook (STY) | NL_STY_TSS | Glenwood (GLN) | NL_GLN_DSS
| TL235 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 230 | 5.568 |  |  |  |  | 322.2 | 0.9 | 241.65 | 289.98 | Stony Brook (STY) | NL_STY_TSS | New Grand Falls (NGF) | NL_NGF_DSS
| L3501 | Nalcor Energy | Labrador | 1 | dc | 700 | 432.1 | 350 | [7 empty] | 450 | 450 | Strait of Belle Isle (SBI) | NL_SBI_JCT | Soldiers Pond (SOL) | NL_SOL_CSS
| L3502 | Nalcor Energy | Labrador | 1 | dc | 700 | 432.1 | 350 | [7 empty] | 450 | 450 | Strait of Belle Isle (SBI) | NL_SBI_JCT | Soldiers Pond (SOL) | NL_SOL_CSS
| 140L | Newfoundland Power | Newfoundland | 1 | ac | 23.5 | 14.5 | 66 | 8.9804 |  |  | 474.6 |  | 54.2 | 0.9 | 40.65 | 48.78 | Summerford (SUM) | NL_SUM_DSS | Twillingate (TWG) | NL_TWG_DSS
| 110L | Newfoundland Power | Newfoundland | 1 | ac | 6 | 3.7 | 138 | 2.6014 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Summerville (SMV) | NL_SMV_DSS | Princeton Pond (PRC) | NL_PRC_DSS
| 100L | Newfoundland Power | Newfoundland | 1 | ac | 38.2 | 23.6 | 138 | 16.5624 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Sunnyside (SUN) | NL_SUN_TSS | Clarenville (CLV) | NL_CLV_DSS
| TL207 | Nalcor Energy | Newfoundland | 1 | ac | 11.6 | 7.2 | 230 | 5.568 |  |  |  |  | 453.9 | 0.9 | 340.425 | 408.51 | Sunnyside (SUN) | NL_SUN_TSS | Come by Chance (CBC) | NL_CBC_ISS
| TL212 | Nalcor Energy | Newfoundland | 1 | ac | 46.5 | 28.7 | 138 | 20.1611 |  |  |  |  | 112.4 | 0.9 | 84.3 | 101.16 | Sunnyside (SUN) | NL_SUN_TSS | Monkstown (MKS) | NL_MKS_TSS
| 109L | Newfoundland Power | Newfoundland | 1 | ac | 18 | 11.1 | 138 | 7.8043 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Sunnyside (SUN) | NL_SUN_TSS | Northwest Brook (NWB) | NL_NWB_DSS
| TL219 | Newfoundland Power | Newfoundland | 1 | ac | 162.8 | 100.5 | 138 | 70.5854 |  |  |  |  | 161.7 | 0.9 | 121.275 | 145.53 | Sunnyside (SUN) | NL_SUN_TSS | Salt Pond (SPO) | NL_SPO_DSS
| TL203 | Nalcor Energy | Newfoundland | 1 | ac | 45 | 27.8 | 230 | 21.6 |  |  |  |  | 347 | 0.9 | 260.25 | 312.3 | Sunnyside (SUN) | NL_SUN_TSS | Western Avalon (WAV) | NL_WAV_DSS
| 124L | Newfoundland Power | Newfoundland | 1 | ac | 14 | 8.6 | 138 | 6.07 |  |  | 712.7 |  | 170.4 | 0.9 | 127.8 | 153.36 | Terra Nova (TNS) | NL_TNS_DSS | Alexander Bay (ALX) | NL_ALX_JCT
| 116L | Newfoundland Power | Newfoundland | 1 | ac | 12 | 7.4 | 66 | 4.5857 |  |  | 474.3 |  | 54.2 | 0.9 | 40.65 | 48.78 | Trinity (TRN) | NL_TRN_DSS | Greenspond (GPD) | NL_GPD_DSS
| 057L | Newfoundland Power | Newfoundland | 1 | ac | 10 | 6.2 | 66 | 3.8214 |  |  | 471.5 |  | 53.9 | 0.9 | 40.425 | 48.51 | Upper Island Cove (ILC) | NL_ILC_DSS | Harbour Grace (HGR) | NL_HGR_DSS
| TL263 | Nalcor Energy | Newfoundland | 1 | ac | 69.8 | 43.1 | 230 | 33.504 |  |  |  |  | 369.5 | 0.9 | 277.125 | 332.55 | Upper Salmon (USL) | NL_USL_GSS | Granite Canal TS (GCL) | NL_GCL_TSS
| 074L | Newfoundland Power | Newfoundland | 1 | ac | 6.3 | 3.9 | 66 | 2.4075 |  |  | 1003.9 |  | 114.8 | 0.9 | 86.1 | 103.32 | Virginia Waters (VIR) | NL_VIR_DSS | Pepperrell (PEP) | NL_PEP_DSS
| 059L | Newfoundland Power | Newfoundland | 1 | ac | 5.3 | 3.2 | 66 | 2.0254 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Virginia Waters (VIR) | NL_VIR_DSS | Pulpit Rock (PUL) | NL_PUL_DSS
| 353L | Newfoundland Power | Newfoundland | 1 | ac | 17.6 | 10.9 | 66 | 6.7257 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Walbournes (WAL) | NL_WAL_DSS | Frenchmans Cove (FRN) | NL_FRN_DSS
| 305L | Newfoundland Power | Newfoundland | 1 | ac | 19 | 11.7 | 66 | 7.2607 |  |  | 712.7 |  | 81.5 | 0.9 | 61.125 | 73.35 | Webbers Cove (WBC) | NL_WBC_DFS | Greenhill (GRH) | NL_GRH_DFS
| 086L | Newfoundland Power | Newfoundland | 1 | ac | 17.6 | 10.9 | 66 | 6.7257 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Western Avalon (WAV) | NL_WAV_DSS | Blaketown (BLK) | NL_BLK_DSS
| TL201 | Nalcor Energy | Newfoundland | 1 | ac | 104.7 | 64.6 | 230 | 50.256 |  |  |  |  | 322.2 | 0.9 | 241.65 | 289.98 | Western Avalon (WAV) | NL_WAV_DSS | Hardwoods (HWD) | NL_HWD_DFS
| TL208 | Vale | Newfoundland | 1 | ac | 23.3 | 14.4 | 230 | 11.184 |  |  |  |  | 369.5 | 0.9 | 277.125 | 332.55 | Western Avalon (WAV) | NL_WAV_DSS | Long Harbour (LHB) | NL_LHB_ISS
| TL217 | Nalcor Energy | Newfoundland | 1 | ac | 69.8 | 43.1 | 230 | 33.504 |  |  |  |  | 453.9 | 0.9 | 340.425 | 408.51 | Western Avalon (WAV) | NL_WAV_DSS | Soldiers Pond (SOL) | NL_SOL_CSS
| 401L | Newfoundland Power | Newfoundland | 1 | ac | 5 | 3.1 | 66 | 1.9107 |  |  | 779.9 |  | 89.2 | 0.9 | 66.9 | 80.28 | Wheelers Tap (WHE) | NL_WHE_JCT | Gallant (GAL) | NL_GAL_DSS
| 404L | Newfoundland Power | Newfoundland | 1 | ac | 8 | 4.9 | 66 | 3.0571 |  |  | 550.4 |  | 62.9 | 0.9 | 47.175 | 56.61 | Wheelers Tap (WHE) | NL_WHE_JCT | Wheelers (WHE) | NL_WHE_DSS
| TL226 | Nalcor Energy | Newfoundland | 1 | ac | 30 | 18.5 | 66 | 11.4643 |  |  |  |  | 53.8 | 0.9 | 40.35 | 48.42 | Wiltondale (WDL) | NL_WDL_DSS | Rocky Harbour (RHR) | NL_RHR_DSS
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)
Specific Notes:
Winter ratings at 0C

## Nodes
NL | EXISTING NODES
| Node Name | Node Code | Owner | Latitude | Longitude | Operating Region | Other References | Notes
| Abraham's Cove (ABC) | NL_ABC_DSS | Newfoundland Power | 48.534 | -58.9217 | Newfoundland
| Alexander Bay (ALX) | NL_ALX_JCT | Newfoundland Power | 48.6757 | -54.1071 | Newfoundland
| Baie Verte Junction (BVJ) | NL_BVJ_DSS | Newfoundland Power | 49.4388 | -56.471 | Newfoundland
| Barachoix (BCX) | NL_BCX_DSS | Nalcor Energy | 47.6844 | -55.613 | Newfoundland
| Bay Despoir (BDE) | NL_BDE_GSS | Nalcor Energy | 47.9901 | -55.7997 | Newfoundland
| Bay Largent (BLA) | NL_BLA_DSS | Newfoundland Power | 47.4164 | -54.883 | Newfoundland
| Bay Roberts (BRB) | NL_BRB_DSS | Newfoundland Power | 47.5887 | -53.2832 | Newfoundland
| Bayview (BVS) | NL_BVS_DSS | Newfoundland Power | 48.9546 | -57.9121 | Newfoundland
| Bear Cove (BRV) | NL_BRV_DSS | Nalcor Energy | 51.2737 | -56.7394 | Newfoundland
| Berry Head (BHD) | NL_BHD_DSS | Newfoundland Power | 48.5565 | -58.6911 | Newfoundland
| Berry Hill (BHL) | NL_BHL_DSS | Nalcor Energy | 49.613 | -57.9213 | Newfoundland
| Big Pond (BIG) | NL_BIG_DSS | Newfoundland Power | 47.417 | -52.7672 | Newfoundland
| Bishops Falls (BFS) | NL_BFS_DFS | Newfoundland Power | 49.0147 | -55.5002 | Newfoundland
| Blaketown (BLK) | NL_BLK_DSS | Newfoundland Power | 47.4479 | -53.5344 | Newfoundland
| Bonavista (BVA) | NL_BVA_DSS | Newfoundland Power | 48.6389 | -53.1025 | Newfoundland
| Bottom Brook (BBK) | NL_BBK_TSS | NP / Nalcor Energy | 48.5303 | -58.257 | Newfoundland
| Bottom Waters (BWT) | NL_BWT_DSS | Nalcor Energy | 49.8947 | -55.7831 | Newfoundland
| Botwood (BOT) | NL_BOT_DSS | Newfoundland Power | 49.1381 | -55.3634 | Newfoundland
| Boyds Cove (BOY) | NL_BOY_DSS | Newfoundland Power | 49.4413 | -54.6168 | Newfoundland
| Broad Cove (BCV) | NL_BCV_DSS | Newfoundland Power | 47.5925 | -52.8836 | Newfoundland
| Buchans (BUC) | NL_BUC_DFS | NP / Nalcor Energy | 48.814 | -56.7923 | Newfoundland
| Cape Broyle (CAB) | NL_CAB_DFS | Newfoundland Power | 47.0959 | -52.9372 | Newfoundland
| Carbonear (CAR) | NL_CAR_DSS | Newfoundland Power | 47.7301 | -53.2437 | Newfoundland
| Cat Arm (CAM) | NL_CAM_GSS | Nalcor Energy | 50.0258 | -56.765 | Newfoundland
| Catalina (CAT) | NL_CAT_DSS | Newfoundland Power | 48.5183 | -53.0901 | Newfoundland
| Chamberlains (CHA) | NL_CHA_DFS | Newfoundland Power | 47.5231 | -52.9304 | Newfoundland
| Churchill Falls (CFP) | NL_CFP_GSS | Nalcor Energy | 53.5277 | -63.9532 | Labrador
| Churchill River (TS1) | NL_TS1_TSS | Nalcor Energy | 53.2685 | -60.7802 | Labrador
| Churchill River (TS3) | NL_TS3_TSS | Nalcor Energy | 53.2761 | -60.53 | Labrador
| Clarenville (CLV) | NL_CLV_DSS | Newfoundland Power | 48.1472 | -53.9691 | Newfoundland
| Clarke's Head (CKH) | NL_CKH_DSS | Newfoundland Power | 49.2851 | -54.4857 | Newfoundland
| Clarkes Pond (CLK) | NL_CLK_DSS | Newfoundland Power | 47.2666 | -53.974 | Newfoundland
| Cobbs Pond (COB) | NL_COB_DSS | Newfoundland Power | 48.9724 | -54.6199 | Newfoundland
| Colliers (COL) | NL_COL_DSS | Newfoundland Power | 47.4761 | -53.2316 | Newfoundland
| Come by Chance (CBC) | NL_CBC_ISS | Nalcor Energy | 47.8008 | -53.9923 | Newfoundland
| Coney Arm (CAM) | NL_CAM_DSS | Nalcor Energy | 49.9516 | -56.7962 | Newfoundland
| Conne River (CRV) | NL_CRV_DSS | Nalcor Energy | 47.8787 | -55.7162 | Newfoundland
| Cow Head (CHD) | NL_CHD_DSS | Nalcor Energy | 49.9237 | -57.774 | Newfoundland
| Daniels Harbour (DHR) | NL_DHR_DSS | Nalcor Energy | 50.2455 | -57.5781 | Newfoundland
| Deer Lake (DLK) | NL_DLK_DFS | NP / Nalcor Energy | 49.1778 | -57.4047 | Newfoundland
| Deer Lake GS (DLP) | NL_DLP_GSS | Kruger | 48.9561 | -57.9496 | Newfoundland
| Doyles (DOY) | NL_DOY_DSS | Newfoundland Power | 47.786 | -59.2255 | Newfoundland
| Duck Pond (DKP) | NL_DKP_DSS | Nalcor Energy | 48.6424 | -56.4917 | Newfoundland
| Duffs (DUF) | NL_DUF_DSS | Newfoundland Power | 47.4507 | -53.0982 | Newfoundland
| Dunville (DUN) | NL_DUN_DSS | Newfoundland Power | 47.2698 | -53.8862 | Newfoundland
| English HR. West (EHW) | NL_EHW_DSS | Nalcor Energy | 47.4647 | -55.5056 | Newfoundland
| Farewell Head (FHD) | NL_FHD_DSS | Nalcor Energy | 49.5541 | -54.4893 | Newfoundland
| Fermeuse (FER) | NL_FER_DFS | Newfoundland Power | 46.9699 | -52.97 | Newfoundland
| Frenchmans Cove (FRN) | NL_FRN_DSS | Newfoundland Power | 49.051 | -58.1835 | Newfoundland
| Gallant (GAL) | NL_GAL_DSS | Newfoundland Power | 48.553 | -58.5913 | Newfoundland
| Gambo (GAM) | NL_GAM_DSS | Newfoundland Power | 48.7345 | -54.2425 | Newfoundland
| Gander (GAN) | NL_GAN_DSS | Newfoundland Power | 48.9478 | -54.6122 | Newfoundland
| Gander Bay (GBY) | NL_GBY_DSS | Newfoundland Power | 49.2851 | -54.4857 | Newfoundland
| Garnish (GAR) | NL_GAR_DSS | Newfoundland Power | 47.1896 | -55.3377 | Newfoundland
| Gillams (GIL) | NL_GIL_DSS | Newfoundland Power | 49.0384 | -58.0979 | Newfoundland
| Glenburnie (GLB) | NL_GLB_DSS | Nalcor Energy | 49.4786 | -57.9246 | Newfoundland
| Glendale (GDL) | NL_GDL_DSS | Newfoundland Power | 47.5014 | -52.8048 | Newfoundland
| Glenwood (GLN) | NL_GLN_DSS | Newfoundland Power | 48.9963 | -54.8829 | Newfoundland
| Glovertown (GLV) | NL_GLV_DSS | Newfoundland Power | 48.6689 | -54.0471 | Newfoundland
| Goulds (GOU) | NL_GOU_DSS | Newfoundland Power | 47.4854 | -52.7664 | Newfoundland
| Grand Bay (GBS) | NL_GBS_DSS | Newfoundland Power | 47.6097 | -59.1828 | Newfoundland
| Grand Beach (GBE) | NL_GBE_DSS | Newfoundland Power | 47.1294 | -55.502 | Newfoundland |  | Location approximate
| Grand Falls (GFS) | NL_GFS_DFS | Newfoundland Power | 48.9309 | -55.668 | Newfoundland
| Grandy Brook (GBK) | NL_GBK_DSS | Nalcor Energy | 47.8012 | -57.6604 | Newfoundland
| Granite Canal (GCL) | NL_GCL_GSS | Nalcor Energy | 48.1966 | -56.8152 | Newfoundland
| Granite Canal TS (GCL) | NL_GCL_TSS | Nalcor Energy | 48.2035 | -56.8494 | Newfoundland
| Greenhill (GRH) | NL_GRH_DFS | Newfoundland Power | 47.0907 | -55.7564 | Newfoundland
| Greenspond (GPD) | NL_GPD_DSS | Newfoundland Power | 49.1093 | -53.7276 | Newfoundland
| Hampden (HDN) | NL_HDN_DSS | Nalcor Energy | 49.5357 | -56.8704 | Newfoundland
| Hampden Tap (HDT) | NL_HDT_DSS | Nalcor Energy | 49.4535 | -56.9345 | Newfoundland
| Happy Valley (HVY) | NL_HVY_DFS | Nalcor Energy | 53.2902 | -60.3593 | Labrador
| Harbour Grace (HGR) | NL_HGR_DSS | Newfoundland Power | 47.6936 | -53.2268 | Newfoundland
| Hardwoods (HWD) | NL_HWD_DFS | Newfoundland Power | 47.5882 | -52.7823 | Newfoundland
| Hare Bay (HBS) | NL_HBS_DSS | Newfoundland Power | 48.8461 | -54.0787 | Newfoundland
| Harmon (HAR) | NL_HAR_DSS | Newfoundland Power | 48.5593 | -58.5481 | Newfoundland
| Hawkes Bay (HBY) | NL_HBY_GSS | Nalcor Energy | 50.614 | -57.1626 | Newfoundland
| Hearts Content (HCT) | NL_HCT_DFS | Newfoundland Power | 47.8628 | -53.3758 | Newfoundland
| Hinds Lake (HLK) | NL_HLK_GSS | Nalcor Energy | 49.0825 | -57.2014 | Newfoundland
| Holyrood (HOL) | NL_HOL_DSS | Newfoundland Power | 47.3765 | -53.1551 | Newfoundland
| Holyrood GS (HOL) | NL_HOL_GSS | Nalcor Energy | 47.3858 | -53.1277 | Newfoundland
| Horsechops (HCP) | NL_HCP_GSS | Newfoundland Power | 47.132 | -52.9816 | Newfoundland
| Horsechops Tap (HCP) | NL_HCP_JCT | Newfoundland Power | 47.1114 | -52.924 | Newfoundland
| Howley (HOW) | NL_HOW_DSS | Newfoundland Power | 49.1697 | -57.1204 | Newfoundland
| Humber (HUM) | NL_HUM_DSS | Newfoundland Power | 48.9554 | -57.9444 | Newfoundland
| IPT Montagnais | PP_QBNL1_IPT | QB-NL Border | 52.1021 | -65.6932 | Labrador
| IPT Woodbine | PP_NSNL1_IPT | NS-NL Border | 46.9965 | -59.44 | Newfoundland |  | Midway across Cabot Strait
| Islington (ISL) | NL_ISL_DSS | Newfoundland Power | 47.7597 | -53.4761 | Newfoundland
| Jacksons Arm (JAM) | NL_JAM_DSS | Nalcor Energy | 49.8637 | -56.815 | Newfoundland
| Jacksons Arm Tap (JAT) | NL_JAT_DSS | Nalcor Energy | 49.7491 | -56.9343 | Newfoundland
| Jonathan's Pond (JON) | NL_JON_DSS | Newfoundland Power | 49.0794 | -54.5254 | Newfoundland
| Kelligrews (KEL) | NL_KEL_DSS | Newfoundland Power | 47.4982 | -53.0003 | Newfoundland
| Kenmount (KEN) | NL_KEN_DSS | Newfoundland Power | 47.5244 | -52.8474 | Newfoundland
| Kings Bridge (KBR) | NL_KBR_DSS | Newfoundland Power | 47.5758 | -52.7034 | Newfoundland
| Laurentian (LAU) | NL_LAU_DSS | Newfoundland Power | 46.9265 | -55.405 | Newfoundland
| Lethbridge (LET) | NL_LET_DSS | Newfoundland Power | 48.3483 | -53.8715 | Newfoundland
| Lewisporte (LEW) | NL_LEW_DSS | Newfoundland Power | 49.2402 | -55.0667 | Newfoundland
| Linton Lake (LLK) | NL_LLK_DSS | Newfoundland Power | 47.1969 | -55.1366 | Newfoundland
| Lockston (LOK) | NL_LOK_DFS | Newfoundland Power | 48.4008 | -53.3786 | Newfoundland
| Long Harbour (LHB) | NL_LHB_ISS | Nalcor Energy | 47.4089 | -53.8119 | Newfoundland
| Long Lake (LGL) | NL_LGL_DFS | Newfoundland Power | 47.61 | -58.8939 | Newfoundland
| Lookout Brook (LBK) | NL_LBK_DFS | Newfoundland Power | 48.3662 | -58.2939 | Newfoundland
| Lower Cove Mine (LCV) | NL_LCV_DSS | Newfoundland Power | 48.5307 | -59.0288 | Newfoundland
| Main Brook (MBK) | NL_MBK_DSS | Nalcor Energy | 51.1729 | -56.0334 | Newfoundland
| Marble Mountain (MMT) | NL_MMT_DSS | Newfoundland Power | 48.9617 | -57.8081 | Newfoundland
| Marystown (MSY) | NL_MSY_DSS | Newfoundland Power | 47.1661 | -55.1789 | Newfoundland
| Massey Drive (MAS) | NL_MAS_TSS | Newfoundland Power | 48.9328 | -57.8993 | Newfoundland
| Memorial (MUN) | NL_MUN_DSS | Newfoundland Power | 47.5748 | -52.7402 | Newfoundland
| Milton (MIL) | NL_MIL_DSS | Newfoundland Power | 48.208 | -53.9575 | Newfoundland
| Mobile (MOB) | NL_MOB_DFS | Newfoundland Power | 47.2479 | -52.8418 | Newfoundland
| Molloys Lane (MOL) | NL_MOL_DSS | Newfoundland Power | 47.5356 | -52.7451 | Newfoundland
| Monkstown (MKS) | NL_MKS_TSS | NP / Nalcor Energy | 47.5881 | -54.4229 | Newfoundland
| Morris (MRP) | NL_MRP_GSS | Newfoundland Power | 47.2537 | -52.9358 | Newfoundland
| Morris Tap (MRP) | NL_MRP_JCT | Newfoundland Power | 47.2119 | -52.8976 | Newfoundland
| Muskrat Falls (TS2) | NL_TS2_CSS | Nalcor Energy | 53.24 | -60.7591 | Labrador
| New Chelsea (NCH) | NL_NCH_DFS | Newfoundland Power | 48.0291 | -53.21 | Newfoundland
| New Grand Falls (NGF) | NL_NGF_DSS | Nalcor Energy | 48.9403 | -55.6522 | Newfoundland
| New Harbour (NHR) | NL_NHR_DSS | Newfoundland Power | 47.5855 | -53.5138 | Newfoundland
| Northwest Brook (NWB) | NL_NWB_DSS | Newfoundland Power | 47.9929 | -53.9555 | Newfoundland
| Notre Dame Junction (NDJ) | NL_NDJ_DSS | Newfoundland Power | 49.1225 | -55.0927 | Newfoundland
| Old Perlican (OPL) | NL_OPL_DSS | Newfoundland Power | 48.0736 | -52.9972 | Newfoundland
| Oxen Pond (OXP) | NL_OXP_DSS | NP / Nalcor Energy | 47.5734 | -52.7558 | Newfoundland
| Paradise River (PRV) | NL_PRV_DFS | Nalcor Energy | 47.6182 | -54.4315 | Newfoundland
| Parsons Pond (PPD) | NL_PPD_DSS | Nalcor Energy | 50.038 | -57.7023 | Newfoundland
| Pasadena (PAS) | NL_PAS_DSS | Newfoundland Power | 49.0168 | -57.6007 | Newfoundland
| Pepperrell (PEP) | NL_PEP_DSS | Newfoundland Power | 47.5848 | -52.6836 | Newfoundland
| Peters Barren (PBN) | NL_PBN_DSS | Newfoundland Power | 50.2718 | -57.547 | Newfoundland
| Petty Harbour (PHR) | NL_PHR_DFS | Newfoundland Power | 47.4654 | -52.7123 | Newfoundland
| Pierres Brook (PBK) | NL_PBK_GSS | Newfoundland Power | 47.2884 | -52.821 | Newfoundland
| Placentia Junction (PJN) | NL_PJN_DSS | Newfoundland Power | 47.3697 | -53.6592 | Newfoundland
| Plum Point (PPT) | NL_PPT_DSS | Nalcor Energy | 51.0635 | -56.8402 | Newfoundland
| Port Aux Basques (PAB) | NL_PAB_DFS | Newfoundland Power | 47.5856 | -59.1486 | Newfoundland
| Port Blandford (PBD) | NL_PBD_DSS | Newfoundland Power | 48.3605 | -54.1735 | Newfoundland
| Port Union (PUN) | NL_PUN_DSS | Newfoundland Power | 48.4983 | -53.0899 | Newfoundland
| Princeton Pond (PRC) | NL_PRC_DSS | Newfoundland Power | 48.3958 | -53.5811 | Newfoundland
| Pulpit Rock (PUL) | NL_PUL_DSS | Newfoundland Power | 47.6606 | -52.7571 | Newfoundland
| Quartz (QTZ) | NL_QTZ_ISS | Newfoundland Power | 47.3153 | -53.7818 | Newfoundland
| Rattle Brook (RTK) | NL_RTK_GSS | Nalcor Energy | 49.8876 | -56.8359 | Newfoundland
| Rattling Brook (RBK) | NL_RBK_DFS | Newfoundland Power | 49.0675 | -55.298 | Newfoundland
| Ridge Road (RRD) | NL_RRD_DSS | Newfoundland Power | 47.5907 | -52.7289 | Newfoundland
| Riverhead (RVH) | NL_RVH_DSS | Newfoundland Power | 46.9879 | -53.4992 | Newfoundland
| Robinsons (ROB) | NL_ROB_DSS | Newfoundland Power | 48.3784 | -58.4741 | Newfoundland
| Robinsons Tap (ROB) | NL_ROB_JCT | Newfoundland Power | 48.4075 | -58.4556 | Newfoundland
| Rocky Harbour (RHR) | NL_RHR_DSS | Nalcor Energy | 49.5779 | -57.9149 | Newfoundland
| Rocky Pond (ROP) | NL_ROP_DFS | Newfoundland Power | 47.2104 | -52.895 | Newfoundland
| Rocky Pond Tap (ROP) | NL_ROP_JCT | Newfoundland Power | 47.2119 | -52.8977 | Newfoundland
| Roddickton (RCK) | NL_RCK_DSS | Nalcor Energy | 50.8899 | -56.1181 | Newfoundland
| Roycefield Mine (RFD) | NL_RFD_ISS | Newfoundland Power | 48.7164 | -55.1971 | Newfoundland
| Roycefield Mine Tap (RFD) | NL_RFD_JCT | Newfoundland Power | 48.9971 | -54.8999 | Newfoundland
| Sallys Cove (SCV) | NL_SCV_DSS | Nalcor Energy | 49.744 | -57.9182 | Newfoundland
| Salt Pond (SPO) | NL_SPO_DSS | Newfoundland Power | 47.0937 | -55.2031 | Newfoundland
| Sandy Brook (SBK) | NL_SBK_GSS | Newfoundland Power | 48.891 | -55.8228 | Newfoundland
| Seal Cove (SCV) | NL_SCV_DFS | Newfoundland Power | 47.457 | -53.0677 | Newfoundland
| Seal Cove Road (SCR) | NL_SCR_DSS | Newfoundland Power | 49.9179 | -56.24 | Newfoundland
| Soldiers Pond (SOL) | NL_SOL_CSS | Nalcor Energy | 47.4179 | -52.9795 | Newfoundland
| South Brook (SOK) | NL_SOK_DSS | Nalcor Energy | 49.4107 | -56.0809 | Newfoundland
| Springdale (SPR) | NL_SPR_DSS | Newfoundland Power | 49.5171 | -56.1068 | Newfoundland
| Springfield (SPF) | NL_SPF_DSS | Newfoundland Power | 47.5236 | -53.2805 | Newfoundland
| St Anthony (SOP) | NL_SOP_GSS | Nalcor Energy | 51.3844 | -55.5911 | Newfoundland
| St Anthony Airport (STA) | NL_STA_DSS | Nalcor Energy | 51.3755 | -56.094 | Newfoundland
| St Catherines (SCT) | NL_SCT_DSS | Newfoundland Power | 47.5535 | -52.7116 | Newfoundland
| St Georges (STG) | NL_STG_DSS | Newfoundland Power | 47.1659 | -53.4312 | Newfoundland
| St Johns Main (SJM) | NL_SJM_DSS | Newfoundland Power | 48.4224 | -58.4746 | Newfoundland
| Stamps Lane (SLA) | NL_SLA_DSS | Newfoundland Power | 47.5607 | -52.7403 | Newfoundland
| Star Lake (SLK) | NL_SLK_GSS | Nalcor Energy | 48.5523 | -57.2057 | Newfoundland
| Stephenville (STV) | NL_STV_GSS | NP / Nalcor Energy | 48.5356 | -58.5177 | Newfoundland
| Stephenville Crossing (STX) | NL_STX_DSS | Newfoundland Power | 48.5147 | -58.4505 | Newfoundland
| Stony Brook (STY) | NL_STY_TSS | Nalcor Energy | 48.9218 | -55.6709 | Newfoundland
| Strait of Belle Isle (SBI) | NL_SBI_JCT | Nalcor Energy | 51.404 | -56.79 | Labrador |  | Midway across Strait of Belle Isle
| Summerford (SUM) | NL_SUM_DSS | Newfoundland Power | 49.4974 | -54.7774 | Newfoundland
| Summerville (SMV) | NL_SMV_DSS | Newfoundland Power | 48.3889 | -53.6409 | Newfoundland
| Sunnyside (SUN) | NL_SUN_TSS | Newfoundland Power | 47.8511 | -53.9512 | Newfoundland
| Terra Nova (TNS) | NL_TNS_DSS | Newfoundland Power | 48.4953 | -54.2462 | Newfoundland
| Tors Cove (TCV) | NL_TCV_GSS | Newfoundland Power | 47.2107 | -52.8483 | Newfoundland
| Trepassey (TRP) | NL_TRP_DSS | Newfoundland Power | 46.7566 | -53.3781 | Newfoundland
| Trinity (TRN) | NL_TRN_DSS | Newfoundland Power | 49.0047 | -53.9044 | Newfoundland
| Twillingate (TWG) | NL_TWG_DSS | Newfoundland Power | 49.6439 | -54.7477 | Newfoundland
| Upper Island Cove (ILC) | NL_ILC_DSS | Newfoundland Power | 47.6432 | -53.2429 | Newfoundland
| Upper Salmon (USL) | NL_USL_GSS | Nalcor Energy | 48.1835 | -56.1725 | Newfoundland
| Victoria (VIC) | NL_VIC_DSS | Newfoundland Power | 47.7745 | -53.2156 | Newfoundland
| Virginia Waters (VIR) | NL_VIR_DSS | Newfoundland Power | 47.6149 | -52.7028 | Newfoundland
| Wabush (WTS) | NL_WTS_DSS | Nalcor Energy | 52.9321 | -66.8846 | Labrador
| Walbournes (WAL) | NL_WAL_DSS | Newfoundland Power | 48.9402 | -57.9715 | Newfoundland
| Webbers Cove (WBC) | NL_WBC_DFS | Newfoundland Power | 46.9517 | -55.5349 | Newfoundland
| Wesleyville (WES) | NL_WES_DFS | Newfoundland Power | 49.1218 | -53.5993 | Newfoundland
| Western Avalon (WAV) | NL_WAV_DSS | Newfoundland Power | 47.5167 | -53.6846 | Newfoundland
| Wheelers (WHE) | NL_WHE_DSS | Newfoundland Power | 48.5699 | -58.527 | Newfoundland
| Wheelers Tap (WHE) | NL_WHE_JCT | Newfoundland Power | 48.5624 | -58.5384 | Newfoundland
| Wiltondale (WDL) | NL_WDL_DSS | Nalcor Energy | 49.3837 | -57.5859 | Newfoundland
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## Distribution
NL | EXISTING DISTRIBUTIONS STATIONS
| Node Name | Node Code | Owner | Operating Region | Transformer | Primary Voltage (kV) | Secondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Other Sources | Notes
[6 empty] | (kV) | (kV) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| Abraham's Cove (ABC) | NL_ABC_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Baie Verte Junction (BVJ) | NL_BVJ_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 2.67 | 3.204 | 0.9 | 2.403 | 2.8836
| Barachoix (BCX) | NL_BCX_DSS | Nalcor Energy | Newfoundland
| Bay Largent (BLA) | NL_BLA_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| Bay Roberts (BRB) | NL_BRB_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Bay Roberts (BRB) | NL_BRB_DSS | Newfoundland Power | Newfoundland | T4 | 138 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Bay Roberts (BRB) | NL_BRB_DSS | Newfoundland Power | Newfoundland | T2 | 138 | 66 | 41.6 | 49.92 | 0.9 | 37.44 | 44.928
| Bay Roberts (BRB) | NL_BRB_DSS | Newfoundland Power | Newfoundland | T3 | 138 | 66 | 41.6 | 49.92 | 0.9 | 37.44 | 44.928
| Bayview (BVS) | NL_BVS_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 15 | 18 | 0.9 | 13.5 | 16.2
| Bayview (BVS) | NL_BVS_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Bear Cove (BRV) | NL_BRV_DSS | Nalcor Energy | Newfoundland
| Berry Head (BHD) | NL_BHD_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 7.46 | 8.952 | 0.9 | 6.714 | 8.0568
| Berry Hill (BHL) | NL_BHL_DSS | Nalcor Energy | Newfoundland
| Big Pond (BIG) | NL_BIG_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 11.1 | 13.32 | 0.9 | 9.99 | 11.988
| Bishops Falls (BFS) | NL_BFS_DFS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 20 | 24 | 0.9 | 18 | 21.6
| Blaketown (BLK) | NL_BLK_DSS | Newfoundland Power | Newfoundland | T2 | 138 | 25 | 20 | 24 | 0.9 | 18 | 21.6
| Blaketown (BLK) | NL_BLK_DSS | Newfoundland Power | Newfoundland | T3 | 138 | 66 | 41.6 | 49.92 | 0.9 | 37.44 | 44.928
| Bonavista (BVA) | NL_BVA_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Bottom Waters (BWT) | NL_BWT_DSS | Nalcor Energy | Newfoundland
| Botwood (BOT) | NL_BOT_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 20 | 24 | 0.9 | 18 | 21.6
| Boyds Cove (BOY) | NL_BOY_DSS | Newfoundland Power | Newfoundland
| Broad Cove (BCV) | NL_BCV_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Buchans (BUC) | NL_BUC_DFS | NP / Nalcor Energy | Newfoundland
| Cape Broyle (CAB) | NL_CAB_DFS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 5 | 6 | 0.9 | 4.5 | 5.4
| Carbonear (CAR) | NL_CAR_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Catalina (CAT) | NL_CAT_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 66 | 16.7 | 20.04 | 0.9 | 15.03 | 18.036
| Catalina (CAT) | NL_CAT_DSS | Newfoundland Power | Newfoundland | T2 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Chamberlains (CHA) | NL_CHA_DFS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 25 | 30 | 0.9 | 22.5 | 27
| Chamberlains (CHA) | NL_CHA_DFS | Newfoundland Power | Newfoundland | T2 | 66 | 25 | 25 | 30 | 0.9 | 22.5 | 27
| Clarenville (CLV) | NL_CLV_DSS | Newfoundland Power | Newfoundland | T2 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Clarenville (CLV) | NL_CLV_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 66 | 25 | 30 | 0.9 | 22.5 | 27
| Clarke's Head (CKH) | NL_CKH_DSS | Newfoundland Power | Newfoundland
| Clarkes Pond (CLK) | NL_CLK_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 10 | 12 | 0.9 | 9 | 10.8
| Clarkes Pond (CLK) | NL_CLK_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 10 | 12 | 0.9 | 9 | 10.8
| Cobbs Pond (COB) | NL_COB_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Cobbs Pond (COB) | NL_COB_DSS | Newfoundland Power | Newfoundland | T3 | 138 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Cobbs Pond (COB) | NL_COB_DSS | Newfoundland Power | Newfoundland | T2 | 138 | 66 | 41.6 | 49.92 | 0.9 | 37.44 | 44.928
| Colliers (COL) | NL_COL_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 12.5 | 16.67 | 20.004 | 0.9 | 15.003 | 18.0036
| Coney Arm (CAM) | NL_CAM_DSS | Nalcor Energy | Newfoundland
| Conne River (CRV) | NL_CRV_DSS | Nalcor Energy | Newfoundland
| Cow Head (CHD) | NL_CHD_DSS | Nalcor Energy | Newfoundland
| Daniels Harbour (DHR) | NL_DHR_DSS | Nalcor Energy | Newfoundland
| Deer Lake (DLK) | NL_DLK_DFS | NP / Nalcor Energy | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Doyles (DOY) | NL_DOY_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 25 | 4 | 4.8 | 0.9 | 3.6 | 4.32
| Duck Pond (DKP) | NL_DKP_DSS | Nalcor Energy | Newfoundland
| Duffs (DUF) | NL_DUF_DSS | Newfoundland Power | Newfoundland
| Dunville (DUN) | NL_DUN_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 8.3 | 9.96 | 0.9 | 7.47 | 8.964
| English HR. West (EHW) | NL_EHW_DSS | Nalcor Energy | Newfoundland
| Farewell Head (FHD) | NL_FHD_DSS | Nalcor Energy | Newfoundland
| Fermeuse (FER) | NL_FER_DFS | Newfoundland Power | Newfoundland | T1 | 69 | 13.8 | 4 | 4.8 | 0.9 | 3.6 | 4.32
| Frenchmans Cove (FRN) | NL_FRN_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| Gallant (GAL) | NL_GAL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Gallant (GAL) | NL_GAL_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Gambo (GAM) | NL_GAM_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| Gambo (GAM) | NL_GAM_DSS | Newfoundland Power | Newfoundland | T2 | 138 | 66 | 41.6 | 49.92 | 0.9 | 37.44 | 44.928
| Gander (GAN) | NL_GAN_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Gander (GAN) | NL_GAN_DSS | Newfoundland Power | Newfoundland | T2 | 138 | 66 | 26.67 | 32.004 | 0.9 | 24.003 | 28.8036
| Gander Bay (GBY) | NL_GBY_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 13.3 | 15.96 | 0.9 | 11.97 | 14.364
| Garnish (GAR) | NL_GAR_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 3.72 | 4.464 | 0.9 | 3.348 | 4.0176
| Gillams (GIL) | NL_GIL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| Glenburnie (GLB) | NL_GLB_DSS | Nalcor Energy | Newfoundland
| Glendale (GDL) | NL_GDL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Glendale (GDL) | NL_GDL_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Glendale (GDL) | NL_GDL_DSS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Glenwood (GLN) | NL_GLN_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 8.34 | 10.008 | 0.9 | 7.506 | 9.0072
| Glovertown (GLV) | NL_GLV_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 20 | 24 | 0.9 | 18 | 21.6
| Goulds (GOU) | NL_GOU_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 33 | 10 | 12 | 0.9 | 9 | 10.8
| Goulds (GOU) | NL_GOU_DSS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Goulds (GOU) | NL_GOU_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Grand Bay (GBS) | NL_GBS_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 14.93 | 17.916 | 0.9 | 13.437 | 16.1244
| Grand Beach (GBE) | NL_GBE_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 7.2 | 0.333 | 0.3996 | 0.9 | 0.2997 | 0.35964
| Grand Falls (GFS) | NL_GFS_DFS | Newfoundland Power | Newfoundland | T5 | 66 | 4.16 | 8.4 | 10.08 | 0.9 | 7.56 | 9.072
| Grand Falls (GFS) | NL_GFS_DFS | Newfoundland Power | Newfoundland | T2 | 138 | 25 | 20 | 24 | 0.9 | 18 | 21.6
| Grand Falls (GFS) | NL_GFS_DFS | Newfoundland Power | Newfoundland | T3 | 138 | 25 | 20 | 24 | 0.9 | 18 | 21.6
| Grand Falls (GFS) | NL_GFS_DFS | Newfoundland Power | Newfoundland | T1 | 138 | 66 | 29.7 | 35.64 | 0.9 | 26.73 | 32.076
| Grandy Brook (GBK) | NL_GBK_DSS | Nalcor Energy | Newfoundland
| Greenhill (GRH) | NL_GRH_DFS | Newfoundland Power | Newfoundland | T2 | 69 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Greenspond (GPD) | NL_GPD_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 2.8 | 3.36 | 0.9 | 2.52 | 3.024
| Hampden (HDN) | NL_HDN_DSS | Nalcor Energy | Newfoundland
| Hampden Tap (HDT) | NL_HDT_DSS | Nalcor Energy | Newfoundland
| Happy Valley (HVY) | NL_HVY_DFS | Nalcor Energy | Labrador
| Harbour Grace (HGR) | NL_HGR_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 6.7 | 8.04 | 0.9 | 6.03 | 7.236
| Harbour Grace (HGR) | NL_HGR_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 10 | 12 | 0.9 | 9 | 10.8
| Hardwoods (HWD) | NL_HWD_DFS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Hardwoods (HWD) | NL_HWD_DFS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Hardwoods (HWD) | NL_HWD_DFS | Newfoundland Power | Newfoundland | T3 | 66 | 25 | 50 | 60 | 0.9 | 45 | 54
| Hare Bay (HBS) | NL_HBS_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 5 | 6 | 0.9 | 4.5 | 5.4
| Harmon (HAR) | NL_HAR_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 14.9 | 17.88 | 0.9 | 13.41 | 16.092
| Hearts Content (HCT) | NL_HCT_DFS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 2.24 | 2.688 | 0.9 | 2.016 | 2.4192
| Holyrood (HOL) | NL_HOL_DSS | NP / Nalcor Energy | Newfoundland | T1 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Howley (HOW) | NL_HOW_DSS | Newfoundland Power | Newfoundland | T3 | 25 | 4.16 | 1 | 1.2 | 0.9 | 0.9 | 1.08
| Humber (HUM) | NL_HUM_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 4.16 | 7.46 | 8.952 | 0.9 | 6.714 | 8.0568
| Humber (HUM) | NL_HUM_DSS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Islington (ISL) | NL_ISL_DSS | Newfoundland Power | Newfoundland | T1 | 69 | 13.8 | 4 | 4.8 | 0.9 | 3.6 | 4.32
| Jacksons Arm (JAM) | NL_JAM_DSS | Nalcor Energy | Newfoundland
| Jacksons Arm Tap (JAT) | NL_JAT_DSS | Nalcor Energy | Newfoundland
| Jonathan's Pond (JON) | NL_JON_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 7.2 | 0.333 | 0.3996 | 0.9 | 0.2997 | 0.35964
| Kelligrews (KEL) | NL_KEL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Kenmount (KEN) | NL_KEN_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 25 | 30 | 0.9 | 22.5 | 27
| Kenmount (KEN) | NL_KEN_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 25 | 25 | 30 | 0.9 | 22.5 | 27
| Kings Bridge (KBR) | NL_KBR_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 4.16 | 10 | 12 | 0.9 | 9 | 10.8
| Kings Bridge (KBR) | NL_KBR_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 4.16 | 10 | 12 | 0.9 | 9 | 10.8
| Kings Bridge (KBR) | NL_KBR_DSS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Laurentian (LAU) | NL_LAU_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 10 | 12 | 0.9 | 9 | 10.8
| Lethbridge (LET) | NL_LET_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 6.7 | 8.04 | 0.9 | 6.03 | 7.236
| Lewisporte (LEW) | NL_LEW_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 25 | 30 | 0.9 | 22.5 | 27
| Linton Lake (LLK) | NL_LLK_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Lockston (LOK) | NL_LOK_DFS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 4 | 4.8 | 0.9 | 3.6 | 4.32
| Long Lake (LGL) | NL_LGL_DFS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 14.9 | 17.88 | 0.9 | 13.41 | 16.092
| Lookout Brook (LBK) | NL_LBK_DFS | Newfoundland Power | Newfoundland
| Lower Cove Mine (LCV) | NL_LCV_DSS | Newfoundland Power | Newfoundland
| Main Brook (MBK) | NL_MBK_DSS | Nalcor Energy | Newfoundland
| Marble Mountain (MMT) | NL_MMT_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 6.7 | 8.04 | 0.9 | 6.03 | 7.236
| Marystown (MSY) | NL_MSY_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Memorial (MUN) | NL_MUN_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 14.83 | 17.796 | 0.9 | 13.347 | 16.0164
| Memorial (MUN) | NL_MUN_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Milton (MIL) | NL_MIL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 16.67 | 20.004 | 0.9 | 15.003 | 18.0036
| Mobile (MOB) | NL_MOB_DFS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 16.67 | 20.004 | 0.9 | 15.003 | 18.0036
| Molloys Lane (MOL) | NL_MOL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Molloys Lane (MOL) | NL_MOL_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Monkstown (MKS) | NL_MKS_TSS | NP / Nalcor Energy | Newfoundland
| New Chelsea (NCH) | NL_NCH_DFS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| New Grand Falls (NGF) | NL_NGF_DSS | Nalcor Energy | Newfoundland
| New Harbour (NHR) | NL_NHR_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Northwest Brook (NWB) | NL_NWB_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 11.2 | 13.44 | 0.9 | 10.08 | 12.096
| Notre Dame Junction (NDJ) | NL_NDJ_DSS | Newfoundland Power | Newfoundland
| Old Perlican (OPL) | NL_OPL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 14.96 | 17.952 | 0.9 | 13.464 | 16.1568
| Oxen Pond (OXP) | NL_OXP_DSS | NP / Nalcor Energy | Newfoundland | T1 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Paradise River (PRV) | NL_PRV_DFS | Nalcor Energy | Newfoundland
| Parsons Pond (PPD) | NL_PPD_DSS | Nalcor Energy | Newfoundland
| Pasadena (PAS) | NL_PAS_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 13.3 | 15.96 | 0.9 | 11.97 | 14.364
| Pepperrell (PEP) | NL_PEP_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Peters Barren (PBN) | NL_PBN_DSS | Newfoundland Power | Newfoundland
| Petty Harbour (PHR) | NL_PHR_DFS | Newfoundland Power | Newfoundland | T3 | 66 | 4.6 | 3 | 3.6 | 0.9 | 2.7 | 3.24
| Placentia Junction (PJN) | NL_PJN_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 7.2 | 0.333 | 0.3996 | 0.9 | 0.2997 | 0.35964
| Plum Point (PPT) | NL_PPT_DSS | Nalcor Energy | Newfoundland
| Port Aux Basques (PAB) | NL_PAB_DFS | Newfoundland Power | Newfoundland | T5 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Port Blandford (PBD) | NL_PBD_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 16.67 | 20.004 | 0.9 | 15.003 | 18.0036
| Port Union (PUN) | NL_PUN_DSS | Newfoundland Power | Newfoundland
| Princeton Pond (PRC) | NL_PRC_DSS | Newfoundland Power | Newfoundland
| Pulpit Rock (PUL) | NL_PUL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Pulpit Rock (PUL) | NL_PUL_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Quartz (QTZ) | NL_QTZ_ISS | Newfoundland Power | Newfoundland | T1 | 66 | 4.16 | 0.725 | 0.87 | 0.9 | 0.6525 | 0.783
| Rattling Brook (RBK) | NL_RBK_DFS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 5 | 6 | 0.9 | 4.5 | 5.4
| Ridge Road (RRD) | NL_RRD_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Ridge Road (RRD) | NL_RRD_DSS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Riverhead (RVH) | NL_RVH_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| Robinsons (ROB) | NL_ROB_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| Rocky Harbour (RHR) | NL_RHR_DSS | Nalcor Energy | Newfoundland
| Rocky Pond (ROP) | NL_ROP_DFS | Newfoundland Power | Newfoundland
| Roddickton (RCK) | NL_RCK_DSS | Nalcor Energy | Newfoundland
| Sallys Cove (SCV) | NL_SCV_DFS | Nalcor Energy | Newfoundland
| Salt Pond (SPO) | NL_SPO_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 15 | 18 | 0.9 | 13.5 | 16.2
| Salt Pond (SPO) | NL_SPO_DSS | Newfoundland Power | Newfoundland | T5 | 138 | 66 | 41.6 | 49.92 | 0.9 | 37.44 | 44.928
| Salt Pond (SPO) | NL_SPO_DSS | Newfoundland Power | Newfoundland | T4 | 138 | 66 | 41.6 | 49.92 | 0.9 | 37.44 | 44.928
| Seal Cove (SCV) | NL_SCV_GSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 11.2 | 13.44 | 0.9 | 10.08 | 12.096
| Seal Cove Road (SCR) | NL_SCR_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 8.33 | 9.996 | 0.9 | 7.497 | 8.9964
| South Brook (SOK) | NL_SOK_DSS | Nalcor Energy | Newfoundland
| Springdale (SPR) | NL_SPR_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 25 | 16.67 | 20.004 | 0.9 | 15.003 | 18.0036
| Springfield (SPF) | NL_SPF_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| St Anthony Airport (STA) | NL_STA_DSS | Nalcor Energy | Newfoundland
| St Catherines (SCT) | NL_SCT_DSS | Newfoundland Power | Newfoundland | T2 | 25 | 12.5 | 4 | 4.8 | 0.9 | 3.6 | 4.32
| St Catherines (SCT) | NL_SCT_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 5 | 6 | 0.9 | 4.5 | 5.4
| St Georges (STG) | NL_STG_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| St Johns Main (SJM) | NL_SJM_DSS | Newfoundland Power | Newfoundland | T4 | 66 | 4.16 | 7.5 | 9 | 0.9 | 6.75 | 8.1
| St Johns Main (SJM) | NL_SJM_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| St Johns Main (SJM) | NL_SJM_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Stamps Lane (SLA) | NL_SLA_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 4.16 | 10.4 | 12.48 | 0.9 | 9.36 | 11.232
| Stamps Lane (SLA) | NL_SLA_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 4.16 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Stamps Lane (SLA) | NL_SLA_DSS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Stamps Lane (SLA) | NL_SLA_DSS | Newfoundland Power | Newfoundland | T4 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Stephenville Crossing (STX) | NL_STX_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| Summerford (SUM) | NL_SUM_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 10 | 12 | 0.9 | 9 | 10.8
| Summerville (SMV) | NL_SMV_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 4 | 4.8 | 0.9 | 3.6 | 4.32
| Sunnyside (SUN) | NL_SUN_TSS | Newfoundland Power | Newfoundland | T5 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27
| Terra Nova (TNS) | NL_TNS_DSS | Newfoundland Power | Newfoundland | T1 | 138 | 14.4 | 1 | 1.2 | 0.9 | 0.9 | 1.08
| Trepassey (TRP) | NL_TRP_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 6.67 | 8.004 | 0.9 | 6.003 | 7.2036
| Trinity (TRN) | NL_TRN_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 5 | 6 | 0.9 | 4.5 | 5.4
| Twillingate (TWG) | NL_TWG_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 13.3 | 15.96 | 0.9 | 11.97 | 14.364
| Upper Island Cove (ILC) | NL_ILC_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Victoria (VIC) | NL_VIC_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 13.33 | 15.996 | 0.9 | 11.997 | 14.3964
| Virginia Waters (VIR) | NL_VIR_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Virginia Waters (VIR) | NL_VIR_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Virginia Waters (VIR) | NL_VIR_DSS | Newfoundland Power | Newfoundland | T3 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Wabush (WTS) | NL_WTS_DSS | Nalcor Energy | Labrador
| Walbournes (WAL) | NL_WAL_DSS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 20 | 24 | 0.9 | 18 | 21.6
| Walbournes (WAL) | NL_WAL_DSS | Newfoundland Power | Newfoundland | T2 | 66 | 12.5 | 25 | 30 | 0.9 | 22.5 | 27
| Webbers Cove (WBC) | NL_WBC_DFS | Newfoundland Power | Newfoundland | T1 | 66 | 25 | 8.33 | 9.996 | 0.9 | 7.497 | 8.9964
| Wesleyville (WES) | NL_WES_DFS | Newfoundland Power | Newfoundland | T1 | 66 | 12.5 | 13.3 | 15.96 | 0.9 | 11.97 | 14.364
| Western Avalon (WAV) | NL_WAV_DSS | Newfoundland Power | Newfoundland | T6 | 66 | 12.5 | 13.3 | 15.96 | 0.9 | 11.97 | 14.364
| Wheelers (WHE) | NL_WHE_DSS | Newfoundland Power | Newfoundland
| Wiltondale (WDL) | NL_WDL_DSS | Nalcor Energy | Newfoundland
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## System
NL | SYSTEM CHARACTERISTICS
| Generator Type | Capacity Adjustment (ELCC) | Capacity Factor | Notes | Reserve Requirements | Nalcor Line Losses | NP Line Losses | Total Line Losses
|  | (%) | (%) |  | (% installed MW) | (% across system) | (% across system) | (% across system)
| Heavy Fuel Oil | by facility | 25% | Only applies to Holyrood, based on 2009-2013 | 13% | 3% | 5.3% | 8.3%
| Light Fuel Oil CT | by facility | 1%
| Biomass / Biogas | by facility | by facility
| NP Hydro | 75% | by facility
| NLH Hydro | by facility | by facility
| Churchill Falls | 98.1% | by facility
| Wind | 22% | by facility
| Maritime Link Base Energy Imports | 98% | 66.7% | Base Block of 16 hours/day
Specific Notes:
Forced outage rate for Churchill Falls assumed same as for Muskrat Falls and Hydro quebec facilities (i.e. 1.9%)
Nalcor line losses reflect average of the three years 2016-2018.
NP Hydro capacity adjustment deduced from total installed capacity (94.7 MW) and the effective capacity used in the Reliability and Resource Adequacy Study (71.5 MW)

## HGWh
NL | HISTORICAL ANNUAL ENERGY DEMAND | UNITS | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2008-2018
Island Interconnected System (IIS)
| January | GWh | 709.557 | 756.052 | 689.77 | 671.804 | 746.654 | 810.453 | 811.502 | 859.746 | 848.627 | 839.093 | 828.343
| February | GWh | 649.483 | 640.621 | 611.313 | 668.015 | 705.276 | 702.914 | 770.834 | 775.621 | 737.007 | 774.801 | 747.963
| March | GWh | 682.088 | 651.624 | 622.771 | 676.063 | 718.638 | 670.445 | 821.344 | 833.099 | 778.625 | 793.62 | 734.658
| April | GWh | 544.534 | 486.352 | 518.11 | 564.342 | 540.545 | 585.78 | 636.085 | 677.821 | 625.547 | 663.161 | 638.529
| May | GWh | 476.772 | 409.676 | 486.896 | 465.366 | 463.364 | 473.606 | 536.986 | 517.882 | 502.45 | 570.738 | 528.642
| June | GWh | 404.418 | 377.599 | 391.866 | 395.297 | 417.484 | 411.837 | 403.916 | 428.191 | 441.428 | 417.148 | 474.399
| July | GWh | 381.357 | 364.92 | 356.393 | 346.047 | 383.675 | 363.747 | 379.695 | 412.093 | 395.668 | 396.341 | 383.884
| August | GWh | 385.271 | 361.033 | 360.628 | 370.572 | 392.261 | 369.052 | 373.978 | 386.163 | 393.706 | 397.144 | 390.671
| September | GWh | 385.648 | 369.22 | 367.027 | 380.113 | 365.141 | 371.343 | 375.815 | 407.019 | 411.575 | 392.918 | 431.94
| October | GWh | 483.462 | 497.489 | 448.443 | 474.733 | 455.61 | 478.508 | 485.488 | 525.157 | 515.95 | 508.423 | 548.836
| November | GWh | 532.032 | 536.314 | 546.811 | 572.951 | 538.332 | 592.283 | 615.694 | 660.158 | 578.012 | 638.185 | 661.697
| December | GWh | 659.021 | 661.194 | 606.428 | 701.308 | 713.719 | 827.077 | 726.184 | 802.233 | 810.642 | 785.168 | 812.181
| Annual IIS Energy Demand (after DSM) | GWh/year | 6293.643 | 6112.094 | 6006.456 | 6286.611 | 6440.699 | 6657.045 | 6937.521 | 7285.183 | 7039.237 | 7176.74 | 7181.743
|  | UNITS | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Labrador Interconnected System (LIS)
| January | GWh | 135.23 | 98.7 | 130.68 | 118.08 | 114.72 | 102.71 | 265.52 | 259.74 | 259.11 | 263.45 | 269.1
| February | GWh | 122.55 | 77.3 | 97.74 | 109.47 | 102.65 | 94.45 | 255.89 | 247.26 | 241.76 | 244.93 | 252.66
| March | GWh | 128.49 | 78.6 | 98.07 | 92.82 | 97.46 | 103.63 | 254.85 | 244.66 | 243.9 | 263.74 | 229.56
| April | GWh | 86.88 | 50.8 | 75.35 | 68.44 | 74.14 | 82.08 | 233.01 | 220.48 | 221.81 | 222.35 | 110.79
| May | GWh | 66.08 | 40.5 | 71.82 | 52.08 | 59.89 | 67.13 | 187.65 | 202.11 | 198.85 | 195.28 | 90.74
| June | GWh | 45.08 | 30.3 | 47.7 | 38.08 | 32.32 | 38.8 | 143.43 | 160.84 | 158.24 | 153.76 | 155
| July | GWh | 37.14 | 19 | 44.57 | 30.38 | 31.14 | 27.29 | 158.25 | 175.65 | 167.7 | 177.05 | 172.64
| August | GWh | 41.36 | 25.6 | 40.18 | 26.88 | 25.79 | 32.19 | 155.33 | 172.32 | 169.03 | 182.98 | 170.69
| September | GWh | 45.83 | 42.9 | 43.12 | 29.87 | 34.46 | 41.36 | 173.47 | 171.49 | 168.09 | 183.58 | 179.53
| October | GWh | 78.41 | 75.7 | 73.91 | 46.02 | 58.31 | 59.05 | 195.24 | 195.49 | 204.15 | 192.68 | 208.3
| November | GWh | 97.81 | 95.3 | 90.31 | 67.22 | 85.02 | 85.36 | 218.22 | 262.35 | 226.59 | 233.16 | 218.84
| December | GWh | 102.37 | 115.8 | 96.11 | 100.18 | 101.81 | 123.11 | 240 | 244.03 | 270.58 | 261.02 | 263.27
| Annual LIS Energy Demand (after DSM) | GWh/year | 987.23 | 750.5 | 909.56 | 779.52 | 817.71 | 857.16 | 2480.86 | 2556.42 | 2529.81 | 2573.98 | 2321.12
| Annual NL Energy Demand (after DSM) | GWh/year | 7280.873 | 6862.594 | 6916.016 | 7066.131 | 7258.409 | 7514.205 | 9418.381 | 9841.603 | 9569.047 | 9750.72 | 9502.863
| Annual Change in Energy Demand | GWh/year |  | -418.279 | 53.422 | 150.115 | 192.278 | 255.796 | 1904.176 | 423.222 | -272.556 | 181.673 | -247.857 | Average
| Percentage Change in Energy Demand | % |  |  | 0.7785% | 2.171% | 2.721% | 3.524% | 25.34% | 4.494% | -2.769% | 1.899% | -2.542% | 2.699%
Notes:
Newfoundland Power MW are purchase requirements. Annual maximum reflects average (P50) peak demand weather conditions, no load curtailed and expected NP generation.
Hydro Rural Interconnected annual maximum MW requirements reflect average (P50) peak demand weather conditions.

## HMW
NL | HISTORICAL PEAK DEMAND | UNITS | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2008-2018
Island Interconnected System (IIS)
| January | MW | 1289 | 1390 | 1253 | 1278.1 | 1385.2 | 1377.5 | 1534.8 | 1493.31 | 1491.64 | 1534.63 | 1502.54
| February | MW | 1212 | 1375 | 1305 | 1292 | 1350.4 | 1374.2 | 1513.01 | 1503.26 | 1446.77 | 1539.92 | 1473.42
| March | MW | 1207 | 1294 | 1142.3 | 1200.3 | 1341.4 | 1271.9 | 1485.95 | 1544.33 | 1432.62 | 1487.21 | 1309.62
| April | MW | 1184 | 997 | 1019.1 | 1130.2 | 1135.5 | 1106.9 | 1236.8 | 1271.44 | 1277.11 | 1253.01 | 1206.7
| May | MW | 965.3 | 870 | 885.1 | 959.6 | 1028.7 | 942.7 | 1031.84 | 1045.67 | 999.75 | 1111.07 | 1004.24
| June | MW | 759 | 781 | 853.2 | 821.5 | 865.5 | 842.9 | 831.85 | 892.29 | 927.6 | 917.01 | 1044.57
| July | MW | 678 | 686 | 685.2 | 680.3 | 666.7 | 646.8 | 661.88 | 768.55 | 763.7 | 702.73 | 697.21
| August | MW | 879 | 659 | 635.9 | 681.9 | 689.3 | 679.5 | 682 | n/a | 693.81 | 702.27 | 678.7
| September | MW | 782 | 736 | 732.4 | 751.4 | 667.1 | 717.9 | 848.91 | 836.04 | 859.01 | 762.2 | 895.39
| October | MW | 965 | 1021 | 881.5 | 969.2 | 952.7 | 1004.7 | 939.9 | 1083.35 | 1046.68 | 1051.47 | 1022.82
| November | MW | 1089 | 1055 | 1180.7 | 1175.5 | 1206.9 | 1194 | 1257.96 | 1390.79 | 1191.76 | 1254.89 | 1306.59
| December | MW | 1323 | 1267.9 | 1206.7 | 1398.8 | 1307.4 | 1500.8 | 1500.38 | 1549.78 | 1520.99 | 1484.75 | 1470.37
| IIS Peak Load (after DSM) | Maximum | 1323 | 1390 | 1305 | 1398.8 | 1385.2 | 1500.8 | 1534.8 | 1549.78 | 1520.99 | 1539.92 | 1502.54
|  | UNITS | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Labrador Interconnected System (LIS)
| January | MW | 441.33 | 402.25 | 433.5 | 416.32 | 416.72 | 408.84 | 413.14 | 409.54 | 402.18 | 413.4 | 420.21
| February | MW | 411.37 | 371.6 | 434.4 | 433.39 | 408.89 | 412.61 | 416.6 | 410.64 | 412.38 | 413.37 | 412.74
| March | MW | 421.19 | 361.17 | 378.57 | 381.18 | 402.85 | 427.07 | 417.81 | 394.59 | 390.07 | 400.37 | 386.47
| April | MW | 383.14 | 306.05 | 339.66 | 283.25 | 350.74 | 375.49 | 359.65 | 372.58 | 363.72 | 372.25 | 216.86
| May | MW | 320.7 | 267.6 | 342.91 | 311.98 | 326.82 | 315.64 | 309.01 | 321.2 | 319.96 | 319.42 | 150.89
| June | MW | 282.1 | 274.77 | 314.4 | 276.26 | 278.11 | 312.96 | 252.96 | 295.13 | 273.08 | 269.75 | 281.27
| July | MW | 276.22 | 59.46 | 296.42 | 269.53 | 270.75 | 265.52 | 240.92 | 267.76 | 263.15 | 274.33 | 281.14
| August | MW | 285.86 | 277.07 | 267.95 | 261.12 | 247.19 | 267.32 | 236.85 | 271.79 | 254.9 | 274.9 | 271.24
| September | MW | 315.76 | 297.5 | 259.15 | 262.16 | 285.36 | 267.26 | 279.06 | 280.08 | 283.13 | 287.88 | 287.38
| October | MW | 352.47 | 313.39 | 331.74 | 293.39 | 294.74 | 345.01 | 301.56 | 322.26 | 327.67 | 311.6 | 328.81
| November | MW | NA | 370.64 | 377.97 | 323.75 | 379.75 | 375.16 | 378.71 | 360.39 | 373.65 | 360.27 | 370.96
| December | MW | 405.75 | 411.23 | 396.9 | 410.04 | 390.57 | 427.92 | 375.66 | 388.62 | 417.33 | 408.32 | 415.313
| LIS Peak Load (after DSM) | Maximum | 441.33 | 411.23 | 434.4 | 433.39 | 416.72 | 427.92 | 417.81 | 410.64 | 417.33 | 413.4 | 420.21
| NL Peak load (after DSM) | Peak | 1764.33 | 1801.23 | 1739.4 | 1832.19 | 1801.92 | 1928.72 | 1952.61 | 1960.42 | 1938.32 | 1953.32 | 1922.75
| Annual Change in Peak Load | GWh/year |  | 36.9 | -61.83 | 92.79 | -30.27 | 126.8 | 23.89 | 7.81 | -22.1 | 15 | -30.57 | Average
| Percentage Change in Peak Load | % |  |  | -3.433% | 5.335% | -1.652% | 7.037% | 1.239% | 0.4% | -1.127% | 0.7739% | -1.565% | 0.8636%
Notes:
Newfoundland Power MW are purchase requirements. Annual maximum reflects average (P50) peak demand weather conditions, no load curtailed and expected NP generation.
Hydro Rural Interconnected annual maximum MW requirements reflect average (P50) peak demand weather conditions.
Labrador Industrial load does not include a forecasted load for the reactiviation of Wabush mines by Tacora Resources.
After 2021, the IIS and LIS will be interconnected, so there will no longer be separate peak demands for the two systems.

## FGWh
NL | FORECAST ANNUAL ENERGY DEMAND | UNITS | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2019 - 2030 | 2019-2050 | Notes
Island Interconnected System (IIS)
| January | GWh | 858 | 853.1 | 865 | 855.7 | 853.6 | 852.7 | 857.3 | 861.8 | 867.6 | 872.7 | 877.3 | 883
| February | GWh | 776.1 | 795.2 | 779 | 779.3 | 777.6 | 776.8 | 780.7 | 785.4 | 790.4 | 795.3 | 800.4 | 805.5
| March | GWh | 778.2 | 769.5 | 787.8 | 777 | 775.3 | 773.8 | 778.3 | 783.3 | 787.2 | 791.7 | 797.5 | 802.6
| April | GWh | 649.5 | 643 | 632.8 | 648.5 | 645.9 | 641.6 | 648.8 | 652.1 | 654.2 | 660.2 | 661.3 | 665.6
| May | GWh | 538.6 | 534.3 | 533.6 | 547.5 | 545 | 539.1 | 545.5 | 545.6 | 551.4 | 552.7 | 550.2 | 553.8
| June | GWh | 452.9 | 457.8 | 451.9 | 468.6 | 465 | 467.7 | 468.1 | 467.9 | 476.1 | 477 | 459.6 | 462.4
| July | GWh | 411.7 | 419.8 | 422 | 431.7 | 429 | 431 | 433.4 | 435.3 | 436.3 | 438.3 | 416.6 | 419.2
| August | GWh | 396 | 410.5 | 404.1 | 424.9 | 422.7 | 422.3 | 426.1 | 426.8 | 427.7 | 431.9 | 407.2 | 409.7
| September | GWh | 412.9 | 422.1 | 411.8 | 429.8 | 427.3 | 424.9 | 429.9 | 430.9 | 430.5 | 435 | 422.3 | 424.9
| October | GWh | 523.9 | 526.5 | 522.7 | 534.2 | 542.8 | 547.7 | 541 | 543.3 | 552.6 | 549.5 | 536.1 | 539.5
| November | GWh | 615 | 618.6 | 632.4 | 625.2 | 623.5 | 622.8 | 625.5 | 628.8 | 632.2 | 635.4 | 629.9 | 633.9
| December | GWh | 800 | 788.6 | 792.2 | 802.1 | 800.3 | 799.2 | 803.3 | 808.1 | 813.3 | 817.9 | 824.4 | 829.6
| IIS Mid-load (before DSM) | GWh/year | 7212.8 | 7239 | 7235.3 | 7324.5 | 7308 | 7299.6 | 7337.9 | 7369.3 | 7419.5 | 7457.6 | 7382.8 | 7429.7
|  | UNITS | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Labrador Interconnected System (LIS)
| January | GWh | 275.8 | 274.1 | 275.8 | 273.3 | 273.6 | 269.9 | 274.5 | 274.8 | 275.3 | 275.8 | 276.1 | 272.4
| February | GWh | 255.4 | 253.8 | 255.4 | 253.3 | 253.4 | 251.6 | 254.1 | 254.6 | 254.9 | 255.3 | 255.7 | 253.8
| March | GWh | 258.6 | 257.4 | 258.6 | 256.6 | 256.7 | 252.5 | 257.5 | 257.8 | 258.2 | 258.6 | 258.9 | 254.5
| April | GWh | 232.2 | 230.9 | 232.2 | 230.3 | 230.5 | 230.2 | 231.2 | 231.4 | 231.6 | 232.1 | 232.3 | 231.8
| May | GWh | 207 | 206.1 | 209.2 | 205.7 | 205.7 | 205.9 | 206.3 | 206.5 | 206.6 | 206.9 | 207 | 207.2
| June | GWh | 163.6 | 163 | 167.8 | 162.7 | 162.8 | 162.9 | 163 | 163.2 | 163.3 | 163.5 | 163.6 | 163.8
| July | GWh | 181.5 | 180.9 | 187.9 | 180.6 | 180.8 | 180.8 | 180.9 | 181.1 | 181.2 | 181.4 | 181.5 | 181.5
| August | GWh | 183.3 | 182.7 | 189.7 | 182.4 | 182.6 | 182.6 | 182.7 | 182.9 | 183 | 183.2 | 183.3 | 183.3
| September | GWh | 182.7 | 181.8 | 189 | 181.6 | 181.7 | 182 | 182.1 | 182.3 | 182.4 | 182.6 | 182.8 | 183
| October | GWh | 206.4 | 205.4 | 212.7 | 204.9 | 205.1 | 205.3 | 205.7 | 206 | 206.1 | 206.3 | 206.6 | 206.8
| November | GWh | 233.5 | 232.3 | 239.9 | 231.7 | 232 | 232.3 | 232.6 | 232.9 | 233.2 | 233.5 | 233.8 | 234.1
| December | GWh | 274.5 | 272.9 | 280.8 | 272.2 | 272.4 | 272.8 | 273.3 | 273.6 | 274 | 274.5 | 274.9 | 275.2
| LIS Mid-load (before DSM) | GWh/year | 2654.5 | 2641.3 | 2699 | 2635.3 | 2637.3 | 2628.8 | 2643.9 | 2647.1 | 2649.8 | 2653.7 | 2656.5 | 2647.4
| NL Mid-load (before DSM) | GWh/year | 9867.3 | 9880.3 | 9934.3 | 9959.8 | 9945.3 | 9928.4 | 9981.8 | 10016.4 | 10069.3 | 10111.3 | 10039.3 | 10077.1
| Cumulative DSM | GWh/year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | NLH does not have DSM programs
| Incremental Annual DSM | GWh/year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mid-load (after DSM) | GWh/year | 9867.3 | 9880.3 | 9934.3 | 9959.8 | 9945.3 | 9928.4 | 9981.8 | 10016.4 | 10069.3 | 10111.3 | 10039.3 | 10077.1
| Annual Change in Energy Demand | GWh/year |  | 13 | 54 | 25.5 | -14.5 | -16.9 | 53.4 | 34.6 | 52.9 | 42 | -72 | 37.8 | 2019-2030 Rate | 2019-2050 Rate | Assume extended to 2051
| Percentage Change in Energy Demand | % |  | 0.1317% | 0.5465% | 0.2567% | -0.1456% | -0.1699% | 0.5379% | 0.3466% | 0.5281% | 0.4171% | -0.7121% | 0.3765% | 0.2106% | 0.2106% | Mid-load forecast for use in COPPER
Notes:
Newfoundland Power MW are purchase requirements. Annual maximum reflects average (P50) peak demand weather conditions, no load curtailed and expected NP generation.
Hydro Rural Interconnected annual maximum MW requirements reflect average (P50) peak demand weather conditions.

## FMW
NL | FORECAST PEAK DEMAND | UNITS | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2019 - 2030 | 2019-2050 | Notes
Island Interconnected System (IIS)
| January | MW | 1560.9 | 1550.4 | 1563.3 | 1564.5 | 1568.7 | 1570.9 | 1576.7 | 1582.2 | 1592.5 | 1602.8 | 1612.9 | 1623.4
| February | MW | 1501.7 | 1491.6 | 1520 | 1505.1 | 1509.2 | 1511.3 | 1516.9 | 1522.2 | 1532.1 | 1542 | 1551.7 | 1561.8
| March | MW | 1446.4 | 1436.6 | 1431.6 | 1449.5 | 1453.4 | 1455.5 | 1460.9 | 1466 | 1475.6 | 1485.1 | 1494.4 | 1504.2
| April | MW | 1255.5 | 1246.6 | 1234.7 | 1257.5 | 1260.9 | 1262.6 | 1267.3 | 1271.6 | 1279.8 | 1288.1 | 1296.2 | 1304.6
| May | MW | 1074.2 | 1066.4 | 1069.3 | 1075 | 1077.8 | 1079.2 | 1083.2 | 1086.7 | 1093.8 | 1100.7 | 1107.4 | 1114.6
| June | MW | 903.2 | 896.2 | 913.9 | 902.6 | 904.7 | 905.9 | 909.1 | 911.9 | 917.6 | 923.1 | 928.6 | 934.4
| July | MW | 768.5 | 762.4 | 786.9 | 767.1 | 768.7 | 769.6 | 772.2 | 774.5 | 779.2 | 783.7 | 788.3 | 793.1
| August | MW | 737.1 | 731 | 744.2 | 735.5 | 737 | 737.8 | 740.4 | 742.5 | 747 | 751.3 | 755.6 | 760.2
| September | MW | 861.7 | 855.2 | 826 | 861 | 863.1 | 864.2 | 867.2 | 869.8 | 875.1 | 880.2 | 885.5 | 890.9
| October | MW | 1053.6 | 1045.9 | 1048.8 | 1054.2 | 1056.8 | 1058.2 | 1062 | 1065.3 | 1072 | 1078.6 | 1085.2 | 1091.9
| November | MW | 1268.9 | 1259.9 | 1250.1 | 1270.8 | 1274.2 | 1276 | 1280.7 | 1285.1 | 1293.4 | 1301.7 | 1309.9 | 1318.4
| December | MW | 1510.2 | 1502 | 1500.6 | 1515.4 | 1519.4 | 1521.5 | 1527.4 | 1532.9 | 1542.3 | 1552.6 | 1562.5 | 1582
| IIS Mid-load (before DSM) | Maximum | 1560.9 | 1550.4 | 1563.3 | 1564.5 | 1568.7 | 1570.9 | 1576.7 | 1582.2 | 1592.5 | 1602.8 | 1612.9 | 1623.4
|  | UNITS | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Labrador Interconnected System (LIS)
| January | MW | 33 | 32.6 | 30.2 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| February | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| March | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| April | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| May | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| June | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| July | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| August | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| September | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| October | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| November | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| December | MW | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| LIS Mid-load (before DSM) | Maximum | 33 | 32.6 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NL Mid-load (before DSM) | Peak | 1560.9 | 1550.4 | 1563.3 | 1564.5 | 1568.7 | 1570.9 | 1576.7 | 1582.2 | 1592.5 | 1602.8 | 1612.9 | 1623.4
| Cumulative DSM | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | NLH does not have DSM programs
| Incremental Annual DSM | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mid-load (after DSM) | MW | 1560.9 | 1550.4 | 1563.3 | 1564.5 | 1568.7 | 1570.9 | 1576.7 | 1582.2 | 1592.5 | 1602.8 | 1612.9 | 1623.4 | 2019-2030 Rate | 2019-2030 Rate | Assume extended to 2051
| Incremental Annual DSM / Mid-load (before DSM) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.3575% | 0.3575% | Mid-load forecast for use in COPPER
Notes:
Newfoundland Power MW are purchase requirements. Annual maximum reflects average (P50) peak demand weather conditions, no load curtailed and expected NP generation.
Hydro Rural Interconnected annual maximum MW requirements reflect average (P50) peak demand weather conditions.
Labrador Industrial load does not include a forecasted load for the reactiviation of Wabush mines by Tacora Resources.
After 2021, the IIS and LIS will be interconnected, so there will no longer be separate peak demands for the two systems.

## Hourly
NL | Hourly
See Hourly2018 file in the Hourly-2018 folder
See Hourly2019 file in the Hourly-2019 folder

## Inputs
NL | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance