## README
NS | LEGEND
| NS-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| Distribution | Characteristics of existing distribution substations
| System | Miscellaneous provincial system characteristics
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review or being gathered
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to sources
See the accompanying calculations file and raw data files for additional supporting information
See the related Gitlab issue for a summary of inventory status

## NS-Sources
NS | SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| Nova Scotia Power Inc. | 2017 | 2017 Annual Capital Expenditure Plan (NSUARB M07745) NSPI Responses to SBA Information Requests | https://uarb.novascotia.ca/fmi/webd/UARB15 |  | Nova Scotia
| Nova Scotia Power Inc. | 2016 | 2016 Annual Capital Expenditure Plan (NSUARB P-128.16/M07176) IR Responses N-4 | https://uarb.novascotia.ca/fmi/webd/UARB15 [ Search M07176] |  | Nova Scotia
| Nova Scotia Power Inc. | 2018 | Hydro Asset Study | https://uarb.novascotia.ca/fmi/webd/UARB15 [Search M08984] |  | Nova Scotia
| Nova Scotia Power Inc. | 2016 | 2016 ACE Plan IR Responses Exhibits N-5. I.R. 14 Attachment | https://uarb.novascotia.ca/fmi/webd/UARB15 [Search M07176] |  | Nova Scotia
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" column of the relevant tab
| Hatch | 2008 | Nova Scotia Wind Integration Study for Nova Scotia Department of Energy | https://energy.novascotia.ca/sites/default/files/NS-Wind-Integration-Study-FINAL.pdf |  | Nova Scotia
| GE Energy Consulting | 2013 | Nova Scotia Renewable Energy Integration Study | https://www.nspower.ca/docs/default-source/pdf-to-upload/2013coss_ca_dr-14_supplemental_reisfinalreport_redacted.pdf?sfvrsn=8e797640_0 |  | Nova Scotia
| Nova Scotia Power Inc. | 2014 | 2014 ACE Plan IR Responses to NSUARB (M05998) I.R.#19 | https://uarb.novascotia.ca/fmi/webd/UARB15 [Search M05998] |  | Nova Scotia
| Nova Scotia Power Inc. | 2020 | NS Power 2020 IRP Modeling Results Release | https://irp.nspower.ca/documents/modeling-results/ |  | Nova Scotia
| Energy and Environmental Economics | 2019 | Planning Reserve Margin and Capacity Value Study | https://irp.nspower.ca/documents/pre-irp-deliverables/ |  | Nova Scotia
| Nova Scotia Power Inc. | 2020 | 2020 ACE NSPI Responses to NSUARB Information Requests | https://uarb.novascotia.ca/fmi/webd/UARB15 [Search M09499] |  | Nova Scotia
| Nova Scotia Power Inc. | 2015 | 2015 ACE NSPI Responses to SBA Information Requests | https://uarb.novascotia.ca/fmi/webd/UARB15 [Search M06514] |  | Nova Scotia
| Nova Scotia Power Inc. | 2019 | How We Make Electricity | https://www.nspower.ca/en/home/about-us/how-we-make-electricity/default.aspx |  | Nova Scotia
| Nova Scotia Power Inc. | 2019 | Hydro Station Map | https://www.nspower.ca/en/home/about-us/how-we-make-electricity/renewable-electricity/hydro-station-map.aspx |  | Nova Scotia
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | National
| Nova Scotia Power Inc. | 2019 | Wind Farm Directory | https://www.nspower.ca/en/home/about-us/how-we-make-electricity/renewable-electricity/wind-farm-directory.aspx |  | Nova Scotia
| Nova Scotia Power Inc. | 2019 | Wind Power Map | https://www.nspower.ca/en/home/about-us/how-we-make-electricity/renewable-electricity/wind-farm-map.aspx |  | Nova Scotia
| Nova Scotia Power Inc. | 2019 | Nova Scotia Power Final Pre-IRP Report | https://irp.nspower.ca/documents/pre-irp-deliverables/ |  | Nova Scotia
| Nova Scotia Power Inc. | 2018 | 10-Year System Outlook [2018 to 2020] | http://oasis.nspower.ca/en/home/oasis/forecasts-and-assessments.aspx |  | Nova Scotia
| Nova Scotia Power Inc. | 2018 | 2019 Load Forecast Report | https://uarb.novascotia.ca/fmi/webd/UARB15 [Search M09191] |  | Nova Scotia
| Nova Scotia Power Inc. | 2019 | 2019 System Average Transmission Loss Factor | http://oasis.nspower.ca/en/home/oasis/system-reports-and-messages/default.aspx |  | Nova Scotia
| Nova Scotia Power Inc. | 2020 | Annual Capital Expenditure Plan [2010 through 2020] | https://nsuarb.novascotia.ca/mandates/electricity/nova-scotia-power-capital-expenditures |  | Nova Scotia
| Nova Scotia Power Maritime Link | 2013 | Maritime Link Project. Responses to Canadian Wind Energy Association Information Requests | https://uarb.novascotia.ca/fmi/webd/UARB15 [NSUARB ML-2013-01] |  | Nova Scotia
| Nova Scotia Power Inc. | 2016 | 2016 ACE Plan IR Responses Exhibits N-4 | https://uarb.novascotia.ca/fmi/webd/UARB15 [Search M07176] |  | Nova Scotia
| Minas Energy | 2019 | Ellerhouse Wind Farm | https://www.minasenergy.com/ellershouse-wind-farm |  | Nova Scotia
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Nova Scotia Power Inc. | 2020 | 2020 Integrated Resource Plan (IRP): Final Assumptions Set | https://irp.nspower.ca/files/key-documents/NS-Power-IRP-Appendices-A-N.pdf
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
NS | EXISTING GENERATION | [12 empty] | DESIGN | [7 empty] | OPERATIONS | [13 empty] | OPERATING COSTS
| Project Name | Gen Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Unit | # of units | Inc Heat Rate @ Max | Minimum Capacity | Maximum Capacity | Minimum Up Time | Minimum Down Time | Spin Up Ramp Rate | Spin Down Ramp Rate | Start Up Ramp Limit | Shut Down Ramp Limit | Must Run | Operating Reserve Fraction | Outage Duration | Forced Outage Rate | Maintenance Outage Rate | Start Up Costs | Fuel Costs | Shut Down Costs | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | (kV) |  |  |  |  | (MW) |  | (MW) | (%) | (GWh/year) |  | (MMBtu/MWh) | (MW) | (MW) | (hours) | (hours) | (%/min) | (%/min) | [MW/hr p MWcap] | [MW/hr p MWcap] | (T/F) | (%) | (hours) | (%) | (days/y) | (S/MWcap) | ($/MWh) | (S/MWcap) | ($/MWh) | ($/MWh)
| Highway 101 Landfill | NS_HLF00_GEN | Highland Energy Inc | Sackville | 44.8112 | -63.7758 | Nova Scotia.a | Mainland | Sackville 90H | NS_90H_DSS | 69 | 2008 | 2100 | Biogas | biomass | 2 | 95% | 1.9 | 36.67% | 6.424 | 1
| Brooklyn Energy Centre | NS_BEC00_GEN | Emera Energy | Brooklyn | 44.0515 | -64.6956 | Nova Scotia.a | Mainland | Milton 50W | NS_50W_DSS | 69 | 1995 | 2100 | Biomass | biomass | 30 | 95% | 28.5 | 36.67% | 96.36 | 1
| Port Hawkesbury Biomass | NS_PHB00_GEN | Nova Scotia Power Inc. | Port Hawkesbury, CBI | 45.5982 | -61.3601 | Nova Scotia.a | Cape Breton | St. Peters 59C | NS_59C_DSS | 69 | 2013 | 2100 | Biomass | biomass | 63.8 | 70% | 44.66 | 36.67% | 204.9256 | 1 | [9 empty] | T
| Taylor Lumber | NS_TYL00_GEN | F W Taylor Ltd. | Upper Musquodoboit | 45.0447 | -63.1389 | Nova Scotia.a | Mainland | Upper Musquodoboit 88H | NS_88H_DSS | 69 | 1995 | 2100 | Biomass | biomass | 1.2 | 95% | 1.14 | 36.67% | 3.8544 | 1
| Lingan_01 | NS_LGN01_GEN | Nova Scotia Power Inc. | Lingan, CBI | 46.2394 | -60.038 | Nova Scotia.a | Cape Breton | Lingan 88S | NS_88S_GSS | 230 | 1979 | 2039 | Coal | coal | 150 | 90% | 135 | 55.78% | 732.92 | 4 | 10.237 | 70 | 146.5 | 24 | 24 | no cycling | no cycling | no cycling | no cycling |  | 20% |  | 2.5 | 24
| Lingan_02 | NS_LGN02_GEN | Nova Scotia Power Inc. | Lingan, CBI | 46.2394 | -60.038 | Nova Scotia.a | Cape Breton | Lingan 88S | NS_88S_GSS | 230 | 1980 | 2020 | Coal | coal | 150 | 90% | 135 | 38.78% | 509.54 | 4 | 10.246 | 70 | 146.5 | 24 | 24 | no cycling | no cycling | no cycling | no cycling |  | 20% |  | 2.5 | 24
| Lingan_03 | NS_LGN03_GEN | Nova Scotia Power Inc. | Lingan, CBI | 46.2394 | -60.038 | Nova Scotia.a | Cape Breton | Lingan 88S | NS_88S_GSS | 230 | 1983 | 2039 | Coal | coal | 150 | 90% | 135 | 48.22% | 633.64 | 4 | 10.19 | 70 | 149.7 | 24 | 24 | no cycling | no cycling | no cycling | no cycling | T | 19% |  | 2.5 | 24
| Lingan_04 | NS_LGN04_GEN | Nova Scotia Power Inc. | Lingan, CBI | 46.2394 | -60.038 | Nova Scotia.a | Cape Breton | Lingan 88S | NS_88S_GSS | 230 | 1984 | 2039 | Coal | coal | 153 | 90% | 137.7 | 56.22% | 753.5352 | 4 | 10.037 | 70 | 146.5 | 24 | 24 | no cycling | no cycling | no cycling | no cycling |  | 20% |  | 2.5 | 24
| Point Aconi Coal | NS_PAC00_GEN | Nova Scotia Power Inc. | Point Aconi, CBI | 46.3207 | -60.3302 | Nova Scotia.a | Cape Breton | Point Aconi 102S | NS_89S_DSS | 230 | 1994 | 2039 | Coal | coal | 165 | 90% | 148.5 | 74.56% | 1077.626 | 1 | 10.591 | 60 | 169.9 | 24 | 24 | no cycling | no cycling | no cycling | no cycling | T | 0% |  | 3 | 28
| Point Tupper Coal | NS_PTC00_GEN | Nova Scotia Power Inc. | Point Tupper, CBI | 45.5879 | -61.3486 | Nova Scotia.a | Cape Breton | Point Tupper 1C | NS_1C_DFS | 138 | 1987 | 2039 | Coal | coal | 150 | 90% | 135 | 68.33% | 897.9 | 1 | 9.855 | 65 | 149.4 | 24 | 24 | no cycling | no cycling | no cycling | no cycling |  | 53% |  | 2 | 21
| Trenton_05 | NS_TRT05_GEN | Nova Scotia Power Inc. | Trenton | 45.6201 | -62.6482 | Nova Scotia.a | Mainland | Trenton 50N | NS_50N_DFS | 138 | 1969 | 2035 | Coal | coal | 150 | 90% | 135 | 48.78% | 640.94 | 2 | 9.993 | 70 | 139.7 | 16 | 24 | no cycling | no cycling | no cycling | no cycling |  | 37% |  | 4 | 28 | [6 empty] | Summer Capacity = 135 MW
| Trenton_06 | NS_TRT06_GEN | Nova Scotia Power Inc. | Trenton | 45.6201 | -62.6482 | Nova Scotia.a | Mainland | Trenton 50N | NS_50N_DFS | 138 | 1991 | 2039 | Coal | coal | 160 | 90% | 144 | 78.22% | 1096.3627 | 2 | 10.007 | 70 | 155.4 | 16 | 24 | no cycling | no cycling | no cycling | no cycling |  | 13% |  | 2.5 | 21
| Avon_01 | NS_AVO01_GEN | Nova Scotia Power Inc. | Windsor | 44.8815 | -64.2173 | Nova Scotia.a | Mainland | Avon 1V | NS_1V_GSS | 69 | 1958 | 2100 | Hydro_daily | hydro_daily | 3.75 | 95% | 3.5625 | 43.33% | 14.235 | 2 |  | 0 | 3.75
| Avon_02 | NS_AVO02_GEN | Nova Scotia Power Inc. | Windsor | 44.8815 | -64.2173 | Nova Scotia.a | Mainland | Avon 1V | NS_1V_GSS | 69 | 1929 | 2100 | Hydro_daily | hydro_daily | 3 | 95% | 2.85 | 43.33% | 11.388 | 2 |  | 0 | 3
| Bear River_01 (Gulch) | NS_BER01_GEN | Nova Scotia Power Inc. | Digby | 44.5672 | -65.6346 | Nova Scotia.a | Mainland | Gulch 13V | NS_13V_DFS | 69 | 1952 | 2100 | Hydro_daily | hydro_daily | 6.2 | 95% | 5.89 | 31.67% | 17.1988 | 3 |  | 0 | 6.2
| Bear River_02 (Ridge) | NS_BER02_GEN | Nova Scotia Power Inc. | Digby | 44.5538 | -65.583 | Nova Scotia.a | Mainland | Ridge 14V | NS_14V_GSS | 69 | 1957 | 2100 | Hydro_daily | hydro_daily | 4.1 | 95% | 3.895 | 31.67% | 11.3734 | 3 |  | 0 | 4.1
| Bear River_03 (Fourth Lake) | NS_BER03_GEN | Nova Scotia Power Inc. | Digby | 44.3696 | -65.7193 | Nova Scotia.a | Mainland | Fourth Lake 91V | NS_91V_GSS | 69 | 1983 | 2100 | Hydro_daily | hydro_daily | 3.1 | 95% | 2.945 | 31.67% | 8.5994 | 3 |  | 0 | 3.1
| Black River_01 (Methals) | NS_BLR01_GEN | Nova Scotia Power Inc. | Kentville | 44.9397 | -64.4315 | Nova Scotia.a | Mainland | Methals 7V | NS_7V_GSS | 69 | 1949 | 2100 | Hydro_daily | hydro_daily | 3.5 | 95% | 3.325 | 43.67% | 13.3882 | 6 |  | 0.9 | 3.5
| Black River_02 (Hollow Bridge) | NS_BLR02_GEN | Nova Scotia Power Inc. | Kentville | 45.0036 | -64.3764 | Nova Scotia.a | Mainland | Hollow Bridge 6V | NS_6V_GSS | 69 | 1942 | 2100 | Hydro_daily | hydro_daily | 5.5 | 95% | 5.225 | 43.67% | 21.0386 | 6 |  | 1.5 | 5.5
| Black River_03 (Lumsden) | NS_BLR03_GEN | Nova Scotia Power Inc. | Kentville | 45.0275 | -64.3967 | Nova Scotia.a | Mainland | Lumsden 5V | NS_5V_GSS | 69 | 1940 | 2100 | Hydro_daily | hydro_daily | 2.9 | 95% | 2.755 | 43.67% | 11.0931 | 6 |  | 0.8 | 2.9
| Black River_04 (Hell's Gate 1) | NS_BLR04_GEN | Nova Scotia Power Inc. | Kentville | 45.0466 | -64.4121 | Nova Scotia.a | Mainland | Hells Gate 3V | NS_3V_GSS | 69 | 1930 | 2100 | Hydro_daily | hydro_daily | 3.5 | 95% | 3.325 | 43.67% | 13.3882 | 6 |  | 0.9 | 3.5
| Black River_05 (Hell's Gate 2) | NS_BLR05_GEN | Nova Scotia Power Inc. | Kentville | 45.0466 | -64.4121 | Nova Scotia.a | Mainland | Hells Gate 3V | NS_3V_GSS | 69 | 1949 | 2100 | Hydro_daily | hydro_daily | 3.7 | 95% | 3.515 | 43.67% | 14.1532 | 6 |  | 1 | 3.7
| Black River_06 (White Rock) | NS_BLR06_GEN | Nova Scotia Power Inc. | Kentville | 45.0623 | -64.3807 | Nova Scotia.a | Mainland | White Rock 4V | NS_4V_GSS | 69 | 1952 | 2100 | Hydro_daily | hydro_daily | 3.4 | 95% | 3.23 | 43.67% | 13.0057 | 6 |  | 0.9 | 3.4
| Dickie Brook | NS_DBK00_GEN | Nova Scotia Power Inc. | Guysborough | 45.3492 | -61.5032 | Nova Scotia.a | Mainland | Dickie Brook 24C | NS_24C_DFS | 69 | 1948 | 2100 | Hydro_daily | hydro_daily | 3.8 | 95% | 3.61 | 20.33% | 6.7686 | 2 |  | 0.03 | 1.2
| Lequille | NS_LQL00_GEN | Nova Scotia Power Inc. | Annapolis Royal | 44.7267 | -65.4967 | Nova Scotia.a | Mainland | Lequille 12V | NS_12V_GSS | 69 | 1968 | 2100 | Hydro_daily | hydro_daily | 11.2 | 95% | 10.64 | 26.67% | 26.1632 | 1 |  | 0 | 11.2
| Lower St. Croix | NS_LSX00_GEN | Minas Basin Pulp and Paper Co Ltd | St. Croix River | 44.9613 | -64.0331 | Nova Scotia.a | Mainland | St. Croix 17V | NS_17V_DSS | 69 | 1935 | 2100 | Hydro_daily | hydro_daily | 3 | 95% | 2.85 | 60.67% | 15.9432 | 1 | [19 empty] | https://www.minasenergy.com/st-croix-hydro
| Mersey_01 (Upper Lake Falls 1) | NS_MSY01_GEN | Nova Scotia Power Inc. | Liverpool | 44.1574 | -64.9984 | Nova Scotia.a | Mainland | Upper Lake Falls 1W | NS_1W_GSS | 69 | 1929 | 2100 | Hydro_daily | hydro_daily | 2.7 | 95% | 2.565 | 60.67% | 14.3489 | 2 |  | 0.4 | 2.7
| Mersey_02 (Upper Lake Falls 2) | NS_MSY02_GEN | Nova Scotia Power Inc. | Liverpool | 44.1574 | -64.9984 | Nova Scotia.a | Mainland | Upper Lake Falls 1W | NS_1W_GSS | 69 | 1929 | 2100 | Hydro_daily | hydro_daily | 2.7 | 95% | 2.565 | 60.67% | 14.3489 | 2 |  | 0.4 | 2.7
| Mersey_03 (Lower Lake Falls 1) | NS_MSY03_GEN | Nova Scotia Power Inc. | Liverpool | 44.1577 | -64.9772 | Nova Scotia.a | Mainland | Lower Lake Falls 2W | NS_2W_GSS | 69 | 1929 | 2100 | Hydro_daily | hydro_daily | 3.7 | 95% | 3.515 | 60.67% | 19.6633 | 2 |  | 0.5 | 3.7
| Mersey_04 (Lower Lake Falls 2) | NS_MSY04_GEN | Nova Scotia Power Inc. | Liverpool | 44.1577 | -64.9772 | Nova Scotia.a | Mainland | Lower Lake Falls 2W | NS_2W_GSS | 69 | 1929 | 2100 | Hydro_daily | hydro_daily | 3.7 | 95% | 3.515 | 60.67% | 19.6633 | 2 |  | 0.5 | 3.7
| Mersey_05 (Big Falls 1) | NS_MSY05_GEN | Nova Scotia Power Inc. | Liverpool | 44.138 | -64.9353 | Nova Scotia.a | Mainland | Big Falls 3W | NS_3W_GSS | 69 | 1929 | 2100 | Hydro_daily | hydro_daily | 4.5 | 95% | 4.275 | 60.67% | 23.9148 | 2 |  | 0.65 | 4.5
| Mersey_06 (Big Falls 2) | NS_MSY06_GEN | Nova Scotia Power Inc. | Liverpool | 44.138 | -64.9353 | Nova Scotia.a | Mainland | Big Falls 3W | NS_3W_GSS | 69 | 1929 | 2100 | Hydro_daily | hydro_daily | 4.5 | 95% | 4.275 | 60.67% | 23.9148 | 2 |  | 0.65 | 4.5
| Mersey_07 (Lower Great Brook 1) | NS_MSY07_GEN | Nova Scotia Power Inc. | Liverpool | 44.09 | -64.848 | Nova Scotia.a | Mainland | Lower Great Brook 4W | NS_4W_GSS | 69 | 1955 | 2100 | Hydro_daily | hydro_daily | 2.25 | 95% | 2.1375 | 60.67% | 11.9574 | 2 |  | 0.3 | 2.25
| Mersey_08 (Lower Great Brook 2) | NS_MSY08_GEN | Nova Scotia Power Inc. | Liverpool | 44.09 | -64.848 | Nova Scotia.a | Mainland | Lower Great Brook 4W | NS_4W_GSS | 69 | 1955 | 2100 | Hydro_daily | hydro_daily | 2.25 | 95% | 2.1375 | 60.67% | 11.9574 | 2 |  | 0.3 | 2.25
| Mersey_09 (Deep Brook 1) | NS_MSY09_GEN | Nova Scotia Power Inc. | Liverpool | 44.0805 | -64.7909 | Nova Scotia.a | Mainland | Milton 50W | NS_50W_DSS | 69 | 1950 | 2100 | Hydro_daily | hydro_daily | 4.5 | 95% | 4.275 | 60.67% | 23.9148 | 2 |  | 0.65 | 4.5
| Mersey_10 (Deep Brook 2) | NS_MSY10_GEN | Nova Scotia Power Inc. | Liverpool | 44.0805 | -64.7909 | Nova Scotia.a | Mainland | Milton 50W | NS_50W_DSS | 69 | 1950 | 2100 | Hydro_daily | hydro_daily | 4.5 | 95% | 4.275 | 60.67% | 23.9148 | 2 |  | 0.65 | 4.5
| Mersey_11(Cowie Falls 1) | NS_MSY11_GEN | Nova Scotia Power Inc. | Liverpool | 44.0744 | -64.7707 | Nova Scotia.a | Mainland | Milton 50W | NS_50W_DSS | 69 | 1938 | 2100 | Hydro_daily | hydro_daily | 3.6 | 95% | 3.42 | 60.67% | 19.1318 | 2 |  | 0.5 | 3.6
| Mersey_12 (Cowie Falls 2) | NS_MSY12_GEN | Nova Scotia Power Inc. | Liverpool | 44.0744 | -64.7707 | Nova Scotia.a | Mainland | Milton 50W | NS_50W_DSS | 69 | 1938 | 2100 | Hydro_daily | hydro_daily | 3.6 | 95% | 3.42 | 60.67% | 19.1318 | 2 |  | 0.5 | 3.6
| Nictaux | NS_NTX00_GEN | Nova Scotia Power Inc. | Annapolis Royal | 44.9091 | -65.0299 | Nova Scotia.a | Mainland | Nictaux 10V | NS_10V_GSS | 69 | 1954 | 2100 | Hydro_daily | hydro_daily | 8.3 | 95% | 7.885 | 52.33% | 38.0505 | 1
| Paradise | NS_PRD00_GEN | Nova Scotia Power Inc. | Annapolis Royal | 44.8117 | -65.2186 | Nova Scotia.a | Mainland | Paradise 11V | NS_11V_DSS | 69 | 1950 | 2100 | Hydro_daily | hydro_daily | 4.7 | 95% | 4.465 | 56.67% | 23.3308 | 1
| Sheet Harbour_01 (Ruth Falls 1) | NS_SHH01_GEN | Nova Scotia Power Inc. | Sheet Harbour | 44.9341 | -62.5005 | Nova Scotia.a | Mainland | Ruth Falls 96H | NS_96H_DSS | 69 | 1925 | 2100 | Hydro_daily | hydro_daily | 2.3 | 95% | 2.185 | 53.67% | 10.8128 | 3 |  | 0.1 | 2.3
| Sheet Harbour_02 (Ruth Falls 2) | NS_SHH02_GEN | Nova Scotia Power Inc. | Sheet Harbour | 44.9341 | -62.5005 | Nova Scotia.a | Mainland | Ruth Falls 96H | NS_96H_DSS | 69 | 1925 | 2100 | Hydro_daily | hydro_daily | 2.8 | 95% | 2.66 | 53.67% | 13.1634 | 3 |  | 0.1 | 2.8
| Sheet Harbour_03 (Ruth Falls 3) | NS_SHH03_GEN | Nova Scotia Power Inc. | Sheet Harbour | 44.9341 | -62.5005 | Nova Scotia.a | Mainland | Ruth Falls 96H | NS_96H_DSS | 69 | 1936 | 2100 | Hydro_daily | hydro_daily | 2.3 | 95% | 2.185 | 53.67% | 10.8128 | 3 |  | 0.1 | 2.3
| Sheet Harbour_04 (Malay Falls 1) | NS_SHH04_GEN | Nova Scotia Power Inc. | Sheet Harbour | 44.9877 | -62.4841 | Nova Scotia.a | Mainland | Malay Falls 95H | NS_95H_GSS | 69 | 1924 | 2100 | Hydro_daily | hydro_daily | 1.15 | 95% | 1.0925 | 53.67% | 5.4064 | 3 |  | 0.03 | 1.15
| Sheet Harbour_05 (Malay Falls 2) | NS_SHH05_GEN | Nova Scotia Power Inc. | Sheet Harbour | 44.9877 | -62.4841 | Nova Scotia.a | Mainland | Malay Falls 95H | NS_95H_GSS | 69 | 1924 | 2100 | Hydro_daily | hydro_daily | 1.15 | 95% | 1.0925 | 53.67% | 5.4064 | 3 |  | 0.03 | 1.15
| Sheet Harbour_06 (Malay Falls 3) | NS_SHH06_GEN | Nova Scotia Power Inc. | Sheet Harbour | 44.9877 | -62.4841 | Nova Scotia.a | Mainland | Malay Falls 95H | NS_95H_GSS | 69 | 1924 | 2100 | Hydro_daily | hydro_daily | 1.1 | 95% | 1.045 | 53.67% | 5.1713 | 3 |  | 0.03 | 1.1
| Sissiboo_01 | NS_SBO01_GEN | Nova Scotia Power Inc. | Digby | 44.4308 | -65.8722 | Nova Scotia.a | Mainland | Sissiboo 15V | NS_15V_GSS | 69 | 1961 | 2100 | Hydro_daily | hydro_daily | 5 | 95% | 4.75 | 35.33% | 15.476 | 1 |  | 1.2 | 5
| Sissiboo_02 (Weymouth 1) | NS_SBO02_GEN | Nova Scotia Power Inc. | Digby | 44.4075 | -65.9491 | Nova Scotia.a | Mainland | Weymouth 16V | NS_16V_GSS | 69 | 1961 | 2100 | Hydro_daily | hydro_daily | 9.5 | 95% | 9.025 | 35.33% | 29.4044 | 2 |  | 2.4 | 9.5
| Sissiboo_03 (Weymouth 2) | NS_SBO03_GEN | Nova Scotia Power Inc. | Digby | 44.4075 | -65.9491 | Nova Scotia.a | Mainland | Weymouth 16V | NS_16V_GSS | 69 | 1967 | 2100 | Hydro_daily | hydro_daily | 9.5 | 95% | 9.025 | 35.33% | 29.4044 | 2 |  | 2.4 | 9.5
| St. Margarets_01 (Mill Lake 1) | NS_STM01_GEN | Nova Scotia Power Inc. | Hubbards | 44.7116 | -63.8962 | Nova Scotia.a | Mainland | Tidewater 92H | NS_92H_GSS | 138 | 1922 | 2100 | Hydro_daily | hydro_daily | 1.3 | 95% | 1.235 | 22% | 2.5054 | 2 |  | 0 | 1.3
| St. Margarets_02 (Mill Lake 2) | NS_STM02_GEN | Nova Scotia Power Inc. | Hubbards | 44.7116 | -63.8962 | Nova Scotia.a | Mainland | Tidewater 92H | NS_92H_GSS | 138 | 1922 | 2100 | Hydro_daily | hydro_daily | 1.3 | 95% | 1.235 | 22% | 2.5054 | 2 |  | 0 | 1.3
| St. Margarets_03 (Sandy Lake 1) | NS_STM03_GEN | Nova Scotia Power Inc. | Hubbards | 44.7116 | -63.896 | Nova Scotia.a | Mainland | Tidewater 92H | NS_92H_GSS | 138 | 1928 | 2100 | Hydro_daily | hydro_daily | 1.8 | 95% | 1.71 | 22% | 3.469 | 2 |  | 0 | 1.8
| St. Margarets_04 (Sandy Lake 2) | NS_STM04_GEN | Nova Scotia Power Inc. | Hubbards | 44.7116 | -63.896 | Nova Scotia.a | Mainland | Tidewater 92H | NS_92H_GSS | 138 | 1928 | 2100 | Hydro_daily | hydro_daily | 1.8 | 95% | 1.71 | 22% | 3.469 | 2 |  | 0 | 1.8
| St. Margarets_05 (Tidewater 1) | NS_STM05_GEN | Nova Scotia Power Inc. | Hubbards | 44.6914 | -63.8913 | Nova Scotia.a | Mainland | Tidewater 92H | NS_92H_GSS | 138 | 1922 | 2100 | Hydro_daily | hydro_daily | 2.3 | 95% | 2.185 | 22% | 4.4326 | 2 |  | 0 | 2.3
| St. Margarets_06 (Tidewater 2) | NS_STM06_GEN | Nova Scotia Power Inc. | Hubbards | 44.6914 | -63.8913 | Nova Scotia.a | Mainland | Tidewater 92H | NS_92H_GSS | 138 | 1922 | 2100 | Hydro_daily | hydro_daily | 2.3 | 95% | 2.185 | 22% | 4.4326 | 2 |  | 0 | 2.3
| Tusket | NS_TSK00_GEN | Nova Scotia Power Inc. | Barrington | 43.8821 | -65.9778 | Nova Scotia.a | Mainland | Tusket 9W | NS_9W_GSS | 69 | 1929 | 2100 | Hydro_daily | hydro_daily | 2.4 | 95% | 2.28 | 55.33% | 11.6333 | 3 |  | 0.3 | 0.8
| Upper St. Croix | NS_USX00_GEN | Minas Basin Pulp and Paper Co Ltd | Panuke Lake | 44.9267 | -64.0394 | Nova Scotia.a | Mainland | St. Croix 17V | NS_17V_DSS | 69 | 1935 | 2100 | Hydro_daily | hydro_daily | 2 | 95% | 1.9 | 60.67% | 10.6288 | 1 | [19 empty] | https://www.minasenergy.com/st-croix-hydro
| Wreck Cove_01 | NS_WRC01_GEN | Nova Scotia Power Inc. | Wreck Cove, CBI | 46.5677 | -60.5252 | Nova Scotia.a | Cape Breton | Wreck Cove 85S | NS_85S_DFS | 138 | 1982 | 2100 | Hydro_daily | hydro_daily | 106 | 95% | 100.7 | 16.33% | 151.6648 | 1 |  | 0 | 106
| Wreck Cove_02 | NS_WRC02_GEN | Nova Scotia Power Inc. | Wreck Cove, CBI | 46.5314 | -60.4402 | Nova Scotia.a | Cape Breton | Wreck Cove 85S | NS_85S_DFS | 138 | 1978 | 2100 | Hydro_daily | hydro_daily | 106 | 95% | 100.7 | 16.33% | 151.6648 | 2 |  | 0 | 106
| Wreck Cove_03 (Gisborne) | NS_WRC03_GEN | Nova Scotia Power Inc. | Wreck Cove, CBI | 46.5314 | -60.4402 | Nova Scotia.a | Cape Breton | Wreck Cove 85S | NS_85S_DFS | 138 | 1978 | 2100 | Hydro_daily | hydro_daily | 3.5 | 95% | 3.325 | 16.33% | 5.0078 | 2 |  | 0 | 3.5
| CONTRACTED - NS-NL | NL_NSNL100_GEN | Nova Scotia Power Inc. | NS-NL Border | 46.9965 | -59.44 | Nova Scotia.a | Cape Breton | IPT Woodbine | PP_NSNL1_IPT | 345 | 2020 | 2055 | Hydro_monthly | hydro_monthly | 153 | 98% | 149.94 | 66.7% | 893.9668 | 1 |  | 0 | 153 | [17 empty] | Energy includes only the Base Block in the contract
| Annapolis Tidal | NS_ANT00_GEN | Nova Scotia Power Inc. | Annapolis Royal | 44.753 | -65.5119 | Nova Scotia.a | Mainland | Cornwallis 74V | NS_74V_DSS | 69 | 1984 | 2100 | Hydro_run | hydro_run | 19 | 12% | 2.28 | 13.2% | 21.9701 | 1 |  | 0 | 19
| Tufts Cove_06 | NS_TFT06_GEN | Nova Scotia Power Inc. | Dartmouth | 44.6768 | -63.5959 | Nova Scotia.a | Mainland | Tuft's Cove 91H | NS_91H_GSS | 138 | 2012 | 2100 | NG_CC | gasCC | 49 | 73% | 35.77 | 23.89% | 102.5407 | 6 | 8.256 | 0 | 50 | 6 | 16 | [5 empty] | 25% |  | 4 | 7
| Tufts Cove_04 | NS_TFT04_GEN | Nova Scotia Power Inc. | Dartmouth | 44.6768 | -63.5959 | Nova Scotia.a | Mainland | Tuft's Cove 91H | NS_91H_GSS | 138 | 2003 | 2100 | NG_CT | gasSC | 47 | 93% | 43.71 | 52.78% | 217.2967 | 6 | 9.826 | 0 | 49 | 1 | 16 | [5 empty] | 49% |  | 4 | 7 | [6 empty] | Summer Capacity = 47 MW
| Tufts Cove_05 | NS_TFT05_GEN | Nova Scotia Power Inc. | Dartmouth | 44.6768 | -63.5959 | Nova Scotia.a | Mainland | Tuft's Cove 91H | NS_91H_GSS | 138 | 2005 | 2100 | NG_CT | gasSC | 47 | 93% | 43.71 | 51% | 209.9772 | 6 | 9.826 | 0 | 49 | 1 | 16 | [5 empty] | 49% |  | 4 | 7 | [6 empty] | Summer capacity = 47 MW
| Burnside_01 | NS_BSD01_GEN | Nova Scotia Power Inc. | Dartmouth | 44.7136 | -63.5826 | Nova Scotia.a | Mainland | Burnside 14H | NS_14H_GSS | 138 | 1976 | 2100 | Oil_CT | diesel | 30 | 78% | 23.4 | 1% | 2.628 | 4 | 11.678 | 0 | 33 | 0 | 0 | [5 empty] | 50 |  | 10 | 21 | [6 empty] | Summer Capacity = 25 MW
| Burnside_02 | NS_BSD02_GEN | Nova Scotia Power Inc. | Dartmouth | 44.7136 | -63.5826 | Nova Scotia.a | Mainland | Burnside 14H | NS_14H_GSS | 138 | 1976 | 2100 | Oil_CT | diesel | 30 | 78% | 23.4 | 1% | 2.628 | 4 | 11.678 | 0 | 33 | 0 | 0 | [5 empty] | 50 |  | 10 | 21 | [6 empty] | Summer Capacity = 25 MW
| Burnside_03 | NS_BSD03_GEN | Nova Scotia Power Inc. | Dartmouth | 44.7136 | -63.5826 | Nova Scotia.a | Mainland | Burnside 14H | NS_14H_GSS | 138 | 1976 | 2100 | Oil_CT | diesel | 30 | 78% | 23.4 | 1% | 2.628 | 4 | 11.678 | 0 | 33 | 0 | 0 | [5 empty] | 50 |  | 10 | 21 | [6 empty] | Summer Capacity = 25 MW
| Burnside_04 | NS_BSD04_GEN | Nova Scotia Power Inc. | Dartmouth | 44.7136 | -63.5826 | Nova Scotia.a | Mainland | Burnside 14H | NS_14H_GSS | 138 | 1976 | 2100 | Oil_CT | diesel | 30 | 78% | 23.4 | 1% | 2.628 | 4 | 11.678 | 0 | 33 | 0 | 0 | [5 empty] | 50 |  | 10 | 21 | [6 empty] | Summer Capacity = 25 MW
| Tusket Oil | NS_TSO00_GEN | Nova Scotia Power Inc. | Tusket | 43.8697 | -65.9684 | Nova Scotia.a | Mainland | Tusket Oil 10W | NS_10W_GSS | 69 | 2020 | 2100 | Oil_CT | diesel | 33 | 78% | 25.74 | 1% | 2.8908 | 1 | 13.435 | 0 | 25 | 0 | 0 | [5 empty] | 50% |  | 10 | 21 | [6 empty] | Summer Capacity = 21 MW
| Victoria Junction_01 | NS_VCJ01_GEN | Nova Scotia Power Inc. | Victoria Junction | 46.1681 | -60.1054 | Nova Scotia.a | Cape Breton | Victoria Junction 83S | NS_83S_GSS | 138 | 1975 | 2100 | Oil_CT | diesel | 30 | 78% | 23.4 | 1% | 2.628 | 2 | 11.678 | 0 | 33 | 0 | 0 | [5 empty] | 50% |  | 10 | 21 | [6 empty] | Summer Capacity = 25 MW
| Victoria Junction_02 | NS_VCJ02_GEN | Nova Scotia Power Inc. | Victoria Junction | 46.1681 | -60.1054 | Nova Scotia.a | Cape Breton | Victoria Junction 83S | NS_83S_GSS | 138 | 1975 | 2100 | Oil_CT | diesel | 30 | 78% | 23.4 | 1% | 2.628 | 2 | 11.678 | 0 | 33 | 0 | 0 | [5 empty] | 50% |  | 10 | 21 | [6 empty] | Summer Capacity = 25 MW
| Tufts Cove_01 | NS_TFT01_GEN | Nova Scotia Power Inc. | Dartmouth | 44.6768 | -63.5959 | Nova Scotia.a | Mainland | Tuft's Cove 91H | NS_91H_GSS | 138 | 2000 | 2025 | Oil_ST | diesel | 100 | 73% | 73 | 34.67% | 303.68 | 6 | 10.711 | 45 | 77 | 16 | 16 |  |  | no cycling | no cycling |  | 0% |  | 2 | 14
| Tufts Cove_02 | NS_TFT02_GEN | Nova Scotia Power Inc. | Dartmouth | 44.6768 | -63.5959 | Nova Scotia.a | Mainland | Tuft's Cove 91H | NS_91H_GSS | 138 | 2000 | 2032 | Oil_ST | diesel | 100 | 73% | 73 | 39.78% | 348.4533 | 6 | 10.668 | 30 | 88.4 | 8 | 16 | [5 empty] | 33% |  | 2 | 14
| Tufts Cove_03 | NS_TFT03_GEN | Nova Scotia Power Inc. | Dartmouth | 44.6768 | -63.5959 | Nova Scotia.a | Mainland | Tuft's Cove 91H | NS_91H_GSS | 138 | 2000 | 2036 | Oil_ST | diesel | 150 | 73% | 109.5 | 43.67% | 573.78 | 6 | 10.23 | 40 | 139.7 | 8 | 16 | [5 empty] | 61% |  | 2 | 14
| Amherst | NS_AMH00_GEN | Amherst Wind Power LP | Amherst | 45.8267 | -64.2417 | Nova Scotia.a | Mainland | Amherst 92N | NS_92N_GSS | 138 | 2012 | 2032 | Wind_Onshore | wind | 30 | 19% | 5.7 | 35.2% | 92.5056
| Amherst Community Wind | NS_ACW00_GEN | Mi'kmaq Wind4All Communities Limited Partnership | Amherst | 45.83 | -64.144 | Nova Scotia.a | Mainland | Amherst 92N | NS_92N_GSS | 138 | 2017 | 2037 | Wind_Onshore | wind | 6 | 19% | 1.14 | 35.2% | 18.5011
| Aulds Mountain | NS_AUM00_GEN | BA Wind Limited Partnership (Natural Forces Wind Inc.) | Antigonish | 45.5949 | -62.3745 | Nova Scotia.a | Mainland | Lochaber Road 4C | NS_4C_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 4.6 | 19% | 0.874 | 35.2% | 14.1842
| Avondale | NS_AVD00_GEN | Avondale Community Wind Park Limited Partnership | Windsor | 45.633 | -62.2784 | Nova Scotia.a | Mainland | Three Mile Plains 79V | NS_79V_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 1.6 | 19% | 0.304 | 35.2% | 4.9336
| Baddeck | NS_BDK00_GEN | ScotianWEB II Limited Partnership | Baddeck | 46.147 | -60.6962 | Nova Scotia.a | Cape Breton | Baddeck 104S | NS_104S_DFS | 138 | 2017 | 2037 | Wind_Onshore | wind | 1.7 | 19% | 0.323 | 35.2% | 5.242
| Barrachois | NS_BRC00_GEN | EM Wind Limited Partnership | Sydney, CBI | 46.1529 | -60.4071 | Nova Scotia.a | Cape Breton | Victoria Junction 2S | NS_2S_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 4 | 19% | 0.76 | 35.2% | 12.3341
| Bateston | NS_BTS00_GEN | Celtic Current Limited Partnership | Sydney, CBI | 45.993 | -59.9077 | Nova Scotia.a | Cape Breton | Donkin Road 97S | NS_97S_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 2.3 | 19% | 0.437 | 35.2% | 7.0921
| Black Pond | NS_BLP00_GEN | ScotianWEB Limited Partnership | Yarmouth | 43.7516 | -66.0204 | Nova Scotia.a | Mainland | Yarmouth 11W | NS_11W_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Brenton | NS_BTN00_GEN | ScotianWEB II Limited Partnership | Yarmouth | 43.974 | -66.0826 | Nova Scotia.a | Mainland | Hebron 16W | NS_16W_DSS | 69 | 2017 | 2037 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Chebucto Pockwock | NS_CHP00_GEN | Pockwock Wind Limited Partnership | Halifax | 44.7707 | -63.8379 | Nova Scotia.a | Mainland | Lakeside 103H | NS_103H_DSS | 138 | 2015 | 2035 | Wind_Onshore | wind | 10 | 19% | 1.9 | 35.2% | 30.8352
| Creighnish Rear | NS_CRG00_GEN | Black River Wind Ltd. | Judique, CBI | 45.7262 | -61.4167 | Nova Scotia.a | Cape Breton | Port Hastings 2C | NS_2C_DSS | 69 | 2013 | 2033 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Dalhousie Mountain | NS_DMN00_GEN | RMS Energy | Truro | 45.5757 | -62.9755 | Nova Scotia.a | Mainland | Dalhousie Mountain 91N | NS_91N_GSS | 230 | 2010 | 2030 | Wind_Onshore | wind | 51 | 19% | 9.69 | 35.2% | 157.2595
| Digby Neck | NS_DGN00_GEN | NS Power | Digby | 44.5914 | -65.9444 | Nova Scotia.a | Mainland | Gullivers Cove 98V | NS_98V_DSS | 69 | 2011 | 2031 | Wind_Onshore | wind | 30 | 19% | 5.7 | 35.2% | 92.5056
| Ellerhouse | NS_ELL00_GEN | Berwick, Antognish and Mahone Bay Municipalities | Ellerhouse | 44.9316 | -64.0276 | Nova Scotia.a | Mainland | Ellershouse 102V | NS_102V_GSS | 69 | 2016 | 2036 | Wind_Onshore | wind | 24 | 19% | 4.56 | 35.2% | 74.0045
| Fairmont | NS_FMT00_GEN | Wind Prospect Inc. | Antigonish | 45.6824 | -61.9913 | Nova Scotia.a | Mainland | Lochaber Road 4C | NS_4C_DSS | 69 | 2012 | 2032 | Wind_Onshore | wind | 4.6 | 19% | 0.874 | 35.2% | 14.1842
| Fitzpatrick Mountain | NS_FTZ00_GEN | Affinity Renewables Inc. | Pictou | 45.6264 | -62.9013 | Nova Scotia.a | Mainland | Haliburton 56N | NS_56N_DSS | 69 | 2007 | 2027 | Wind_Onshore | wind | 1.4 | 19% | 0.266 | 35.2% | 4.3169
| Gaetz Brook | NS_GBK00_GEN | HG Wind Limited Partnership (Natural Forces Wind Inc.) | Musquodoboit Harbour | 44.7588 | -63.2043 | Nova Scotia.a | Mainland | Musquodoboit Harbour 87H | NS_87H_DSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 2.3 | 19% | 0.437 | 35.2% | 7.0921
| Gardiner Mines | NS_GMN00_GEN | Gardiner Mines Wind Farm Limited Partnership | Sydney, CBI | 46.195 | -60.0839 | Nova Scotia.a | Cape Breton | Victoria Junction 2S | NS_2S_DSS | 69 | 2016 | 2036 | Wind_Onshore | wind | 5.4 | 19% | 1.026 | 35.2% | 16.651
| Glen Dhu | NS_GDU00_GEN | Shear Wind | Antigonish | 45.6467 | -62.2216 | Nova Scotia.a | Mainland | Glen Dhu 93N | NS_93N_GSS | 138 | 2011 | 2031 | Wind_Onshore | wind | 62.1 | 19% | 11.799 | 35.2% | 191.4866
| Granville Ferry | NS_GVF00_GEN | Scotian Web Limited Partnership | Digby | 44.7653 | -65.5118 | Nova Scotia.a | Mainland | Annapolis 81V | NS_81V_GSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 2 | 19% | 0.38 | 35.2% | 6.167
| Greenfield | NS_GRF00_GEN | Affinity Wind LP | Truro | 45.3467 | -63.139 | Nova Scotia.a | Mainland | Onslow 1N | NS_1N_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 3.2 | 19% | 0.608 | 35.2% | 9.8673
| Hardwood Lands | NS_HDL00_GEN | ScotianWEB II Limited Partnership | Enfield | 45.0892 | -63.5178 | Nova Scotia.a | Mainland | Elmsdale 82V | NS_82V_DSS | 69 | 2017 | 2037 | Wind_Onshore | wind | 6 | 19% | 1.14 | 35.2% | 18.5011
| Higgins Mountain | NS_HGM00_GEN | Confederation Power Ltd. | Springhill | 45.5892 | -63.614 | Nova Scotia.a | Mainland | Springhill 74N | NS_74N_DFS | 69 | 2007 | 2027 | Wind_Onshore | wind | 3.6 | 19% | 0.684 | 35.2% | 11.1007
| Hillside-Boularderie | NS_HLB00_GEN | HG Wind Limited Partnership (Natural Forces Wind Inc.) | Sydney, CBI | 46.2448 | -60.3488 | Nova Scotia.a | Cape Breton | Victoria Junction 2S | NS_2S_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 4 | 19% | 0.76 | 35.2% | 12.3341
| Irish Mountain | NS_IRM00_GEN | Black River Wind Ltd. | Antigonish | 45.4933 | -62.6245 | Nova Scotia.a | Mainland | Lochaber Road 4C | NS_4C_DSS | 69 | 2013 | 2033 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Isle Madame | NS_ISM00_GEN | ScotianWEB Limited Partnership | Isle Madame | 45.569 | -61.0745 | Nova Scotia.a | Cape Breton | St. Peters 59C | NS_59C_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Kaizer Meadow | NS_KMW00_GEN | Municipality of the District of Chester | Chester | 44.7278 | -64.2544 | Nova Scotia.a | Mainland | Robinson's Corner 84W | NS_84W_DSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 2 | 19% | 0.38 | 35.2% | 6.167
| Kemptown | NS_KMP00_GEN | Affinity Wind LP | Truro | 45.4485 | -63.1148 | Nova Scotia.a | Mainland | Onslow 1N | NS_1N_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 4.99 | 19% | 0.9481 | 35.2% | 15.3868
| Ketch Harbour | NS_KHB00_GEN | Watts Wind 4 Limited Partnership | Halifax | 44.5372 | -63.6098 | Nova Scotia.a | Mainland | Lakeside 103H | NS_103H_DSS | 69 | 2016 | 2036 | Wind_Onshore | wind | 4.6 | 19% | 0.874 | 35.2% | 14.1842
| Limerock | NS_LMK00_GEN | Affinity Wind LP | New Glasgow | 45.5397 | -62.8225 | Nova Scotia.a | Mainland | Trenton 50N | NS_50N_DFS | 69 | 2015 | 2035 | Wind_Onshore | wind | 4.99 | 19% | 0.9481 | 35.2% | 15.3868
| Lingan Wind | NS_LNW00_GEN | Glace Bay Lingan Wind Power Ltd. | Lingan, CBI | 46.2453 | -60.0387 | Nova Scotia.a | Cape Breton | Lingan Wind 109S | NS_109S_GSS | 69 | 2012 | 2032 | Wind_Onshore | wind | 16.3 | 19% | 3.097 | 35.2% | 50.2614
| Little River | NS_LTR00_GEN | ScotianWEB Limited Partnership | Digby | 43.7532 | -66.0303 | Nova Scotia.a | Mainland | Gullivers Cove 98V | NS_98V_DSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Martock Ridge | NS_MTR00_GEN | ScotianWEB Limited Partnership | Windsor | 44.927 | -64.1192 | Nova Scotia.a | Mainland | Three Mile Plains 79V | NS_79V_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 6 | 19% | 1.14 | 35.2% | 18.5011
| Maryvale | NS_MVL00_GEN | Maryvale Wind LP | Antigonish | 45.7288 | -62.0635 | Nova Scotia.a | Mainland | Lochaber Road 4C | NS_4C_DSS | 69 | 2010 | 2030 | Wind_Onshore | wind | 6 | 19% | 1.14 | 35.2% | 18.5011
| Mulgrave | NS_MLG00_GEN | Celtic Current Limited Partnership | Antigonish | 45.6207 | -61.4343 | Nova Scotia.a | Mainland | Lochaber Road 4C | NS_4C_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 2.3 | 19% | 0.437 | 35.2% | 7.0921
| New Glasgow | NS_NGL00_GEN | Watts Wind II Limited Partnership | New Glasgow | 45.5057 | -62.6099 | Nova Scotia.a | Mainland | Trenton 50N | NS_50N_DFS | 69 | 2015 | 2035 | Wind_Onshore | wind | 6.4 | 19% | 1.216 | 35.2% | 19.7345
| Nine Mile River | NS_NMR00_GEN | ScotianWEB Limited Partnership | Enfield | 45.0222 | -63.6552 | Nova Scotia.a | Mainland | Elmsdale 82V | NS_82V_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 4 | 19% | 0.76 | 35.2% | 12.3341
| North Beaverbank | NS_NBK00_GEN | ScotianWEB Limited Partnership | Truro | 44.9155 | -63.6815 | Nova Scotia.a | Mainland | Onslow 1N | NS_1N_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 8 | 19% | 1.52 | 35.2% | 24.6682
| Nuttby Mountain | NS_NUT00_GEN | Nova Scotia Power Inc. | Truro | 45.5607 | -63.2037 | Nova Scotia.a | Mainland | Nuttby Mountain 89N | NS_89N_GSS | 69 | 2011 | 2031 | Wind_Onshore | wind | 50.6 | 19% | 9.614 | 35.2% | 156.0261
| Parker Mountain | NS_PRM00_GEN | Scotia Windfields Inc. | Annapolis Royal | 44.786 | -65.4905 | Nova Scotia.a | Mainland | Conway 77V | NS_77V_DSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 2 | 19% | 0.38 | 35.2% | 6.167
| Pictou Landing | NS_PCT00_GEN | Mi'kmaq Wind4All Communities Limited Partnership | Pictou | 45.6668 | -62.688 | Nova Scotia.a | Mainland | Pictou 55N | NS_55N_DSS | 69 | 2017 | 2037 | Wind_Onshore | wind | 1.6 | 19% | 0.304 | 35.2% | 4.9336
| Point Aconi Wind | NS_PAW00_GEN | Celtic Current Limited Partnership | Sydney, CBI | 46.322 | -60.32 | Nova Scotia.a | Cape Breton | Point Aconi 89S | NS_102S_GSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 1.9 | 19% | 0.361 | 35.2% | 5.8587
| Point Tupper Wind | NS_PTW00_GEN | Renewable Energy Services Ltd./NS Power (47.4%) | Point Tupper | 45.572 | -61.3112 | Nova Scotia.a | Mainland | Point Tupper 1C | NS_1C_DFS | 69 | 2010 | 2030 | Wind_Onshore | wind | 22.8 | 19% | 4.332 | 35.2% | 70.3043
| Porters Lake | NS_PLK00_GEN | Watts wind III Limited Partnership | Musquodoboit Harbour | 44.725 | -63.3569 | Nova Scotia.a | Mainland | Musquodoboit Harbour 87H | NS_87H_DSS | 69 | 2016 | 2036 | Wind_Onshore | wind | 3.2 | 19% | 0.608 | 35.2% | 9.8673
| Pubnico Point | NS_PUP00_GEN | Pubnico Point Wind Farm Inc. | Yarmouth | 43.6071 | -65.7948 | Nova Scotia.a | Mainland | Pubnico Point 106W | NS_106W_GSS | 69 | 2005 | 2025 | Wind_Onshore | wind | 30.6 | 19% | 5.814 | 35.2% | 94.3557
| Sable | NS_SBL00_GEN | Municipality of the District of Guysborough | Guysborough | 45.3161 | -60.9995 | Nova Scotia.a | Mainland | Dickie Brook 24C | NS_24C_DFS | 69 | 2015 | 2035 | Wind_Onshore | wind | 13.8 | 19% | 2.622 | 35.2% | 42.5526
| Shag Harbour | NS_SHG00_GEN | Watts Wind II Limited Partnership | Barrington | 43.5196 | -65.6624 | Nova Scotia.a | Mainland | Woods Harbour 21W | NS_21W_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 3.2 | 19% | 0.608 | 35.2% | 9.8673
| South Canoe | NS_SCN00_GEN | South Canoe Development Partnership | Bridgewater | 44.7668 | -64.335 | Nova Scotia.a | Mainland | South Canoe 110W | NS_110W_GSS | 138 | 2015 | 2035 | Wind_Onshore | wind | 102 | 19% | 19.38 | 35.2% | 314.519
| South Cape Mabou | NS_SCM00_GEN | Black River Wind Ltd. | Mabou, CBI | 46.1508 | -61.3816 | Nova Scotia.a | Cape Breton | Whycocomagh 67C | NS_67C_DSS | 69 | 2013 | 2033 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Spiddle Hill | NS_SPD00_GEN | Colchester-Cumberland Wind Field Inc. | Truro | 45.5532 | -63.2229 | Nova Scotia.a | Mainland | Nuttby Mountain 89N | NS_89N_GSS | 69 | 2013 | 2033 | Wind_Onshore | wind | 1.6 | 19% | 0.304 | 35.2% | 4.9336
| Springhill | NS_SPH00_GEN | Confederation Power Ltd. | Springhill | 45.6115 | -64.0239 | Nova Scotia.a | Mainland | Springhill 74N | NS_74N_DFS | 69 | 2012 | 2032 | Wind_Onshore | wind | 2.1 | 19% | 0.399 | 35.2% | 6.4754
| St.Rose | NS_STR00_GEN | ScotianWEB Limited Partnership | Margaree Harbour | 46.3307 | -61.1768 | Nova Scotia.a | Cape Breton | SW Margaree 58C | NS_58C_DSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Terence Bay | NS_TRB00_GEN | Chebucto Terence Bay Wind Field Ltd. | Halifax | 44.5419 | -63.6036 | Nova Scotia.a | Mainland | Lakeside 103H | NS_103H_DSS | 69 | 2017 | 2037 | Wind_Onshore | wind | 7.05 | 19% | 1.3395 | 35.2% | 21.7388
| Truro Heights | NS_TRH00_GEN | Truro Heights Wind Limited Partnership | Truro | 45.3181 | -63.3411 | Nova Scotia.a | Mainland | Willow Lane 15N | NS_15N_DSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 4 | 19% | 0.76 | 35.2% | 12.3341
| Truro-Millbrook | NS_TRM00_GEN | Truro-Millbrook Wind Limited Partnership | Truro | 45.3263 | -63.3441 | Nova Scotia.a | Mainland | Lafarge 11N | NS_11N_DSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 6 | 19% | 1.14 | 35.2% | 18.5011
| Walton | NS_WTL00_GEN | ScotianWEB II Limited Partnership | Kentville | 45.197 | -63.9688 | Nova Scotia.a | Mainland | Upper Burlington 18V | NS_18V_DSS | 69 | 2016 | 2036 | Wind_Onshore | wind | 1.99 | 19% | 0.3781 | 35.2% | 6.1362
| Watt Section | NS_WTS00_GEN | Watts Wind Energy Inc. | Sheet Harbour | 44.8991 | -62.4661 | Nova Scotia.a | Mainland | Ruth Falls 96H | NS_96H_DSS | 69 | 2011 | 2031 | Wind_Onshore | wind | 1.5 | 19% | 0.285 | 35.2% | 4.6253
| Wedgeport | NS_WDP00_GEN | Watts Wind II Limited Partnership | Yarmouth | 43.7528 | -66.0139 | Nova Scotia.a | Mainland | Pleasant St. 88W | NS_88W_DSS | 69 | 2015 | 2035 | Wind_Onshore | wind | 1.68 | 19% | 0.3192 | 35.2% | 5.1803
| Whynotts | NS_WNT00_GEN | Whynotts Wind Limited Partnership | Bridgewater | 44.4078 | -64.4662 | Nova Scotia.a | Mainland | Bridgewater 99W | NS_99W_DSS | 69 | 2014 | 2034 | Wind_Onshore | wind | 4 | 19% | 0.76 | 35.2% | 12.3341
Specific Notes:
NPCC says 238 MW of dependable wind capacity. But based on the total installed capacity, using the NSPI ELCC of 17% yields only 74 MW.
Average Annual Energy for Nalcor Purchases based on 16 hours per day, or 66.67%
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Unless noted otherwise, the wind generating stations are presumed to be connected to the nearest 69 kV substation
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit Hydro_run facilities treated as single-unit facilities
RH Additions, Comments and TODOs
Remote projects are not included in this list.
See calculations sheets for sources of values.
Sources

## Storage
NS | EXISTING STORAGE | [12 empty] | DESIGN | [7 empty] | OPERATIONS
| Project Name | Storage Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Technology | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Days | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | kV | [5 empty] | (MW) | (MWh) | (Hours) |  | ($M) | (hours) | (hours) | (%) | (days/y) | ($/year) | ($/MWh)
Specific Notes:

## Transmission
NS | EXISTING TRANSMISSION
| Circuit ID | Owner | Planning Region | Number of Circuits | Current | Length | Length | Voltage | Reactance | Smax | Summer Ampacity | Winter Ampacity | Winter Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes | Count
[5 empty] | (ad/dc) | (km) | (miles) | (kV) | (ohm) |  | (A) | (A) | (MVA) | (MVA) |  | (MW) | (MW)
| L5502 | NSPI | Mainland | 1 | ac | 6.1 | 3.8 | 69 | 2.3441 | 3 | [5 empty] | 36 | 39 | Trenton 50N | NS_50N_DFS | Abercrombie 54N | NS_54N_DSS |  |  | 82
| L6537 | NSPI | Cape Breton | 1 | ac | 60 | 37 | 138 | 26.0143 | 3 | [5 empty] | 141 | 156 | Port Hastings 2C | NS_2C_DSS | Aberdeen 9C | NS_9C_DSS |  |  | 238
| L5505 | NSPI | Cape Breton | 1 | ac | 11.5 | 7.1 | 69 | 4.4193 | 3 | [5 empty] | 36 | 39 | Whycocomagh 67C | NS_67C_DSS | Aberdeen 9C | NS_9C_DSS |  |  | 83
| L6510 | NSPI | Cape Breton | 1 | ac | 10 | 6.2 | 138 | 4.3357 | 3 | [5 empty] | 141 | 156 | Whycocomagh 67C | NS_67C_DSS | Aberdeen 9C | NS_9C_DSS |  |  | 216
| L5030 | NSPI | Mainland | 1 | ac | 0.1 | 0.1 | 69 | 0.038429 | 3 | [5 empty] | 36 | 39 | Springhill 74N | NS_74N_DFS | Aberdeen St. 10N | NS_10N_DSS |  |  | 47
| L6050 | NSPI | Mainland | 1 | ac | 2 | 1.2 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Aerotech Park Tap 127H | NS_127H_JCT | Aerotech Park 127H | NS_127H_DSS |  |  | 207
| L6001 | NSPI | Mainland | 1 | ac | 15 | 9.3 | 138 | 6.5036 | 3 | [5 empty] | 141 | 156 | Elmsdale 82V | NS_82V_DSS | Aerotech Park Tap 127H | NS_127H_JCT |  |  | 163
| L5003 | NSPI | Mainland | 1 | ac | 5.5 | 3.4 | 69 | 2.1136 | 3 | [5 empty] | 36 | 39 | Farrell St. 99H | NS_99H_DSS | Akerly 124H | NS_124H_DSS |  |  | 3
| L5565 | NSPI | Cape Breton | 1 | ac | 18.9 | 11.7 | 69 | 7.263 | 3 | [5 empty] | 36 | 39 | Seaboard 1S | NS_1S_DSS | Albert Bridge 57S | NS_57S_DSS |  |  | 151
| L5042 | NSPI | Mainland | 1 | ac | 2 | 1.2 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Farrell St. 99H | NS_99H_DSS | Albro Lake 62H | NS_62H_DSS |  |  | 63
| L5548 | NSPI | Mainland | 1 | ac | 7 | 4.3 | 69 | 2.69 | 3 | [5 empty] | 36 | 39 | Domtar 75N | NS_75N_ISS | Amherst 92N | NS_92N_GSS |  |  | 133
| L5549 | NSPI | Mainland | 1 | ac | 14.1 | 8.7 | 69 | 5.4184 | 3 | [5 empty] | 36 | 39 | Maccan 30N | NS_30N_DSS | Amherst 92N | NS_92N_GSS |  |  | 136
| L6551 | NSPI | Mainland | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Maccan 30N | NS_30N_DSS | Amherst 92N | NS_92N_GSS |  |  | 247
| L5056 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Lequille 12V | NS_12V_GSS | Annapolis 81V | NS_81V_GSS |  |  | 76
| L5026 | NSPI | Mainland | 1 | ac | 17.5 | 10.8 | 69 | 6.725 | 3 | [5 empty] | 36 | 39 | Bridgetown Tap 70V | NS_70V_JCT | Annapolis Tap 81V | NS_81V_JCT |  |  | 33
| L5027 | NSPI | Mainland | 1 | ac | 16 | 9.9 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Tusket 9W | NS_9W_GSS | Argyle 19W | NS_19W_DSS |  |  | 36
| L6033 | NSPI | Mainland | 1 | ac | 6 | 3.7 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Lakeside 103H | NS_103H_DSS | Armdale 2H | NS_2H_DSS |  |  | 197
| L5015 | NSPI | Mainland | 1 | ac | 10 | 6.2 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Three Mile Plains 79V | NS_79V_DSS | Avon 1V | NS_1V_GSS |  |  | 16
| L6512 | NSPI | Cape Breton | 1 | ac | 2 | 1.2 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Baddeck Tap 104S | NS_104S_JCT | Baddeck 104S | NS_104S_DFS |  |  | 219
| L6537 | NSPI | Cape Breton | 1 | ac | 25 | 15.4 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Aberdeen 9C | NS_9C_DSS | Baddeck Tap 104S | NS_104S_JCT |  |  | 239
| L5027 | NSPI | Mainland | 1 | ac | 22.5 | 13.9 | 69 | 8.6464 | 3 | [5 empty] | 36 | 39 | Woods Harbour 21W | NS_21W_DSS | Barrington 22W | NS_22W_DSS |  |  | 40
| L5036 | NSPI | Mainland | 1 | ac | 3.4 | 2.1 | 69 | 1.3066 | 3 | [5 empty] | 36 | 39 | Berwick Tap 53V | NS_53V_JCT | Berwick 52V | NS_52V_DSS |  |  | 56
| L5053 | NSPI | Mainland | 1 | ac | 7.7 | 4.8 | 69 | 2.959 | 3 | [5 empty] | 36 | 39 | Michelin 92V | NS_92V_ISS | Berwick Tap 53V | NS_53V_JCT |  |  | 71
| L5541B | NSPI | Mainland | 1 | ac | 8 | 4.9 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Lower Great Brook 4W | NS_4W_GSS | Big Falls 3W | NS_3W_GSS |  |  | 119
| L5532 | NSPI | Mainland | 1 | ac | 15 | 9.3 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Middlefield 91W | NS_91W_DSS | Big Falls 3W | NS_3W_GSS |  |  | 104
| L5030 | NSPI | Mainland | 1 | ac | 2.9 | 1.8 | 69 | 1.1144 | 3 | [5 empty] | 36 | 39 | Aberdeen St. 10N | NS_10N_DSS | Black River Rd. 6N | NS_6N_DSS |  |  | 48
| L5500 | NSPI | Mainland | 1 | ac | 12.5 | 7.7 | 69 | 4.8036 | 3 | [5 empty] | 36 | 39 | Trenton 50N | NS_50N_DFS | Bridge Avenue 62N | NS_62N_DSS |  |  | 80
| L5501 | NSPI | Mainland | 1 | ac | 7.6 | 4.7 | 69 | 2.9206 | 3 | [5 empty] | 36 | 39 | Trenton 50N | NS_50N_DFS | Bridge Avenue 62N | NS_62N_DSS |  |  | 81
| L5047 | NSPI | Mainland | 1 | ac | 3.1 | 1.9 | 69 | 1.1913 | 3 | [5 empty] | 36 | 39 | Bridgetown Tap 70V | NS_70V_JCT | Bridgetown 70V | NS_70V_DSS |  |  | 67
| L5026 | NSPI | Mainland | 1 | ac | 5 | 3.1 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Paradise 11V | NS_11V_DSS | Bridgetown Tap 70V | NS_70V_JCT |  |  | 32
| L5545 | NSPI | Mainland | 1 | ac | 3.2 | 2 | 69 | 1.2297 | 3 | [5 empty] | 36 | 39 | Auburndale 73W | NS_73W_DSS | Bridgewater 99W | NS_99W_DSS |  |  | 122
| L6531 | NSPI | Mainland | 1 | ac | 40 | 24.7 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | Brooklyn 104W | NS_104W_DSS | Bridgewater 99W | NS_99W_DSS |  | Brooklyn presumed to be on L6531 | 232
| L7008 | NSPI | Mainland | 1 | ac | 95 | 58.6 | 230 | 45.6 | 2.8936 | [5 empty] | 387.7414 | 419.5709 | Brushy Hill 120H | NS_120H_DSS | Bridgewater 99W | NS_99W_DSS |  |  | 256
| L7009 | NSPI | Mainland | 1 | ac | 95 | 58.6 | 230 | 45.6 | 2.8936 | [5 empty] | 387.7414 | 419.5709 | Brushy Hill 120H | NS_120H_DSS | Bridgewater 99W | NS_99W_DSS |  |  | 257
| L6002 | NSPI | Mainland | 1 | ac | 2 | 1.2 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Michelin Bridgewater 74W | NS_74W_ISS | Bridgewater 99W | NS_99W_DSS |  |  | 172
| L5545 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | High St. 70W | NS_70W_DSS | Bridgewater East 89W | NS_89W_DSS |  |  | 124
| L5530 | NSPI | Mainland | 1 | ac | 14 | 8.6 | 69 | 5.38 | 3 | [5 empty] | 36 | 39 | Milton 50W | NS_50W_DSS | Broad River 46W | NS_46W_DSS |  |  | 95
| L6531 | NSPI | Mainland | 1 | ac | 5 | 3.1 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Milton 50W | NS_50W_DSS | Brooklyn 104W | NS_104W_DSS |  | Brooklyn presumed to be on L6531 | 231
| L5549 | NSPI | Mainland | 1 | ac | 2 | 1.2 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Hickman St. 19N | NS_19N_DSS | Brownell St. 17N | NS_17N_DSS |  |  | 138
| L5548 | NSPI | Mainland | 1 | ac | 2 | 1.2 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Park St. 20N | NS_20N_DSS | Brownell St. 17N | NS_17N_DSS |  |  | 135
| L6010 | NSPI | Mainland | 1 | ac | 16 | 9.9 | 138 | 6.9371 | 3 | [5 empty] | 141 | 156 | Cobequid Rd. 101H | NS_101H_DSS | Brushy Hill 120H | NS_120H_DSS |  |  | 185
| L7001 | NSPI | Mainland | 1 | ac | 90 | 55.6 | 230 | 43.2 | 2.9956 | [5 empty] | 401.4152 | 434.3672 | Onslow 67N | NS_67N_DSS | Brushy Hill 120H | NS_120H_DSS |  |  | 251
| L7002 | NSPI | Mainland | 1 | ac | 90 | 55.6 | 230 | 43.2 | 2.9956 | [5 empty] | 401.4152 | 434.3672 | Onslow 67N | NS_67N_DSS | Brushy Hill 120H | NS_120H_DSS |  |  | 252
| L7018 | NSPI | Mainland | 1 | ac | 90 | 55.6 | 230 | 43.2 | 2.9956 | [5 empty] | 401.4152 | 434.3672 | Onslow 67N | NS_67N_DSS | Brushy Hill 120H | NS_120H_DSS |  |  | 263
| L6009 | NSPI | Mainland | 1 | ac | 8 | 4.9 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Sackville 90H | NS_90H_DSS | Burnside 108H | NS_108H_DSS |  |  | 182
| L6001 | NSPI | Mainland | 1 | ac | 8 | 4.9 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Spider Lake 132H | NS_132H_DSS | Burnside 108H | NS_108H_DSS |  |  | 165
| L6007 | NSPI | Mainland | 1 | ac | 5 | 3.1 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Tuft's Cove 91H | NS_91H_GSS | Burnside 108H | NS_108H_DSS |  |  | 179
| L6001 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Burnside 108H | NS_108H_DSS | Burnside 14H | NS_14H_GSS |  |  | 166
| L6007 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Burnside 108H | NS_108H_DSS | Burnside 14H | NS_14H_GSS |  |  | 180
| L6009 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 138 | 0.43357 | 3 | [5 empty] | 141 | 156 | Burnside 108H | NS_108H_DSS | Burnside 14H | NS_14H_GSS |  |  | 183
| L5532 | NSPI | Mainland | 1 | ac | 5.3 | 3.3 | 69 | 2.0367 | 3 | [5 empty] | 36 | 39 | Harmony 7W | NS_7W_DSS | Caledonia 57W | NS_57W_DSS |  |  | 102
| L5035 | NSPI | Mainland | 1 | ac | 0.8 | 0.5 | 69 | 0.30743 | 3 | [5 empty] | 36 | 39 | Hells Gate 3V | NS_3V_GSS | Canaan Rd. 43V | NS_43V_DSS |  |  | 55
| L6012 | NSPI | Mainland | 1 | ac | 40 | 24.7 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | St. Croix 17V | NS_17V_DSS | Canaan Rd. 43V | NS_43V_DSS |  |  | 188
| L5017 | NSPI | Mainland | 1 | ac | 5.4 | 3.3 | 69 | 2.0751 | 3 | [5 empty] | 36 | 39 | White Rock 4V | NS_4V_GSS | Canaan Rd. 43V | NS_43V_DSS |  |  | 20
| L5037 | NSPI | Mainland | 1 | ac | 3.7 | 2.3 | 69 | 1.4219 | 3 | [5 empty] | 36 | 39 | East River 86E | NS_86E_JCT | Canexel 85W | NS_85W_ISS |  | East River 86E is a junction and not a substation | 57
| L5527 | NSPI | Mainland | 1 | ac | 50 | 30.9 | 69 | 19.2143 | 3 | [5 empty] | 36 | 39 | Dickie Brook 24C | NS_24C_DFS | Canso 19C | NS_19C_DSS |  |  | 94
| L6515 | NSPI | Mainland | 1 | ac | 60 | 37 | 138 | 26.0143 | 3 | [5 empty] | 141 | 156 | Lochaber Road 4C | NS_4C_DSS | Cape Porcupine 100C | NS_100C_DSS |  |  | 221
| L5535 | NSPI | Mainland | 1 | ac | 8 | 4.9 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Rio Algoma Tap 99X | NS_99X_JCT | Carleton 92W | NS_92W_DSS |  |  | 108
| L6536 | NSPI | Mainland | 1 | ac | 25 | 15.4 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Springhill 74N | NS_74N_DFS | Church St. 22N | NS_22N_DSS |  |  | 236
| L6516 | NSPI | Cape Breton | 1 | ac | 13 | 8 | 138 | 5.6364 | 3 | [5 empty] | 141 | 156 | Port Hastings 2C | NS_2C_DSS | Cleveland 22C | NS_22C_DSS |  |  | 223
| L5027 | NSPI | Mainland | 1 | ac | 10 | 6.2 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Barrington 22W | NS_22W_DSS | Clyde River 23W | NS_23W_DSS |  |  | 41
| L6010 | NSPI | Mainland | 1 | ac | 2 | 1.2 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Sackville 90H | NS_90H_DSS | Cobequid Rd. 101H | NS_101H_DSS |  | Cobequid Rd. presumed to be on L6010 | 184
| L5533 | NSPI | Mainland | 1 | ac | 13.1 | 8.1 | 69 | 5.0341 | 3 | [5 empty] | 36 | 39 | Gulch 13V | NS_13V_DFS | Conway 77V | NS_77V_DSS |  |  | 105
| L5057 | NSPI | Mainland | 1 | ac | 2.2 | 1.4 | 69 | 0.84543 | 3 | [5 empty] | 36 | 39 | Cornwallis Tap 74V | NS_74V_JCT | Cornwallis 74V | NS_74V_DSS |  |  | 77
| L5026 | NSPI | Mainland | 1 | ac | 15 | 9.3 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Annapolis Tap 81V | NS_81V_JCT | Cornwallis Tap 74V | NS_74V_JCT |  |  | 34
| L5540 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Milton 50W | NS_50W_DSS | Cowie Falls 6W | NS_6W_GSS |  |  | 116
| L7019 | NSPI | Mainland | 1 | ac | 40 | 24.7 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Onslow 67N | NS_67N_DSS | Dalhousie Mountain 91N | NS_91N_GSS |  |  | 264
| L7004 | NSPI | Cape Breton | 1 | ac | 140 | 86.4 | 230 | 67.2 | 2.2399 | [5 empty] | 300.151 | 324.7903 | Port Hastings 3C | NS_3C_DSS | Dalhousie Mountain 91N | NS_91N_GSS |  |  | 254
| L6040 | NSPI | Mainland | 1 | ac | 4 | 2.5 | 138 | 1.7343 | 3 | [5 empty] | 141 | 156 | Tuft's Cove 91H | NS_91H_GSS | Dartmouth Crossing 139H | NS_139H_DSS |  |  | 201
| L6040 | NSPI | Mainland | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Spider Lake 132H | NS_132H_DSS | Dartmouth East 113H | NS_113H_DSS |  |  | 203
| L6042 | NSPI | Mainland | 1 | ac | 16 | 9.9 | 138 | 6.9371 | 3 | [5 empty] | 141 | 156 | Tuft's Cove 91H | NS_91H_GSS | Dartmouth East 113H | NS_113H_DSS |  |  | 204
| L6613 | NSPI | Mainland | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Onslow 1N | NS_1N_DSS | Debert 81N | NS_81N_DSS |  | Formerly L6513 | 249
| L5540 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Cowie Falls 6W | NS_6W_GSS | Deep Brook 5W | NS_5W_GSS |  |  | 117
| L5527 | NSPI | Mainland | 1 | ac | 15 | 9.3 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Salmon River Lake 57C | NS_57C_DSS | Dickie Brook 24C | NS_24C_DFS |  |  | 93
| L5548 | NSPI | Mainland | 1 | ac | 7.1 | 4.4 | 69 | 2.7284 | 3 | [5 empty] | 36 | 39 | Maccan 30N | NS_30N_DSS | Domtar 75N | NS_75N_ISS |  |  | 132
| L5556 | NSPI | Cape Breton | 1 | ac | 10 | 6.2 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Seaboard 1S | NS_1S_DSS | Donkin Road 97S | NS_97S_DSS |  |  | 143
| L5031 | NSPI | Mainland | 1 | ac | 10 | 6.2 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Hubbards 87W | NS_87W_DSS | East River 86E | NS_86E_JCT |  | East River 86E is a junction and not a substation | 49
| L6001 | NSPI | Mainland | 1 | ac | 54 | 33.3 | 138 | 23.4129 | 3 | [5 empty] | 141 | 156 | Onslow 1N | NS_1N_DSS | Elmsdale 82V | NS_82V_DSS |  |  | 162
| L5049 | NSPI | Mainland | 1 | ac | 0.5 | 0.3 | 69 | 0.19214 | 3 | [5 empty] | 36 | 39 | Tuft's Cove 91H | NS_91H_GSS | Farrell St. 99H | NS_99H_DSS |  |  | 69
| L5016 | NSPI | Mainland | 1 | ac | 6.7 | 4.1 | 69 | 2.5747 | 3 | [5 empty] | 36 | 39 | Three Mile Plains 79V | NS_79V_DSS | Five Points 20V | NS_20V_DSS |  |  | 17
| L5050 | NSPI | Mainland | 1 | ac | 15.9 | 9.8 | 69 | 6.1101 | 3 | [5 empty] | 36 | 39 | Sissiboo 15V | NS_15V_GSS | Fourth Lake 91V | NS_91V_GSS |  |  | 70
| L6538 | NSPI | Cape Breton | 1 | ac | 25 | 15.4 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Glen Tosh 5S | NS_5S_DSS | Gannon Rd. 3S | NS_3S_DSS |  |  | 241
| L5039 | NSPI | Mainland | 1 | ac | 3.5 | 2.2 | 69 | 1.345 | 3 | [5 empty] | 36 | 39 | Lakeside 103H | NS_103H_DSS | Geizer Hill 34H | NS_34H_DSS |  |  | 58
| L5004 | NSPI | Mainland | 1 | ac | 2.2 | 1.4 | 69 | 0.84543 | 3 | [5 empty] | 36 | 39 | Rockingham Tap 23H | NS_23H_JCT | Geizer Hill 34H | NS_34H_DSS |  |  | 6
| L6552 | NSPI | Mainland | 1 | ac | 19.7 | 12.2 | 138 | 8.5414 | 3 | [5 empty] | 141 | 156 | Lochaber Road 4C | NS_4C_DSS | Glen Dhu 93N | NS_93N_GSS |  |  | 248
| L6511 | NSPI | Mainland | 1 | ac | 40 | 24.7 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | Trenton 50N | NS_50N_DFS | Glen Dhu 93N | NS_93N_GSS |  |  | 217
| L6537 | NSPI | Cape Breton | 1 | ac | 14 | 8.6 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Baddeck Tap 104S | NS_104S_JCT | Glen Tosh 5S | NS_5S_DSS |  |  | 240
| L6545 | NSPI | Cape Breton | 1 | ac | 50 | 30.9 | 138 | 21.6786 | 3 | [5 empty] | 141 | 156 | Wreck Cove 85S | NS_85S_DFS | Glen Tosh 5S | NS_5S_DSS |  |  | 244
| L6549 | NSPI | Cape Breton | 1 | ac | 50 | 30.9 | 138 | 21.6786 | 3 | [5 empty] | 141 | 156 | Wreck Cove 85S | NS_85S_DFS | Glen Tosh 5S | NS_5S_DSS |  |  | 246
| L6002 | NSPI | Mainland | 1 | ac | 28 | 17.3 | 138 | 12.14 | 3 | [5 empty] | 141 | 156 | Hubbards 87W | NS_87W_DSS | Gold River 103W | NS_103W_DSS |  |  | 169
| L6503 | NSPI | Mainland | 1 | ac | 60 | 37 | 138 | 26.0143 | 3 | [5 empty] | 141 | 156 | Onslow 1N | NS_1N_DSS | Granton 49N | NS_49N_ISS |  |  | 212
| L5530 | NSPI | Mainland | 1 | ac | 37.5 | 23.1 | 69 | 14.4107 | 3 | [5 empty] | 36 | 39 | Broad River 46W | NS_46W_DSS | Green Harbour 36W | NS_36W_DSS |  |  | 96
| L5024 | NSPI | Mainland | 1 | ac | 2 | 1.2 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Tremont 51V | NS_51V_DSS | Greenwood 64V | NS_64V_DSS |  |  | 28
| L5026 | NSPI | Mainland | 1 | ac | 10 | 6.2 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Cornwallis Tap 74V | NS_74V_JCT | Gulch 13V | NS_13V_DFS |  |  | 35
| L5581 | NSPI | Mainland | 1 | ac | 16 | 9.9 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Conway 77V | NS_77V_DSS | Gullivers Cove 98V | NS_98V_DSS |  |  | 161
| L5506 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Pictou 55N | NS_55N_DSS | Haliburton 56N | NS_56N_DSS |  |  | 85
| L6004 | NSPI | Mainland | 1 | ac | 14 | 8.6 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Sackville 90H | NS_90H_DSS | Hammonds 137H | NS_137H_DSS |  | Hammonds presumed to be on L6004 | 174
| L5532 | NSPI | Mainland | 1 | ac | 12 | 7.4 | 69 | 4.6114 | 3 | [5 empty] | 36 | 39 | Maitland Bridge 76V | NS_76V_DSS | Harmony 7W | NS_7W_DSS |  |  | 101
| L5534 | NSPI | Mainland | 1 | ac | 8.4 | 5.2 | 69 | 3.228 | 3 | [5 empty] | 36 | 39 | Tusket 9W | NS_9W_GSS | Hebron 16W | NS_16W_DSS |  |  | 106
| L5536 | NSPI | Mainland | 1 | ac | 6.2 | 3.8 | 69 | 2.3826 | 3 | [5 empty] | 36 | 39 | Yarmouth 11W | NS_11W_DSS | Hebron 16W | NS_16W_DSS |  |  | 112
| L5549 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Amherst 92N | NS_92N_GSS | Hickman St. 19N | NS_19N_DSS |  |  | 137
| L5545 | NSPI | Mainland | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Bridgewater 99W | NS_99W_DSS | High St. 70W | NS_70W_DSS |  |  | 123
| L6052 | NSPI | Mainland | 1 | ac | 5 | 3.1 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Canaan Rd. 43V | NS_43V_DSS | Highbury 99V | NS_99V_DSS |  |  | 209
| L5033 | NSPI | Mainland | 1 | ac | 10.2 | 6.3 | 69 | 3.9197 | 3 | [5 empty] | 36 | 39 | New Minas 22V | NS_22V_DSS | Hillaton 36V | NS_36V_DSS |  |  | 54
| L5019 | NSPI | Mainland | 1 | ac | 1.4 | 0.9 | 69 | 0.538 | 3 | [5 empty] | 36 | 39 | Lumsden 5V | NS_5V_GSS | Hollow Bridge 6V | NS_6V_GSS |  |  | 22
| L8003 | NSPI | Nova Scotia | 1 | ac | 45 | 27.8 | 345 | 19.9708 | 3 | [5 empty] | 975 | 1275 | Onslow 67N | NS_67N_DSS | Hopewell 79N | NS_79N_DSS |  |  | 269
| L6507 | NSPI | Mainland | 1 | ac | 17 | 10.5 | 138 | 7.3707 | 3 | [5 empty] | 141 | 156 | Trenton 50N | NS_50N_DFS | Hopewell 79N | NS_79N_DSS |  |  | 214
| L6508 | NSPI | Nova Scotia | 1 | ac | 17 | 10.5 | 138 | 7.3707 | 3 | [5 empty] | 141 | 156 | Trenton 50N | NS_50N_DFS | Hopewell 79N | NS_79N_DSS |  |  | 215
| L6002 | NSPI | Nova Scotia | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Tidewater 92H | NS_92H_GSS | Hubbards 87W | NS_87W_DSS |  |  | 168
| L5010 | NSPI | Nova Scotia | 1 | ac | 0.1 | 0.1 | 69 | 0.038429 | 3 | [5 empty] | 36 | 39 | Imperial Oil 58H | NS_58H_ISS | Imperial Oil 58H | NS_58H_ISS |  | Internal transmission line | 7
| L5012 | NSPI | Nova Scotia | 1 | ac | 3.7 | 2.3 | 69 | 1.4219 | 3 | [5 empty] | 36 | 39 | Penhorn 48H | NS_48H_DSS | Imperial Oil 58H | NS_58H_ISS |  |  | 12
| L5011 | NSPI | Nova Scotia | 1 | ac | 3.3 | 2 | 69 | 1.2681 | 3 | [5 empty] | 36 | 39 | Woodlawn 40H | NS_40H_DSS | Imperial Oil 58H | NS_58H_ISS |  |  | 9
| L6535 | NSPI | Nova Scotia | 1 | ac | 20 | 12.3 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Amherst 92N | NS_92N_GSS | IPT Amherst | PP_NSNB2_IPT |  |  | 235
| L6536 | NSPI | Nova Scotia | 1 | ac | 5 | 3.1 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Church St. 22N | NS_22N_DSS | IPT Church St | PP_NSNB3_IPT |  |  | 237
| L8001 | NSPI | Nova Scotia | 1 | ac | 100 | 61.7 | 345 | 44.3796 | 2.7969 | [5 empty] | 908.9838 | 1188.6711 | Onslow 67N | NS_67N_DSS | IPT Onslow | PP_NSNB1_IPT |  |  | 267
| 301NS1 | Emera Inc. | Nova Scotia | 1 | dc | 46 | 28.4 | 200 | [7 empty] | 250 | 250 | Woodbine 101S | NS_101S_DSS | IPT Woodbine | PP_NSNL1_IPT |  | Capacities on DC side of converter; Length to midpoint across Cabot Strait | 1
| 301NS2 | Emera Inc. | Nova Scotia | 1 | dc | 46 | 28.4 | 200 | [7 empty] | 250 | 250 | Woodbine 101S | NS_101S_DSS | IPT Woodbine | PP_NSNL1_IPT |  | Capacities on DC side of converter; Length to midpoint across Cabot Strait | 2
| L6038 | NSPI | Nova Scotia | 1 | ac | 4 | 2.5 | 138 | 1.7343 | 3 | [5 empty] | 141 | 156 | Lakeside 103H | NS_103H_DSS | Kearney Lake 129H | NS_129H_DSS |  |  | 200
| L5576 | NSPI | Nova Scotia | 1 | ac | 20.2 | 12.5 | 69 | 7.7626 | 3 | [5 empty] | 36 | 39 | Gannon Rd. 3S | NS_3S_DSS | Keltic Drive 11S | NS_11S_DSS |  |  | 158
| L5564 | NSPI | Nova Scotia | 1 | ac | 19.1 | 11.8 | 69 | 7.3399 | 3 | [5 empty] | 36 | 39 | Victoria Junction 2S | NS_2S_DSS | Keltic Drive 11S | NS_11S_DSS |  |  | 150
| L6035 | NSPI | Nova Scotia | 1 | ac | 10 | 6.2 | 138 | 4.3357 | 3 | [5 empty] | 141 | 156 | Water St. 1H | NS_1H_DSS | Kempt Road 104H | NS_104H_DSS |  |  | 199
| L5024 | NSPI | Nova Scotia | 1 | ac | 2.7 | 1.7 | 69 | 1.0376 | 3 | [5 empty] | 36 | 39 | Greenwood 64V | NS_64V_DSS | Kingston 63V | NS_63V_DSS |  |  | 29
| L5021 | NSPI | Nova Scotia | 1 | ac | 7.2 | 4.4 | 69 | 2.7669 | 3 | [5 empty] | 36 | 39 | Canaan Rd. 43V | NS_43V_DSS | Klondike 50V | NS_50V_DSS |  |  | 24
| L5028 | NSPI | Nova Scotia | 1 | ac | 13.1 | 8.1 | 69 | 5.0341 | 3 | [5 empty] | 36 | 39 | Onslow 1N | NS_1N_DSS | Lafarge 11N | NS_11N_DSS |  |  | 44
| L6016 | NSPI | Nova Scotia | 1 | ac | 30 | 18.5 | 138 | 13.0071 | 3 | [5 empty] | 141 | 156 | Brushy Hill 120H | NS_120H_DSS | Lakeside 103H | NS_103H_DSS |  |  | 192
| L8002 | NSPI | Nova Scotia | 1 | ac | 100 | 61.7 | 345 | 44.3796 | 2.7969 | [5 empty] | 908.9838 | 1188.6711 | Onslow 67N | NS_67N_DSS | Lakeside 103H | NS_103H_DSS |  |  | 268
| L6008 | NSPI | Nova Scotia | 1 | ac | 16 | 9.9 | 138 | 6.9371 | 3 | [5 empty] | 141 | 156 | Sackville 90H | NS_90H_DSS | Lakeside 103H | NS_103H_DSS |  |  | 181
| L5056 | NSPI | Nova Scotia | 1 | ac | 3 | 1.9 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Annapolis Tap 81V | NS_81V_JCT | Lequille 12V | NS_12V_GSS |  |  | 75
| L7011 | NSPI | Nova Scotia | 1 | ac | 160 | 98.8 | 230 | 76.8 | 2.0503 | [5 empty] | 274.7441 | 297.2978 | Port Hastings 3C | NS_3C_DSS | Lingan 88S | NS_88S_GSS |  |  | 258
| L7012 | NSPI | Nova Scotia | 1 | ac | 160 | 98.8 | 230 | 76.8 | 2.0503 | [5 empty] | 274.7441 | 297.2978 | Port Hastings 3C | NS_3C_DSS | Lingan 88S | NS_88S_GSS |  |  | 259
| L6533 | NSPI | Nova Scotia | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Victoria Junction 2S | NS_2S_DSS | Lingan 88S | NS_88S_GSS |  |  | 233
| L6534 | NSPI | Nova Scotia | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Victoria Junction 2S | NS_2S_DSS | Lingan 88S | NS_88S_GSS |  |  | 234
| L5573 | NSPI | Nova Scotia | 1 | ac | 15.8 | 9.8 | 69 | 6.0717 | 3 | [5 empty] | 36 | 39 | Victoria Junction 2S | NS_2S_DSS | Lingan Mine 80S | NS_80S_DSS |  |  | 156
| L5580 | NSPI | Nova Scotia | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | New Waterford 15S | NS_15S_DSS | Lingan Wind 109S | NS_109S_GSS |  |  | 160
| L5539 | NSPI | Nova Scotia | 1 | ac | 8.4 | 5.2 | 69 | 3.228 | 3 | [5 empty] | 36 | 39 | Milton 50W | NS_50W_DSS | Liverpool 48W | NS_48W_DSS |  |  | 115
| L6511 | NSPI | Nova Scotia | 1 | ac | 19.7 | 12.2 | 138 | 8.5414 | 3 | [5 empty] | 141 | 156 | Glen Dhu 93N | NS_93N_GSS | Lochaber Road 4C | NS_4C_DSS |  |  | 218
| L5048 | NSPI | Nova Scotia | 1 | ac | 5.5 | 3.4 | 69 | 2.1136 | 3 | [5 empty] | 36 | 39 | Green Harbour 36W | NS_36W_DSS | Lockeport 37W | NS_37W_DSS |  |  | 68
| L5541 | NSPI | Nova Scotia | 1 | ac | 6 | 3.7 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Milton 50W | NS_50W_DSS | Lower Great Brook 4W | NS_4W_GSS |  |  | 118
| L5544 | NSPI | Nova Scotia | 1 | ac | 4 | 2.5 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Big Falls 3W | NS_3W_GSS | Lower Lake Falls 2W | NS_2W_GSS |  |  | 120
| L6005 | NSPI | Nova Scotia | 1 | ac | 13 | 8 | 138 | 5.6364 | 3 | [5 empty] | 141 | 156 | Brushy Hill 120H | NS_120H_DSS | Lucasville 131H | NS_131H_DSS |  |  | 176
| L5019 | NSPI | Nova Scotia | 1 | ac | 2 | 1.2 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Canaan Rd. 43V | NS_43V_DSS | Lumsden 5V | NS_5V_GSS |  | Assumed Lumsden 5V on L5019 | 21
| L5547 | NSPI | Nova Scotia | 1 | ac | 2 | 1.2 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Lunenburg SW 79W | NS_79W_DSS | Lunenburg 81W | NS_81W_DSS |  |  | 129
| L5547 | NSPI | Nova Scotia | 1 | ac | 6 | 3.7 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Martins Brook 78W | NS_78W_DSS | Lunenburg SW 79W | NS_79W_DSS |  |  | 128
| L6054 | NSPI | Nova Scotia | 1 | ac | 30 | 18.5 | 138 | 13.0071 | 3 | [5 empty] | 141 | 156 | Canaan Rd. 43V | NS_43V_DSS | MacDonald Pond 101V | NS_101V_DSS |  |  | 211
| L6004 | NSPI | Nova Scotia | 1 | ac | 40 | 24.7 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | Hammonds 137H | NS_137H_DSS | MacDonald Pond 101V | NS_101V_DSS |  | Hammonds presumed to be on L6004 | 175
| L5547A | NSPI | Nova Scotia | 1 | ac | 3 | 1.9 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Mahone Bay Tap 77W | NS_77W_JCT | Mahone Bay 76W | NS_76W_DSS |  |  | 131
| L5547 | NSPI | Nova Scotia | 1 | ac | 3.5 | 2.2 | 69 | 1.345 | 3 | [5 empty] | 36 | 39 | Westhavers Elbow 75W | NS_75W_DSS | Mahone Bay Tap 77W | NS_77W_JCT |  |  | 126
| L5532 | NSPI | Nova Scotia | 1 | ac | 38 | 23.5 | 69 | 14.6029 | 3 | [5 empty] | 36 | 39 | Ridge 14V | NS_14V_GSS | Maitland Bridge 76V | NS_76V_DSS |  |  | 100
| L5510 | NSPI | Nova Scotia | 1 | ac | 35.6 | 22 | 69 | 13.6806 | 3 | [5 empty] | 36 | 39 | Trafalgar 89H | NS_89H_DSS | Malay Falls 95H | NS_95H_GSS |  |  | 88
| L5012 | NSPI | Nova Scotia | 1 | ac | 2.5 | 1.5 | 69 | 0.96071 | 3 | [5 empty] | 36 | 39 | Tuft's Cove 91H | NS_91H_GSS | Maple St. 54H | NS_54H_DSS |  |  | 10
| L5547 | NSPI | Nova Scotia | 1 | ac | 5 | 3.1 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Mahone Bay Tap 77W | NS_77W_JCT | Martins Brook 78W | NS_78W_DSS |  |  | 127
| L5020 | NSPI | Nova Scotia | 1 | ac | 9.2 | 5.7 | 69 | 3.5354 | 3 | [5 empty] | 36 | 39 | Hollow Bridge 6V | NS_6V_GSS | Methals 7V | NS_7V_GSS |  |  | 23
| L5022 | NSPI | Nova Scotia | 1 | ac | 10 | 6.2 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Waterville Tap 56V | NS_56V_JCT | Michelin 92V | NS_92V_ISS |  |  | 26
| L6002 | NSPI | Nova Scotia | 1 | ac | 15 | 9.3 | 138 | 6.5036 | 3 | [5 empty] | 141 | 156 | Westhavers Elbow 75W | NS_75W_DSS | Michelin Bridgewater 74W | NS_74W_ISS |  |  | 171
| L5031 | NSPI | Nova Scotia | 1 | ac | 8 | 4.9 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | East River 86E | NS_86E_JCT | Mid River 86W | NS_86W_JCT |  | East River 86E / Mid River 86W are junctions and not substations | 50
| L5532 | NSPI | Nova Scotia | 1 | ac | 22 | 13.6 | 69 | 8.4543 | 3 | [5 empty] | 36 | 39 | Caledonia 57W | NS_57W_DSS | Middlefield 91W | NS_91W_DSS |  |  | 103
| L5044 | NSPI | Nova Scotia | 1 | ac | 2 | 1.2 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Nictaux 10V | NS_10V_GSS | Middleton 65V | NS_65V_DSS |  |  | 65
| L5025 | NSPI | Nova Scotia | 1 | ac | 19 | 11.7 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Paradise 11V | NS_11V_DSS | Middleton Tap 65V | NS_65V_JCT |  |  | 30
| L6006 | NSPI | Nova Scotia | 1 | ac | 45 | 27.8 | 138 | 19.5107 | 3 | [5 empty] | 141 | 156 | Bridgewater 99W | NS_99W_DSS | Milton 50W | NS_50W_DSS |  |  | 178
| L6025 | NSPI | Nova Scotia | 1 | ac | 45 | 27.8 | 138 | 19.5107 | 3 | [5 empty] | 141 | 156 | Bridgewater 99W | NS_99W_DSS | Milton 50W | NS_50W_DSS |  |  | 196
| L6043 | NSPI | Nova Scotia | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Porters Lake 126H | NS_126H_DSS | Musquodoboit Harbour 87H | NS_87H_DSS |  |  | 206
| L5547 | NSPI | Nova Scotia | 1 | ac | 3 | 1.9 | 69 | 1.1529 | 3 | [5 empty] | 36 | 39 | Lunenburg 81W | NS_81W_DSS | National Sea 82W | NS_82W_ISS |  |  | 130
| L5033 | NSPI | Nova Scotia | 1 | ac | 2 | 1.2 | 69 | 0.76857 | 3 | [5 empty] | 36 | 39 | Canaan Rd. 43V | NS_43V_DSS | New Minas 22V | NS_22V_DSS |  |  | 53
| L5575 | NSPI | Nova Scotia | 1 | ac | 12.6 | 7.8 | 69 | 4.842 | 3 | [5 empty] | 36 | 39 | Whitney Pier 82S | NS_82S_DSS | New Waterford 15S | NS_15S_DSS |  |  | 157
| L5044 | NSPI | Nova Scotia | 1 | ac | 1.8 | 1.1 | 69 | 0.69171 | 3 | [5 empty] | 36 | 39 | Middleton Tap 65V | NS_65V_JCT | Nictaux 10V | NS_10V_GSS |  |  | 64
| L5508 | NSPI | Nova Scotia | 1 | ac | 1.7 | 1 | 69 | 0.65329 | 3 | [5 empty] | 36 | 39 | Abercrombie 54N | NS_54N_DSS | Northern Pulp 53N | NS_53N_ISS |  |  | 86
| L5040 | NSPI | Nova Scotia | 1 | ac | 22.3 | 13.8 | 69 | 8.5696 | 3 | [5 empty] | 36 | 39 | Onslow 1N | NS_1N_DSS | Nuttby Mountain 89N | NS_89N_GSS |  |  | 60
| L6527 | NSPI | Nova Scotia | 1 | ac | 0.1 | 0.1 | 138 | 0.043357 | 3 | [5 empty] | 141 | 156 | Onslow 1N | NS_1N_DSS | Onslow 67N | NS_67N_DSS |  | Internal transmission line | 230
| L5058 | NSPI | Nova Scotia | 1 | ac | 18 | 11.1 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | Springhill 74N | NS_74N_DFS | Oxford 3N | NS_3N_DSS |  |  | 78
| L5548 | NSPI | Nova Scotia | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Amherst 92N | NS_92N_GSS | Park St. 20N | NS_20N_DSS |  |  | 134
| L5550 | NSPI | Nova Scotia | 1 | ac | 33.7 | 20.8 | 69 | 12.9504 | 3 | [5 empty] | 36 | 39 | Maccan 30N | NS_30N_DSS | Parrsboro 37N | NS_37N_DSS |  |  | 139
| L5012 | NSPI | Nova Scotia | 1 | ac | 2.5 | 1.5 | 69 | 0.96071 | 3 | [5 empty] | 36 | 39 | Maple St. 54H | NS_54H_DSS | Penhorn 48H | NS_48H_DSS |  |  | 11
| L5506 | NSPI | Nova Scotia | 1 | ac | 7.4 | 4.6 | 69 | 2.8437 | 3 | [5 empty] | 36 | 39 | Abercrombie 54N | NS_54N_DSS | Pictou 55N | NS_55N_DSS |  |  | 84
| L5536 | NSPI | Nova Scotia | 1 | ac | 13 | 8 | 69 | 4.9957 | 3 | [5 empty] | 36 | 39 | Tusket 9W | NS_9W_GSS | Pleasant St. 88W | NS_88W_DSS |  |  | 110
| L7015 | NSPI | Nova Scotia | 1 | ac | 1 | 0.6 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Point Aconi 102S | NS_102S_GSS | Point Aconi 89S | NS_89S_DSS |  |  | 261
| L5555 | NSPI | Nova Scotia | 1 | ac | 5.5 | 3.4 | 69 | 2.1136 | 3 | [5 empty] | 36 | 39 | Prince Mine 86S | NS_86S_ISS | Point Aconi 89S | NS_89S_DSS |  |  | 142
| L6521 | NSPI | Nova Scotia | 1 | ac | 2 | 1.2 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Point Tupper 1C | NS_1C_DFS | Point Tupper 1C | NS_1C_DFS |  |  | 228
| L6517 | NSPI | Nova Scotia | 1 | ac | 8 | 4.9 | 138 | 3.4686 | 3 | [5 empty] | 141 | 156 | Port Hastings 2C | NS_2C_DSS | Point Tupper 1C | NS_1C_DFS |  |  | 226
| L6515 | NSPI | Nova Scotia | 1 | ac | 2 | 1.2 | 138 | 0.86714 | 3 | [5 empty] | 141 | 156 | Cape Porcupine 100C | NS_100C_DSS | Port Hastings 2C | NS_2C_DSS |  |  | 222
| L7003 | NSPI | Nova Scotia | 1 | ac | 175 | 108 | 230 | 84 | 1.9334 | [5 empty] | 259.0763 | 280.3438 | Onslow 67N | NS_67N_DSS | Port Hastings 3C | NS_3C_DSS |  |  | 253
| L7005 | NSPI | Nova Scotia | 1 | ac | 175 | 108 | 230 | 84 | 1.9334 | [5 empty] | 259.0763 | 280.3438 | Onslow 67N | NS_67N_DSS | Port Hastings 3C | NS_3C_DSS |  |  | 255
| L6543 | NSPI | Nova Scotia | 1 | ac | 0.1 | 0.1 | 138 | 0.043357 | 3 | [5 empty] | 141 | 156 | Port Hastings 2C | NS_2C_DSS | Port Hastings 3C | NS_3C_DSS |  | Internal transmission line | 243
| L6548 | NSPI | Nova Scotia | 1 | ac | 0.1 | 0.1 | 138 | 0.043357 | 3 | [5 empty] | 141 | 156 | Port Hastings 2C | NS_2C_DSS | Port Hastings 3C | NS_3C_DSS |  | Internal transmission line | 245
| L6043 | NSPI | Nova Scotia | 1 | ac | 18 | 11.1 | 138 | 7.8043 | 3 | [5 empty] | 141 | 156 | Dartmouth East 113H | NS_113H_DSS | Porters Lake 126H | NS_126H_DSS |  | Porters Lake presumed to be on L6043 | 205
| L5555 | NSPI | Nova Scotia | 1 | ac | 10 | 6.2 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Gannon Rd. 3S | NS_3S_DSS | Prince Mine 86S | NS_86S_ISS |  |  | 141
| L5027 | NSPI | Nova Scotia | 1 | ac | 12.5 | 7.7 | 69 | 4.8036 | 3 | [5 empty] | 36 | 39 | Argyle 19W | NS_19W_DSS | Pubnico 20W | NS_20W_DSS |  |  | 37
| L5027 | NSPI | Nova Scotia | 1 | ac | 12.5 | 7.7 | 69 | 4.8036 | 3 | [5 empty] | 36 | 39 | Pubnico 20W | NS_20W_DSS | Pubnico Point 106W | NS_106W_GSS |  |  | 38
| L5058 | NSPI | Nova Scotia | 1 | ac | 21.3 | 13.1 | 69 | 8.1853 | 3 | [5 empty] | 36 | 39 | Oxford 3N | NS_3N_DSS | Pugwash 7N | NS_7N_DSS |  |  | 79
| L5572 | NSPI | Nova Scotia | 1 | ac | 9.6 | 5.9 | 69 | 3.6891 | 3 | [5 empty] | 36 | 39 | Victoria Junction 2S | NS_2S_DSS | Reserve 81S | NS_81S_DSS |  |  | 154
| L5532 | NSPI | Nova Scotia | 1 | ac | 4 | 2.5 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Gulch 13V | NS_13V_DFS | Ridge 14V | NS_14V_GSS |  |  | 99
| L5055 | NSPI | Nova Scotia | 1 | ac | 20.8 | 12.8 | 69 | 7.9931 | 3 | [5 empty] | 36 | 39 | Rio Algoma Tap 99X | NS_99X_JCT | Rio Algoma 99X | NS_99X_DSS |  | 99X name given to Rio Algoma | 74
| L5535 | NSPI | Nova Scotia | 1 | ac | 40.3 | 24.9 | 69 | 15.4867 | 3 | [5 empty] | 36 | 39 | Sissiboo 15V | NS_15V_GSS | Rio Algoma Tap 99X | NS_99X_JCT |  |  | 107
| L5551 | NSPI | Nova Scotia | 1 | ac | 9.7 | 6 | 69 | 3.7276 | 3 | [5 empty] | 36 | 39 | Lunenburg SW 79W | NS_79W_DSS | Riverport 80W | NS_80W_DSS |  |  | 140
| L5031 | NSPI | Nova Scotia | 1 | ac | 1.8 | 1.1 | 69 | 0.69171 | 3 | [5 empty] | 36 | 39 | Mid River 86W | NS_86W_JCT | Robinson's Corner 84W | NS_84W_DSS |  | Mid River 86W is a junction not a substation | 51
| L5032 | NSPI | Nova Scotia | 1 | ac | 0.8 | 0.5 | 69 | 0.30743 | 3 | [5 empty] | 36 | 39 | Rockingham Tap 23H | NS_23H_JCT | Rockingham 23H | NS_23H_DSS |  |  | 52
| L5004 | NSPI | Nova Scotia | 1 | ac | 9.9 | 6.1 | 69 | 3.8044 | 3 | [5 empty] | 36 | 39 | Sackville 90H | NS_90H_DSS | Rockingham Tap 23H | NS_23H_JCT |  |  | 5
| L5512 | NSPI | Nova Scotia | 1 | ac | 6.5 | 4 | 69 | 2.4979 | 3 | [5 empty] | 36 | 39 | Malay Falls 95H | NS_95H_GSS | Ruth Falls 96H | NS_96H_DSS |  |  | 90
| L5003 | NSPI | Nova Scotia | 1 | ac | 8 | 4.9 | 69 | 3.0743 | 3 | [5 empty] | 36 | 39 | Akerly 124H | NS_124H_DSS | Sackville 90H | NS_90H_DSS |  |  | 4
| L6005 | NSPI | Nova Scotia | 1 | ac | 7 | 4.3 | 138 | 3.035 | 3 | [5 empty] | 141 | 156 | Lucasville 131H | NS_131H_DSS | Sackville 90H | NS_90H_DSS |  |  | 177
| L6003 | NSPI | Nova Scotia | 1 | ac | 12 | 7.4 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Tuft's Cove 91H | NS_91H_GSS | Sackville 90H | NS_90H_DSS |  |  | 173
| L5524 | NSPI | Nova Scotia | 1 | ac | 35.4 | 21.9 | 69 | 13.6037 | 3 | [5 empty] | 36 | 39 | Lochaber Road 4C | NS_4C_DSS | Salmon River Lake 57C | NS_57C_DSS |  |  | 92
| L5054 | NSPI | Nova Scotia | 1 | ac | 23.4 | 14.4 | 69 | 8.9923 | 3 | [5 empty] | 36 | 39 | Weymouth 16V | NS_16V_GSS | Saulnierville 93V | NS_93V_DSS |  |  | 73
| L5572 | NSPI | Nova Scotia | 1 | ac | 4 | 2.5 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Reserve 81S | NS_81S_DSS | Seaboard 1S | NS_1S_DSS |  |  | 155
| L5561 | NSPI | Nova Scotia | 1 | ac | 15 | 9.3 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | VIctoria Junction 2S | NS_2S_DSS | Seaboard 1S | NS_1S_DSS |  |  | 147
| L5530 | NSPI | Nova Scotia | 1 | ac | 16 | 9.9 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Green Harbour 36W | NS_36W_DSS | Shelburne 25W | NS_25W_DSS |  |  | 97
| L5027 | NSPI | Nova Scotia | 1 | ac | 6 | 3.7 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Souriquois 30W | NS_30W_DSS | Shelburne 25W | NS_25W_DSS |  |  | 43
| L5531 | NSPI | Nova Scotia | 1 | ac | 23.9 | 14.8 | 69 | 9.1844 | 3 | [5 empty] | 36 | 39 | Gulch 13V | NS_13V_DFS | Sissiboo 15V | NS_15V_GSS |  |  | 98
| L5027 | NSPI | Nova Scotia | 1 | ac | 15 | 9.3 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Clyde River 23W | NS_23W_DSS | Souriquois 30W | NS_30W_DSS |  |  | 42
| L6020 | NSPI | Nova Scotia | 1 | ac | 70 | 43.2 | 138 | 30.35 | 3 | [5 empty] | 141 | 156 | Milton 50W | NS_50W_DSS | Souriquois 30W | NS_30W_DSS |  |  | 193
| L6053 | NSPI | Nova Scotia | 1 | ac | 25 | 15.4 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | MacDonald Pond 101V | NS_101V_DSS | South Canoe 110W | NS_110W_GSS |  |  | 210
| L6001 | NSPI | Nova Scotia | 1 | ac | 15 | 9.3 | 138 | 6.5036 | 3 | [5 empty] | 141 | 156 | Aerotech Park Tap 127H | NS_127H_JCT | Spider Lake 132H | NS_132H_DSS |  |  | 164
| L6040 | NSPI | Nova Scotia | 1 | ac | 4 | 2.5 | 138 | 1.7343 | 3 | [5 empty] | 141 | 156 | Dartmouth Crossing 139H | NS_139H_DSS | Spider Lake 132H | NS_132H_DSS |  |  | 202
| L6613 | NSPI | Nova Scotia | 1 | ac | 50 | 30.9 | 138 | 21.6786 | 3 | [5 empty] | 141 | 156 | Debert 81N | NS_81N_DSS | Springhill 74N | NS_74N_DFS |  | Formerly L6513 | 250
| L5029 | NSPI | Nova Scotia | 1 | ac | 20.2 | 12.5 | 69 | 7.7626 | 3 | [5 empty] | 36 | 39 | Maccan 30N | NS_30N_DSS | Springhill 74N | NS_74N_DFS |  |  | 46
| L6514 | NSPI | Nova Scotia | 1 | ac | 13 | 8 | 138 | 5.6364 | 3 | [5 empty] | 141 | 156 | Maccan 30N | NS_30N_DSS | Springhill 74N | NS_74N_DFS |  |  | 220
| L5039 | NSPI | Nova Scotia | 1 | ac | 6 | 3.7 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Geizer Hill 34H | NS_34H_DSS | Spryfield 20H | NS_20H_DSS |  |  | 59
| L6011 | NSPI | Nova Scotia | 1 | ac | 25 | 15.4 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Brushy Hill 120H | NS_120H_DSS | St. Croix 17V | NS_17V_DSS |  |  | 186
| L6012 | NSPI | Nova Scotia | 1 | ac | 25 | 15.4 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Brushy Hill 120H | NS_120H_DSS | St. Croix 17V | NS_17V_DSS |  |  | 187
| L6051 | NSPI | Nova Scotia | 1 | ac | 25 | 15.4 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Brushy Hill 120H | NS_120H_DSS | St. Croix 17V | NS_17V_DSS |  |  | 208
| L5014 | NSPI | Nova Scotia | 1 | ac | 2.8 | 1.7 | 69 | 1.076 | 3 | [5 empty] | 36 | 39 | Ellershouse 102V | NS_102V_GSS | St. Croix 17V | NS_17V_DSS |  | Assumed L5014 transmission connection | 13
| L6516 | NSPI | Nova Scotia | 1 | ac | 27 | 16.7 | 138 | 11.7064 | 3 | [5 empty] | 141 | 156 | Cleveland 22C | NS_22C_DSS | St. Peters 59C | NS_59C_DSS |  |  | 224
| L5028 | NSPI | Nova Scotia | 1 | ac | 15.9 | 9.8 | 69 | 6.1101 | 3 | [5 empty] | 36 | 39 | Lafarge 11N | NS_11N_DSS | Stewiacke 16N | NS_16N_DSS |  |  | 45
| L6523 | NSPI | Nova Scotia | 1 | ac | 4 | 2.5 | 138 | 1.7343 | 3 | [5 empty] | 141 | 156 | Point Tupper 1C | NS_1C_DFS | Stora 47C | NS_47C_DSS |  |  | 229
| L6518 | NSPI | Nova Scotia | 1 | ac | 10 | 6.2 | 138 | 4.3357 | 3 | [5 empty] | 141 | 156 | Port Hastings 2C | NS_2C_DSS | Stora 47C | NS_47C_DSS |  |  | 227
| L5579 | NSPI | Nova Scotia | 1 | ac | 41.1 | 25.4 | 69 | 15.7941 | 3 | [5 empty] | 36 | 39 | Cheticamp 103C | NS_103C_DSS | SW Margaree 58C | NS_58C_DSS |  |  | 159
| L5559 | NSPI | Nova Scotia | 1 | ac | 38.7 | 23.9 | 69 | 14.8719 | 3 | [5 empty] | 36 | 39 | Whycocomagh 67C | NS_67C_DSS | SW Margaree 58C | NS_58C_DSS |  |  | 144
| L5040 | NSPI | Nova Scotia | 1 | ac | 20 | 12.3 | 69 | 7.6857 | 3 | [5 empty] | 36 | 39 | Nuttby Mountain 89N | NS_89N_GSS | Tatamagouche 4N | NS_4N_DSS |  |  | 61
| L5015 | NSPI | Nova Scotia | 1 | ac | 9 | 5.6 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | St. Croix 17V | NS_17V_DSS | Three Mile Plains 79V | NS_79V_DSS |  |  | 15
| L6002 | NSPI | Nova Scotia | 1 | ac | 25 | 15.4 | 138 | 10.8393 | 3 | [5 empty] | 141 | 156 | Sackville 90H | NS_90H_DSS | Tidewater 92H | NS_92H_GSS |  |  | 167
| L5569 | NSPI | Nova Scotia | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Terrace St. 6S | NS_6S_DSS | Townsend St. 4S | NS_4S_DSS |  |  | 152
| L5560 | NSPI | Nova Scotia | 1 | ac | 0.1 | 0.1 | 69 | 0.038429 | 3 | [5 empty] | 36 | 39 | Victoria Junction 83S | NS_83S_GSS | Townsend St. 4S | NS_4S_DSS |  |  | 146
| L5563 | NSPI | Nova Scotia | 1 | ac | 0.1 | 0.1 | 69 | 0.038429 | 3 | [5 empty] | 36 | 39 | Victoria Junction 83S | NS_83S_GSS | Townsend St. 4S | NS_4S_DSS |  |  | 149
| L5510 | NSPI | Nova Scotia | 1 | ac | 34.8 | 21.5 | 69 | 13.3731 | 3 | [5 empty] | 36 | 39 | Bridge Avenue 62N | NS_62N_DSS | Trafalgar 89H | NS_89H_DSS |  |  | 87
| L5053 | NSPI | Nova Scotia | 1 | ac | 18 | 11.1 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | Berwick Tap 53V | NS_53V_JCT | Tremont 51V | NS_51V_DSS |  |  | 72
| L6013 | NSPI | Nova Scotia | 1 | ac | 40 | 24.7 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | Canaan Rd. 43V | NS_43V_DSS | Tremont 51V | NS_51V_DSS |  |  | 189
| L6015 | NSPI | Nova Scotia | 1 | ac | 40 | 24.7 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | Canaan Rd. 43V | NS_43V_DSS | Tremont 51V | NS_51V_DSS |  |  | 191
| L5025 | NSPI | Nova Scotia | 1 | ac | 11.2 | 6.9 | 69 | 4.304 | 3 | [5 empty] | 36 | 39 | Middleton Tap 65V | NS_65V_JCT | Tremont 51V | NS_51V_DSS |  |  | 31
| L6503 | NSPI | Nova Scotia | 1 | ac | 10 | 6.2 | 138 | 4.3357 | 3 | [5 empty] | 141 | 156 | Granton 49N | NS_49N_ISS | Trenton 50N | NS_50N_DFS |  |  | 213
| L6014 | NSPI | Nova Scotia | 1 | ac | 3 | 1.9 | 138 | 1.3007 | 3 | [5 empty] | 141 | 156 | Kempt Road 104H | NS_104H_DSS | Tuft's Cove 91H | NS_91H_GSS |  |  | 190
| L5041 | NSPI | Nova Scotia | 1 | ac | 0.1 | 0.1 | 69 | 0.038429 | 3 | [5 empty] | 36 | 39 | Tuft's Cove 91H | NS_91H_GSS | Tuft's Cove 91H | NS_91H_GSS |  | Internal transmission line | 62
| L5535 | NSPI | Nova Scotia | 1 | ac | 16 | 9.9 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Carleton 92W | NS_92W_DSS | Tusket 9W | NS_9W_GSS |  |  | 109
| L6024 | NSPI | Nova Scotia | 1 | ac | 120 | 74.1 | 138 | 52.0286 | 2.4787 | [5 empty] | 116.498 | 128.8914 | Milton 50W | NS_50W_DSS | Tusket 9W | NS_9W_GSS |  |  | 195
| L6021 | NSPI | Nova Scotia | 1 | ac | 50 | 30.9 | 138 | 21.6786 | 3 | [5 empty] | 141 | 156 | Souriquois 30W | NS_30W_DSS | Tusket 9W | NS_9W_GSS |  |  | 194
| L5537 | NSPI | Nova Scotia | 1 | ac | 3.4 | 2.1 | 69 | 1.3066 | 3 | [5 empty] | 36 | 39 | Tusket 9W | NS_9W_GSS | Tusket Oil 10W | NS_10W_GSS |  |  | 113
| L5014 | NSPI | Nova Scotia | 1 | ac | 10.8 | 6.7 | 69 | 4.1503 | 3 | [5 empty] | 36 | 39 | St. Croix 17V | NS_17V_DSS | Upper Burlington 18V | NS_18V_DSS |  |  | 14
| L5544 | NSPI | Nova Scotia | 1 | ac | 1.5 | 0.9 | 69 | 0.57643 | 3 | [5 empty] | 36 | 39 | Lower Lake Falls 2W | NS_2W_GSS | Upper Lake Falls 1W | NS_1W_GSS |  |  | 121
| L5511 | NSPI | Nova Scotia | 1 | ac | 31.7 | 19.6 | 69 | 12.1819 | 3 | [5 empty] | 36 | 39 | Trafalgar 89H | NS_89H_DSS | Upper Musquodoboit 88H | NS_88H_DSS |  |  | 89
| L6539 | NSPI | Nova Scotia | 1 | ac | 30 | 18.5 | 138 | 13.0071 | 3 | [5 empty] | 141 | 156 | Gannon Rd. 3S | NS_3S_DSS | Victoria Junction 2S | NS_2S_DSS |  |  | 242
| L6516 | NSPI | Nova Scotia | 1 | ac | 95 | 58.6 | 138 | 41.1893 | 2.8936 | [5 empty] | 135.9989 | 150.4668 | St. Peters 59C | NS_59C_DSS | Victoria Junction 2S | NS_2S_DSS |  |  | 225
| L5560 | NSPI | Nova Scotia | 1 | ac | 7.4 | 4.6 | 69 | 2.8437 | 3 | [5 empty] | 36 | 39 | Victoria Junction 2S | NS_2S_DSS | Victoria Junction 83S | NS_83S_GSS |  |  | 145
| L5563 | NSPI | Nova Scotia | 1 | ac | 7.4 | 4.6 | 69 | 2.8437 | 3 | [5 empty] | 36 | 39 | Victoria Junction 2S | NS_2S_DSS | Victoria Junction 83S | NS_83S_GSS |  |  | 148
| L6033 | NSPI | Nova Scotia | 1 | ac | 6 | 3.7 | 138 | 2.6014 | 3 | [5 empty] | 141 | 156 | Armdale 2H | NS_2H_DSS | Water St. 1H | NS_1H_DSS |  |  | 198
| L5023 | NSPI | Nova Scotia | 1 | ac | 1.2 | 0.7 | 69 | 0.46114 | 3 | [5 empty] | 36 | 39 | Waterville Tap 56V | NS_56V_JCT | Waterville 55V | NS_55V_DSS |  |  | 27
| L5022 | NSPI | Nova Scotia | 1 | ac | 5 | 3.1 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Canaan Rd. 43V | NS_43V_DSS | Waterville Tap 56V | NS_56V_JCT |  |  | 25
| L5546 | NSPI | Nova Scotia | 1 | ac | 12.5 | 7.7 | 69 | 4.8036 | 3 | [5 empty] | 36 | 39 | Bridgewater 99W | NS_99W_DSS | Westhavers Elbow 75W | NS_75W_DSS |  |  | 125
| L6002 | NSPI | Nova Scotia | 1 | ac | 15 | 9.3 | 138 | 6.5036 | 3 | [5 empty] | 141 | 156 | Gold River 103W | NS_103W_DSS | Westhavers Elbow 75W | NS_75W_DSS |  |  | 170
| L5538 | NSPI | Nova Scotia | 1 | ac | 7.5 | 4.6 | 69 | 2.8821 | 3 | [5 empty] | 36 | 39 | Sissiboo 15V | NS_15V_GSS | Weymouth 16V | NS_16V_GSS |  |  | 114
| L5017 | NSPI | Nova Scotia | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Wolfville Ridge Tap 83V | NS_83V_JCT | White Rock 4V | NS_4V_GSS |  | Assumed White Rock 4V on L5017 | 19
| L5571 | NSPI | Nova Scotia | 1 | ac | 6.4 | 4 | 69 | 2.4594 | 3 | [5 empty] | 36 | 39 | Victoria Junction 2S | NS_2S_DSS | Whitney Pier 82S | NS_82S_DSS |  |  | 153
| L5521 | NSPI | Nova Scotia | 1 | ac | 4.5 | 2.8 | 69 | 1.7293 | 3 | [5 empty] | 36 | 39 | Onslow 1N | NS_1N_DSS | Willow Lane 15N | NS_15N_DSS |  |  | 91
| L5046 | NSPI | Nova Scotia | 1 | ac | 2.7 | 1.7 | 69 | 1.0376 | 3 | [5 empty] | 36 | 39 | Wolfville Ridge Tap 83V | NS_83V_JCT | Wolfville Ridge 83V | NS_83V_DSS |  |  | 66
| L5017 | NSPI | Nova Scotia | 1 | ac | 12 | 7.4 | 69 | 4.6114 | 3 | [5 empty] | 36 | 39 | Five Points 20V | NS_20V_DSS | Wolfville Ridge Tap 83V | NS_83V_JCT |  |  | 18
| L8004 | NSPI | Nova Scotia | 1 | ac | 320 | 197.5 | 345 | 142.0148 | 1.2985 | [5 empty] | 422.01 | 551.8592 | Hopewell 79N | NS_79N_DSS | Woodbine 101S | NS_101S_DSS |  |  | 270
| L7014 | NSPI | Nova Scotia | 1 | ac | 40 | 24.7 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Lingan 88S | NS_88S_GSS | Woodbine 101S | NS_101S_DSS |  |  | 260
| L7021 | NSPI | Nova Scotia | 1 | ac | 40 | 24.7 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Lingan 88S | NS_88S_GSS | Woodbine 101S | NS_101S_DSS |  |  | 265
| L7022 | NSPI | Nova Scotia | 1 | ac | 40 | 24.7 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Lingan 88S | NS_88S_GSS | Woodbine 101S | NS_101S_DSS |  |  | 266
| L7015 | NSPI | Nova Scotia | 1 | ac | 45 | 27.8 | 230 | 21.6 | 3 | [5 empty] | 402 | 435 | Point Aconi 89S | NS_89S_DSS | Woodbine 101S | NS_101S_DSS |  |  | 262
| L5011 | NSPI | Nova Scotia | 1 | ac | 6 | 3.7 | 69 | 2.3057 | 3 | [5 empty] | 36 | 39 | Farrell St. 99H | NS_99H_DSS | Woodlawn 40H | NS_40H_DSS |  |  | 8
| L5027 | NSPI | Nova Scotia | 1 | ac | 10 | 6.2 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Pubnico Point 106W | NS_106W_GSS | Woods Harbour 21W | NS_21W_DSS |  |  | 39
| L5536 | NSPI | Nova Scotia | 1 | ac | 1 | 0.6 | 69 | 0.38429 | 3 | [5 empty] | 36 | 39 | Pleasant St. 88W | NS_88W_DSS | Yarmouth 11W | NS_11W_DSS |  |  | 111
Legend:
CSS = Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
ISS = Industrial Customer Substation
JCT = Junction
SWS = Switching Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## Nodes
NS | EXISTING SUBSTATIONS
| Node Name | Node Code | Owner | Latitude | Longitude | Operating Region | Other References | Notes
| Abercrombie 54N | NS_54N_DSS | NSPI | 45.6407 | -62.706 | Nova Scotia
| Aberdeen 9C | NS_9C_DSS | NSPI | 45.993 | -61.0071 | Nova Scotia
| Aberdeen St. 10N | NS_10N_DSS | NSPI | 45.6593 | -64.0623 | Nova Scotia
| Aerotech Park 127H | NS_127H_DSS | NSPI | 44.8512 | -63.5508 | Nova Scotia
| Aerotech Park Tap 127H | NS_127H_JCT | NSPI | 44.8557 | -63.5987 | Nova Scotia
| Akerly 124H | NS_124H_DSS | NSPI | 44.7191 | -63.5838 | Nova Scotia
| Albert Bridge 57S | NS_57S_DSS | NSPI | 46.0343 | -60.0699 | Nova Scotia
| Albro Lake 62H | NS_62H_DSS | NSPI | 44.6858 | -63.574 | Nova Scotia
| Amherst 92N | NS_92N_GSS | NSPI | 45.8257 | -64.24 | Nova Scotia
| Annapolis 81V | NS_81V_GSS | NSPI | 44.7524 | -65.5113 | Nova Scotia
| Annapolis Tap 81V | NS_81V_JCT | NSPI | 44.7231 | -65.4938 | Nova Scotia
| Argyle 19W | NS_19W_DSS | NSPI | 43.7834 | -65.8448 | Nova Scotia
| Armdale 2H | NS_2H_DSS | NSPI | 44.6427 | -63.6193 | Nova Scotia
| Auburndale 73W | NS_73W_DSS | NSPI | 44.3861 | -64.5561 | Nova Scotia
| Avon 1V | NS_1V_GSS | NSPI | 44.8814 | -64.2172 | Nova Scotia
| Baddeck 104S | NS_104S_DFS | NSPI | 46.1079 | -60.7538 | Nova Scotia
| Baddeck Tap 104S | NS_104S_JCT | NSPI | 46.1241 | -60.7657 | Nova Scotia
| Barrington 22W | NS_22W_DSS | NSPI | 43.523 | -65.6148 | Nova Scotia
| Berwick 52V | NS_52V_DSS | NSPI | 45.0445 | -64.7355 | Nova Scotia |  | Location approximate
| Berwick Tap 53V | NS_53V_JCT | NSPI | 45.027 | -64.7344 | Nova Scotia |  | Location approximate
| Big Falls 3W | NS_3W_GSS | NSPI | 44.1384 | -64.9344 | Nova Scotia
| Black River Rd. 6N | NS_6N_DSS | NSPI | 45.6347 | -64.075 | Nova Scotia
| Bridge Avenue 62N | NS_62N_DSS | NSPI | 45.5644 | -62.6553 | Nova Scotia
| Bridgetown 70V | NS_70V_DSS | NSPI | 44.8368 | -65.2989 | Nova Scotia |  | Location approximate
| Bridgetown Tap 70V | NS_70V_JCT | NSPI | 44.8192 | -65.2785 | Nova Scotia
| Bridgewater 99W | NS_99W_DSS | NSPI | 44.3947 | -64.5565 | Nova Scotia
| Bridgewater East 89W | NS_89W_DSS | NSPI | 44.3983 | -64.4894 | Nova Scotia
| Broad River 46W | NS_46W_DSS | NSPI | 43.9539 | -64.8348 | Nova Scotia
| Brooklyn 104W | NS_104W_DSS | NSPI | 44.0516 | -64.6992 | Nova Scotia
| Brownell St. 17N | NS_17N_DSS | NSPI | 45.8377 | -64.2152 | Nova Scotia
| Brushy Hill 120H | NS_120H_DSS | NSPI | 44.8532 | -63.7636 | Nova Scotia
| Burnside 108H | NS_108H_DSS | NSPI | 44.713 | -63.6113 | Nova Scotia
| Burnside 14H | NS_14H_GSS | NSPI | 44.713 | -63.6113 | Nova Scotia
| Caledonia 57W | NS_57W_DSS | NSPI | 44.3769 | -65.0241 | Nova Scotia
| Canaan Rd. 43V | NS_43V_DSS | NSPI | 45.0495 | -64.4199 | Nova Scotia
| Canexel 85W | NS_85W_ISS | NSPI | 44.5852 | -64.1621 | Nova Scotia
| Canso 19C | NS_19C_DSS | NSPI | 45.3366 | -61.0014 | Nova Scotia
| Cape Porcupine 100C | NS_100C_DSS | NSPI | 45.6399 | -61.4307 | Nova Scotia
| Carleton 92W | NS_92W_DSS | NSPI | 43.9932 | -65.9397 | Nova Scotia
| Cheticamp 103C | NS_103C_DSS | NSPI | 46.619 | -60.9928 | Nova Scotia
| Church St. 22N | NS_22N_DSS | NSPI | 45.823 | -64.1882 | Nova Scotia
| Cleveland 22C | NS_22C_DSS | NSPI | 45.6714 | -61.239 | Nova Scotia
| Clyde River 23W | NS_23W_DSS | NSPI | 43.6371 | -65.4796 | Nova Scotia
| Cobequid Rd. 101H | NS_101H_DSS | NSPI | 44.7553 | -63.6611 | Nova Scotia
| Conway 77V | NS_77V_DSS | NSPI | 44.6 | -65.7782 | Nova Scotia
| Cornwallis 74V | NS_74V_DSS | NSPI | 44.6542 | -65.6318 | Nova Scotia
| Cornwallis Tap 74V | NS_74V_JCT | NSPI | 44.6419 | -65.6167 | Nova Scotia
| Cowie Falls 6W | NS_6W_GSS | NSPI | 44.0744 | -64.7707 | Nova Scotia
| Dalhousie Mountain 91N | NS_91N_GSS | NSPI | 45.4656 | -63.1076 | Nova Scotia
| Dartmouth Crossing 139H | NS_139H_DSS | NSPI | 44.716 | -63.5662 | Nova Scotia
| Dartmouth East 113H | NS_113H_DSS | NSPI | 44.7014 | -63.4814 | Nova Scotia
| Debert 81N | NS_81N_DSS | NSPI | 45.44 | -63.453 | Nova Scotia
| Deep Brook 5W | NS_5W_GSS | NSPI | 44.0805 | -64.7909 | Nova Scotia
| Dickie Brook 24C | NS_24C_DFS | NSPI | 45.3481 | -61.5032 | Nova Scotia
| Domtar 75N | NS_75N_ISS | NSPI | 45.7835 | -64.2323 | Nova Scotia
| Donkin Road 97S | NS_97S_DSS | NSPI | 46.1786 | -59.8267 | Nova Scotia
| East River 86E | NS_86E_JCT | NSPI | 44.6168 | -64.1564 | Nova Scotia
| Ellershouse 102V | NS_102V_GSS | NSPI | 44.9355 | -64.0283 | Nova Scotia
| Elmsdale 82V | NS_82V_DSS | NSPI | 44.9635 | -63.4984 | Nova Scotia
| Farrell St. 99H | NS_99H_DSS | NSPI | 44.6766 | -63.5903 | Nova Scotia
| Five Points 20V | NS_20V_DSS | NSPI | 45.0641 | -64.1925 | Nova Scotia
| Fourth Lake 91V | NS_91V_GSS | NSPI | 44.3696 | -65.7193 | Nova Scotia
| Gannon Rd. 3S | NS_3S_DSS | NSPI | 46.2299 | -60.2573 | Nova Scotia
| Geizer Hill 34H | NS_34H_DSS | NSPI | 44.6466 | -63.6482 | Nova Scotia
| Glen Dhu 93N | NS_93N_GSS | NSPI | 45.6467 | -62.2216 | Nova Scotia
| Glen Tosh 5S | NS_5S_DSS | NSPI | 46.1806 | -60.621 | Nova Scotia
| Gold River 103W | NS_103W_DSS | NSPI | 44.5584 | -64.3318 | Nova Scotia
| Granton 49N | NS_49N_ISS | NSPI | 45.6146 | -62.7376 | Nova Scotia
| Green Harbour 36W | NS_36W_DSS | NSPI | 43.739 | -65.1348 | Nova Scotia
| Greenwood 64V | NS_64V_DSS | NSPI | 44.9671 | -64.9408 | Nova Scotia
| Gulch 13V | NS_13V_DFS | NSPI | 44.567 | -65.635 | Nova Scotia
| Gullivers Cove 98V | NS_98V_DSS | NSPI | 44.5913 | -65.9447 | Nova Scotia
| Haliburton 56N | NS_56N_DSS | NSPI | 45.6757 | -62.7314 | Nova Scotia
| Hammonds 137H | NS_137H_DSS | NSPI | 44.7234 | -63.7351 | Nova Scotia
| Harmony 7W | NS_7W_DSS | NSPI | 44.4161 | -65.0562 | Nova Scotia
| Hebron 16W | NS_16W_DSS | NSPI | 43.8935 | -66.0803 | Nova Scotia
| Hells Gate 3V | NS_3V_GSS | NSPI | 45.0354 | -64.4033 | Nova Scotia
| Hickman St. 19N | NS_19N_DSS | NSPI | 45.818 | -64.2102 | Nova Scotia
| High St. 70W | NS_70W_DSS | NSPI | 44.3705 | -64.5279 | Nova Scotia
| Highbury 99V | NS_99V_DSS | NSPI | 45.0488 | -64.422 | Nova Scotia
| Hillaton 36V | NS_36V_DSS | NSPI | 45.145 | -64.4503 | Nova Scotia
| Hollow Bridge 6V | NS_6V_GSS | NSPI | 45.0038 | -64.3759 | Nova Scotia
| Hopewell 79N | NS_79N_DSS | NSPI | 45.4543 | -62.6676 | Nova Scotia
| Hubbards 87W | NS_87W_DSS | NSPI | 44.6444 | -64.0884 | Nova Scotia
| Imperial Oil 58H | NS_58H_ISS | NSPI | 44.644 | -63.5373 | Nova Scotia
| IPT Amherst | PP_NSNB2_IPT | NSPI | 45.8638 | -64.2629 | Nova Scotia
| IPT Church St | PP_NSNB3_IPT | NSPI | 45.8975 | -64.2274 | Nova Scotia
| IPT Onslow | PP_NSNB1_IPT | NSPI | 45.8975 | -64.2274 | Nova Scotia
| IPT Woodbine | PP_NSNL1_IPT | NSPI | 46.9965 | -59.44 | Nova Scotia |  | Midway across Cabot Strait
| Kearney Lake 129H | NS_129H_DSS | NSPI | 44.684 | -63.6788 | Nova Scotia
| Keltic Drive 11S | NS_11S_DSS | NSPI | 46.1201 | -60.2365 | Nova Scotia
| Kempt Road 104H | NS_104H_DSS | NSPI | 44.6589 | -63.6063 | Nova Scotia
| Kingston 63V | NS_63V_DSS | NSPI | 44.9853 | -64.9539 | Nova Scotia
| Klondike 50V | NS_50V_DSS | NSPI | 45.0687 | -64.502 | Nova Scotia
| Lafarge 11N | NS_11N_DSS | NSPI | 45.2493 | -63.3004 | Nova Scotia
| Lakeside 103H | NS_103H_DSS | NSPI | 44.644 | -63.6835 | Nova Scotia
| Lequille 12V | NS_12V_GSS | NSPI | 44.7255 | -65.4968 | Nova Scotia
| Lingan 88S | NS_88S_GSS | NSPI | 46.2357 | -60.0411 | Nova Scotia
| Lingan Mine 80S | NS_80S_DSS | NSPI | 46.2437 | -60.0619 | Nova Scotia
| Lingan Wind 109S | NS_109S_GSS | NSPI | 46.2423 | -60.0426 | Nova Scotia
| Liverpool 48W | NS_48W_DSS | NSPI | 44.0351 | -64.7143 | Nova Scotia
| Lochaber Road 4C | NS_4C_DSS | NSPI | 45.6069 | -61.9983 | Nova Scotia
| Lockeport 37W | NS_37W_DSS | NSPI | 43.7019 | -65.114 | Nova Scotia
| Lower Great Brook 4W | NS_4W_GSS | NSPI | 44.09 | -64.848 | Nova Scotia
| Lower Lake Falls 2W | NS_2W_GSS | NSPI | 44.1577 | -64.9772 | Nova Scotia
| Lucasville 131H | NS_131H_DSS | NSPI | 44.7552 | -63.7367 | Nova Scotia
| Lumsden 5V | NS_5V_GSS | NSPI | 45.027 | -64.3965 | Nova Scotia
| Lunenburg 81W | NS_81W_DSS | NSPI | 44.3818 | -64.3183 | Nova Scotia
| Lunenburg SW 79W | NS_79W_DSS | NSPI | 44.3689 | -64.3389 | Nova Scotia
| Maccan 30N | NS_30N_DSS | NSPI | 45.7174 | -64.2641 | Nova Scotia
| MacDonald Pond 101V | NS_101V_DSS | NSPI | 44.8818 | -64.2216 | Nova Scotia
| Mahone Bay 76W | NS_76W_DSS | NSPI | 44.4464 | -64.3817 | Nova Scotia
| Mahone Bay Tap 77W | NS_77W_JCT | NSPI | 44.438 | -64.3938 | Nova Scotia
| Maitland Bridge 76V | NS_76V_DSS | NSPI | 44.4439 | -65.1928 | Nova Scotia
| Malay Falls 95H | NS_95H_GSS | NSPI | 44.9873 | -62.4836 | Nova Scotia
| Maple St. 54H | NS_54H_DSS | NSPI | 44.6704 | -63.5648 | Nova Scotia
| Martins Brook 78W | NS_78W_DSS | NSPI | 44.4012 | -64.3491 | Nova Scotia
| Methals 7V | NS_7V_GSS | NSPI | 44.9405 | -64.4288 | Nova Scotia
| Michelin 92V | NS_92V_ISS | NSPI | 45.0469 | -64.6535 | Nova Scotia
| Michelin Bridgewater 74W | NS_74W_ISS | NSPI | 44.3834 | -64.5428 | Nova Scotia
| Mid River 86W | NS_86W_JCT | NSPI | 44.5929 | -64.2752 | Nova Scotia
| Middlefield 91W | NS_91W_DSS | NSPI | 44.2077 | -64.8631 | Nova Scotia
| Middleton 65V | NS_65V_DSS | NSPI | 44.9297 | -65.0619 | Nova Scotia
| Middleton Tap 65V | NS_65V_JCT | NSPI | 44.9044 | -65.0321 | Nova Scotia
| Milton 50W | NS_50W_DSS | NSPI | 44.0789 | -64.7729 | Nova Scotia
| Musquodoboit Harbour 87H | NS_87H_DSS | NSPI | 44.7824 | -63.1787 | Nova Scotia
| National Sea 82W | NS_82W_ISS | NSPI | 44.3663 | -64.2955 | Nova Scotia
| New Minas 22V | NS_22V_DSS | NSPI | 45.0776 | -64.4267 | Nova Scotia
| New Waterford 15S | NS_15S_DSS | NSPI | 46.2448 | -60.0972 | Nova Scotia
| Nictaux 10V | NS_10V_GSS | NSPI | 44.9091 | -65.0298 | Nova Scotia
| Northern Pulp 53N | NS_53N_ISS | NSPI | 45.6486 | -62.7174 | Nova Scotia
| Nuttby Mountain 89N | NS_89N_GSS | NSPI | 45.5607 | -63.2037 | Nova Scotia
| Onslow 1N | NS_1N_DSS | NSPI | 45.3899 | -63.311 | Nova Scotia
| Onslow 67N | NS_67N_DSS | NSPI | 45.4022 | -63.3079 | Nova Scotia
| Oxford 3N | NS_3N_DSS | NSPI | 45.696 | -63.8857 | Nova Scotia
| Paradise 11V | NS_11V_DSS | NSPI | 44.8324 | -65.2313 | Nova Scotia
| Park St. 20N | NS_20N_DSS | NSPI | 45.8211 | -64.2105 | Nova Scotia
| Parrsboro 37N | NS_37N_DSS | NSPI | 45.4255 | -64.3187 | Nova Scotia
| Penhorn 48H | NS_48H_DSS | NSPI | 44.6693 | -63.5415 | Nova Scotia
| Pictou 55N | NS_55N_DSS | NSPI | 45.6825 | -62.7095 | Nova Scotia
| Pleasant St. 88W | NS_88W_DSS | NSPI | 43.8406 | -66.1077 | Nova Scotia
| Point Aconi 102S | NS_102S_GSS | NSPI | 46.3172 | -60.3377 | Nova Scotia
| Point Aconi 89S | NS_89S_DSS | NSPI | 46.3213 | -60.3315 | Nova Scotia
| Point Tupper 1C | NS_1C_DFS | NSPI | 45.5793 | -61.337 | Nova Scotia
| Port Hastings 2C | NS_2C_DSS | NSPI | 45.6579 | -61.4034 | Nova Scotia
| Port Hastings 3C | NS_3C_DSS | NSPI | 45.6579 | -61.4034 | Nova Scotia
| Porters Lake 126H | NS_126H_DSS | NSPI | 44.7374 | -63.3141 | Nova Scotia
| Prince Mine 86S | NS_86S_ISS | NSPI | 46.3178 | -60.309 | Nova Scotia
| Pubnico 20W | NS_20W_DSS | NSPI | 43.6068 | -65.7705 | Nova Scotia
| Pubnico Point 106W | NS_106W_GSS | NSPI | 43.6071 | -65.7948 | Nova Scotia
| Pugwash 7N | NS_7N_DSS | NSPI | 45.8432 | -63.6517 | Nova Scotia
| Reserve 81S | NS_81S_DSS | NSPI | 46.1909 | -59.9834 | Nova Scotia
| Ridge 14V | NS_14V_GSS | NSPI | 44.554 | -65.5831 | Nova Scotia
| Rio Algoma 99X | NS_99X_DSS | NSPI | 44.1115 | -65.6826 | Nova Scotia
| Rio Algoma Tap 99X | NS_99X_JCT | NSPI | 44.1095 | -65.9249 | Nova Scotia
| Riverport 80W | NS_80W_DSS | NSPI | 44.3059 | -64.3496 | Nova Scotia
| Robinson's Corner 84W | NS_84W_DSS | NSPI | 44.56 | -64.2637 | Nova Scotia
| Rockingham 23H | NS_23H_DSS | NSPI | 44.6669 | -63.6575 | Nova Scotia
| Rockingham Tap 23H | NS_23H_JCT | NSPI | 44.6626 | -63.6626 | Nova Scotia
| Ruth Falls 96H | NS_96H_DSS | NSPI | 44.9341 | -62.5004 | Nova Scotia
| Sackville 90H | NS_90H_DSS | NSPI | 44.7461 | -63.6842 | Nova Scotia
| Salmon River Lake 57C | NS_57C_DSS | NSPI | 45.3602 | -61.713 | Nova Scotia
| Saulnierville 93V | NS_93V_DSS | NSPI | 44.2586 | -66.1213 | Nova Scotia
| Seaboard 1S | NS_1S_DSS | NSPI | 46.1634 | -59.9563 | Nova Scotia
| Shelburne 25W | NS_25W_DSS | NSPI | 43.7813 | -65.3416 | Nova Scotia
| Sissiboo 15V | NS_15V_GSS | NSPI | 44.4312 | -65.8718 | Nova Scotia
| Souriquois 30W | NS_30W_DSS | NSPI | 43.7918 | -65.2948 | Nova Scotia
| South Canoe 110W | NS_110W_GSS | NSPI | 44.7668 | -64.335 | Nova Scotia
| Spider Lake 132H | NS_132H_DSS | NSPI | 44.7438 | -63.5472 | Nova Scotia
| Springhill 74N | NS_74N_DFS | NSPI | 45.6635 | -64.0392 | Nova Scotia
| Spryfield 20H | NS_20H_DSS | NSPI | 44.611 | -63.6189 | Nova Scotia
| St. Croix 17V | NS_17V_DSS | NSPI | 44.9572 | -64.0384 | Nova Scotia |  | Also called "Indian Path 80W"
| St. Peters 59C | NS_59C_DSS | NSPI | 45.66 | -60.878 | Nova Scotia
| Stewiacke 16N | NS_16N_DSS | NSPI | 45.1495 | -63.3518 | Nova Scotia
| Stora 47C | NS_47C_DSS | NSPI | 45.5952 | -61.3507 | Nova Scotia
| SW Margaree 58C | NS_58C_DSS | NSPI | 46.2905 | -61.1382 | Nova Scotia
| Tatamagouche 4N | NS_4N_DSS | NSPI | 45.7125 | -63.3079 | Nova Scotia
| Terrace St. 6S | NS_6S_DSS | NSPI | 46.1313 | -60.17 | Nova Scotia
| Three Mile Plains 79V | NS_79V_DSS | NSPI | 44.9585 | -64.1066 | Nova Scotia
| Tidewater 92H | NS_92H_GSS | NSPI | 44.692 | -63.8911 | Nova Scotia
| Townsend St. 4S | NS_4S_DSS | NSPI | 46.137 | -60.1868 | Nova Scotia
| Trafalgar 89H | NS_89H_DSS | NSPI | 45.2914 | -62.6556 | Nova Scotia
| Tremont 51V | NS_51V_DSS | NSPI | 44.9557 | -64.92 | Nova Scotia
| Trenton 50N | NS_50N_DFS | NSPI | 45.6232 | -62.6481 | Nova Scotia
| Tuft's Cove 91H | NS_91H_GSS | NSPI | 44.6771 | -63.5944 | Nova Scotia
| Tusket 9W | NS_9W_GSS | NSPI | 43.8821 | -65.9768 | Nova Scotia
| Tusket Oil 10W | NS_10W_GSS | NSPI | 43.86 | -65.9933 | Nova Scotia
| Upper Burlington 18V | NS_18V_DSS | NSPI | 45.0464 | -64.0385 | Nova Scotia
| Upper Lake Falls 1W | NS_1W_GSS | NSPI | 44.1573 | -64.9984 | Nova Scotia
| Upper Musquodoboit 88H | NS_88H_DSS | NSPI | 45.13 | -62.969 | Nova Scotia
| Victoria Junction 2S | NS_2S_DSS | NSPI | 46.1599 | -60.1145 | Nova Scotia |  | Also called "New Page 47C"
| Victoria Junction 83S | NS_83S_GSS | NSPI | 46.1585 | -60.1136 | Nova Scotia
| Water St. 1H | NS_1H_DSS | NSPI | 44.642 | -63.5682 | Nova Scotia
| Waterville 55V | NS_55V_DSS | NSPI | 45.0486 | -64.6761 | Nova Scotia
| Waterville Tap 56V | NS_56V_JCT | NSPI | 45.0384 | -64.6707 | Nova Scotia
| Westhavers Elbow 75W | NS_75W_DSS | NSPI | 44.435 | -64.4411 | Nova Scotia
| Weymouth 16V | NS_16V_GSS | NSPI | 44.4076 | -65.9488 | Nova Scotia
| White Rock 4V | NS_4V_GSS | NSPI | 45.0616 | -64.3804 | Nova Scotia
| Whitney Pier 82S | NS_82S_DSS | NSPI | 46.1657 | -60.1778 | Nova Scotia
| Whycocomagh 67C | NS_67C_DSS | NSPI | 45.9777 | -61.1317 | Nova Scotia
| Willow Lane 15N | NS_15N_DSS | NSPI | 45.3565 | -63.2937 | Nova Scotia
| Wolfville Ridge 83V | NS_83V_DSS | NSPI | 45.0825 | -64.3355 | Nova Scotia
| Wolfville Ridge Tap 83V | NS_83V_JCT | NSPI | 45.0617 | -64.3278 | Nova Scotia
| Woodbine 101S | NS_101S_DSS | NSPI | 45.9922 | -60.2787 | Nova Scotia
| Woodlawn 40H | NS_40H_DSS | NSPI | 44.6818 | -63.5209 | Nova Scotia
| Woods Harbour 21W | NS_21W_DSS | NSPI | 43.5182 | -65.7314 | Nova Scotia
| Wreck Cove 85S | NS_85S_DFS | NSPI | 46.5302 | -60.4398 | Nova Scotia
| Yarmouth 11W | NS_11W_DSS | NSPI | 43.841 | -66.1178 | Nova Scotia
Legend:
CSS = Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
ISS = Industrial Customer Substation
JCT = Junction
SWS = Switching Station
TSS = Terminal Station

## Distribution
NS | EXISTING SUBSTATIONS
| Node Name | Node Code | Owner | Latitude | Longitude | Planning Region | Transformer | Primary Voltage | Secondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Other References | Notes
[8 empty] | (kV) | (kV) | (MVA) | (MVA) |  | (MW) | (MW)
| Abercrombie 54N | NS_54N_DSS | NSPI | 45.6407 | -62.706 | Mainland
| Aberdeen 9C | NS_9C_DSS | NSPI | 45.993 | -61.0071 | Cape Breton
| Aberdeen St. 10N | NS_10N_DSS | NSPI | 45.6593 | -64.0623 | Mainland
| Aerotech Park 127H | NS_127H_DSS | NSPI | 44.8512 | -63.5508 | Mainland
| Aerotech Park Tap 127H | NS_127H_JCT | NSPI | 44.8557 | -63.5987 | Mainland
| Akerly 124H | NS_124H_DSS | NSPI | 44.7191 | -63.5838 | Mainland
| Albert Bridge 57S | NS_57S_DSS | NSPI | 46.0343 | -60.0699 | Cape Breton
| Albro Lake 62H | NS_62H_DSS | NSPI | 44.6858 | -63.574 | Mainland
| Amherst 92N | NS_92N_GSS | NSPI | 45.8257 | -64.24 | Mainland
| Annapolis 81V | NS_81V_GSS | NSPI | 44.7524 | -65.5113 | Mainland
| Annapolis Tap 81V | NS_81V_JCT | NSPI | 44.7231 | -65.4938 | Mainland
| Argyle 19W | NS_19W_DSS | NSPI | 43.7834 | -65.8448 | Mainland
| Armdale 2H | NS_2H_DSS | NSPI | 44.6427 | -63.6193 | Mainland
| Auburndale 73W | NS_73W_DSS | NSPI | 44.3861 | -64.5561 | Mainland
| Avon 1V | NS_1V_GSS | NSPI | 44.8814 | -64.2172 | Mainland
| Baddeck 104S | NS_104S_DFS | NSPI | 46.1079 | -60.7538 | Cape Breton
| Baddeck Tap 104S | NS_104S_JCT | NSPI | 46.1241 | -60.7657 | Cape Breton
| Barrington 22W | NS_22W_DSS | NSPI | 43.523 | -65.6148 | Mainland
| Berwick 52V | NS_52V_DSS | NSPI | 45.0445 | -64.7355 | Mainland | [9 empty] | Location approximate
| Berwick Tap 53V | NS_53V_JCT | NSPI | 45.027 | -64.7344 | Mainland | [9 empty] | Location approximate
| Big Falls 3W | NS_3W_GSS | NSPI | 44.1384 | -64.9344 | Mainland
| Black River Rd. 6N | NS_6N_DSS | NSPI | 45.6347 | -64.075 | Mainland
| Bridge Avenue 62N | NS_62N_DSS | NSPI | 45.5644 | -62.6553 | Mainland
| Bridgetown 70V | NS_70V_DSS | NSPI | 44.8368 | -65.2989 | Mainland | [9 empty] | Location approximate
| Bridgetown Tap 70V | NS_70V_JCT | NSPI | 44.8192 | -65.2785 | Mainland
| Bridgewater 99W | NS_99W_DSS | NSPI | 44.3947 | -64.5565 | Mainland
| Bridgewater East 89W | NS_89W_DSS | NSPI | 44.3983 | -64.4894 | Mainland
| Broad River 46W | NS_46W_DSS | NSPI | 43.9539 | -64.8348 | Mainland
| Brooklyn 104W | NS_104W_DSS | NSPI | 44.0516 | -64.6992 | Mainland
| Brownell St. 17N | NS_17N_DSS | NSPI | 45.8377 | -64.2152 | Mainland
| Brushy Hill 120H | NS_120H_DSS | NSPI | 44.8532 | -63.7636 | Mainland
| Burnside 108H | NS_108H_DSS | NSPI | 44.713 | -63.6113 | Mainland
| Burnside 14H | NS_14H_GSS | NSPI | 44.713 | -63.6113 | Mainland
| Caledonia 57W | NS_57W_DSS | NSPI | 44.3769 | -65.0241 | Mainland
| Canaan Rd. 43V | NS_43V_DSS | NSPI | 45.0495 | -64.4199 | Mainland
| Canexel 85W | NS_85W_ISS | NSPI | 44.5852 | -64.1621 | Mainland
| Canso 19C | NS_19C_DSS | NSPI | 45.3366 | -61.0014 | Mainland
| Cape Porcupine 100C | NS_100C_DSS | NSPI | 45.6399 | -61.4307 | Cape Breton
| Carleton 92W | NS_92W_DSS | NSPI | 43.9932 | -65.9397 | Mainland
| Cheticamp 103C | NS_103C_DSS | NSPI | 46.619 | -60.9928 | Cape Breton
| Church St. 22N | NS_22N_DSS | NSPI | 45.823 | -64.1882 | Mainland
| Cleveland 22C | NS_22C_DSS | NSPI | 45.6714 | -61.239 | Cape Breton
| Clyde River 23W | NS_23W_DSS | NSPI | 43.6371 | -65.4796 | Mainland
| Cobequid Rd. 101H | NS_101H_DSS | NSPI | 44.7553 | -63.6611 | Mainland
| Conway 77V | NS_77V_DSS | NSPI | 44.6 | -65.7782 | Mainland
| Cornwallis 74V | NS_74V_DSS | NSPI | 44.6542 | -65.6318 | Mainland
| Cornwallis Tap 74V | NS_74V_JCT | NSPI | 44.6419 | -65.6167 | Mainland
| Cowie Falls 6W | NS_6W_GSS | NSPI | 44.0744 | -64.7707 | Mainland
| Dalhousie Mountain 91N | NS_91N_GSS | NSPI | 45.4656 | -63.1076 | Mainland
| Dartmouth Crossing 139H | NS_139H_DSS | NSPI | 44.716 | -63.5662 | Mainland
| Dartmouth East 113H | NS_113H_DSS | NSPI | 44.7014 | -63.4814 | Mainland
| Debert 81N | NS_81N_DSS | NSPI | 45.44 | -63.453 | Mainland
| Deep Brook 5W | NS_5W_GSS | NSPI | 44.0805 | -64.7909 | Mainland
| Dickie Brook 24C | NS_24C_DFS | NSPI | 45.3481 | -61.5032 | Mainland
| Domtar 75N | NS_75N_ISS | NSPI | 45.7835 | -64.2323 | Mainland
| Donkin Road 97S | NS_97S_DSS | NSPI | 46.1786 | -59.8267 | Cape Breton
| East River 86E | NS_86E_JCT | NSPI | 44.6168 | -64.1564 | Mainland
| Ellershouse 102V | NS_102V_GSS | NSPI | 44.9355 | -64.0283 | Mainland
| Elmsdale 82V | NS_82V_DSS | NSPI | 44.9635 | -63.4984 | Mainland
| Farrell St. 99H | NS_99H_DSS | NSPI | 44.6766 | -63.5903 | Mainland
| Five Points 20V | NS_20V_DSS | NSPI | 45.0641 | -64.1925 | Mainland
| Fourth Lake 91V | NS_91V_GSS | NSPI | 44.3696 | -65.7193 | Mainland
| Gannon Rd. 3S | NS_3S_DSS | NSPI | 46.2299 | -60.2573 | Cape Breton
| Geizer Hill 34H | NS_34H_DSS | NSPI | 44.6466 | -63.6482 | Mainland
| Glen Dhu 93N | NS_93N_GSS | NSPI | 45.6467 | -62.2216 | Mainland
| Glen Tosh 5S | NS_5S_DSS | NSPI | 46.1806 | -60.621 | Cape Breton
| Gold River 103W | NS_103W_DSS | NSPI | 44.5584 | -64.3318 | Mainland
| Granton 49N | NS_49N_ISS | NSPI | 45.6146 | -62.7376 | Mainland
| Green Harbour 36W | NS_36W_DSS | NSPI | 43.739 | -65.1348 | Mainland
| Greenwood 64V | NS_64V_DSS | NSPI | 44.9671 | -64.9408 | Mainland
| Gulch 13V | NS_13V_DFS | NSPI | 44.567 | -65.635 | Mainland
| Gullivers Cove 98V | NS_98V_DSS | NSPI | 44.5913 | -65.9447 | Mainland
| Haliburton 56N | NS_56N_DSS | NSPI | 45.6757 | -62.7314 | Mainland
| Hammonds 137H | NS_137H_DSS | NSPI | 44.7234 | -63.7351 | Mainland
| Harmony 7W | NS_7W_DSS | NSPI | 44.4161 | -65.0562 | Mainland
| Hebron 16W | NS_16W_DSS | NSPI | 43.8935 | -66.0803 | Mainland
| Hells Gate 3V | NS_3V_GSS | NSPI | 45.0354 | -64.4033 | Mainland
| Hickman St. 19N | NS_19N_DSS | NSPI | 45.818 | -64.2102 | Mainland
| High St. 70W | NS_70W_DSS | NSPI | 44.3705 | -64.5279 | Mainland
| Highbury 99V | NS_99V_DSS | NSPI | 45.0488 | -64.422 | Mainland
| Hillaton 36V | NS_36V_DSS | NSPI | 45.145 | -64.4503 | Mainland
| Hollow Bridge 6V | NS_6V_GSS | NSPI | 45.0038 | -64.3759 | Mainland
| Hopewell 79N | NS_79N_DSS | NSPI | 45.4543 | -62.6676 | Mainland
| Hubbards 87W | NS_87W_DSS | NSPI | 44.6444 | -64.0884 | Mainland
| Imperial Oil 58H | NS_58H_ISS | NSPI | 44.644 | -63.5373 | Mainland
| IPB Amherst | PP_NSNB2_IPT | NSPI | 45.8638 | -64.2629 | Mainland
| IPB Church St | PP_NSNB3_IPT | NSPI | 45.8975 | -64.2274 | Mainland
| IPB Onslow | PP_NSNB1_IPT | NSPI | 45.8975 | -64.2274 | Mainland
| IPB Woodbine | PP_NSNL1_IPT | NSPI | 46.9965 | -59.44 | Cape Breton | [9 empty] | Midway across Cabot Strait
| Kearney Lake 129H | NS_129H_DSS | NSPI | 44.684 | -63.6788 | Mainland
| Keltic Drive 11S | NS_11S_DSS | NSPI | 46.1201 | -60.2365 | Cape Breton
| Kempt Road 104H | NS_104H_DSS | NSPI | 44.6589 | -63.6063 | Mainland
| Kingston 63V | NS_63V_DSS | NSPI | 44.9853 | -64.9539 | Mainland
| Klondike 50V | NS_50V_DSS | NSPI | 45.0687 | -64.502 | Mainland
| Lafarge 11N | NS_11N_DSS | NSPI | 45.2493 | -63.3004 | Mainland
| Lakeside 103H | NS_103H_DSS | NSPI | 44.644 | -63.6835 | Mainland
| Lequille 12V | NS_12V_GSS | NSPI | 44.7255 | -65.4968 | Mainland
| Lingan 88S | NS_88S_GSS | NSPI | 46.2357 | -60.0411 | Cape Breton
| Lingan Mine 80S | NS_80S_DSS | NSPI | 46.2437 | -60.0619 | Cape Breton
| Lingan Wind 109S | NS_109S_GSS | NSPI | 46.2423 | -60.0426 | Cape Breton
| Liverpool 48W | NS_48W_DSS | NSPI | 44.0351 | -64.7143 | Mainland
| Lochaber Road 4C | NS_4C_DSS | NSPI | 45.6069 | -61.9983 | Mainland
| Lockeport 37W | NS_37W_DSS | NSPI | 43.7019 | -65.114 | Mainland
| Lower Great Brook 4W | NS_4W_GSS | NSPI | 44.09 | -64.848 | Mainland
| Lower Lake Falls 2W | NS_2W_GSS | NSPI | 44.1577 | -64.9772 | Mainland
| Lucasville 131H | NS_131H_DSS | NSPI | 44.7552 | -63.7367 | Mainland
| Lumsden 5V | NS_5V_GSS | NSPI | 45.027 | -64.3965 | Mainland
| Lunenburg 81W | NS_81W_DSS | NSPI | 44.3818 | -64.3183 | Mainland
| Lunenburg SW 79W | NS_79W_DSS | NSPI | 44.3689 | -64.3389 | Mainland
| Maccan 30N | NS_30N_DSS | NSPI | 45.7174 | -64.2641 | Mainland
| MacDonald Pond 101V | NS_101V_DSS | NSPI | 44.8818 | -64.2216 | Mainland
| Mahone Bay 76W | NS_76W_DSS | NSPI | 44.4464 | -64.3817 | Mainland
| Mahone Bay Tap 77W | NS_77W_JCT | NSPI | 44.438 | -64.3938 | Mainland
| Maitland Bridge 76V | NS_76V_DSS | NSPI | 44.4439 | -65.1928 | Mainland
| Malay Falls 95H | NS_95H_GSS | NSPI | 44.9873 | -62.4836 | Mainland
| Maple St. 54H | NS_54H_DSS | NSPI | 44.6704 | -63.5648 | Mainland
| Martins Brook 78W | NS_78W_DSS | NSPI | 44.4012 | -64.3491 | Mainland
| Methals 7V | NS_7V_GSS | NSPI | 44.9405 | -64.4288 | Mainland
| Michelin 92V | NS_92V_ISS | NSPI | 45.0469 | -64.6535 | Mainland
| Michelin Bridgewater 74W | NS_74W_ISS | NSPI | 44.3834 | -64.5428 | Mainland
| Mid River 86W | NS_86W_JCT | NSPI | 44.5929 | -64.2752 | Mainland
| Middlefield 91W | NS_91W_DSS | NSPI | 44.2077 | -64.8631 | Mainland
| Middleton 65V | NS_65V_DSS | NSPI | 44.9297 | -65.0619 | Mainland
| Middleton Tap 65V | NS_65V_JCT | NSPI | 44.9044 | -65.0321 | Mainland
| Milton 50W | NS_50W_DSS | NSPI | 44.0789 | -64.7729 | Mainland
| Musquodoboit Harbour 87H | NS_87H_DSS | NSPI | 44.7824 | -63.1787 | Mainland
| National Sea 82W | NS_82W_ISS | NSPI | 44.3663 | -64.2955 | Mainland
| New Minas 22V | NS_22V_DSS | NSPI | 45.0776 | -64.4267 | Mainland
| New Waterford 15S | NS_15S_DSS | NSPI | 46.2448 | -60.0972 | Cape Breton
| Nictaux 10V | NS_10V_GSS | NSPI | 44.9091 | -65.0298 | Mainland
| Northern Pulp 53N | NS_53N_ISS | NSPI | 45.6486 | -62.7174 | Mainland
| Nuttby Mountain 89N | NS_89N_GSS | NSPI | 45.5607 | -63.2037 | Mainland
| Onslow 1N | NS_1N_DSS | NSPI | 45.3899 | -63.311 | Mainland
| Onslow 67N | NS_67N_DSS | NSPI | 45.4022 | -63.3079 | Mainland
| Oxford 3N | NS_3N_DSS | NSPI | 45.696 | -63.8857 | Mainland
| Paradise 11V | NS_11V_DSS | NSPI | 44.8324 | -65.2313 | Mainland
| Park St. 20N | NS_20N_DSS | NSPI | 45.8211 | -64.2105 | Mainland
| Parrsboro 37N | NS_37N_DSS | NSPI | 45.4255 | -64.3187 | Mainland
| Penhorn 48H | NS_48H_DSS | NSPI | 44.6693 | -63.5415 | Mainland
| Pictou 55N | NS_55N_DSS | NSPI | 45.6825 | -62.7095 | Mainland
| Pleasant St. 88W | NS_88W_DSS | NSPI | 43.8406 | -66.1077 | Mainland
| Point Aconi 102S | NS_102S_GSS | NSPI | 46.3172 | -60.3377 | Cape Breton
| Point Aconi 89S | NS_89S_DSS | NSPI | 46.3213 | -60.3315 | Cape Breton
| Point Tupper 1C | NS_1C_DFS | NSPI | 45.5793 | -61.337 | Cape Breton
| Port Hastings 2C | NS_2C_DSS | NSPI | 45.6579 | -61.4034 | Cape Breton
| Port Hastings 3C | NS_3C_DSS | NSPI | 45.6579 | -61.4034 | Cape Breton
| Porters Lake 126H | NS_126H_DSS | NSPI | 44.7374 | -63.3141 | Mainland
| Prince Mine 86S | NS_86S_ISS | NSPI | 46.3178 | -60.309 | Cape Breton
| Pubnico 20W | NS_20W_DSS | NSPI | 43.6068 | -65.7705 | Mainland
| Pubnico Point 106W | NS_106W_GSS | NSPI | 43.6071 | -65.7948 | Mainland
| Pugwash 7N | NS_7N_DSS | NSPI | 45.8432 | -63.6517 | Mainland
| Reserve 81S | NS_81S_DSS | NSPI | 46.1909 | -59.9834 | Cape Breton
| Ridge 14V | NS_14V_GSS | NSPI | 44.554 | -65.5831 | Mainland
| Rio Algoma 99X | NS_99X_DSS | NSPI | 44.1115 | -65.6826 | Mainland
| Rio Algoma Tap 99X | NS_99X_JCT | NSPI | 44.1095 | -65.9249 | Mainland
| Riverport 80W | NS_80W_DSS | NSPI | 44.3059 | -64.3496 | Mainland
| Robinson's Corner 84W | NS_84W_DSS | NSPI | 44.56 | -64.2637 | Mainland
| Rockingham 23H | NS_23H_DSS | NSPI | 44.6669 | -63.6575 | Mainland
| Rockingham Tap 23H | NS_23H_JCT | NSPI | 44.6626 | -63.6626 | Mainland
| Ruth Falls 96H | NS_96H_DSS | NSPI | 44.9341 | -62.5004 | Mainland
| Sackville 90H | NS_90H_DSS | NSPI | 44.7461 | -63.6842 | Mainland
| Salmon River Lake 57C | NS_57C_DSS | NSPI | 45.3602 | -61.713 | Mainland
| Saulnierville 93V | NS_93V_DSS | NSPI | 44.2586 | -66.1213 | Mainland
| Seaboard 1S | NS_1S_DSS | NSPI | 46.1634 | -59.9563 | Cape Breton
| Shelburne 25W | NS_25W_DSS | NSPI | 43.7813 | -65.3416 | Mainland
| Sissiboo 15V | NS_15V_GSS | NSPI | 44.4312 | -65.8718 | Mainland
| Souriquois 30W | NS_30W_DSS | NSPI | 43.7918 | -65.2948 | Mainland
| South Canoe 110W | NS_110W_GSS | NSPI | 44.7668 | -64.335 | Mainland
| Spider Lake 132H | NS_132H_DSS | NSPI | 44.7438 | -63.5472 | Mainland
| Springhill 74N | NS_74N_DFS | NSPI | 45.6635 | -64.0392 | Mainland
| Spryfield 20H | NS_20H_DSS | NSPI | 44.611 | -63.6189 | Mainland
| St. Croix 17V | NS_17V_DSS | NSPI | 44.9572 | -64.0384 | Mainland | [9 empty] | Also called "Indian Path 80W"
| St. Peters 59C | NS_59C_DSS | NSPI | 45.66 | -60.878 | Cape Breton
| Stewiacke 16N | NS_16N_DSS | NSPI | 45.1495 | -63.3518 | Mainland
| Stora 47C | NS_47C_DSS | NSPI | 45.5952 | -61.3507 | Mainland
| SW Margaree 58C | NS_58C_DSS | NSPI | 46.2905 | -61.1382 | Cape Breton
| Tatamagouche 4N | NS_4N_DSS | NSPI | 45.7125 | -63.3079 | Mainland
| Terrace St. 6S | NS_6S_DSS | NSPI | 46.1313 | -60.17 | Cape Breton
| Three Mile Plains 79V | NS_79V_DSS | NSPI | 44.9585 | -64.1066 | Mainland
| Tidewater 92H | NS_92H_GSS | NSPI | 44.692 | -63.8911 | Mainland
| Townsend St. 4S | NS_4S_DSS | NSPI | 46.137 | -60.1868 | Cape Breton
| Trafalgar 89H | NS_89H_DSS | NSPI | 45.2914 | -62.6556 | Mainland
| Tremont 51V | NS_51V_DSS | NSPI | 44.9557 | -64.92 | Mainland
| Trenton 50N | NS_50N_DFS | NSPI | 45.6232 | -62.6481 | Mainland
| Tuft's Cove 91H | NS_91H_GSS | NSPI | 44.6771 | -63.5944 | Mainland
| Tusket 9W | NS_9W_GSS | NSPI | 43.8821 | -65.9768 | Mainland
| Tusket Oil 10W | NS_10W_GSS | NSPI | 43.86 | -65.9933 | Mainland
| Upper Burlington 18V | NS_18V_DSS | NSPI | 45.0464 | -64.0385 | Mainland
| Upper Lake Falls 1W | NS_1W_GSS | NSPI | 44.1573 | -64.9984 | Mainland
| Upper Musquodoboit 88H | NS_88H_DSS | NSPI | 45.13 | -62.969 | Mainland
| Victoria Junction 2S | NS_2S_DSS | NSPI | 46.1599 | -60.1145 | Cape Breton | [9 empty] | Also called "New Page 47C"
| Victoria Junction 83S | NS_83S_GSS | NSPI | 46.1585 | -60.1136 | Cape Breton
| Water St. 1H | NS_1H_DSS | NSPI | 44.642 | -63.5682 | Mainland
| Waterville 55V | NS_55V_DSS | NSPI | 45.0486 | -64.6761 | Mainland
| Waterville Tap 56V | NS_56V_JCT | NSPI | 45.0384 | -64.6707 | Mainland
| Westhavers Elbow 75W | NS_75W_DSS | NSPI | 44.435 | -64.4411 | Mainland
| Weymouth 16V | NS_16V_GSS | NSPI | 44.4076 | -65.9488 | Mainland
| White Rock 4V | NS_4V_GSS | NSPI | 45.0616 | -64.3804 | Mainland
| Whitney Pier 82S | NS_82S_DSS | NSPI | 46.1657 | -60.1778 | Cape Breton
| Whycocomagh 67C | NS_67C_DSS | NSPI | 45.9777 | -61.1317 | Cape Breton
| Willow Lane 15N | NS_15N_DSS | NSPI | 45.3565 | -63.2937 | Mainland
| Wolfville Ridge 83V | NS_83V_DSS | NSPI | 45.0825 | -64.3355 | Mainland
| Wolfville Ridge Tap 83V | NS_83V_JCT | NSPI | 45.0617 | -64.3278 | Mainland
| Woodbine 101S | NS_101S_DSS | NSPI | 45.9922 | -60.2787 | Cape Breton
| Woodlawn 40H | NS_40H_DSS | NSPI | 44.6818 | -63.5209 | Mainland
| Woods Harbour 21W | NS_21W_DSS | NSPI | 43.5182 | -65.7314 | Mainland
| Wreck Cove 85S | NS_85S_DFS | NSPI | 46.5302 | -60.4398 | Cape Breton
| Yarmouth 11W | NS_11W_DSS | NSPI | 43.841 | -66.1178 | Mainland
Legend:
CSS = Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
ISS = Industrial Customer Substation
JCT = Junction
SWS = Switching Station
TSS = Terminal Station

## System
NS | SYSTEM CHARACTERISTICS
| Generator Type | Capacity Adjustment (ELCC) | Capacity Factor | Notes | Reserve Requirements | Line Losses
|  | (%) | (%) |  | (% installed MW) | (% across system)
| Coal | 90% | by facility |  | 21% | 6.6%
| Heavy Fuel Oil | 73% | by facility
| Light Fuel Oil CT | 78% | 1%
| Natural Gas CC | 73% | by facility
| Natural Gas CT | 93% | 1%
| Biomass / Biogas | 95% | by facility
| Hydro_daily | 95% | by facility
| Annapolis Tidal | 12% | 13.2%
| Wind | 19% | 35.2%
| Solar | 5% | 15%
| Maritime Link Base Energy Imports | 98% | 66.7% | Base Block of 16 hours/day
Specific Notes:
ELCC is a dynamic value that changes as the wind penetration level changes, and is unique to each electricity system depending upon the capabilities of the other system generating units and the load shape.
ELCC factors for existing resources have been calculated using the most recent 3 year average DAFOR (de-rated adjusted forced outage rate)

## HGWh
NS | HISTORICAL ANNUAL ENERGY DEMAND | UNIT | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2010-2019
| Annual Energy Demand (After DSM) | GWh/year | 12158 | 11907 | 10475 | 11194 | 11037 | 11099 | 10809 | 10873 | 11250 | 11331
| Annual Change in Energy Demand | GWh/year |  | -251 | -1432 | 719 | -157 | 62 | -290 | 64 | 377 | 81 | Average
| Percentage Change in Energy Demand | % |  | -2.064% | -12.03% | 6.864% | -1.403% | 0.5617% | -2.613% | 0.5921% | 3.467% | 0.72% | -0.7797%
Notes:

## HMW
NS | HISTORICAL PEAK DEMAND | UNIT | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2010-2019
| Peak Demand (After DSM) | MW | 2114 | 2168 | 1882 | 2033 | 2118 | 2015 | 2111 | 2018 | 2073 | 2221
| Annual Change in Peak Demand | MW |  | 54 | -286 | 151 | 85 | -103 | 96 | -93 | 55 | 148 | Average
| Percentage Change in Peak Demand | % |  | 2.554% | -13.19% | 8.023% | 4.181% | -4.863% | 4.764% | -4.405% | 2.725% | 7.139% | 0.5501%
Notes:

## FGWh
NS | FORECAST ANNUAL ENERGY DEMAND | UNIT | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2020-2030 | 2020-2050 | Notes | Year | BAU+High DER+Max Ach. DSM | BAU. Base DSM | BAU Low DSM | BAU - No New DSM | Mid E. Base DSM | Mid E Low DSM | Mid E. High DER. Mid DSM | Mid E. - Max Ach. DSM | High E./High DER Base DSM | High E. Mid DSM | High E - Max Ach. DSM | High E. - Low DSM
| Mid-load Forecast Energy Demand (After DSM) | GWh/year | 11350 | 11403 | 11458 | 11449 | 11459 | 11391 | 11323 | 11269 | 11232 | 11165 | 11100 | 11086 | 11113 | 11122 | 11177 | 11240 | 11333 | 11401 | 11485 | 11578 | 11670 | 11730 | 11819 | 11905 | 11979 | 12072
| Annual Change in Energy Demand | GWh/year |  | 53 | 55 | -9 | 10 | -68 | -68 | -54 | -37 | -67 | -65 | -14 | 27 | 9 | 55 | 63 | 93 | 68 | 84 | 93 | 92 | 60 | 89 | 86 | 74 | 93 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050 | Electrification | BAU | BAU | BAU | BAU | Mid | Mid | Mid | Mid | High | High | High | High
| Percentage Change in Energy Demand | % |  | 0.467% | 0.4823% | -0.07855% | 0.08734% | -0.5934% | -0.597% | -0.4769% | -0.3283% | -0.5965% | -0.5822% | -0.1261% | 0.2436% | 0.08099% | 0.4945% | 0.5637% | 0.8274% | 0.6% | 0.7368% | 0.8098% | 0.7946% | 0.5141% | 0.7587% | 0.7276% | 0.6216% | 0.7764% | -0.2472% | 0.247% | Mid-load forecast for use in COPPER | DER | High | [7 empty] | High
[32 empty] | DSM | Maximum | Base | Low | None | Base | Low | Mid | Maximum | Base | Mid | Maximum | Low
| Low-load Forecast Energy Demand (After DSM) | GWh/year | 11350 | 11327 | 11302 | 11260 | 11242 | 11165 | 11100 | 11044 | 11002 | 10924 | 10843 | 10809 | 10811 | 10786 | 10800 | 10816 | 10860 | 10873 | 10904 | 10944 | 10987 | 11003 | 11053 | 11104 | 11149 | 11216 |  |  |  | 2021 | 11252 | 11327 | 11327 | 11695 | 11403 | 11403 | 11329 | 11403 | 11457 | 11531 | 11531 | 11531
| Annual Change in Energy Demand | GWh/year |  | -23 | -25 | -42 | -18 | -77 | -65 | -56 | -42 | -78 | -81 | -34 | 2 | -25 | 14 | 16 | 44 | 13 | 31 | 40 | 43 | 16 | 50 | 51 | 45 | 67 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050 | 2022 | 11199 | 11302 | 11302 | 11797 | 11458 | 11458 | 11355 | 11458 | 11613 | 11715 | 11715 | 11715
| Percentage Change in Energy Demand | % |  | -0.2026% | -0.2207% | -0.3716% | -0.1599% | -0.6849% | -0.5822% | -0.5045% | -0.3803% | -0.709% | -0.7415% | -0.3136% | 0.0185% | -0.2312% | 0.1298% | 0.1481% | 0.4068% | 0.1197% | 0.2851% | 0.3668% | 0.3929% | 0.1456% | 0.4544% | 0.4614% | 0.4053% | 0.601% | -0.5065% | -0.04749% | Low-load forecast for use in COPPER | 2023 | 11015 | 11260 | 11306 | 11886 | 11449 | 11541 | 11315 | 11384 | 11748 | 11835 | 11770 | 11927
[32 empty] | 2024 | 10835 | 11242 | 11333 | 11993 | 11459 | 11643 | 11265 | 11337 | 11860 | 11961 | 11839 | 12144
| High-load Forecast Energy Demand (After DSM) | GWh/year | 11350 | 11531 | 11715 | 11835 | 11961 | 11972 | 11956 | 11955 | 11969 | 11949 | 11928 | 11958 | 12029 | 12084 | 12187 | 12302 | 12449 | 12570 | 12705 | 12848 | 12988 | 13086 | 13209 | 13324 | 13424 | 13537 |  |  |  | 2025 | 10588 | 11165 | 11300 | 12038 | 11391 | 11662 | 11113 | 11228 | 11829 | 11972 | 11809 | 12243
| Annual Change in Energy Demand | GWh/year |  | 181 | 184 | 120 | 126 | 11 | -16 | -1 | 14 | -20 | -21 | 30 | 71 | 55 | 103 | 115 | 147 | 121 | 135 | 143 | 140 | 98 | 123 | 115 | 100 | 113 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050 | 2026 | 10321 | 11100 | 11281 | 12108 | 11323 | 11679 | 10919 | 11123 | 11728 | 11956 | 11757 | 12313
| Percentage Change in Energy Demand | % |  | 1.595% | 1.596% | 1.024% | 1.065% | 0.09197% | -0.1336% | -0.008364% | 0.1171% | -0.1671% | -0.1757% | 0.2515% | 0.5937% | 0.4572% | 0.8524% | 0.9436% | 1.195% | 0.972% | 1.074% | 1.126% | 1.09% | 0.7545% | 0.9399% | 0.8706% | 0.7505% | 0.8418% | 0.5534% | 0.7073% | High-load forecast for use in COPPER | 2027 | 10079 | 11044 | 11270 | 12187 | 11269 | 11708 | 10744 | 11042 | 11643 | 11955 | 11728 | 12394
[32 empty] | 2028 | 9821 | 11002 | 11276 | 12293 | 11232 | 11753 | 10548 | 10982 | 11534 | 11969 | 11719 | 12490
[32 empty] | 2029 | 9504 | 10924 | 11236 | 12342 | 11165 | 11751 | 10276 | 10908 | 11334 | 11949 | 11692 | 12535
Notes: | [31 empty] | 2030 | 9170 | 10843 | 11192 | 12392 | 11100 | 11744 | 9983 | 10838 | 11106 | 11928 | 11667 | 12572
[32 empty] | 2031 | 9054 | 10809 | 11192 | 12483 | 11086 | 11781 | 9902 | 10827 | 11085 | 11958 | 11699 | 12653
[32 empty] | 2032 | 8984 | 10811 | 11227 | 12615 | 11113 | 11854 | 9868 | 10856 | 11109 | 12029 | 11771 | 12770
[32 empty] | 2033 | 8898 | 10786 | 11226 | 12699 | 11122 | 11893 | 9815 | 10873 | 11107 | 12084 | 11834 | 12855
[32 empty] | 2034 | 8862 | 10800 | 11261 | 12822 | 11177 | 11973 | 9816 | 10934 | 11161 | 12187 | 11944 | 12983
[32 empty] | 2035 | 8829 | 10816 | 11297 | 12947 | 11240 | 12055 | 9825 | 11003 | 11221 | 12302 | 12064 | 13117
[32 empty] | 2036 | 8831 | 10860 | 11358 | 13104 | 11333 | 12167 | 9875 | 11099 | 11326 | 12449 | 12214 | 13283
[32 empty] | 2037 | 8811 | 10873 | 11380 | 13207 | 11401 | 12239 | 9898 | 11173 | 11399 | 12570 | 12342 | 13408
[32 empty] | 2038 | 8818 | 10904 | 11420 | 13335 | 11485 | 12329 | 9952 | 11259 | 11501 | 12705 | 12480 | 13549
[32 empty] | 2039 | 8841 | 10944 | 11464 | 13462 | 11578 | 12419 | 10014 | 11359 | 11606 | 12848 | 12629 | 13689
[32 empty] | 2040 | 8856 | 10987 | 11511 | 13596 | 11670 | 12511 | 10074 | 11451 | 11710 | 12988 | 12769 | 13829
[32 empty] | 2041 | 8848 | 11003 | 11525 | 13681 | 11730 | 12563 | 10102 | 11513 | 11770 | 13086 | 12870 | 13920
[32 empty] | 2042 | 8877 | 11053 | 11572 | 13801 | 11819 | 12643 | 10159 | 11608 | 11854 | 13209 | 12999 | 14033
[32 empty] | 2043 | 8905 | 11104 | 11619 | 13919 | 11905 | 12718 | 10211 | 11698 | 11928 | 13324 | 13117 | 14137
[32 empty] | 2044 | 8923 | 11149 | 11661 | 14036 | 11979 | 12784 | 10251 | 11773 | 11988 | 13424 | 13217 | 14228
[32 empty] | 2045 | 8963 | 11216 | 11721 | 14151 | 12072 | 12862 | 10310 | 11868 | 12060 | 13537 | 13333 | 14327

## FMW
NS | FORECAST ANNUAL PEAK DEMAND | UNIT | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2020-2030 | 2020-2050 | Notes | Year | BAU+High DER+Max Ach. DSM | BAU. Base DSM | BAU Low DSM | BAU - No New DSM | Mid E. Base DSM | Mid E Low DSM | Mid E. High DER. Mid DSM | Mid E. - Max Ach. DSM | High E./High DER Base DSM | High E. Mid DSM | High E - Max Ach. DSM | High E. - Low DSM
| Mid-load Forecast Peak Demand (After DSM) | MW | 2245 | 2121 | 2176 | 2205 | 2240 | 2236 | 2257 | 2261 | 2268 | 2272 | 2240 | 2281 | 2295 | 2312 | 2330 | 2351 | 2374 | 2398 | 2421 | 2447 | 2468 | 2487 | 2508 | 2528 | 2548 | 2566
| Annual Change in Peak Demand | MW |  | -124 | 55 | 29 | 35 | -4 | 21 | 4 | 7 | 4 | -32 | 41 | 14 | 17 | 18 | 21 | 23 | 24 | 23 | 26 | 21 | 19 | 21 | 20 | 20 | 18 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050 | Electrification | BAU | BAU | BAU | BAU | Mid | Mid | Mid | Mid | High | High | High | High
| Percentage Change in Peak Demand | % |  | -5.523% | 2.593% | 1.333% | 1.587% | -0.1786% | 0.9392% | 0.1772% | 0.3096% | 0.1764% | -1.408% | 1.83% | 0.6138% | 0.7407% | 0.7785% | 0.9013% | 0.9783% | 1.011% | 0.9591% | 1.074% | 0.8582% | 0.7699% | 0.8444% | 0.7974% | 0.7911% | 0.7064% | 0.7818% | 0.536% | Mid-load forecast for use in COPPER | DER | High | [7 empty] | High
[32 empty] | DSM | Maximum | Base | Low | None | Base | Low | Mid | Maximum | Base | Mid | Maximum | Low
| Low-load Forecast Peak Demand (After DSM) | MW | 2100 | 2073 | 2078 | 2081 | 2089 | 2093 | 2092 | 2093 | 2094 | 2094 | 2093 | 2094 | 2099 | 2106 | 2115 | 2125 | 2137 | 2150 | 2163 | 2178 | 2191 | 2202 | 2216 | 2230 | 2245 | 2260 |  |  |  | 2021 | 2073 | 2073 | 2073 | 2148 | 2121 | 2121 | 2121 | 2121 | 2205 | 2205 | 2205 | 2205
| Annual Change in Peak Demand | MW |  | -27 | 5 | 3 | 8 | 4 | -1 | 1 | 1 | 0 | -1 | 1 | 5 | 7 | 9 | 10 | 12 | 13 | 13 | 15 | 13 | 11 | 14 | 14 | 15 | 15 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050 | 2022 | 2078 | 2078 | 2078 | 2180 | 2176 | 2176 | 2176 | 2176 | 2347 | 2347 | 2347 | 2347
| Percentage Change in Peak Demand | % |  | -1.286% | 0.2412% | 0.1444% | 0.3844% | 0.1915% | -0.04778% | 0.0478% | 0.04778% | 0% | -0.04776% | 0.04778% | 0.2388% | 0.3335% | 0.4274% | 0.4728% | 0.5647% | 0.6083% | 0.6047% | 0.6935% | 0.5969% | 0.5021% | 0.6358% | 0.6318% | 0.6726% | 0.6682% | -0.03709% | 0.2941% | Low-load forecast for use in COPPER | 2023 | 2055 | 2081 | 2091 | 2209 | 2205 | 2222 | 2222 | 2241 | 2482 | 2491 | 2465 | 2501
[32 empty] | 2024 | 2040 | 2089 | 2110 | 2242 | 2240 | 2271 | 2271 | 2309 | 2617 | 2635 | 2586 | 2656
| High-load Forecast Peak Demand (After DSM) | MW | 2100 | 2205 | 2347 | 2491 | 2635 | 2732 | 2780 | 2827 | 2870 | 2890 | 2904 | 2919 | 2942 | 2966 | 2986 | 3010 | 3036 | 3063 | 3088 | 3114 | 3138 | 3158 | 3178 | 3196 | 3214 | 3231 |  |  |  | 2025 | 2023 | 2093 | 2124 | 2270 | 2257 | 2301 | 2301 | 2358 | 2706 | 2732 | 2663 | 2763
| Annual Change in Peak Demand | MW |  | 105 | 142 | 144 | 144 | 97 | 48 | 47 | 43 | 20 | 14 | 15 | 23 | 24 | 20 | 24 | 26 | 27 | 25 | 26 | 24 | 20 | 20 | 18 | 18 | 17 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050 | 2026 | 2004 | 2092 | 2133 | 2294 | 2257 | 2310 | 2310 | 2385 | 2746 | 2780 | 2692 | 2821
| Percentage Change in Peak Demand | % |  | 5% | 6.44% | 6.135% | 5.781% | 3.681% | 1.757% | 1.691% | 1.521% | 0.6969% | 0.4844% | 0.5165% | 0.7879% | 0.8158% | 0.6743% | 0.8038% | 0.8638% | 0.8893% | 0.8162% | 0.842% | 0.7707% | 0.6373% | 0.6333% | 0.5664% | 0.5632% | 0.5289% | 3.667% | 1.738% | High-load forecast for use in COPPER | 2027 | 1992 | 2093 | 2143 | 2320 | 2261 | 2322 | 2322 | 2413 | 2786 | 2827 | 2725 | 2877
[32 empty] | 2028 | 1982 | 2094 | 2154 | 2346 | 2268 | 2333 | 2333 | 2440 | 2824 | 2870 | 2759 | 2930
[32 empty] | 2029 | 1978 | 2094 | 2163 | 2371 | 2272 | 2338 | 2338 | 2457 | 2840 | 2890 | 2774 | 2959
Notes: | [31 empty] | 2030 | 1973 | 2093 | 2169 | 2393 | 2274 | 2340 | 2341 | 2469 | 2851 | 2904 | 2784 | 2980
[32 empty] | 2031 | 1974 | 2094 | 2177 | 2417 | 2281 | 2346 | 2346 | 2484 | 2865 | 2919 | 2799 | 3002
[32 empty] | 2032 | 1980 | 2099 | 2187 | 2443 | 2295 | 2358 | 2358 | 2501 | 2887 | 2942 | 2824 | 3030
[32 empty] | 2033 | 1990 | 2106 | 2198 | 2470 | 2312 | 2373 | 2373 | 2520 | 2911 | 2966 | 2850 | 3058
[32 empty] | 2034 | 2003 | 2115 | 2211 | 2499 | 2330 | 2388 | 2388 | 2538 | 2933 | 2986 | 2874 | 3082
[32 empty] | 2035 | 2018 | 2125 | 2224 | 2528 | 2351 | 2407 | 2407 | 2557 | 2959 | 3010 | 2903 | 3109
[32 empty] | 2036 | 2034 | 2137 | 2237 | 2557 | 2374 | 2428 | 2428 | 2577 | 2986 | 3036 | 2933 | 3136
[32 empty] | 2037 | 2051 | 2150 | 2251 | 2587 | 2398 | 2449 | 2449 | 2597 | 3015 | 3063 | 2964 | 3163
[32 empty] | 2038 | 2068 | 2163 | 2264 | 2616 | 2421 | 2471 | 2471 | 2616 | 3043 | 3088 | 2994 | 3189
[32 empty] | 2039 | 2089 | 2178 | 2277 | 2644 | 2447 | 2494 | 2494 | 2636 | 3073 | 3114 | 3026 | 3214
[32 empty] | 2040 | 2105 | 2191 | 2289 | 2670 | 2468 | 2515 | 2515 | 2653 | 3099 | 3138 | 3053 | 3237
[32 empty] | 2041 | 2119 | 2202 | 2299 | 2694 | 2487 | 2532 | 2533 | 2667 | 3121 | 3158 | 3075 | 3255
[32 empty] | 2042 | 2137 | 2216 | 2310 | 2718 | 2508 | 2552 | 2552 | 2681 | 3143 | 3178 | 3099 | 3272
[32 empty] | 2043 | 2155 | 2230 | 2322 | 2742 | 2528 | 2570 | 2570 | 2694 | 3164 | 3196 | 3122 | 3288
[32 empty] | 2044 | 2173 | 2245 | 2334 | 2765 | 2548 | 2589 | 2589 | 2708 | 3185 | 3214 | 3143 | 3303
[32 empty] | 2045 | 2191 | 2260 | 2346 | 2788 | 2566 | 2607 | 2607 | 2721 | 3203 | 3231 | 3162 | 3317

## Hourly
NS | Hourly
See Hourly2018 file in the Hourly-2018 folder
See Hourly2019 file in the Hourly-2019 folder

## Inputs
NS | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance

## NS-Hydro-Sources
NS | SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| Nova Scotia Power Maritime Link | 2013 | Maritime Link Project. Responses to Canadian Wind Energy Association Information Requests | https://uarb.novascotia.ca/fmi/webd/UARB15 [NSUARB ML-2013-01] |  | Nova Scotia
| Nova Scotia Power Inc. | 2016 | 2016 Annual Capital Expenditure Plan (NSUARB P-128.16/M07176) IR Responses N-4 | https://uarb.novascotia.ca/fmi/webd/UARB15 [ Search M07176] |  | Nova Scotia
| Nova Scotia Power Maritime Link | 2013 | Maritime Link Project. Responses to Consumer Advocate Information Requests | https://uarb.novascotia.ca/fmi/webd/UARB15 [NSUARB ML-2013-01] |  | Nova Scotia
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Energy and Environmental Economics | 2019 | Planning Reserve Margin and Capacity Value Study | https://irp.nspower.ca/documents/pre-irp-deliverables/ |  | Nova Scotia
| Nova Scotia Power Inc. | 2015 | 2015 ACE NSPI Responses to SBA Information Requests | https://uarb.novascotia.ca/fmi/webd/UARB15 [Search M06514] |  | Nova Scotia
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | National

## HydroExisting
NS | EXISTING STORAGE HYDROELECTRIC | [25 empty] | RESERVOIR
| Project Name | Generation Type | Installed Capacity (ICAP) | Capacity Adjustment (Annual) | Effective Capacity | Capacity Factor | Annual Average Energy | # of units | Renewal Year | Dam Type | Penstock | Rated Head | Maximum Head | Minimum Head | Operating Flow (Facility) | Rated Discharge (Unit) | Rated Discharge (Facility) | Upstream Reservoir Area | Upstream Reservoir Storage | Turbine Type | Station Flow | Upper Storage | Upper Storage Level | Lower Storage | Lower Storage Level | Notes | Reservoir or System Name | Maximum Live Storage | Minimum Level | Maximum Level | Initial Level | Low Reference Level | High Reference Level | Low Volume | High Volume | Live Storage | M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10 | M11 | M12
|  |  | (MW) |  | (MW) | (%) | (GWh/year) |  |  |  | (m) | (m) | (m) | (m) | (m3/s) | (m3/s) | (m3/s) | (km2) | (hours) |  | (WSC#) |  | (WSC#) |  | (WSC#) |  |  | (GWh) | (m) | (m) | (m) | (m) | (m) | (m3) | (m3) | (m3) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s)
| Avon_01 | Hydro_daily | 3.75 | 95% | 3.5625 | 43.33% | 14.235 | 2 | 1992 | Earth fill embankment | 65 | 35.8 | 35.8 | 32.8 | [5 empty] | Francis | [6 empty] | Avon | 6
| Avon_02 | Hydro_daily | 3 | 95% | 2.85 | 43.33% | 11.388 | 2 | 2004 | Earth fill embankment | 53 | 35.8 | 35.8 | 32.8 | [5 empty] | Francis | [6 empty] | Black | 35.4
| Bear River_01 (Gulch) | Hydro_daily | 6.2 | 95% | 5.89 | 31.67% | 17.1988 | 3 |  | Earth fill embankment | 3158 | 76.2 | 77.4 | 76 | [5 empty] | Francis | [6 empty] | Nictaux | 7.9
| Bear River_02 (Ridge) | Hydro_daily | 4.1 | 95% | 3.895 | 31.67% | 11.3734 | 3 |  | Earth fill embankment | 955 | 42.7 | 45.1 | 43.88 | [5 empty] | Francis | [6 empty] | Lequille | 3.8
| Bear River_03 (Fourth Lake) | Hydro_daily | 3.1 | 95% | 2.945 | 31.67% | 8.5994 | 3 |  | Earth fill embankment | 93 | 21.3 | 22.7 | 15.2 | 16.26 |  |  |  |  | Kaplan | [5 empty] | Head range suggests storage capability | Paradise | 11.1
| Black River_01(Methals) | Hydro_daily | 3.5 | 95% | 3.325 | 43.67% | 13.3882 | 6 | 1996 | Earth fill embankment | 10 | 18.3 | 18.3 | 17.1 | 31.15 |  |  |  |  | Kaplan | [6 empty] | Mersey | 105
| Black River_02 (Hollow Bridge) | Hydro_daily | 5.5 | 95% | 5.225 | 43.67% | 21.0386 | 6 | 1987 | Earth fill embankment | 510 | 45.3 | 45.3 | 43.9 | 16.08 |  |  |  |  | Francis | [6 empty] | Sissiboo | 28
| Black River_03 (Lumsden) | Hydro_daily | 2.9 | 95% | 2.755 | 43.67% | 11.0931 | 6 | 1996 | Earth fill embankment | 100 | 22 | 22 | 20.4 | 17.84 |  |  |  |  | Francis | [6 empty] | Bear | 16.5
| Black River_04 (Hell's Gate 1) | Hydro_daily | 3.5 | 95% | 3.325 | 43.67% | 13.3882 | 6 | 2012 | Concrete gravity | 1465 | 56.4 | 56.4 | 54.3 | 15.86 |  |  |  |  | Francis | [6 empty] | Tusket | 0.7
| Black River_05 (Hell's Gate 2) | Hydro_daily | 3.7 | 95% | 3.515 | 43.67% | 14.1532 | 6 | 2005 | Concrete gravity | 1465 | 56.4 | 56.4 | 54.3 | [5 empty] | Francis | [6 empty] | St. Margaret's Bay | 8.6
| Black River_06 (White Rock) | Hydro_daily | 3.4 | 95% | 3.23 | 43.67% | 13.0057 | 6 | 2003 | Concrete gravity | 30 | 17.7 | 18.3 | 17.1 | 25.5 |  |  |  |  | Francis | [6 empty] | Sheet Harbour | 4
| Dickie Brook_01 | Hydro_daily | 1.2 | 95% | 1.14 | 20.33% | 2.1374 | 2 | 1998 | Earth fill embankment |  | 11.3 | 11.3 | 11.3 | [5 empty] | Francis | [6 empty] | Dickie Brook | 1.8
| Dickie Brook_02 | Hydro_daily | 2.6 | 95% | 2.47 | 20.33% | 4.6311 | 2 |  | Earth fill embankment |  | 11.3 | 11.3 | 11.3 | [5 empty] | Francis | [6 empty] | Wreck Cove | 108
| Lequille | Hydro_daily | 11.2 | 95% | 10.64 | 26.67% | 26.1632 | 1 |  | Earth fill embankment | 488 | 118.3 | 118.3 | 116.3 | 6.34 |  |  |  |  | Francis
| Lower St. Croix | Hydro_daily | 3 | 95% | 2.85 | 60.67% | 15.9432 | 1
| Upper St. Croix | Hydro_daily | 2 | 95% | 1.9 | 60.67% | 10.6288 | 1
| Mersey_01 (Upper Lake Falls 1) | Hydro_daily | 2.7 | 95% | 2.565 | 60.67% | 14.3489 | 2 | 1992 | Earth fill embankment |  | 10.7 | 12.8 | 6.4 | 53.2 |  |  |  |  | Kaplan
| Mersey_02 (Upper Lake Falls 2) | Hydro_daily | 2.7 | 95% | 2.565 | 60.67% | 14.3489 | 2 |  | Earth fill embankment |  | 10.7 | 12.8 | 6.4 | [5 empty] | Kaplan | 01ED003 | Lake Rossignol |  |  |  | Head range suggests storage capability
| Mersey_03 (Lower Lake Falls 1) | Hydro_daily | 3.7 | 95% | 3.515 | 60.67% | 19.6633 | 2 |  | Earth fill embankment |  | 14.6 | 14.6 | 13.1 | 68.8 |  |  |  |  | Francis | 01ED003 | Lake Rossignol |  |  |  | Head range suggests storage capability
| Mersey_04 (Lower Lake Falls 2) | Hydro_daily | 3.7 | 95% | 3.515 | 60.67% | 19.6633 | 2 |  | Earth fill embankment |  | 14.6 | 14.6 | 13.1 | [5 empty] | Francis
| Mersey_05 (Big Falls 1) | Hydro_daily | 4.5 | 95% | 4.275 | 60.67% | 23.9148 | 2 |  | Earth fill embankment |  | 17.7 | 17.7 | 16 | [5 empty] | Francis
| Mersey_06 (Big Falls 2) | Hydro_daily | 4.5 | 95% | 4.275 | 60.67% | 23.9148 | 2 |  | Earth fill embankment |  | 17.7 | 17.7 | 16 | [5 empty] | Francis
| Mersey_07 (Lower Great Brook 1) | Hydro_daily | 2.25 | 95% | 2.1375 | 60.67% | 11.9574 | 2 |  | Earth fill embankment |  | 6.7 | 6.7 | 6.1 | 88.4 |  |  |  |  | Kaplan
| Mersey_08 (Lower Great Brook 2) | Hydro_daily | 2.25 | 95% | 2.1375 | 60.67% | 11.9574 | 2 |  | Earth fill embankment |  | 6.7 | 6.7 | 6.1 | [5 empty] | Kaplan
| Mersey_09 (Deep Brook 1) | Hydro_daily | 4.5 | 95% | 4.275 | 60.67% | 23.9148 | 2 |  | Earth fill embankment |  | 14 | 14 | 12.5 | 86.6 |  |  |  |  | Kaplan
| Mersey_10 (Deep Brook 2) | Hydro_daily | 4.5 | 95% | 4.275 | 60.67% | 23.9148 | 2 |  | Earth fill embankment |  | 14 | 14 | 12.5 | [5 empty] | *Mix Flow
| Mersey_11(Cowie Falls 1) | Hydro_daily | 3.6 | 95% | 3.42 | 60.67% | 19.1318 | 2 |  | Concrete gravity |  | 12.7 | 12.7 | 10.3 | 76.4 |  |  |  |  | *Mix Flow
| Mersey_12 (Cowie Falls 2) | Hydro_daily | 3.6 | 95% | 3.42 | 60.67% | 19.1318 | 2 |  | Concrete gravity |  | 12.7 | 12.7 | 10.3 | [5 empty] | *Mix Flow
| Nictaux | Hydro_daily | 8.3 | 95% | 7.885 | 52.33% | 38.0505 | 1 |  | Earth fill embankment | 1350 | 122 | 123.9 | 121.2 | [5 empty] | Francis
| Paradise | Hydro_daily | 4.7 | 95% | 4.465 | 56.67% | 23.3308 | 1 | 2013 | Earth fill embankment | 3688 | 153.92 | 153.92 | 152.54 | [5 empty] | Francis
| Sheet Harbour_01 (Ruth Falls 1) | Hydro_daily | 2.3 | 95% | 2.185 | 53.67% | 10.8128 | 3 | 1999 | Earth fill embankment |  | 33.2 | 33.2 | [6 empty] | Francis
| Sheet Harbour_02 (Ruth Falls 2) | Hydro_daily | 2.8 | 95% | 2.66 | 53.67% | 13.1634 | 3 |  | Earth fill embankment |  | 33.2 | 33.2 | [6 empty] | Francis
| Sheet Harbour_03 (Ruth Falls 3) | Hydro_daily | 2.3 | 95% | 2.185 | 53.67% | 10.8128 | 3 |  | Earth fill embankment |  | 33.2 | 33.2 | [6 empty] | Francis
| Sheet Harbour_04 (Malay Falls 1) | Hydro_daily | 1.15 | 95% | 1.0925 | 53.67% | 5.4064 | 3 |  | Earth fill embankment |  | 12.5 | 12.5 | [6 empty] | Francis
| Sheet Harbour_05 (Malay Falls 2) | Hydro_daily | 1.15 | 95% | 1.0925 | 53.67% | 5.4064 | 3 |  | Earth fill embankment |  | 12.5 | 12.5 | [6 empty] | Francis
| Sheet Harbour_06 (Malay Falls 3) | Hydro_daily | 1.1 | 95% | 1.045 | 53.67% | 5.1713 | 3 |  | Earth fill embankment |  | 12.5 | 12.5 | [6 empty] | Francis
| Sissiboo_01 | Hydro_daily | 5 | 95% | 4.75 | 35.33% | 15.476 | 1 | 2015 | Concrete gravity | 49 | 26.5 | 26.5 | 25.9 | [5 empty] | Francis
| Sissiboo_02 (Weymouth 1) | Hydro_daily | 9.5 | 95% | 9.025 | 35.33% | 29.4044 | 2 | 2010 | Earth fill embankment | 261 | 37.2 | 39.01 | 36 | [5 empty] | Francis
| Sissiboo_03 (Weymouth 2) | Hydro_daily | 9.5 | 95% | 9.025 | 35.33% | 29.4044 | 2 | 2013 | Earth fill embankment | 261 | 37.2 | 39.01 | 36 | [5 empty] | Francis
| St. Margarets_01 (Mill Lake 1) | Hydro_daily | 1.3 | 95% | 1.235 | 22% | 2.5054 | 2 |  | Concrete gravity | 1056 | 49.4 | 49.4 | 48.8 | 6.6 |  |  |  |  | Francis
| St. Margarets_02 (Mill Lake 2) | Hydro_daily | 1.3 | 95% | 1.235 | 22% | 2.5054 | 2 |  | Concrete gravity | 1056 | 49.4 | 49.4 | 48.8 | [5 empty] | Francis
| St. Margarets_03 (Sandy Lake 1) | Hydro_daily | 1.8 | 95% | 1.71 | 22% | 3.469 | 2 |  | Concrete gravity | 1757 | 38.1 | 38.1 | 35.5 | 13 |  |  |  |  | Francis
| St. Margarets_04 (Sandy Lake 2) | Hydro_daily | 1.8 | 95% | 1.71 | 22% | 3.469 | 2 |  | Concrete gravity | 1757 | 38.1 | 38.1 | 35.5 | [5 empty] | Francis
| St. Margarets_05 (Tidewater 1) | Hydro_daily | 2.3 | 95% | 2.185 | 22% | 4.4326 | 2 |  | Concrete gravity | 1037 | 29 | 29 | 28.4 | 17.6 |  |  |  |  | Francis
| St. Margarets_06 (Tidewater 2) | Hydro_daily | 2.3 | 95% | 2.185 | 22% | 4.4326 | 2 |  | Concrete gravity | 1037 | 29 | 29 | 28.4 | [5 empty] | Francis
| Tusket_01 | Hydro_daily | 0.8 | 95% | 0.76 | 55.33% | 3.8778 | 3 | 1981 | Concrete gravity |  | 6.7 | 8.53 | 7.31 | [5 empty] | Kaplan
| Tusket_02 | Hydro_daily | 0.8 | 95% | 0.76 | 55.33% | 3.8778 | 3 | 2014 | Concrete gravity |  | 6.7 | 8.53 | 7.31 | [5 empty] | Kaplan
| Tusket_03 | Hydro_daily | 0.8 | 95% | 0.76 | 55.33% | 3.8778 | 3 | 2009 | Concrete gravity |  | 6.7 | 8.53 | 7.31 | [5 empty] | Kaplan
| Wreck Cove_01 | Hydro_daily | 106 | 95% | 100.7 | 16.33% | 151.6648 | 1 | 2007 | Rock fill embankment | 490 | 366 | 366 | 351 | 66 |  |  |  |  | Francis | [5 empty] | Limits: 500 MWh/day in Jun; 800 MWh/day in April, Jul-Nov; 1,100 MWh/day in Dec-Mar
| Wreck Cove_02 | Hydro_daily | 106 | 95% | 100.7 | 16.33% | 151.6648 | 2 | 1998 | Rock fill embankment | 490 | 366 | 366 | 351 | [5 empty] | Francis | [5 empty] | Limits: 500 MWh/day in Jun; 800 MWh/day in April, Jul-Nov; 1,100 MWh/day in Dec-Mar
| Wreck Cove_03 (Gisborne) | Hydro_daily | 3.5 | 95% | 3.325 | 16.33% | 5.0078 | 2 | 2002 | Earth fill embankment | 122 | 25 | 25 | 10.6 | 21.5 |  |  |  |  | Kaplan
General Notes:
Hydroelectric generation type has been estimated based on available information concerning operations, reservoir size and operations, facility location and design flows.
The WSC# refers to the Water Survey of Canada Hydrometric station

## HydroRenewals
NS | HYDROELECTRIC RENEWAL | [6 empty] | EXISTING DESIGN |  |  |  |  | RENEWAL | [7 empty] | COSTS |  | 1.77% | 1.05 |  |  | 7% | 70
| Existing Project Name | Owner | Location | Substation Name | Bus Voltage | Start Year | Turbine Renewal Year | Generation Type | Installed Capacity | Dependable Capacity | Annual Average Energy (WECC) | Existing #units | Renewal Project Name | Renewal Project Code | Balancing Area | Distance to Market Grid | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Additional Annual Energy | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed Cost Existing Project | Fixed Cost Renewed Project | Fixed O&M | Variable Costs | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
[9 empty] | (MW) | (MW) | (GWh/year) |  |  |  |  | (km) |  | (MW) | (MW) | (GWh/year) | ($2017M) | ($2018M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M/year) | ($M/MW-year) | ($/year) | ($/year) | ($2018M/year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
NONE
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroGreenfield
NS | HYDROELECTRIC GREENFIELD | [9 empty] | DESIGN | [5 empty] | COSTS |  | 1.77% | 1.05 |  |  | 7% | 70
| Project Name | Project Code | Owner | Location | Latitude | Longitude | Balancing Area | Distance to Market Grid | Substation Name | Substation Voltage | Generation Type | Generation Type - COPPER | Installed Capacity | Dependable Capacity | Average Annual Energy | # of units | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed O&M | Variable Costs | Water Rentals | Variable O&M | Construction Time | Development Time | Notes
[10 empty] | (kV) |  |  | (MW) | (MW) | (GWh/year) |  | ($2008M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($M/MW-year) | ($2018M/year) | ($/MWh) | ($/MWh) | ($/MWh) | (years) | (years)
NONE
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to didtance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume Hydro_daily and Hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroPS
NS | HYDROELECTRIC PUIMPED STORAGE | [15 empty] | Existing Design | [8 empty] | Reservoir Design | [13 empty] | Costs | 1.77% | 1.06 |  |  | 7% | 70
| Pumped Storage Project | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Estimated Round Trip Efficiency | Existing Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Salt/Fresh | Reservoir Types | Reservoir Storage | Storage Requirement | Gross Head | Penstock | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping) | Turbine Type | Pump Type | Generation Duration at Peak Output | Efficient Pumping Capacity Duration | Total Footprint | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Cost of Capacity | Unit Cost of Stored Energy | Levelized Cost | Construction Time | Development Time | Notes
[5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) |  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) |  |  |  |  | (m3) | (MWh) | (m) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2018/MW) | ($2018/MWh) | ($2018/kW-year) | (years) | (years)
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume Hydro_daily and Hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset