## README
ON | LEGEND
| ON-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| Distribution | Characteristics of existing distribution substations
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review or being gathered
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to sources
See the accompanying calculations file and raw data files for additional supporting information
See the related Gitlab issue for a summary of inventory status

## ON-Sources
ON | PRIMARY SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| Hydro One Networks Inc. | 2019 | List of Transmission Lines by Functional Category | http://www.rds.oeb.ca/HPECMWebDrawer/Record?q=casenumber:EB-2019-0082&sortBy=recRegisteredOn-&pageSize=400#form1 | EB-2019-0082, Exhibit I1, Tab 2, Schedule 1 | Ontario
| Hydro One Networks Inc. | 2020 | Hydro One List of Station Capacity | https://www.hydroone.com/businessservices_/generators_/Documents/honi_lsc.pdf |  | Ontario
| IESO | 2020 | Annual Planning Outlook: A view of Ontario's electricity system needs [including data tables] | http://www.ieso.ca/en/Sector-Participants/Planning-and-Forecasting/Annual-Planning-Outlook |  | Ontario
| IESO | 2019 | Conservation and Demand Management Cost-Effectiveness Tool User Guide - Tool V7 | https://www.ieso.ca/en/Sector-Participants/Energy-Efficiency/Evaluation-Measurement-and-Verification |  | Ontario
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" Column of the relevant tab
| CBC | 2020 | TC Energy joins hydroelectric power storage project at retired coal mine site | https://www.cbc.ca/news/canada/calgary/tc-energy-joins-pumped-hydro-power-storage-project-retired-coal-mine-site-1.5577377 |  | Ontario, Alberta
| TC Energy | 2021 | Proposed Meaford Storage Project | https://www.tcenergy.com/operations/power/pumped-storage-project/ |  | Ontario
| Hatch Acres | 2005 | Evaluation and Assessment of Ontario's Waterpower Potential. Final Report. | https://www.owa.ca/wp-content/uploads/2017/01/Evaluation-and-Assessment-of-Ontarios-Waterpower-Potential-Final-Report-.pdf |  | Ontario |  | 14
| IESO | 2019 | IESO Active Contracted Generation List (June 30, 2019). | http://www.ieso.ca/-/media/Files/IESO/Document-Library/power-data/supply/IESO-Active-Contracted-Generation-List.xlsx?la=en |  | Ontario
| OPG | 2019 | Generating power with purpose. | https://www.opg.com/powering-ontario/our-generation/ |  | Ontario
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | National
| Natural Resources Canada | 2019 | The Atlas of Canada - Clean Energy Resources and Projects (CERP) | https://atlas.gc.ca/cerp-rpep/en/ |  | Ontario
| IESO | 2019 | Generator Output and Capability Report | http://reports.ieso.ca/public/GenOutputCapability/ |  | Ontario
| Hatch | 2013 | Northern Hydro Assessment Waterpower Potential in the Far North of Ontario. | https://owa.ca/wp-content/uploads/2017/01/NorthernHydroFinal-Executive-Summary.pdf | Commissioned by the Ontario Waterpower Association | Ontario
| IESO | 2016 | Ontario Planning Outlook: A technical report on the electricity system prepared by the IESO | http://www.ieso.ca/sector-participants/planning-and-forecasting/ontario-planning-outlook |  | Ontario
| Electricity Act | 1998 | Taxes and Charges on Hydroelectric Generating Stations, Ontario Regulation 124/02, s.3(1). | https://www.canlii.org/en/on/laws/regu/o-reg-124-02/latest/o-reg-124-02.html?autocompleteStr=Taxes%20and%20charge&autocompletePos=1 |  | Ontario
| IESO | 2018 | Ontario Reserve Margin Requirements From 2019 to 2023 | http://www.ieso.ca/en/Sector-Participants/Planning-and-Forecasting/Reliability-Outlook |  | Ontario
| IESO | 2019 | Demand Overview | http://www.ieso.ca/en/Power-Data/Demand-Overview/Historical-Demand |  | Ontario
| IESO | 2019 | Hourly Demand Report | http://reports.ieso.ca/public/Demand/ |  | Ontario
| Northland Power | 2015 | Marmora Storage-Hydro Power | https://www.northlandpower.com/en/assets-and-infrastructure/Marmora_Pumped_Storage_spread.pdf
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Hydro Québec | 2019 | Hydro Quebec Power Exports: A Winning Solution | http://www.hydroquebec.com/international/en/exports/markets/
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
ON | EXISTING GENERATION | [12 empty] | DESIGN | [7 empty] | OPERATIONS | [13 empty] | OPERATING COSTS
| Project Name | Gen Gode | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy | # of units | Inc Heat Rate @ Max | Minimum Capacity | Maximum Capacity | Minimum Up Time | Minimum Down Time | Spin Up Ramp Rate | Spin Down Ramp Rate | Start Up Ramp Limit | Shut Down Ramp Limit | Must Run | Operating Reserve Fraction | Outage Duration | Forced Outage Rate | Maintenance Outage Rate | Start Up Costs | Fuel Costs | Shut Down Costs | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | (kV) |  |  |  |  | (MW) |  | (MW) | (%) | (GWh/year) |  | (MMBtu/MWh) | (MW) | (MW) | (hours) | (hours) | (%/min) | (%/min) | [MW/hr p MWcap] | [MW/hr p MWcap] | (T/F) | (%) | (hours) | (%) | (days/y) | (S/MWcap) | ($/MWh) | (S/MWcap) | ($/year) | ($/MWh)
| 13th Sideroad | ON_13T00_GEN | SunE Sky 13th Sideroad LP | Langton | 42.855 | -80.3607 | Ontario.a | Ontario | Bloomsburg DS | ON_BLO_DSS | 115 | 2010 | 2030 | solar | solar | 9.5 | 18.54% | 1.7618 | 18% | 14.9796
| Abitibi Canyon | ON_ABC00_GEN | Ontario Power Generation Inc | Smooth Rock Falls | 49.8822 | -81.567 | Ontario.b | Ontario | Abitibi Canyon GS | ON_ABC_GSS | 115 | 1933 | 2100 | hydro_daily | hydro_daily | 355 | 68.43% | 242.9295 | 30.06% | 934.738 | 5
| Adelaide Solar | ON_ADS00_GEN | Met Fiera Solar Adelaide 1 LP | Strathroy | 42.9585 | -81.6708 | Ontario.a | Ontario | Strathroy TS | ON_SRY_DSS | 115 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Adelaide Wind | ON_ADW00_GEN | Kerwood Wind LP | Kerwood | 42.9877 | -81.7068 | Ontario.a | Ontario | Strathroy TS | ON_SRY_DSS | 115 | 2014 | 2034 | wind_onshore | wind | 60 | 21.14% | 12.6852 | 27.39% | 143.987
| Aguasabon | ON_AGU00_GEN | Ontario Power Generation Inc | Thunder Bay | 48.7867 | -87.161 | Ontario.b | Ontario | Aguasabon SWS | ON_AGU_SWS | 115 | 1948 | 2100 | hydro_daily | hydro_daily | 52 | 68.43% | 35.584 | 62.93% | 286.643 | 2
| Alderville 3 | ON_ALD00_GEN | Alderville Solar Limited Partnership | Roseneath | 44.1939 | -78.0946 | Ontario.a | Ontario | Port Hope TS | ON_PTH_DSS | 115 | 2013 | 2033 | solar | solar | 5 | 18.54% | 0.92724 | 18% | 7.884
| Alexander | ON_ALX00_GEN | Ontario Power Generation Inc | Nipigon | 49.1355 | -88.358 | Ontario.b | Ontario | Alexander GS | ON_ALX_GSS | 115 | 1930 | 2100 | hydro_run | hydro_run | 65 | 68.43% | 44.48 | 68.3% | 388.905 | 5
| Alfred | ON_ALF00_GEN | 2225228 Ontario Inc | Alfred | 45.54 | -74.8878 | Ontario.b | Ontario | Longueuil TS | ON_LGU_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Algoma | ON_ALG00_GEN | Essar Steel Algoma | Sault Ste. Marie | 46.5244 | -84.3712 | Ontario.b | Ontario | Third Line TS | ON_TDL_DSS | 115 | 2009 | 2029 | NG_CG | gasCC | 63 | 85.12% | 53.6235 | 13% | 71.7444
| Almonte | ON_ALM00_GEN | Mississippi River Power Corporation | Almonte | 45.2258 | -76.1981 | Ontario.b | Ontario | Almonte TS | ON_ALM_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 5 | 68.43% | 3.4215 | 65% | 28.47
| Amaranth | ON_AMA00_GEN | Melancthon Wolfe Wind LP | Dundalk | 44.082 | -80.287 | Ontario.a | Ontario | Amaranth TS | ON_AMA_ISS | 230 | 2008 | 2028 | wind_onshore | wind | 199.5 | 21.14% | 42.1784 | 24.06% | 420.475
| Amherst Island | ON_AMI00_GEN | Windlectric Inc | Stella | 44.1522 | -76.7219 | Ontario.a | Ontario | Cataraqui TS | ON_CTQ_TSS | 115 | 2018 | 2038 | wind_onshore | wind | 73 | 21.14% | 15.4337 | 16.46% | 105.229
| Amherstburg Solar 1 | ON_AMS00_GEN | ABW Solar General Partnership | Amherstburg | 42.1449 | -83.0769 | Ontario.a | Ontario | Keith TS | ON_KEI_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Amherstburg_01 | ON_AMB01_GEN | Capstone Infrastructure Corp | Amherstburg | 42.1637 | -83.0807 | Ontario.a | Ontario | Keith TS | ON_KEI_DSS | 230 | 2011 | 2031 | solar | solar | 20 | 18.54% | 3.709 | 18% | 31.536
| Amherstburg_02 | ON_AMB02_GEN | Enbridge Inc | Amherstburg | 42.169 | -83.0876 | Ontario.a | Ontario | Keith TS | ON_KEI_DSS | 230 | 2011 | 2031 | solar | solar | 15 | 18.54% | 2.7817 | 18% | 23.652
| Andrews | ON_AND00_GEN | Brookfield Renewable Power Inc | Batchawana Bay | 47.2386 | -84.6461 | Ontario.b | Ontario | Andrews TS | ON_AND_DSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 47 | 68.43% | 32.1625 | 65% | 267.618
| AP Calstock | ON_APC00_GEN | Atlantic Power Corp | Calstock | 49.7456 | -84.0736 | Ontario.b | Ontario | AP Calstock GS | ON_APC_GSS | 115 | 2000 | 2100 | biomass | biomass | 38 | 94.51% | 35.9146 | 39.35% | 130.98
| Appleton | ON_APP00_GEN | Canadian Hydro Developers, Inc | Almonte | 45.1829 | -76.1267 | Ontario.b | Ontario | Almonte TS | ON_ALM_DSS | 230 | 2011 | 2031 | hydro_run | hydro_run | 1.4 | 68.43% | 0.95803 | 65% | 7.9716
| Aria | ON_ARI00_GEN | Concord Aria Partnership | Elmvale | 44.629 | -79.8493 | Ontario.a | Ontario | Midhurst TS | ON_MDH_DSS | 230 | 2015 | 2035 | solar | solar | 9 | 18.54% | 1.669 | 18% | 14.1912
| Armow | ON_ARM00_GEN | Sp Armow Wind Ontario LP | Kincardine | 44.2044 | -81.4574 | Ontario.a | Ontario | Armow GS | ON_ARM_GSS | 230 | 2015 | 2035 | wind_onshore | wind | 180 | 21.14% | 38.0557 | 27.71% | 436.906
| Arnprior Hydro | ON_ARN00_GEN | Ontario Power Generation Inc | Arnprior | 45.4187 | -76.347 | Ontario.b | Ontario | Arnprior GS | ON_ARN_GSS | 230 | 1976 | 2100 | hydro_daily | hydro_daily | 82 | 68.43% | 56.1133 | 21.14% | 151.873 | 2
| Arnprior Solar | ON_ARS00_GEN | EDF Energies Nouvelles | Arnprior | 45.4083 | -76.275 | Ontario.b | Ontario | Arnprior TS | ON_ARN_DSS | 115 | 2010 | 2030 | solar | solar | 23.4 | 18.54% | 4.3395 | 18% | 36.8971
| Arthur | ON_ART00_GEN | Arthur Wind Farm Ltd Partnership | Arthur | 43.8478 | -80.5152 | Ontario.a | Ontario | Fergus TS | ON_FGS_DSS | 230 | 2011 | 2031 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Atikokan | ON_ATK00_GEN | Ontario Power Generation Inc | Atikokan | 48.8381 | -91.5708 | Ontario.b | Ontario | Atikokan TGS | ON_ATK_GSS | 230 | 2014 | 2024 | biomass | biomass | 215 | 94.51% | 203.2012 | 8.588% | 161.754 | 1
| Aubrey Falls | ON_AUB00_GEN | Brookfield Renewable Power Inc | Elliot Lake | 46.9095 | -83.2129 | Ontario.b | Ontario | Aubrey Falls GS | ON_AUB_GSS | 230 | 2009 | 2029 | hydro_daily | hydro_daily | 146 | 68.43% | 99.909 | 13.13% | 167.936
| Auburn | ON_ABN00_GEN | Ontario Power Generation Inc | Peterborough | 44.3235 | -78.314 | Ontario.a | Ontario | Otonabee TS | ON_OTB_DSS | 230 | 1911 | 2100 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388 | 3
| AV Terrace Bay | ON_AVT00_GEN | Kimberley-Clark | Terrace Bay | 48.7975 | -87.1066 | Ontario.b | Ontario | AV Terrace Bay TS | ON_AVT_ISS | 115 | 2000 | 2100 | biomass | biomass | 20 | 94.51% | 18.9024 | 20% | 35.04
| Balsam Lake | ON_BLM00_GEN | Balsam Lake LP | Coboconk | 44.651 | -78.7587 | Ontario.a | Ontario | Lindsay TS | ON_LND_DSS | 230 | 2015 | 2035 | solar | solar | 3 | 18.54% | 0.55634 | 18% | 4.7304
| Barlow Solar Energy Centre | ON_BLW00_GEN | Barlow Energy Centre Limited Partnership | Cornwall | 45.0679 | -74.9468 | Ontario.b | Ontario | Newington DS | ON_NWG_DSS | 115 | 2019 | 2039 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Barrett Chute | ON_BTC00_GEN | Ontario Power Generation Inc | Renfrew | 45.2499 | -76.759 | Ontario.b | Ontario | Barrett Chute SWS | ON_BTC_SWS | 115 | 1942 | 2100 | hydro_run | hydro_run | 179 | 68.43% | 122.4912 | 13.18% | 206.617 | 4
| Batawa | ON_BTW00_GEN | Innergex Inc | Batawa | 44.1685 | -77.5881 | Ontario.a | Ontario | Sidney TS | ON_SDY_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 5 | 68.43% | 3.4215 | 65% | 28.47
| Beamlight | ON_BMT00_GEN | Beamlight LP | Pefferlaw | 44.2588 | -79.293 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Beare Road | ON_BRR00_GEN | E. S. Fox Ltd | Scarborough | 43.8233 | -79.1639 | Ontario.a | Ontario | Cherrywood TS | ON_CHW_DSS | 230 | 2000 | 2100 | biogas | biomass | 5 | 94.51% | 4.7256 | 20% | 8.76
| Beck 1_01 | ON_BK101_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 2022 | 2100 | hydro_run | hydro_run | 62.5 | 68.43% | 42.7693 | 54.79% | 300 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_02 | ON_BK102_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 2022 | 2100 | hydro_run | hydro_run | 62.5 | 68.43% | 42.7693 | 54.79% | 300 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_03 | ON_BK103_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 1921 | 2100 | hydro_run | hydro_run | 56 | 68.43% | 38.3213 | 55.04% | 270 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_04 | ON_BK104_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 1921 | 2100 | hydro_run | hydro_run | 56 | 68.43% | 38.3213 | 55.04% | 270 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_05 | ON_BK105_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 1921 | 2100 | hydro_run | hydro_run | 56 | 68.43% | 38.3213 | 55.04% | 270 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_06 | ON_BK106_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 1921 | 2100 | hydro_run | hydro_run | 56 | 68.43% | 38.3213 | 55.04% | 270 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_07 | ON_BK107_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 1921 | 2100 | hydro_run | hydro_run | 56 | 68.43% | 38.3213 | 55.04% | 270 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_08 | ON_BK108_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 1921 | 2100 | hydro_run | hydro_run | 56 | 68.43% | 38.3213 | 55.04% | 270 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_09 | ON_BK109_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 1921 | 2100 | hydro_run | hydro_run | 56 | 68.43% | 38.3213 | 55.04% | 270 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 1_10 | ON_BK110_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1492 | -79.0443 | Ontario.a | Ontario | Beck #1 SWS | ON_BK1_SWS | 115 | 1921 | 2100 | hydro_run | hydro_run | 56 | 68.43% | 38.3213 | 55.04% | 270 | 10 | [19 empty] | https://www.opg.com/story/two-historic-units-at-sir-adam-beck-i-station-set-to-be-replaced/
| Beck 2_01 | ON_BK201_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_02 | ON_BK202_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_03 | ON_BK203_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_04 | ON_BK204_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_05 | ON_BK205_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_06 | ON_BK206_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_07 | ON_BK207_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_08 | ON_BK208_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_09 | ON_BK209_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_10 | ON_BK210_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_11 | ON_BK211_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_12 | ON_BK212_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_13 | ON_BK213_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_14 | ON_BK214_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_15 | ON_BK215_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck 2_16 | ON_BK216_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1456 | -79.0436 | Ontario.a | Ontario | Beck #2 TS | ON_BK2_TSS | 230 | 1954 | 2100 | hydro_run | hydro_run | 94 | 68.43% | 64.325 | 72.26% | 595 | 16 | [19 empty] | https://www.opg.com/powering-ontario/our-generation/hydro/
| Beck Pump | ON_BKP00_GEN | Ontario Power Generation Inc | Niagara Falls | 43.1446 | -79.0599 | Ontario.a | Ontario | Beck Pump Storage GS | ON_BKP_GSS | 230 | 1957 | 2100 | hydro_pump | hydro_pump | 146 | 0% | 0 | 0.5684% | 7.269 | 6 | [20 empty] | Facility operates only when required
| Becker | ON_BKR00_GEN | Hornepayne Power Inc | Hornepayne | 49.2105 | -84.6673 | Ontario.b | Ontario | Manitouwadge TS | ON_MTW_DSS | 115 | 2014 | 2024 | biomass | biomass | 15 | 94.51% | 14.1768 | 20% | 26.28
| Belle River | ON_BLR00_GEN | Belle River Wind LP | South Woodslee | 42.2496 | -82.6523 | Ontario.a | Ontario | Belle River GS | ON_BLR_GSS | 230 | 2017 | 2037 | wind_onshore | wind | 100 | 21.14% | 21.142 | 27.82% | 243.708
| Belleville TS Demorestville | ON_BLV00_GEN | Sune Demorestville LP | Demorestville | 44.0652 | -77.2579 | Ontario.a | Ontario | Picton TS | ON_PCT_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Belmont | ON_BEL00_GEN | ABW Solar General Partnership | Belmont | 42.8913 | -81.1134 | Ontario.a | Ontario | Buchanan TS | ON_BUC_DSS | 115 | 2013 | 2033 | solar | solar | 20 | 18.54% | 3.709 | 18% | 31.536
| Bensfort Road | ON_BSF00_GEN | LFG Power Corporation | Peterborough | 44.2271 | -78.2873 | Ontario.a | Ontario | Otonabee TS | ON_OTB_DSS | 230 | 2013 | 2033 | biogas | biomass | 1.6 | 94.51% | 1.5122 | 20% | 2.8032
| Big Beaver Falls | ON_BBF00_GEN | Amik-BBF HydroKap LP | Kapuskasing | 49.2998 | -82.5273 | Ontario.b | Ontario | Kapuskasing TS | ON_KAP_DSS | 115 | 2013 | 2053 | hydro_run | hydro_run | 5.5 | 68.43% | 3.7637 | 65% | 31.317
| Big Chute | ON_BGC00_GEN | Ontario Power Generation Inc | Coldwater | 44.8843 | -79.6761 | Ontario.b | Ontario | Waubaushene TS | ON_WBS_DSS | 230 | 1909 | 2100 | hydro_run | hydro_run | 10 | 68.43% | 6.8431 | 65% | 56.94 | 1
| Big Eddy | ON_BED00_GEN | Ontario Power Generation Inc | Bala | 45.0206 | -79.753 | Ontario.b | Ontario | Waubaushene TS | ON_WBS_DSS | 230 | 1941 | 2100 | hydro_run | hydro_run | 8 | 68.43% | 5.4745 | 65% | 45.552 | 2
| Big Eddy Inco | ON_BEI00_GEN | Vale Canada Limited | Nairn Centre | 46.3839 | -81.5781 | Ontario.b | Ontario | Espanola TS | ON_ESP_DSS | 115 | 1929 | 2100 | hydro_run | hydro_run | 27.6 | 68.43% | 18.8869 | 65% | 157.1544 | [20 empty] | http://www.vale.com/EN/business/energy/assets-and-equity/canada/Pages/default.aspx
| Bingham Chute | ON_BNC00_GEN | Ontario Power Generation Inc | Powassan | 46.0761 | -79.3968 | Ontario.b | Ontario | Trout Lake TS | ON_TRL_DSS | 230 | 1923 | 2100 | hydro_run | hydro_run | 1 | 68.43% | 0.68431 | 65% | 5.694 | 2
| Birchmount Energy Centre | ON_BEC00_GEN | Markham District Energy Inc | Aurora | 43.8444 | -79.3241 | Ontario.a | Ontario | Markham #1 MTS | ON_MM1_DSS | 230 | 2013 | 2033 | NG_CG | gasCC | 2.6 | 85.12% | 2.213 | 13% | 2.9609
| Bisnett Line | ON_BSN00_GEN | Bisnett Wind Farm Limited Partnership | Blenheim | 42.2787 | -81.9917 | Ontario.a | Ontario | Kent TS | ON_KNT_DSS | 115 | 2009 | 2029 | wind_onshore | wind | 9 | 21.14% | 1.9028 | 27% | 21.2868
| Black Bay 2 | ON_BKB00_GEN | 2397995 Ontario Inc | Red Rock | 48.9428 | -88.3141 | Ontario.b | Ontario | Red Rock DS | ON_RRK_DSS | 115 | 2015 | 2035 | solar | solar | 1 | 18.54% | 0.18545 | 18% | 1.5768
| Bluewater | ON_BLU00_GEN | Varna Wind LP | Zurich | 43.4846 | -81.6282 | Ontario.a | Ontario | Seaforth TS | ON_SFT_DSS | 115 | 2014 | 2034 | wind_onshore | wind | 60 | 21.14% | 12.6852 | 29.75% | 156.368
| Bornish | ON_BNS00_GEN | Bornish Wind LP | Kerwood | 43.1128 | -81.7024 | Ontario.a | Ontario | Evergreen SWS | ON_EVG_SWS | 500 | 2014 | 2034 | wind_onshore | wind | 73 | 21.14% | 15.4337 | 26.67% | 170.525
| Bow Lake | ON_BWL00_GEN | Nodin Kitagan LP | Montreal River Harbour | 47.2214 | -84.5235 | Ontario.b | Ontario | Batchawana TS | ON_BWA_DSS | 115 | 2015 | 2035 | wind_onshore | wind | 57 | 21.14% | 12.051 | 33.07% | 165.108
| Bracebridge Falls | ON_BRA00_GEN | Bracebridge Generation Limited | Bracebridge | 45.0388 | -79.3086 | Ontario.b | Ontario | Bracebridge TS | ON_BRA_DSS | 230 | 2012 | 2032 | hydro_run | hydro_run | 1.9 | 68.43% | 1.3002 | 65% | 10.8186
| Brampton | ON_BRM00_GEN | Algonquin Power | Brampton | 43.697 | -79.6825 | Ontario.a | Ontario | Bramalea TS | ON_BML_DSS | 230 | 2000 | 2100 | biomass | biomass | 15.1 | 94.51% | 14.2713 | 20% | 26.4552
| Breen 2 | ON_BRN00_GEN | Met Fiera Solar Breen 2 LP | Putnam | 42.9854 | -80.9604 | Ontario.a | Ontario | Ingersoll TS | ON_ING_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Brighton Beach | ON_BTB00_GEN | Shell Energy North America (Canada) Inc | Windsor | 42.2798 | -83.0946 | Ontario.a | Ontario | Brighton Interface JCT | ON_BTN_JCT | 230 | 2010 | 2025 | NG_CT | gasSC | 560 | 85.12% | 476.653 | 4.822% | 236.558
| Britannia | ON_BRT00_GEN | Region of Peel | Mississauga | 43.6067 | -79.6972 | Ontario.a | Ontario | Erindale TS | ON_ERD_DSS | 230 | 2007 | 2027 | biogas | biomass | 5.5 | 94.51% | 5.1982 | 20% | 9.636
| Brockville 1 | ON_BRO00_GEN | TransCanada Energy Ltd | Brockville | 44.6329 | -75.6982 | Ontario.a | Ontario | Brockville TS | ON_BRO_DSS | 115 | 2012 | 2032 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Brockville 2 | ON_BRO02_GEN | TransCanada Energy Ltd | Brockville | 44.6301 | -75.8033 | Ontario.a | Ontario | Brockville TS | ON_BRO_DSS | 115 | 2013 | 2033 | solar | solar | 9 | 18.54% | 1.669 | 18% | 14.1912
| Brockville Solar | ON_BRS00_GEN | Brockville Solar Inc | Lyn | 44.5939 | -75.7354 | Ontario.a | Ontario | Wingham TS | ON_WNG_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Bruce A_01 | ON_BCA01_GEN | Bruce Power LP | Tiverton | 44.3391 | -81.5747 | Ontario.a | Ontario | Bruce A TS | ON_BCA_TSS | 230 | 2000 | 2100 | nuclear | nuclear | 779 | 92.83% | 723.1607 | 79.57% | 5429.58
| Bruce A_02 | ON_BCA02_GEN | Bruce Power LP | Tiverton | 44.3391 | -81.5747 | Ontario.a | Ontario | Bruce A TS | ON_BCA_TSS | 230 | 2000 | 2100 | nuclear | nuclear | 779 | 92.83% | 723.1607 | 87.62% | 5979.281
| Bruce A_03 | ON_BCA03_GEN | Bruce Power LP | Tiverton | 44.3391 | -81.5747 | Ontario.a | Ontario | Bruce A TS | ON_BCA_TSS | 230 | 2000 | 2100 | nuclear | nuclear | 784 | 92.83% | 727.8023 | 91.43% | 6279.082
| Bruce A_04 | ON_BCA04_GEN | Bruce Power LP | Tiverton | 44.3391 | -81.5747 | Ontario.a | Ontario | Bruce A TS | ON_BCA_TSS | 230 | 2000 | 2100 | nuclear | nuclear | 784 | 92.83% | 727.8023 | 67.67% | 4647.39
| Bruce B_01 | ON_BCB01_GEN | Bruce Power LP | Tiverton | 44.319 | -81.6027 | Ontario.a | Ontario | Bruce B SWS | ON_BCB_SWS | 230 | 2000 | 2100 | nuclear | nuclear | 817 | 92.83% | 758.4368 | 99.11% | 7093.015
| Bruce B_02 | ON_BCB02_GEN | Bruce Power LP | Tiverton | 44.319 | -81.6027 | Ontario.a | Ontario | Bruce B SWS | ON_BCB_SWS | 230 | 2000 | 2100 | nuclear | nuclear | 817 | 92.83% | 758.4368 | 98.45% | 7045.711
| Bruce B_03 | ON_BCB03_GEN | Bruce Power LP | Tiverton | 44.319 | -81.6027 | Ontario.a | Ontario | Bruce B SWS | ON_BCB_SWS | 230 | 2000 | 2100 | nuclear | nuclear | 817 | 92.83% | 758.4368 | 99.67% | 7133.332
| Bruce B_04 | ON_BCB04_GEN | Bruce Power LP | Tiverton | 44.319 | -81.6027 | Ontario.a | Ontario | Bruce B SWS | ON_BCB_SWS | 230 | 2000 | 2100 | nuclear | nuclear | 817 | 92.83% | 758.4368 | 66.97% | 4792.885
| Bur Oak Energy Centre | ON_BOE00_GEN | Markham District Energy Inc | Markham | 43.8471 | -79.3327 | Ontario.a | Ontario | Markham #1 MTS | ON_MM1_DSS | 230 | 2014 | 2034 | NG_CG | gasCC | 3.25 | 85.12% | 2.7663 | 13% | 3.7011
| Burk's Falls | ON_BKS00_GEN | Bracebridge Generation Limited | Burks Falls | 45.6198 | -79.4118 | Ontario.b | Ontario | Muskoka TS | ON_MSK_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 1.1 | 68.43% | 0.75274 | 65% | 6.2634
| Burritts Rapids | ON_BRP00_GEN | TransCanada Energy Ltd | Merrickville | 44.9778 | -75.8198 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2013 | 2033 | solar | solar | 7 | 18.54% | 1.2981 | 18% | 11.0376
| C.L. Solutions | ON_CLS00_GEN | Under Sun Acres Green Energy Inc | Leamington | 42.1532 | -82.5894 | Ontario.a | Ontario | Leamington TS | ON_LEM_DSS | 230 | 2000 | 2100 | NG_CG | gasCC | 12.932 | 85.12% | 11.0073 | 13% | 14.727
| Calabogie | ON_CBG00_GEN | Ontario Power Generation Inc | Renfrew | 45.3047 | -76.7087 | Ontario.b | Ontario | Barrett Chute SWS | ON_BTC_SWS | 115 | 1917 | 2100 | hydro_run | hydro_run | 5 | 68.43% | 3.4215 | 65% | 28.47 | 2
| Calm Lake | ON_CLM00_GEN | H2O Power LP | Atikokan | 48.7937 | -92.154 | Ontario.b | Ontario | H2O Power Calm Lake GS | ON_H2C_GSS | 230 | 2009 | 2029 | hydro_run | hydro_run | 8.8 | 68.43% | 6.0219 | 65% | 50.1072 | [20 empty] | http://www.h2opower.com/our-locations/
| Cameron Falls BRP | ON_CAF00_GEN | Brookfield Renewable Power Inc | Walford | 46.2822 | -82.1493 | Ontario.b | Ontario | Spanish DS | ON_SPA_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 4.2 | 68.43% | 2.8741 | 65% | 23.9148
| Cameron Falls OPG | ON_CAM00_GEN | Ontario Power Generation Inc | Nipigon | 49.1536 | -88.3457 | Ontario.b | Ontario | Cameron Falls GS | ON_CAM_GSS | 115 | 1920 | 2100 | hydro_run | hydro_run | 108 | 68.43% | 73.9053 | 50.52% | 477.937 | 7
| Camp Three Rapids | ON_CTR00_GEN | Amik-Ctr Hydrokap LP | Kapuskasing | 49.2964 | -82.5373 | Ontario.b | Ontario | Kapuskasing TS | ON_KAP_DSS | 115 | 2013 | 2053 | hydro_run | hydro_run | 5.5 | 68.43% | 3.7637 | 65% | 31.317
| Campbellford | ON_CBF00_GEN | Campbellford-Seymour Electric Generation Inc | Campbellford | 44.3351 | -77.7725 | Ontario.a | Ontario | Havelock TS | ON_HVL_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388
| Cardinal | ON_CRD00_GEN | Cardinal Power LP | Cardinal | 44.7846 | -75.3779 | Ontario.b | Ontario | Cardinal Power GS | ON_CDP_GSS | 115 | 2015 | 2035 | NG_CT | gasSC | 184 | 85.12% | 156.6146 | 5.074% | 81.782
| Caribou Falls | ON_CRF00_GEN | Ontario Power Generation Inc | Kenora | 50.2625 | -94.9744 | Ontario.b | Ontario | Caribou Falls GS | ON_CRF_GSS | 115 | 1958 | 2100 | hydro_run | hydro_run | 91 | 68.43% | 62.2721 | 40.99% | 326.773 | 3
| Carmichael | ON_CRM00_GEN | Great Lakes Hydro | Moonbeam | 49.1458 | -82.0308 | Ontario.b | Ontario | Fauquier DS | ON_FAU_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 20 | 68.43% | 13.6862 | 48.01% | 84.118
| Cascade Street | ON_CSC00_GEN | Bracebridge Generation Limited | Bracebridge | 45.3504 | -80.0267 | Ontario.b | Ontario | Bracebridge TS | ON_BRA_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 1.2 | 68.43% | 0.82117 | 65% | 6.8328
| Cedar Point | ON_CDP00_GEN | Cedar Point II LP | Forest | 43.0828 | -82.0528 | Ontario.a | Ontario | Wanstead TS | ON_WAN_DSS | 115 | 2015 | 2035 | wind_onshore | wind | 100 | 21.14% | 21.142 | 31.96% | 280.003
| Cedarline Greenhouse | ON_CLG00_GEN | 1579303 Ontario Ltd | Dresden | 42.5704 | -82.1331 | Ontario.a | Ontario | Wallaceburg TS | ON_WLB_DSS | 115 | 2000 | 2100 | NG_CG | gasCC | 5.156 | 85.12% | 4.3886 | 13% | 5.8717
| Cervini | ON_CRV00_GEN | Elliott Cogeneration Inc | Leamington | 42.0634 | -82.6053 | Ontario.a | Ontario | Leamington TS | ON_LEM_DSS | 230 | 2000 | 2100 | NG_CG | gasCC | 9.699 | 85.12% | 8.2555 | 13% | 11.0452
| Chapleau | ON_CHP00_GEN | Tembec Inc | Chapleau | 47.8431 | -83.428 | Ontario.b | Ontario | Chapleau DS | ON_CHP_DSS | 115 | 2014 | 2022 | biomass | biomass | 7.2 | 94.51% | 6.8049 | 20% | 12.6144
| Chats Falls | ON_CHF00_GEN | Ontario Power Generation Inc | Ottawa | 45.4752 | -76.2382 | Ontario.b | Ontario | Chats Falls SWS | ON_CHF_SWS | 115 | 1931 | 2100 | hydro_daily | hydro_daily | 200 | 68.43% | 136.8617 | 61.93% | 1085.062 | 8
| Chaudiere 2 | ON_CH200_GEN | Energy Ottawa Inc | Ottawa | 45.4191 | -75.7139 | Ontario.b | Ontario | King Edward TS | ON_KNE_DSS | 115 | 2010 | 2030 | hydro_run | hydro_run | 8.4 | 68.43% | 5.7482 | 65% | 47.8296 | [20 empty] | http://portagepower.com/hydroelectric/chaudiere-falls/
| Chaudiere 4 | ON_CH400_GEN | Energy Ottawa Inc | Ottawa | 45.4204 | -75.7149 | Ontario.b | Ontario | King Edward TS | ON_KNE_DSS | 115 | 2010 | 2030 | hydro_run | hydro_run | 9.3 | 68.43% | 6.3641 | 65% | 52.9542 | [20 empty] | http://portagepower.com/hydroelectric/chaudiere-falls/
| Chenaux | ON_CHX00_GEN | Ontario Power Generation Inc | Renfrew | 45.5838 | -76.6738 | Ontario.b | Ontario | Chenaux TS | ON_CHX_TSS | 230 | 1950 | 2100 | hydro_daily | hydro_daily | 158 | 68.43% | 108.1207 | 49.06% | 679.096 | 8
| Chiblow Lake | ON_CLB00_GEN | 1149377 Ontario Limited | Blind River | 46.3126 | -83.0655 | Ontario.b | Ontario | Blind River TS | ON_BLD_DSS | 115 | 2014 | 2034 | hydro_run | hydro_run | 1.7 | 68.43% | 1.1633 | 65% | 9.6798
| Chute Falls | ON_CHU00_GEN | Ontario Power Generation Inc | Elk Lake | 47.84 | -80.4486 | Ontario.b | Ontario | Kirkland Lake TS | ON_KLL_DSS | 115 | 1923 | 2100 | hydro_run | hydro_run | 3 | 68.43% | 2.0529 | 65% | 17.082 | 2
| Citylights | ON_CTY00_GEN | Axium City Light LP | Chesterville | 45.1563 | -75.2245 | Ontario.b | Ontario | Chesterville TS | ON_CHS_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Clear Creek | ON_CCR00_GEN | AIM Powergen Corporation | Clear Creek | 42.5879 | -80.5722 | Ontario.a | Ontario | Tillsonburg TS | ON_TLL_DSS | 115 | 2008 | 2028 | wind_onshore | wind | 9.9 | 21.14% | 2.0931 | 27% | 23.4155
| Clergue | ON_CGU00_GEN | Brookfield Renewable Power Inc | Sault Ste. Marie | 46.5148 | -84.3472 | Ontario.b | Ontario | Clergue TS | ON_CGU_DSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 53 | 68.43% | 36.2683 | 70.35% | 326.643
| Comber | ON_COM00_GEN | 2016 Comber Wind LP | Comber | 42.2195 | -82.5614 | Ontario.a | Ontario | Comber WF GS | ON_COM_GSS | 230 | 2011 | 2031 | wind_onshore | wind | 166 | 21.14% | 35.0958 | 29.44% | 428.093
| Conestogo | ON_CST00_GEN | Conestogo Wind LP | Alma | 43.7943 | -80.5888 | Ontario.a | Ontario | Fergus TS | ON_FGS_DSS | 230 | 2012 | 2032 | wind_onshore | wind | 22.9 | 21.14% | 4.8415 | 27% | 54.1631
| Coniston | ON_CTN00_GEN | Ontario Power Generation Inc | Sudbury | 46.4746 | -80.8183 | Ontario.b | Ontario | Coniston TS | ON_CTN_DSS | 115 | 1905 | 2100 | hydro_run | hydro_run | 4 | 68.43% | 2.7372 | 65% | 22.776 | 2
| CONTRACTED - ON-QB | PP_ONQB01_GEN | Hydro-Quebec Production | ON-QB Border | 45.3095 | 74.0612 | Quebec.a | Ontario | IPT Beauharnois | PP_ONQB1_IPT | 230 | 2009 | 2029 | hydro_monthly | hydro_monthly | 145 | 100% | 145 | 47.24% | 600 | [20 empty] | https://www.cornwallnewswatch.com/2016/08/22/cornwall-electric-10-year-hydro-quebec-deal-in-the-works/ | Sales to Cornwall Ontario
| Cornwall | ON_CWL00_GEN | Cornwall Solar Inc | Cornwall | 45.1024 | -74.6899 | Ontario.b | Ontario | St. Lawrence TS | ON_STL_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Countryside London | ON_CSL00_GEN | London District Energy LP | London | 42.9831 | -81.2387 | Ontario.a | Ontario | Buchanan TS | ON_BUC_DSS | 115 | 2008 | 2028 | NG_CG | gasCC | 21 | 85.12% | 17.8745 | 13% | 23.9148
| Crowe Bay | ON_CRB00_GEN | Town of Campellford | Campbellford | 44.3353 | -77.7723 | Ontario.a | Ontario | Havelock TS | ON_HVL_DSS | 230 | 2000 | 2100 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388
| Cruickshank | ON_CKS00_GEN | Enbridge Inc | Tiverton | 44.2478 | -81.5714 | Ontario.a | Ontario | Bruce A TS | ON_BCA_TSS | 230 | 2008 | 2028 | wind_onshore | wind | 8.3 | 21.14% | 1.7548 | 27% | 19.6312
| Crystal Falls | ON_CRY00_GEN | Ontario Power Generation Inc | Sturgeon Falls | 46.4501 | -79.8629 | Ontario.b | Ontario | Crystal Falls TS | ON_CRY_DSS | 230 | 1921 | 2100 | hydro_run | hydro_run | 8 | 68.43% | 5.4745 | 65% | 45.552 | 4
| Cultus | ON_CLT00_GEN | AIM Powergen Corporation | Clear Creek | 42.6009 | -80.6048 | Ontario.a | Ontario | Tillsonburg TS | ON_TLL_DSS | 115 | 2008 | 2028 | wind_onshore | wind | 9.9 | 21.14% | 2.0931 | 27% | 23.4155
| Darlington_01 | ON_DLG01_GEN | Ontario Power Generation Inc | Clarington | 43.8697 | -78.7239 | Ontario.a | Ontario | Bowmanville SWS | ON_BOW_SWS | 500 | 1990 | 2100 | nuclear | nuclear | 881 | 92.83% | 817.8492 | 97.16% | 7498.691 | 4
| Darlington_02 | ON_DLG02_GEN | Ontario Power Generation Inc | Clarington | 43.8697 | -78.7239 | Ontario.a | Ontario | Bowmanville SWS | ON_BOW_SWS | 500 | 2026 | 2100 | nuclear | nuclear | 881 | 92.83% | 817.8492 | 75.15% | 5800 | 4 | [20 empty] | Under refurbishment until 2027
| Darlington_03 | ON_DLG03_GEN | Ontario Power Generation Inc | Clarington | 43.8697 | -78.7239 | Ontario.a | Ontario | Bowmanville SWS | ON_BOW_SWS | 500 | 1990 | 2100 | nuclear | nuclear | 881 | 92.83% | 817.8492 | 75.1% | 5795.714 | 4
| Darlington_04 | ON_DLG04_GEN | Ontario Power Generation Inc | Clarington | 43.8697 | -78.7239 | Ontario.a | Ontario | Bowmanville SWS | ON_BOW_SWS | 500 | 1990 | 2100 | nuclear | nuclear | 881 | 92.83% | 817.8492 | 90.52% | 6985.938 | 4
| Dave Rampel | ON_DVR00_GEN | Rainy River First Nations Solar 3 LP | Rainy River | 48.7152 | -94.2518 | Ontario.b | Ontario | Barwick TS | ON_BWK_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| David Brown | ON_DVB00_GEN | Saturn Solar 2 LP | Ingleside | 45.0085 | -74.9996 | Ontario.b | Ontario | St. Lawrence TS | ON_STL_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Decew Falls 1 | ON_DEC01_GEN | Ontario Power Generation Inc | St. Catharines | 43.1183 | -79.2643 | Ontario.a | Ontario | DeCew Falls SWS | ON_DEC_SWS | 115 | 1898 | 2100 | hydro_daily | hydro_daily | 144 | 68.43% | 98.5404 | 46.54% | 587.101 | 5
| Decew Falls 2 | ON_DEC02_GEN | Ontario Power Generation Inc | St. Catharines | 43.1189 | -79.2612 | Ontario.a | Ontario | DeCew Falls SWS | ON_DEC_SWS | 115 | 1943 | 2100 | hydro_run | hydro_run | 23 | 68.43% | 15.7391 | 76.47% | 154.073 | 2
| Des-Joachims | ON_DEJ00_GEN | Ontario Power Generation Inc | Deep River | 46.1827 | -77.697 | Ontario.b | Ontario | Des Joachims TS | ON_DEJ_TSS | 230 | 1950 | 2100 | hydro_daily | hydro_daily | 475 | 68.43% | 325.0464 | 51.19% | 2129.832 | 8
| Destec | ON_DTC00_GEN | Northland Power | Kingston | 44.2098 | -76.7247 | Ontario.a | Ontario | NPIF Kingston GS | ON_NPK_GSS | 230 | 2000 | 2100 | NG_CC | gasCC | 140 | 85.12% | 119.1632 | 0.1274% | 1.562 | [20 empty] | https://www.northlandpower.com/What-We-Do/Operating-Assets/Thermal/Kingston.aspx
| Dillon | ON_DIL00_GEN | Terraform Iwg Ontario Holdings LLC | Chatham | 42.2743 | -82.1824 | Ontario.a | Ontario | Dillon RWEC GS | ON_DIL_GSS | 230 | 2011 | 2031 | wind_onshore | wind | 78 | 21.14% | 16.4908 | 27.43% | 187.452 | [21 empty] | Also called Raleigh
| Discovery Light | ON_DVL00_GEN | Axium Discovery Light LP | Beaverton | 44.4384 | -79.0681 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Douglas | ON_DGL00_GEN | Multistream Power Corporation | Douglas | 45.5088 | -76.9388 | Ontario.b | Ontario | Cobden TS | ON_CBD_DSS | 115 | 2010 | 2050 | hydro_run | hydro_run | 1.5 | 68.43% | 1.0265 | 0.3044% | 0.04
| Dow | ON_DOW00_GEN | Dow Chemical | Sarnia | 42.9225 | -82.4372 | Ontario.a | Ontario | Sarnia Scott TS | ON_SNS_TSS | 230 | 2000 | 2100 | NG_CG | gasCC | 46 | 85.12% | 39.1536 | 25.72% | 103.637
| Dufferin | ON_DFF00_GEN | Dufferin Wind Power Inc | Shelburne | 44.2134 | -80.2673 | Ontario.a | Ontario | Shannon GS | ON_SHN_DSS | 230 | 2014 | 2034 | wind_onshore | wind | 91.4 | 21.14% | 19.3238 | 33.55% | 268.617 | [21 empty] | Also called Shannon
| Dunford | ON_DNF00_GEN | Brookfield Renewable Power Inc | Wawa | 47.9069 | -84.7156 | Ontario.b | Ontario | DA Watson TS | ON_DAW_DSS | 115 | 2009 | 2029 | hydro_run | hydro_daily | 45 | 68.43% | 30.7939 | 30.07% | 118.5233
| Dupont Maitland | ON_DPM00_GEN | Invista (Canada) Company | Maitland | 44.6606 | -75.5788 | Ontario.a | Ontario | Brockville TS | ON_BRO_DSS | 115 | 2016 | 2036 | NG_CG | gasCC | 52 | 85.12% | 44.2606 | 1.796% | 8.182
| Durham College | ON_DMC00_GEN | Oshawa PUC Energy Services Inc | Durham | 43.9439 | -78.896 | Ontario.a | Ontario | Wilson TS | ON_WLS_DSS | 230 | 2008 | 2028 | NG_CG | gasCC | 2.4 | 85.12% | 2.0428 | 13% | 2.7331
| Durham York Energy Centre | ON_DYE00_GEN | The Regional Municipalities of Durham and of York | Courtice | 43.8756 | -78.7522 | Ontario.a | Ontario | Wilson TS | ON_WLS_DSS | 230 | 2015 | 2035 | MSW | biomass | 17.5 | 94.51% | 16.5396 | 20% | 30.66
| Eagle River | ON_EGL00_GEN | Capstone Infrastructure Corp | Eagle River | 49.7911 | -93.1969 | Ontario.b | Ontario | Eton DS | ON_ETO_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 1.8 | 68.43% | 1.2318 | 65% | 10.2492
| Ear Falls | ON_EAF00_GEN | Ontario Power Generation Inc | Ear Falls | 50.6307 | -93.2206 | Ontario.b | Ontario | Ear Falls TS | ON_EAF_DSS | 115 | 2009 | 2059 | hydro_run | hydro_run | 17 | 68.43% | 11.6332 | 83.09% | 123.735 | 4
| Earthlight | ON_ETL00_GEN | Concord Earthlight Partnership | Pefferlaw | 44.2875 | -79.2834 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| East Durham | ON_EDH00_GEN | East Durham Wind LP | Priceville | 44.1972 | -80.7005 | Ontario.a | Ontario | Hanover TS | ON_HNV_DSS | 230 | 2015 | 2035 | wind_onshore | wind | 22.4 | 21.14% | 4.7358 | 27% | 52.9805
| East Lake St. Clair | ON_ESC00_GEN | East Lake St. Clair Wind LP | Wallaceburg | 42.4776 | -82.3603 | Ontario.a | Ontario | East Lake St. Clair GS | ON_ESC_GSS | 230 | 2013 | 2033 | wind_onshore | wind | 99 | 21.14% | 20.9306 | 31.96% | 277.188
| East LFG | ON_EST00_GEN | Integrated Gas Recovery Services Inc | Thorold | 43.1216 | -79.1739 | Ontario.a | Ontario | Thorold TS | ON_THL_DSS | 115 | 2007 | 2027 | biogas | biomass | 1 | 94.51% | 0.94512 | 20% | 1.752
| East Windsor_01 | ON_EWI01_GEN | Capital Power | Windsor | 42.3258 | -83.0005 | Ontario.b | Ontario | East Windsor GS | ON_EWI_GSS | 115 | 2009 | 2029 | NG_CG | gasCC | 46 | 85.12% | 39.1536 | 1.233% | 4.967
| East Windsor_02 | ON_EWI02_GEN | Capital Power | Windsor | 42.3258 | -83.0005 | Ontario.a | Ontario | East Windsor GS | ON_EWI_GSS | 115 | 2009 | 2029 | NG_CG | gasCC | 46 | 85.12% | 39.1536 | 1.202% | 4.844
| Eastview LFG | ON_ETV00_GEN | Envida Community Energy Inc | Guelph | 43.5741 | -80.2323 | Ontario.a | Ontario | Campbell TS | ON_CBL_DSS | 230 | 2005 | 2025 | biogas | biomass | 1.7 | 94.51% | 1.6067 | 20% | 2.9784
| Eddy Ottawa | ON_EDO00_GEN | Energy Ottawa Inc | Ottawa | 45.4208 | -75.7185 | Ontario.b | Ontario | King Edward TS | ON_KNE_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 9.2 | 68.43% | 6.2956 | 65% | 52.3848 | [20 empty] | http://portagepower.com/hydroelectric/chaudiere-falls/
| EffiSolar Beckwith | ON_ESB00_GEN | Beckwith Solar Inc | Smiths Falls | 45.0564 | -76.0795 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Elliot Chute | ON_ELC00_GEN | Ontario Power Generation Inc | Powassan | 46.0602 | -79.3894 | Ontario.b | Ontario | Trout Lake TS | ON_TRL_DSS | 230 | 1929 | 2100 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388 | 1
| Elmsley | ON_ELY00_GEN | EDF Energies Nouvelles | Smiths Falls | 44.8406 | -76.0866 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2010 | 2030 | solar | solar | 24 | 18.54% | 4.4507 | 18% | 37.8432
| Elora | ON_ELO00_GEN | Shaman Power Corporation | Elora | 43.6809 | -80.4329 | Ontario.a | Ontario | Fergus TS | ON_FGS_DSS | 230 | 2000 | 2100 | hydro_run | hydro_run | 1 | 68.43% | 0.68431 | 65% | 5.694
| Emerald | ON_EMD00_GEN | Emerald Energy From Waste Inc | Brampton | 43.6972 | -79.6832 | Ontario.a | Ontario | Bramalea TS | ON_BML_DSS | 230 | 2015 | 2030 | MSW | biomass | 10.3 | 94.51% | 9.7348 | 20% | 18.0456
| Enature | ON_ENT00_GEN | 2553187 Ontario Inc | Freelton | 43.3822 | -80 | Ontario.a | Ontario | Dundas TS | ON_DDS_DSS | 115 | 2000 | 2100 | NG_CG | gasCC | 5.157 | 85.12% | 4.3895 | 13% | 5.8728
| Erie Ridge | ON_ERR00_GEN | Sunedison / Skypower Ltd | Ridgetown | 42.4454 | -81.8504 | Ontario.a | Ontario | Duart TS | ON_DUA_DSS | 230 | 2011 | 2031 | solar | solar | 9.4 | 18.54% | 1.7432 | 18% | 14.8219
| Erieau | ON_ERI00_GEN | Erieau Wind LP | Blenheim | 42.3011 | -82.0047 | Ontario.a | Ontario | Erieau WF GS | ON_ERI_GSS | 230 | 2013 | 2033 | wind_onshore | wind | 99 | 21.14% | 20.9306 | 33.5% | 290.498
| Ernestown | ON_ERN00_GEN | Ernestown Windpark LP | Bath | 44.228 | -76.7195 | Ontario.a | Ontario | Napanee TS | ON_NAP_DSS | 115 | 2014 | 2034 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Espanola Biomass | ON_ESP00_GEN | Domtar Inc | Espanola | 46.2691 | -81.7672 | Ontario.b | Ontario | Espanola GS | ON_ESP_GSS | 115 | 2000 | 2100 | biomass | biomass | 25 | 94.51% | 23.628 | 20% | 43.8
| Espanola Mill Hydro | ON_ESH00_GEN | Domtar Inc | Espanola | 46.2697 | -81.7706 | Ontario.b | Ontario | Espanola TS | ON_ESP_DSS | 115 | 2012 | 2032 | hydro_run | hydro_run | 18 | 68.43% | 12.3175 | 65% | 102.492 | [20 empty] | https://www.northeasternontario.com/river-walleye-espanola/
| Eugenia | ON_EUG00_GEN | Ontario Power Generation Inc | Meaford | 44.3398 | -80.537 | Ontario.a | Ontario | Owen Sound TS | ON_OWS_DSS | 115 | 1915 | 2100 | hydro_run | hydro_run | 6 | 68.43% | 4.1058 | 65% | 34.164 | 3
| Fenelon Falls | ON_FNF00_GEN | Shaman Power Corporation | Fenelon Falls | 44.5356 | -78.7373 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 1997 | 2039 | hydro_run | hydro_run | 2.6 | 68.43% | 1.7792 | 65% | 14.8044
| Ferndale | ON_FND00_GEN | Sky Generation LP | Lions Head | 44.9465 | -81.2632 | Ontario.b | Ontario | Owen Sound TS | ON_OWS_DSS | 230 | 2007 | 2027 | wind_onshore | wind | 5.1 | 21.14% | 1.0782 | 27% | 12.0625
| First Light 1 | ON_FLT01_GEN | Sunedison / Skypower Ltd | Centreville | 44.2904 | -76.9257 | Ontario.a | Ontario | Napanee TS | ON_NAP_DSS | 115 | 2009 | 2029 | solar | solar | 9.1 | 18.54% | 1.6876 | 18% | 14.3489
| First Light 2 | ON_FLT02_GEN | Sunedison / Skypower Ltd | Centreville | 44.2984 | -76.9425 | Ontario.a | Ontario | Napanee TS | ON_NAP_DSS | 115 | 2011 | 2031 | solar | solar | 10.4 | 18.54% | 1.9287 | 18% | 16.3987
| Foothill Greenhouses Ltd. | ON_FHG00_GEN | Foothill Greenhouses Limited | King City | 44.0278 | -79.6068 | Ontario.a | Ontario | Holland TS | ON_HLD_DSS | 230 | 2017 | 2037 | NG_CG | gasCC | 3.233 | 85.12% | 2.7518 | 13% | 3.6817
| Fort Frances | ON_FRF00_GEN | H2O Power LP | Fort Frances | 48.6091 | -93.4023 | Ontario.b | Ontario | H2O Power Fort Frances GS | ON_H2F_GSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 10 | 68.43% | 6.8431 | 65% | 56.94 | [20 empty] | http://www.h2opower.com/our-locations/
| Fort William | ON_FTW00_GEN | Thunder Bay Solar 2 LP | Thunder Bay | 48.3603 | -89.2536 | Ontario.b | Ontario | Birch TS | ON_BIR_DSS | 115 | 2012 | 2032 | solar | solar | 10.9 | 18.54% | 2.0214 | 18% | 17.1871
| Fotolight | ON_FTL00_GEN | Axium Foto Light LP | Picton | 44.0199 | -77.094 | Ontario.a | Ontario | Picton TS | ON_PCT_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Frankford | ON_FKF00_GEN | Ontario Power Generation Inc | Frankford | 44.1865 | -77.5945 | Ontario.a | Ontario | Sidney TS | ON_SDY_DSS | 115 | 1913 | 2100 | hydro_run | hydro_run | 3 | 68.43% | 2.0529 | 65% | 17.082 | 4
| Frogmore | ON_FGM00_GEN | AIM SOP Phase I LP | Clear Creek | 42.6069 | -80.6598 | Ontario.a | Ontario | Tillsonburg TS | ON_TLL_DSS | 115 | 2008 | 2028 | wind_onshore | wind | 9.9 | 21.14% | 2.0931 | 27% | 23.4155
| Front Line | ON_FRT00_GEN | Front Line Wind Farm Limited Partnership | Morpeth | 42.3964 | -81.8657 | Ontario.a | Ontario | Spence SWS | ON_SPC_SWS | 230 | 2010 | 2030 | wind_onshore | wind | 9 | 21.14% | 1.9028 | 27% | 21.2868
| Galetta | ON_GLT00_GEN | Canadian Hydro Developers Inc | Arnprior | 45.4262 | -76.2537 | Ontario.b | Ontario | Arnprior TS | ON_ARN_DSS | 115 | 2011 | 2031 | hydro_run | hydro_run | 1.6 | 68.43% | 1.0949 | 65% | 9.1104
| Ganaraska | ON_GSK00_GEN | Ganaraska Wind Development Joint Venture | Orono | 44.0197 | -78.581 | Ontario.a | Ontario | Wilson TS | ON_WLS_DSS | 230 | 2016 | 2036 | wind_onshore | wind | 17.6 | 21.14% | 3.721 | 27% | 41.6275
| Gartshore | ON_GSO00_GEN | Brookfield Renewable Power Inc | Wawa | 47.2402 | -84.5835 | Ontario.b | Ontario | Gartshore GS | ON_GSO_GSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 100 | 68.43% | 68.4308 | 37.27% | 326.473
| Gatineau | ON_GTU00_GEN | Chaudière Hydro North LP | Ottawa | 45.4792 | -75.6552 | Ontario.b | Ontario | King Edward TS | ON_KNE_DSS | 115 | 2000 | 2100 | biomass | biomass | 15 | 94.51% | 14.1768 | 20% | 26.28
| Geisler Falls / Corkery Falls | ON_GFS00_GEN | Carlisle LP No. 1 | Trout Creek | 45.9879 | -79.419 | Ontario.b | Ontario | Trout Lake TS | ON_TRL_DSS | 230 | 2015 | 2035 | hydro_run | hydro_run | 2.9 | 68.43% | 1.9845 | 65% | 16.5126
| Gesner | ON_GSR00_GEN | Gesner Wind Farm LP | Muirkirk | 42.5193 | -81.7571 | Ontario.a | Ontario | Duart TS | ON_DUA_DSS | 230 | 2013 | 2033 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Gitchi Animki Bezhig | ON_GAB00_GEN | Pic Mobert Hydro Inc | Mobert | 48.6439 | -85.7659 | Ontario.b | Ontario | White River DS | ON_WHT_DSS | 115 | 2016 | 2056 | Hydro_run | hydro_run | 12 | 68.43% | 8.2117 | 33.91% | 35.646
| Gitchi Animki Niizh | ON_GAN00_GEN | Pic Mobert Hydro Inc | Mobert | 48.5977 | -85.8779 | Ontario.b | Ontario | White River DS | ON_WHT_DSS | 115 | 2016 | 2056 | Hydro_run | hydro_run | 10 | 68.43% | 6.8431 | 60.91% | 53.358
| Gitzler Falls | ON_GTZ00_GEN | Carlisle Ltd Partnership | Powassan | 46.0022 | -79.4247 | Ontario.b | Ontario | Trout Lake TS | ON_TRL_DSS | 230 | 2000 | 2100 | hydro_run | hydro_run | 1.2 | 68.43% | 0.82117 | 65% | 6.8328
| Glanbrook | ON_GLB00_GEN | Hamilton Renewable Power Inc | Binbrook | 43.0677 | -79.795 | Ontario.a | Ontario | Caledonia TS | ON_CAL_DSS | 230 | 2008 | 2028 | biogas | biomass | 3.2 | 94.51% | 3.0244 | 20% | 5.6064
| Glen Miller | ON_GLM00_GEN | Glen Miller Power LP | Trenton | 44.1525 | -77.5819 | Ontario.a | Ontario | Sidney TS | ON_SDY_DSS | 115 | 2005 | 2025 | hydro_run | hydro_run | 8 | 68.43% | 5.4745 | 65% | 45.552
| Glenarm | ON_GLR00_GEN | Csi Glenarm LP | Woodville | 44.4633 | -78.9662 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Goldlight | ON_GLD00_GEN | Goldlight LP | Pefferlaw | 44.2878 | -79.2936 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Goodlight | ON_GOO00_GEN | Goodlight LP | Kirkfield | 44.5117 | -78.992 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Goreway_01 | ON_GRW01_GEN | Capital Power | Brampton | 43.7465 | -79.6799 | Ontario.a | Ontario | Goreway TS | ON_GRW_DSS | 230 | 2009 | 2029 | NG_CC | gasCC | 193 | 85.12% | 164.275 | 9.351% | 158.103 | [20 empty] | https://www.capitalpower.com/operations/goreway-power-station/
| Goreway_02 | ON_GRW02_GEN | Capital Power | Brampton | 43.7465 | -79.6799 | Ontario.a | Ontario | Goreway TS | ON_GRW_DSS | 230 | 2009 | 2029 | NG_CC | gasCC | 193 | 85.12% | 164.275 | 9.625% | 162.732 | [20 empty] | https://www.capitalpower.com/operations/goreway-power-station/
| Goreway_03 | ON_GRW03_GEN | Capital Power | Brampton | 43.7465 | -79.6799 | Ontario.a | Ontario | Goreway TS | ON_GRW_DSS | 230 | 2009 | 2029 | NG_CC | gasCC | 193 | 85.12% | 164.275 | 8.688% | 146.892 | [20 empty] | https://www.capitalpower.com/operations/goreway-power-station/
| Goreway_04 | ON_GRW04_GEN | Capital Power | Brampton | 43.7465 | -79.6799 | Ontario.a | Ontario | Goreway TS | ON_GRW_DSS | 230 | 2009 | 2029 | NG_CC | gasCC | 348 | 85.12% | 296.2058 | 10.11% | 308.245 | [20 empty] | https://www.capitalpower.com/operations/goreway-power-station/
| Gosfield | ON_GOS00_GEN | Gosfield Wind LP | Kingsville | 42.1269 | -82.6835 | Ontario.a | Ontario | Gosfield GS | ON_GOS_GSS | 115 | 2010 | 2030 | wind_onshore | wind | 51 | 21.14% | 10.7824 | 29.31% | 130.938
| Goshen | ON_GSH00_GEN | Goshen Wind LP | Dashwood | 43.2986 | -81.6144 | Ontario.a | Ontario | Goshen GS | ON_GSH_GSS | 115 | 2015 | 2035 | wind_onshore | wind | 102.4 | 21.14% | 21.6494 | 27.97% | 250.891
| Goulais | ON_GLA00_GEN | Chi-Wiikwedong LP | Sault Ste. Marie | 46.6615 | -84.3587 | Ontario.b | Ontario | Goulais SWS | ON_GLA_SWS | 230 | 2015 | 2035 | wind_onshore | wind | 25.3 | 21.14% | 5.3489 | 31.88% | 70.65
| Gracey | ON_GCY00_GEN | Gengrowth LP | Tilbury | 42.2718 | -82.4882 | Ontario.a | Ontario | Tilbury TS | ON_TLB_DSS | 115 | 2010 | 2030 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Grand Bend | ON_GBD00_GEN | Grand Bend Wind LP | Zurich | 43.3937 | -81.6578 | Ontario.a | Ontario | Zurich GS | ON_ZUR_DSS | 230 | 2016 | 2036 | wind_onshore | wind | 99.3 | 21.14% | 20.994 | 35.92% | 312.472
| Grand SF | ON_GRDS00_GEN | Grand Renewable Solar LP | Cayuga | 42.8883 | -79.819 | Ontario.a | Ontario | Grand GS | ON_GRD_GSS | 230 | 2015 | 2035 | solar | solar | 100 | 18.54% | 18.5448 | 17.52% | 153.452
| Grand Valley 1/2 | ON_GRV01_GEN | Grand Valley 1 LP | Dundalk | 44.0078 | -80.3556 | Ontario.a | Ontario | GV3 WF GS | ON_GV3_GSS | 230 | 2012 | 2032 | wind_onshore | wind | 19.8 | 21.14% | 4.1861 | 27% | 46.831
| Grand Valley 3 | ON_GRV03_GEN | Grand Valley 2 LP | Grand Valley | 43.9294 | -80.3437 | Ontario.a | Ontario | GV3 WF GS | ON_GV3_GSS | 230 | 2015 | 2035 | wind_onshore | wind | 40.1 | 21.14% | 8.478 | 36.88% | 129.55
| Grand WF | ON_GRDW00_GEN | Grand Renewable Wind LP | Cayuga | 42.8814 | -79.7879 | Ontario.a | Ontario | Grand GS | ON_GRD_GSS | 230 | 2014 | 2034 | wind_onshore | wind | 149 | 21.14% | 31.5016 | 24.41% | 318.587
| Great Northern Tri-Gen | ON_GNT00_GEN | Soave Hydroponics Company | Kingsville | 42.0644 | -82.6805 | Ontario.a | Ontario | Kingsville TS | ON_KSV_DSS | 115 | 2008 | 2028 | NG_CG | gasCC | 12 | 85.12% | 10.214 | 13% | 13.6656
| Green Electron | ON_GRN00_GEN | Greenfield South Power Corporation | Courtright | 42.7902 | -82.4273 | Ontario.a | Ontario | Greenfield Energy GS | ON_GRF_GSS | 230 | 2017 | 2037 | NG_CT | gasSC | 314 | 85.12% | 267.2661 | 12% | 330.0768
| Greenfield Energy Centre_01 | ON_GRF01_GEN | Greenfield Energy Centre LP | Courtright | 42.7701 | -82.4528 | Ontario.a | Ontario | Greenfield Energy GS | ON_GRF_GSS | 230 | 2008 | 2028 | NG_CT | gasSC | 180 | 85.12% | 153.2099 | 31.06% | 489.793
| Greenfield Energy Centre_02 | ON_GRF02_GEN | Greenfield Energy Centre LP | Courtright | 42.7701 | -82.4528 | Ontario.a | Ontario | Greenfield Energy GS | ON_GRF_GSS | 230 | 2008 | 2028 | NG_CT | gasSC | 180 | 85.12% | 153.2099 | 33.19% | 523.32
| Greenfield Energy Centre_03 | ON_GRF03_GEN | Greenfield Energy Centre LP | Courtright | 42.7701 | -82.4528 | Ontario.a | Ontario | Greenfield Energy GS | ON_GRF_GSS | 230 | 2008 | 2028 | NG_CT | gasSC | 180 | 85.12% | 153.2099 | 25.3% | 398.868
| Greenfield Energy Centre_04 | ON_GRF04_GEN | Greenfield Energy Centre LP | Courtright | 42.7701 | -82.4528 | Ontario.a | Ontario | Greenfield Energy GS | ON_GRF_GSS | 230 | 2008 | 2028 | NG_CT | gasSC | 505 | 85.12% | 429.8389 | 20.05% | 886.923
| Greenfield South_01 | ON_GRS01_GEN | Greenfield South Power Corporation | Sarnia | 42.7897 | -82.4414 | Ontario.a | Ontario | Greenfield Energy GS | ON_GRF_GSS | 230 | 2019 | 2039 | NG_CC | gasCC | 192 | 85.12% | 163.4239 | 13.75% | 231.327
| Greenfield South_02 | ON_GRS02_GEN | Greenfield South Power Corporation | Sarnia | 42.7897 | -82.4414 | Ontario.a | Ontario | Greenfield Energy GS | ON_GRF_GSS | 230 | 2019 | 2039 | NG_CC | gasCC | 133 | 85.12% | 113.2051 | 12.09% | 140.867
| Greenwich | ON_GRH00_GEN | Greenwich Wind Farm LP | Dorion | 48.7606 | -88.7667 | Ontario.b | Ontario | Greenwich WF GS | ON_GRH_GSS | 230 | 2011 | 2031 | wind_onshore | wind | 98.9 | 21.14% | 20.9095 | 26.76% | 231.88
| Grey Highlands | ON_GRD00_GEN | Grey Highlands Clean Energy Development LP | Singhampton | 44.3085 | -80.3138 | Ontario.a | Ontario | Stayner TS | ON_STY_DSS | 115 | 2016 | 2036 | wind_onshore | wind | 18.5 | 21.14% | 3.9113 | 27% | 43.7562
| Grey Highlands Zero Emission People | ON_GRZ00_GEN | Capstone Infrastructure Corp 50% | Singhampton | 44.314 | -80.289 | Ontario.a | Ontario | Stayner TS | ON_STY_DSS | 115 | 2016 | 2036 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Grimsby Bioreactor | ON_GRM00_GEN | Grimsby Energy Inc | Grimsby | 43.1474 | -79.5389 | Ontario.a | Ontario | Niagara West MTS | ON_NIW_DSS | 230 | 2015 | 2035 | biogas | biomass | 1 | 94.51% | 0.94512 | 20% | 1.752
| GS One | ON_GSN00_GEN | GS One - Parkway Solar Farm LP | Edwards | 45.3031 | -75.458 | Ontario.b | Ontario | Russell DS | ON_RSL_DSS | 115 | 2012 | 2032 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| GTAA Cogeneration_01 | ON_GTA01_GEN | Transalta | Mississauga | 43.6911 | -79.6105 | Ontario.a | Ontario | Richview TS | ON_RCV_DSS | 230 | 2006 | 2026 | NG_CG | gasCC | 47 | 85.12% | 40.0048 | 7.804% | 32.13
| GTAA Cogeneration_02 | ON_GTA02_GEN | Transalta | Mississauga | 43.6911 | -79.6105 | Ontario.a | Ontario | Richview TS | ON_RCV_DSS | 230 | 2006 | 2026 | NG_CG | gasCC | 47 | 85.12% | 40.0048 | 9.526% | 39.222
| GTAA Cogeneration_03 | ON_GTA03_GEN | Transalta | Mississauga | 43.6911 | -79.6105 | Ontario.a | Ontario | Richview TS | ON_RCV_DSS | 230 | 2006 | 2026 | NG_CG | gasCC | 23 | 85.12% | 19.5768 | 12.9% | 25.996
| Gunn's Hill | ON_GNH00_GEN | Gunn's Hill LP | Woodstock | 43.0858 | -80.7142 | Ontario.a | Ontario | Woodstock TS | ON_WDK_DSS | 115 | 2016 | 2036 | wind_onshore | wind | 18 | 21.14% | 3.8056 | 27% | 42.5736
| HAF Energy | ON_HAF00_GEN | Vineland Power Inc | Caistor Centre | 43.122 | -79.7108 | Ontario.a | Ontario | Vineland DS | ON_VNL_DSS | 115 | 2014 | 2034 | wind_onshore | wind | 9 | 21.14% | 1.9028 | 27% | 21.2868
| Hagues Reach | ON_HGR00_GEN | Ontario Power Generation Inc | Campbellford | 44.2752 | -77.7954 | Ontario.a | Ontario | Havelock TS | ON_HVL_DSS | 230 | 1925 | 2100 | hydro_run | hydro_run | 4 | 68.43% | 2.7372 | 65% | 22.776 | 3
| Halton Hills_01 | ON_HHL01_GEN | TransCanada Corp | Halton Hills | 43.5613 | -79.8447 | Ontario.a | Ontario | Halton Hills GS | ON_HHL_GSS | 230 | 2010 | 2030 | NG_CT | gasSC | 211 | 85.12% | 179.596 | 21.73% | 401.613
| Halton Hills_02 | ON_HHL02_GEN | TransCanada Corp | Halton Hills | 43.5613 | -79.8447 | Ontario.a | Ontario | Halton Hills GS | ON_HHL_GSS | 230 | 2010 | 2030 | NG_CT | gasSC | 211 | 85.12% | 179.596 | 21.61% | 399.481
| Halton Hills_03 | ON_HHL03_GEN | TransCanada Corp | Halton Hills | 43.5613 | -79.8447 | Ontario.a | Ontario | Halton Hills GS | ON_HHL_GSS | 230 | 2010 | 2030 | NG_CT | gasSC | 290 | 85.12% | 246.8382 | 16.79% | 426.423
| Halton Landfill | ON_HLF00_GEN | Oakville Hydro Energy Services Inc | Milton | 43.4759 | -79.82 | Ontario.a | Ontario | Palermo TS | ON_PAL_DSS | 230 | 2007 | 2027 | biogas | biomass | 2.1 | 94.51% | 1.9848 | 20% | 3.6792
| Hamilton Digester | ON_HDG00_GEN | Hamilton Renewable Power Inc | Hamilton | 43.2534 | -79.77 | Ontario.a | Ontario | Beach TS | ON_BCH_DSS | 115 | 2006 | 2026 | biogas | biomass | 1.6 | 94.51% | 1.5122 | 20% | 2.8032
| Hanna Chute | ON_HNC00_GEN | Ontario Power Generation Inc | Bracebridge | 45.0008 | -79.2977 | Ontario.b | Ontario | Bracebridge TS | ON_BRA_DSS | 230 | 1926 | 2100 | hydro_run | hydro_run | 1 | 68.43% | 0.68431 | 65% | 5.694 | 1
| Harmon_01 | ON_HRJ01_GEN | Ontario Power Generation Inc | Val Rita | 50.1112 | -82.2081 | Ontario.b | Ontario | Harmon GS | ON_HRJ_GSS | 230 | 2010 | 2060 | hydro_daily | hydro_daily | 156 | 68.43% | 106.7521 | 25.64% | 350.356 | 2
| Harmon_02 | ON_HRJ02_GEN | Ontario Power Generation Inc | Val Rita | 50.1112 | -82.2081 | Ontario.b | Ontario | Harmon GS | ON_HRJ_GSS | 230 | 2010 | 2060 | hydro_daily | hydro_daily | 78 | 68.43% | 53.376 | 27.77% | 189.73 | 1
| Harris | ON_HRS00_GEN | Brookfield Renewable Power Inc | Wawa | 47.9572 | -84.8303 | Ontario.b | Ontario | Harris GS | ON_HRS_GSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 12 | 68.43% | 8.2117 | 43.17% | 45.382
| Harrow | ON_HRR00_GEN | AIM Harrow Wind Farm LP | Harrow | 42.0323 | -82.9618 | Ontario.a | Ontario | Kingsville TS | ON_KSV_DSS | 115 | 2010 | 2030 | wind_onshore | wind | 39.6 | 21.14% | 8.3722 | 27% | 93.6619
| HCE Port Lands West | ON_HCE00_GEN | HCE Energy Inc | Hamilton | 43.2757 | -79.8521 | Ontario.a | Ontario | Birmingham TS | ON_BRM_DSS | 115 | 2000 | 2100 | NG_CG | gasCC | 1.98 | 85.12% | 1.6853 | 13% | 2.2548
| Healey Falls | ON_HLY00_GEN | Ontario Power Generation Inc | Campbellford | 44.373 | -77.7787 | Ontario.a | Ontario | Havelock TS | ON_HVL_DSS | 230 | 2010 | 2060 | hydro_run | hydro_run | 18 | 68.43% | 12.3175 | 65% | 102.492 | 3
| Henvey Inlet | ON_HVL00_GEN | Nigig Power Corporation | Henvey Inlet | 45.8518 | -80.62 | Ontario.a | Ontario | Parry Sound TS | ON_PRS_DSS | 230 | 2020 | 2040 | wind_onshore | wind | 300 | 21.14% | 63.4261 | 27% | 709.56
| Heywood | ON_HYW00_GEN | St. Catharines Hydro Generation Inc | St. Catharines | 43.199 | -79.2646 | Ontario.a | Ontario | Carlton TS | ON_CLT_DSS | 115 | 2010 | 2030 | hydro_run | hydro_run | 7.2 | 68.43% | 4.927 | 65% | 40.9968
| High Falls and Manitou Falls | ON_HFM00_GEN | Biigtigong Dbenjgan | Nairn Centre | 46.3792 | -81.5696 | Ontario.b | Ontario | Espanola TS | ON_ESP_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 6 | 68.43% | 4.1058 | 65% | 34.164
| High Falls BGL | ON_HFB00_GEN | Bracebridge Generation Ltd | Bracebridge | 45.0888 | 79.3027 | Ontario.b | Ontario | Bracebridge TS | ON_BRA_DSS | 230 | 2007 | 2027 | hydro_run | hydro_run | 2.6 | 68.43% | 1.7792 | 65% | 14.8044
| High Falls HFD | ON_HFH00_GEN | High Falls Development Partnership | Atitkokan | 48.4434 | -92.3562 | Ontario.b | Ontario | Mackenzie TS | ON_MKZ_TSS | 230 | 2000 | 2100 | hydro_run | hydro_run | 5.4 | 68.43% | 3.6953 | 65% | 30.7476
| High Falls OPG | ON_HFO00_GEN | Ontario Power Generation Inc | Perth | 44.9538 | -76.6087 | Ontario.b | Ontario | Sharbot DS | ON_SHR_DSS | 115 | 1920 | 2100 | hydro_run | hydro_run | 3 | 68.43% | 2.0529 | 65% | 17.082 | 3
| Hogg | ON_HOG00_GEN | Brookfield Renewable Power Inc | Batchawana Bay | 47.2134 | -84.6188 | Ontario.b | Ontario | Hogg GS | ON_HOG_GSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 18 | 68.43% | 12.3175 | 65% | 102.492
| Hollingsworth | ON_HGW00_GEN | Brookfield Renewable Power Inc | Wawa | 47.9605 | -84.504 | Ontario.b | Ontario | Hollingsworth TS | ON_HGW_DSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 23 | 68.43% | 15.7391 | 54.68% | 110.164
| Hound Chute | ON_HCT00_GEN | Ontario Power Generation / Umh Energy | Kenabeek | 47.3047 | -79.6966 | Ontario.b | Ontario | Dymond TS | ON_DYM_DSS | 230 | 2010 | 2060 | hydro_run | hydro_run | 9 | 68.43% | 6.1588 | 65% | 51.246 | 2
| HPG Site A | ON_HPG00_GEN | Potentia Solar 14 LP | Newtonville | 43.9294 | -78.5454 | Ontario.a | Ontario | Port Hope TS | ON_PTH_DSS | 115 | 2016 | 2036 | solar | solar | 2 | 18.54% | 0.3709 | 18% | 3.1536
| Hull_01 | ON_HLL01_GEN | Energy Ottawa Inc | Ottawa | 45.4235 | -75.7207 | Ontario.b | Ontario | King Edward TS | ON_KNE_DSS | 115 | 2007 | 2027 | hydro_run | hydro_run | 12 | 68.43% | 8.2117 | 65% | 68.328 | [20 empty] | http://portagepower.com/hydroelectric/chaudiere-falls/
| Hull_02 | ON_HLL02_GEN | Energy Ottawa Inc | Ottawa | 45.4217 | -75.7197 | Ontario.b | Ontario | King Edward TS | ON_KNE_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 27 | 68.43% | 18.4763 | 65% | 153.738 | [20 empty] | http://portagepower.com/hydroelectric/chaudiere-falls/
| Humber Treatment Plant | ON_HTP00_GEN | City of Toronto | Toronto | 43.6333 | -79.4806 | Ontario.a | Ontario | Manby TS | ON_MBY_DSS | 115 | 2000 | 2100 | biogas | biomass | 4.7 | 94.51% | 4.4421 | 20% | 8.2344
| Huron | ON_HRN00_GEN | Huron Wind | Tiverton | 44.3115 | -81.5463 | Ontario.a | Ontario | Bruce A TS | ON_BCA_TSS | 230 | 2008 | 2028 | wind_onshore | wind | 9 | 21.14% | 1.9028 | 27% | 21.2868
| Illumination | ON_ILL00_GEN | Illumination LP | Port Perry | 44.0636 | -78.8664 | Ontario.a | Ontario | Wilson TS | ON_WLS_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Index Energy Mills Road Corp | ON_IEM00_GEN | Index Energy Mills Road Corp | Ajax | 43.8474 | -79.0249 | Ontario.a | Ontario | Whitby TS | ON_WHB_DSS | 230 | 2015 | 2035 | MSW | biomass | 17.8 | 94.51% | 16.8232 | 20% | 31.1856 | [20 empty] | https://www.indexenergy.ca/facility-1#facility
| Ingersoll 1 | ON_ING00_GEN | Fiera Solar Ingersoll 1 LP | Ingersoll | 43.088 | -80.8462 | Ontario.a | Ontario | Ingersoll TS | ON_ING_DSS | 230 | 2014 | 2034 | solar | solar | 9.5 | 18.54% | 1.7618 | 18% | 14.9796
| Iroquois Falls Gas | ON_IQG00_GEN | Iroquois Falls Power Corp | Iroquois Falls | 48.7692 | -80.6666 | Ontario.b | Ontario | Iroquois Falls DS | ON_IQF_DSS | 115 | 2017 | 2022 | NG_CC | gasCC | 131 | 85.12% | 111.5028 | 0.9612% | 11.03 | [20 empty] | https://www.northlandpower.com/What-We-Do/Operating-Assets/Thermal/Iroquois_Falls.aspx
| Iroquois Falls Hydro | ON_IQH00_GEN | H2O Power LP | Iroquois Falls | 48.7638 | -80.6688 | Ontario.b | Ontario | Iroquois Falls DS | ON_IQF_DSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 29.7 | 68.43% | 20.324 | 58.01% | 150.9257 | [20 empty] | http://www.h2opower.com/our-locations/
| Island Falls | ON_ISF00_GEN | H2O Power LP | Iroquois Falls | 49.5772 | -81.3821 | Ontario.b | Ontario | Island Falls GS | ON_ISF_GSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 44.3 | 68.43% | 30.3149 | 58.01% | 225.1182 | [20 empty] | http://www.h2opower.com/our-locations/
| Jericho | ON_JCO00_GEN | Jericho Wind LP | Thedford | 43.1333 | -81.8938 | Ontario.a | Ontario | Evergreen SWS | ON_EVG_SWS | 500 | 2014 | 2034 | wind_onshore | wind | 149 | 21.14% | 31.5016 | 27.07% | 353.277
| Jones Falls | ON_JFS00_GEN | Fortis Generation East LP | Elgin | 44.5476 | -76.2367 | Ontario.a | Ontario | Crosby TS | ON_CRO_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 2.4 | 68.43% | 1.6423 | 65% | 13.6656
| K2 | ON_K2W00_GEN | K2 Wind Ontario LP | Dungannon | 43.9373 | -81.6399 | Ontario.a | Ontario | K2 Wind GS | ON_K2W_GSS | 500 | 2015 | 2035 | wind_onshore | wind | 270 | 21.14% | 57.0835 | 28.17% | 666.328
| Kakabeka | ON_KKB00_GEN | Ontario Power Generation Inc | Thunder Bay | 48.3975 | -89.6165 | Ontario.b | Ontario | Murillo DS | ON_MRL_DSS | 115 | 1906 | 2100 | hydro_run | hydro_run | 25 | 68.43% | 17.1077 | 59.33% | 129.933 | 4
| Kap | ON_KAP00_GEN | New Ospvf 7 LP | Kapuskasing | 49.375 | -82.3928 | Ontario.b | Ontario | Kapuskasing TS | ON_KAP_DSS | 115 | 2014 | 2034 | solar | solar | 6 | 18.54% | 1.1127 | 18% | 9.4608
| Kapuskasing | ON_KPK00_GEN | Hydromega | Kapuskasing | 49.4131 | -82.4299 | Ontario.b | Ontario | Kapuskasing TS | ON_KAP_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 2.8 | 68.43% | 1.9161 | 65% | 15.9432
| Kenora | ON_KNR00_GEN | H2O Power LP | Kenora | 49.7725 | -94.5035 | Ontario.b | Ontario | Rabbit Lake SWS | ON_RBL_SWS | 115 | 2009 | 2029 | hydro_run | hydro_run | 14 | 68.43% | 9.5803 | 71.37% | 87.53 | [20 empty] | http://www.h2opower.com/our-locations/
| Kent Breeze | ON_KNT00_GEN | TransAlta | Thamesville | 42.5452 | -82.0506 | Ontario.a | Ontario | Kent TS | ON_KNT_DSS | 115 | 2011 | 2031 | wind_onshore | wind | 20 | 21.14% | 4.2284 | 27% | 47.304
| Kingsbridge 1 | ON_KNG00_GEN | CP Renewable Energy (Kingsbridge) LP | Goderich | 43.8589 | -81.692 | Ontario.a | Ontario | Goderich TS | ON_GOD_DSS | 115 | 2006 | 2026 | wind_onshore | wind | 39.6 | 21.14% | 8.3722 | 29.82% | 103.436
| Kingston Mills | ON_KNM00_GEN | Fortis Generation East LP | Glenburnie | 44.2934 | -76.4405 | Ontario.a | Ontario | Gardiner TS | ON_GAR_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 1.9 | 68.43% | 1.3002 | 65% | 10.8186
| Kingston Solar | ON_KSS00_GEN | Kingston Solar LP | Odessa | 44.3118 | -76.6511 | Ontario.a | Ontario | Kingston Solar GS | ON_KSS_GSS | 230 | 2015 | 2035 | solar | solar | 100 | 18.54% | 18.5448 | 18% | 157.68
| Kipling_01 | ON_KPG01_GEN | Ontario Power Generation Inc | Val Rita | 50.1449 | -82.2086 | Ontario.b | Ontario | Kipling GS | ON_KPG_GSS | 230 | 2010 | 2060 | hydro_daily | hydro_daily | 166 | 68.43% | 113.5952 | 22.82% | 331.843 | 3
| Kipling_02 | ON_KPG02_GEN | Ontario Power Generation Inc | Val Rita | 50.1449 | -82.2086 | Ontario.b | Ontario | Kipling 2 GS | ON_KPG2_GSS | 230 | 2010 | 2060 | hydro_daily | hydro_daily | 79 | 68.43% | 54.0604 | 22.58% | 156.239 | 3
| Kirkland Lake_01 | ON_KLL01_GEN | Northland Power | Kirkland Lake | 48.135 | -80.0405 | Ontario.b | Ontario | Kirkland Lake TS | ON_KLL_DSS | 115 | 2015 | 2035 | NG_CC | gasCC | 122 | 85.12% | 103.8423 | 52.57% | 561.839
| Kirkland Lake_02 | ON_KLL02_GEN | Northland Power | Kirkland Lake | 48.135 | -80.0405 | Ontario.b | Ontario | Kirkland Lake TS | ON_KLL_DSS | 115 | 2015 | 2035 | NG_CT | gasSC | 34 | 85.12% | 28.9396 | 1.884% | 5.61
| Lac Seul | ON_LCS00_GEN | Ontario Power Generation Inc | Ear Falls | 50.6307 | -93.2206 | Ontario.b | Ontario | Ear Falls TS | ON_EAF_DSS | 115 | 2009 | 2059 | hydro_run | hydro_run | 12 | 68.43% | 8.2117 | 65% | 68.328 | 1 | [19 empty] | https://www.power-technology.com/projects/lac-seul-plant/
| Lafleche | ON_LFC00_GEN | Moose Creek Energy LP | Moose Creek | 45.3044 | -74.9928 | Ontario.b | Ontario | St. Isidore TS | ON_STI_DSS | 230 | 2013 | 2033 | biogas | biomass | 4.2 | 94.51% | 3.9695 | 20% | 7.3584
| Lake Superior | ON_LSU00_GEN | St. Mary's Paper Company | Sault Ste. Marie | 46.5158 | -84.3689 | Ontario.b | Ontario | St. Marys MTS | ON_STM_DSS | 115 | 2000 | 2100 | NG_CG | gasCC | 110 | 85.12% | 93.6283 | 13% | 125.268
| Lakefield | ON_LKF00_GEN | Ontario Power Generation Inc | Lakefield | 44.421 | -78.2722 | Ontario.a | Ontario | Otonabee TS | ON_OTB_DSS | 230 | 1928 | 2100 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388 | 1
| Landon | ON_LND00_GEN | Suncor Adelaide Wind LP | Strathroy | 43.0184 | -81.7392 | Ontario.a | Ontario | Landon GS | ON_LND_GSS | 115 | 2015 | 2035 | wind_onshore | wind | 40 | 21.14% | 8.4568 | 29.87% | 104.65
| Lennox_01 | ON_LEN01_GEN | Ontario Power Generation Inc | Stella | 44.1442 | -76.848 | Ontario.a | Ontario | Lennox TS | ON_LEN_TSS | 230 | 2013 | 2023 | NG_CT | gasSC | 525 | 85.12% | 446.8622 | 0.3043% | 13.996 | 4
| Lennox_02 | ON_LEN02_GEN | Ontario Power Generation Inc | Stella | 44.1442 | -76.848 | Ontario.a | Ontario | Lennox TS | ON_LEN_TSS | 230 | 2013 | 2023 | NG_CT | gasSC | 525 | 85.12% | 446.8622 | 0.4498% | 20.685 | 4
| Lennox_03 | ON_LEN03_GEN | Ontario Power Generation Inc | Stella | 44.1442 | -76.848 | Ontario.a | Ontario | Lennox TS | ON_LEN_TSS | 230 | 2013 | 2023 | NG_CT | gasSC | 525 | 85.12% | 446.8622 | 0.4019% | 18.484 | 4
| Lennox_04 | ON_LEN04_GEN | Ontario Power Generation Inc | Stella | 44.1442 | -76.848 | Ontario.a | Ontario | Lennox TS | ON_LEN_TSS | 230 | 2013 | 2023 | NG_CT | gasSC | 525 | 85.12% | 446.8622 | 0.174% | 8.004 | 4
| Liberty Energy Centre | ON_LEC00_GEN | Liberty Energy Inc | Hamilton | 43.2608 | -79.792 | Ontario.a | Ontario | Kenilworth TS | ON_KNL_DSS | 115 | 2000 | 2100 | biomass | biomass | 11.4 | 94.51% | 10.7744 | 20% | 19.9728
| Lily Lake | ON_LLK00_GEN | Peterborough Utilities Inc | Peterborough | 44.3136 | -78.3926 | Ontario.a | Ontario | Dobbin TS | ON_DOB_DSS | 230 | 2011 | 2031 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Liskeard 1 | ON_LSK01_GEN | TransCanada Energy Ltd | New Liskeard | 47.5126 | -79.708 | Ontario.b | Ontario | Dymond TS | ON_DYM_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Liskeard 3 | ON_LSK03_GEN | TransCanada Energy Ltd | New Liskeard | 47.49 | -79.7115 | Ontario.b | Ontario | Dymond TS | ON_DYM_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Liskeard 4 | ON_LSK04_GEN | TransCanada Energy Ltd | New Liskeard | 47.5049 | -79.7115 | Ontario.b | Ontario | Dymond TS | ON_DYM_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Little Creek | ON_LTC00_GEN | Bluearth Renewables Inc | Napanee | 44.2044 | -76.9251 | Ontario.a | Ontario | Napanee TS | ON_NAP_DSS | 115 | 2014 | 2034 | solar | solar | 8.5 | 18.54% | 1.5763 | 18% | 13.4028
| Little Long_01 | ON_LLG01_GEN | Ontario Power Generation Inc | Kapuskasing | 50.0036 | -82.1649 | Ontario.b | Ontario | Little Long SWS | ON_LLG_SWS | 230 | 2010 | 2060 | hydro_daily | hydro_daily | 144 | 68.43% | 98.5404 | 15.83% | 199.71 | 2
| Little Long_02 | ON_LLG02_GEN | Ontario Power Generation Inc | Kapuskasing | 50.0036 | -82.1649 | Ontario.b | Ontario | Little Long SWS | ON_LLG_SWS | 230 | 2010 | 2060 | hydro_daily | hydro_daily | 75 | 68.43% | 51.3231 | 29.53% | 194.017 | 2
| London Biogas | ON_LBG00_GEN | StormFisher Environmental Ltd | London | 42.9214 | -81.1921 | Ontario.a | Ontario | Buchanan TS | ON_BUC_DSS | 115 | 2011 | 2031 | biogas | biomass | 2.85 | 94.51% | 2.6936 | 20% | 4.9932
| London District Energy | ON_LDT00_GEN | London District Energy LP | London | 42.983 | -81.2382 | Ontario.a | Ontario | Talbot TS | ON_TBT_DSS | 115 | 2000 | 2100 | NG_CG | gasCC | 17.9 | 85.12% | 15.2359 | 13% | 20.3845
| London Street | ON_LDS01_GEN | Peterborough Utilities Inc | Peterborough | 44.3114 | -78.3143 | Ontario.a | Ontario | Otonabee TS | ON_OTB_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 4.1 | 68.43% | 2.8057 | 65% | 23.3454
| London Street Expansion | ON_LDX02_GEN | Peterborough Utilities Inc | Peterborough | 44.3114 | -78.3143 | Ontario.a | Ontario | Otonabee TS | ON_OTB_DSS | 230 | 2016 | 2036 | hydro_run | hydro_run | 5.9 | 68.43% | 4.0374 | 65% | 33.5946
| Long Sault Rapids | ON_LSR00_GEN | Algonquin Power | Cochrane | 49.2136 | -81.0204 | Ontario.b | Ontario | Cochrane West DS | ON_CCW_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 20 | 68.43% | 13.6862 | 56.3% | 98.63
| Longlac | ON_LLC00_GEN | Kenogami Industries | Longlac | 49.7678 | -86.5421 | Ontario.b | Ontario | Longlac TS | ON_LLC_DSS | 115 | 2000 | 2100 | biomass | biomass | 25 | 94.51% | 23.628 | 20% | 43.8
| Longueil TS Malbouef | ON_LGU00_GEN | Sune Alfred LP | Alfred | 45.574 | -74.8192 | Ontario.b | Ontario | Longueuil TS | ON_LGU_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Lower Notch | ON_LWN00_GEN | Ontario Power Generation Inc | North Cobalt | 47.1389 | -79.4541 | Ontario.b | Ontario | Lower Notch GS | ON_LWN_GSS | 230 | 1971 | 2100 | hydro_daily | hydro_daily | 274 | 68.43% | 187.5005 | 13.55% | 325.151 | 2
| Lower Sturgeon | ON_LWS00_GEN | Ontario Power Generation / Umh Energy | Timmins | 48.8132 | -81.4875 | Ontario.b | Ontario | Timmins TS | ON_TMM_DSS | 115 | 2010 | 2060 | hydro_run | hydro_run | 14 | 68.43% | 9.5803 | 65% | 79.716 | 2
| Loyalist | ON_LYL00_GEN | Loyalist Solar LP | Centreville | 44.4084 | -76.9154 | Ontario.a | Ontario | Napanee TS | ON_NAP_DSS | 115 | 2019 | 2039 | solar | solar | 54 | 18.54% | 10.0142 | 18% | 85.1472
| Lunarlight | ON_LNR00_GEN | Lunarlight LP | Stirling | 44.3145 | -77.432 | Ontario.a | Ontario | Belleville TS | ON_BLV_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| MacKay | ON_MKY00_GEN | Brookfield Renewable Power Inc | Batchawana Bay | 47.2688 | -84.4364 | Ontario.b | Ontario | Mackay TS | ON_MKY_DSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 62 | 68.43% | 42.4271 | 46.4% | 251.996
| Manitou Falls | ON_MNF00_GEN | Ontario Power Generation Inc | Ear Falls | 50.5837 | -93.4554 | Ontario.b | Ontario | Manitou Falls GS | ON_MNF_GSS | 115 | 1956 | 2100 | hydro_run | hydro_run | 88 | 68.43% | 60.2191 | 32.05% | 247.067 | 5
| Marmora | ON_MRM00_GEN | Shaman Power Corp | Marmora | 44.4851 | -77.6876 | Ontario.a | Ontario | Havelock TS | ON_HVL_DSS | 230 | 2013 | 2033 | hydro_run | hydro_run | 1 | 68.43% | 0.68431 | 65% | 5.694
| Matabitchuan | ON_MTB00_GEN | Ontario Power Generation Inc | New Liskeard | 47.1233 | -79.4946 | Ontario.b | Ontario | Temagami DS | ON_TMG_DSS | 115 | 1910 | 2100 | hydro_run | hydro_run | 10 | 68.43% | 6.8431 | 65% | 56.94 | 4
| Mattawishkwia | ON_MTT00_GEN | New Ospvf 10 LP | Hearst | 49.6807 | -83.6816 | Ontario.b | Ontario | Hearst TS | ON_HST_DSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Matthias | ON_MTH00_GEN | Orillia Power Generation Corp | Bracebridge | 44.9934 | -79.2019 | Ontario.b | Ontario | Bracebridge TS | ON_BRA_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 3 | 68.43% | 2.0529 | 65% | 17.082
| McKenzie Falls | ON_MKZ00_GEN | Capstone Infrastructure Corp | Eagle River | 49.8047 | -93.1887 | Ontario.b | Ontario | Eton DS | ON_ETO_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 1.1 | 68.43% | 0.75274 | 65% | 6.2634
| McLeans Mountain | ON_MCL00_GEN | McLean's Mountain Wind LP | Little Current | 45.9355 | -81.9835 | Ontario.b | Ontario | McLeans Mountain GS | ON_MCL_GSS | 115 | 2014 | 2034 | wind_onshore | wind | 60 | 21.14% | 12.6852 | 28.65% | 150.564
| McPhail | ON_MCP00_GEN | Brookfield Renewable Power Inc | Wawa | 47.9054 | -84.6705 | Ontario.b | Ontario | DA Watson TS | ON_DAW_DSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 13 | 68.43% | 8.896 | 30.07% | 34.24
| McVittie | ON_MCV00_GEN | Ontario Power Generation Inc | Sudbury | 46.2846 | -80.8484 | Ontario.b | Ontario | Martindale TS | ON_MTD_DSS | 115 | 1912 | 2100 | hydro_run | hydro_run | 3 | 68.43% | 2.0529 | 65% | 17.082 | 2
| Merrick Landfill | ON_MLF00_GEN | North Bay Hydro Services Inc | North Bay | 46.5158 | -79.4932 | Ontario.b | Ontario | North Bay TS | ON_NBY_DSS | 115 | 2012 | 2032 | biogas | biomass | 1.6 | 94.51% | 1.5122 | 20% | 2.8032
| Merrickville | ON_MRK00_GEN | Ontario Power Generation Inc | Smiths Falls | 44.9178 | -75.8373 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 1915 | 2100 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388 | 2
| Meyersburg | ON_MYB00_GEN | Ontario Power Generation Inc | Campbellford | 44.2482 | -77.8019 | Ontario.a | Ontario | Havelock TS | ON_HVL_DSS | 230 | 1924 | 2100 | hydro_run | hydro_run | 5 | 68.43% | 3.4215 | 65% | 28.47 | 2
| Midhurst 2 | ON_MDH02_GEN | Met Fiera Solar Midhurst 2 LP | Phelpston | 44.5392 | -79.765 | Ontario.a | Ontario | Midhurst TS | ON_MDH_DSS | 230 | 2013 | 2033 | solar | solar | 3.5 | 18.54% | 0.64907 | 18% | 5.5188
| Midhurst 3 | ON_MDH03_GEN | Met Fiera Solar Midhurst 3 LP | Oro Station | 44.4724 | -79.5693 | Ontario.a | Ontario | Midhurst TS | ON_MDH_DSS | 230 | 2013 | 2033 | solar | solar | 3.5 | 18.54% | 0.64907 | 18% | 5.5188
| Midhurst 4 | ON_MDH04_GEN | Met Fiera Solar Midhurst 4 LP | Oro | 44.4696 | -79.5615 | Ontario.a | Ontario | Midhurst TS | ON_MDH_DSS | 230 | 2014 | 2034 | solar | solar | 6.5 | 18.54% | 1.2054 | 18% | 10.2492
| Midhurst 6 | ON_MDH06_GEN | Met Fiera Solar Midhurst 6 LP | Midhurst | 44.4762 | -79.7194 | Ontario.a | Ontario | Midhurst TS | ON_MDH_DSS | 230 | 2013 | 2033 | solar | solar | 8.5 | 18.54% | 1.5763 | 18% | 13.4028
| Mighty Solar | ON_MTY00_GEN | Concord Mighty Solar Partnership | Chesterville | 45.1276 | -75.2581 | Ontario.b | Ontario | Chesterville TS | ON_CHS_DSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Minden | ON_MND00_GEN | Orillia Power Generation Corp | Minden | 44.941 | -78.7083 | Ontario.b | Ontario | Minden TS | ON_MND_DSS | 230 | 1935 | 2031 | hydro_run | hydro_run | 4 | 68.43% | 2.7372 | 65% | 22.776 | [20 empty] | https://www.orilliapower.ca/about/history/
| Misema | ON_MSM00_GEN | TransAlta | Englehart | 47.8996 | -79.8759 | Ontario.b | Ontario | Kirkland Lake TS | ON_KLL_DSS | 115 | 2007 | 2027 | hydro_run | hydro_run | 3 | 68.43% | 2.0529 | 65% | 17.082
| Mission | ON_MSF00_GEN | Brookfield Renewable Power Inc | Wawa | 47.9384 | -84.8373 | Ontario.b | Ontario | Mission Falls GS | ON_MSF_GSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 15 | 68.43% | 10.2646 | 36.33% | 47.742
| Mississippi Mills | ON_MSS00_GEN | TransCanada Energy Ltd | Pakenham | 45.3092 | -76.2435 | Ontario.b | Ontario | Almonte TS | ON_ALM_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Mohawk Point | ON_MHP00_GEN | AIM SOP Phase I LP | Lowbanks | 42.8514 | -79.4903 | Ontario.a | Ontario | Dunnville TS | ON_DNV_DSS | 115 | 2008 | 2028 | wind_onshore | wind | 9.9 | 21.14% | 2.0931 | 27% | 23.4155
| Mohawk Street | ON_MHS00_GEN | The Corporation of the City of Brantford | Brantford | 43.1265 | -80.2288 | Ontario.a | Ontario | Brantford TS | ON_BRF_DSS | 230 | 2010 | 2030 | biogas | biomass | 5.4 | 94.51% | 5.1037 | 20% | 9.4608
| Moose Rapids | ON_MRP00_GEN | Canadian Hydro Developers Inc | Sudbury | 46.6292 | -80.6646 | Ontario.b | Ontario | Martindale TS | ON_MTD_DSS | 115 | 2011 | 2031 | hydro_run | hydro_run | 1.4 | 68.43% | 0.95803 | 65% | 7.9716
| Morley | ON_MRL00_GEN | Rainy River First Nations Solar 1 LP | Stratton | 48.7069 | -94.2503 | Ontario.b | Ontario | Barwick TS | ON_BWK_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Mother Earth | ON_MTE00_GEN | Mere General Partner Inc | M’Chigeeng | 45.8185 | -82.1428 | Ontario.b | Ontario | Manitoulin TS | ON_MNT_DSS | 115 | 2012 | 2032 | wind_onshore | wind | 4 | 21.14% | 0.84568 | 27% | 9.4608
| Mountain Chute | ON_MTC00_GEN | Ontario Power Generation Inc | Renfrew | 45.1957 | -76.9074 | Ontario.b | Ontario | Mountain Chute GS | ON_MTC_GSS | 230 | 1967 | 2100 | hydro_daily | hydro_daily | 173 | 68.43% | 118.3853 | 20.18% | 305.854 | 2
| Nagagami | ON_NAG00_GEN | Brookfield Renewable Power Inc | Hornepayne | 49.8087 | -84.499 | Ontario.b | Ontario | Nagagami GS | ON_NAG_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 18 | 68.43% | 12.3175 | 31.76% | 50.085
| Nairn | ON_NRN00_GEN | Vale Canada Limited | Nairn Centre | 46.344 | -81.5734 | Ontario.b | Ontario | Espanola TS | ON_ESP_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 4.5 | 68.43% | 3.0794 | 65% | 25.623
| Namewaminikan | ON_NMK00_GEN | Namewaminikan Hydro Inc | Beardmore | 49.6826 | -88.0049 | Ontario.b | Ontario | Namewaminikan GS | ON_NAM_GSS | 115 | 2017 | 2057 | hydro_run | hydro_run | 10 | 68.43% | 6.8431 | 65% | 56.94
| Nanticoke | ON_NTK00_GEN | Ontario Power Generation Inc | Nanticoke | 42.8037 | -80.0461 | Ontario.a | Ontario | Nanticoke TS | ON_NTK_TSS | 230 | 2019 | 2039 | solar | solar | 44 | 18.54% | 8.1597 | 18% | 69.3792
| Napanee TS Taylor Kidd | ON_NAK00_GEN | Sune Taylor Kidd LP | Kingston | 44.2175 | -76.7082 | Ontario.a | Ontario | Napanee TS | ON_NAP_DSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Napanee_01 | ON_NAP01_GEN | TransCanada Energy Ltd | Stella | 44.1481 | -76.8413 | Ontario.a | Ontario | Napanee GS | ON_NAP_GSS | 230 | 2000 | 2100 | NG_CT | gasSC | 260 | 85.12% | 221.3032 | 12% | 273.312
| Napanee_02 | ON_NAP02_GEN | TransCanada Energy Ltd | Stella | 44.1481 | -76.8413 | Ontario.a | Ontario | Napanee GS | ON_NAP_GSS | 230 | 2000 | 2100 | NG_CT | gasSC | 260 | 85.12% | 221.3032 | 12% | 273.312
| Napanee_03 | ON_NAP03_GEN | TransCanada Energy Ltd | Stella | 44.1481 | -76.8413 | Ontario.a | Ontario | Napanee GS | ON_NAP_GSS | 230 | 2000 | 2100 | NG_CT | gasSC | 458 | 85.12% | 389.834 | 12% | 481.4496
| Napier | ON_NPR00_GEN | WPD Napier Wind Inc | Kerwood | 42.9564 | -81.7328 | Ontario.a | Ontario | Strathroy TS | ON_SRY_DSS | 115 | 2015 | 2035 | wind_onshore | wind | 4.1 | 21.14% | 0.86682 | 27% | 9.6973
| Nation Rise | ON_NTR00_GEN | Nation Rise Wind Farm Limited Partnership | Crysler | 45.2195 | -75.1629 | Ontario.b | Ontario | Chesterville TS | ON_CHS_DSS | 115 | 2021 | 2041 | wind_onshore | wind | 100 | 21.14% | 21.142 | 27% | 236.52
| Naylor | ON_NYL00_GEN | Naylor Wind Farm Limited Partnership | Essex | 42.1941 | -82.8105 | Ontario.a | Ontario | Malden TS | ON_MLD_DSS | 230 | 2010 | 2030 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Neven Produce | ON_NVP00_GEN | Neven Produce Inc | Lynden | 43.237 | -80.0961 | Ontario.a | Ontario | Powerline MTS | ON_PWL_DSS | 115 | 2017 | 2037 | NG_CG | gasCC | 3.233 | 85.12% | 2.7518 | 13% | 3.6817
| Nipigon | ON_NIP00_GEN | Atlantic Power Limited Partnership | Nipigon | 49.2946 | -88.0999 | Ontario.b | Ontario | AP Nipigon GS | ON_APN_GSS | 115 | 2018 | 2022 | NG_CT | gasSC | 23 | 85.12% | 19.5768 | 0.07544% | 0.152
| Nipissing | ON_NPS00_GEN | Ontario Power Generation Inc | Nipissing | 46.0967 | -79.4796 | Ontario.b | Ontario | Trout Lake TS | ON_TRL_DSS | 230 | 1909 | 2100 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388 | 2
| Norfolk Bloomsburg | ON_NOR00_GEN | Sune Norfolk Bloomsburg LP | Simcoe | 42.8745 | -80.2972 | Ontario.a | Ontario | Norfolk TS | ON_NOR_DSS | 115 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Norman | ON_NRM01_GEN | H2O Power LP | Kenora | 49.7717 | -94.5243 | Ontario.b | Ontario | Rabbit Lake SWS | ON_RBL_SWS | 115 | 2009 | 2029 | hydro_run | hydro_run | 9.5 | 68.43% | 6.5009 | 65% | 54.093 | [20 empty] | http://www.h2opower.com/our-locations/
| Norman Expansion | ON_NRX02_GEN | H2O Power LP | Kenora | 49.7717 | -94.5243 | Ontario.b | Ontario | Rabbit Lake SWS | ON_RBL_SWS | 115 | 2017 | 2029 | hydro_run | hydro_run | 2.726 | 68.43% | 1.8654 | 65% | 15.5218
| North Bala | ON_NBA00_GEN | Swift River LP | Bala | 45.0121 | -79.6127 | Ontario.b | Ontario | Muskoka TS | ON_MSK_DSS | 230 | 2020 | 2100 | hydro_run | hydro_run | 5 | 68.43% | 3.4215 | 65% | 28.47
| North Kent | ON_NOK00_GEN | North Kent Wind 1 LP | Dresden | 42.5613 | -82.2203 | Ontario.a | Ontario | North Kent 1 GS | ON_NOK_GSS | 115 | 2018 | 2038 | wind_onshore | wind | 99.12 | 21.14% | 20.956 | 22.71% | 197.186
| North Maiden | ON_MLD00_GEN | Gengrowth LP | Essex | 42.1538 | -82.8478 | Ontario.a | Ontario | Malden TS | ON_MLD_DSS | 230 | 2011 | 2031 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Northland Power Abitibi | ON_NPAB00_GEN | Northland Power Solar Abitibi LP | Cochrane | 49.1444 | -80.9717 | Ontario.b | Ontario | Cochrane West DS | ON_CCW_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Belleville North | ON_NPBN00_GEN | Northland Power Solar Belleville North LP | Ameliasburgh | 44.059 | -77.3315 | Ontario.a | Ontario | Picton TS | ON_PCT_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Belleville South | ON_NPBS00_GEN | Northland Power Solar Belleville South LP | Ameliasburgh | 44.066 | -77.3151 | Ontario.a | Ontario | Picton TS | ON_PCT_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Burks Falls East | ON_NPBE00_GEN | Northland Power Solar Burks Falls East LP | Burks Falls | 45.612 | -79.3572 | Ontario.b | Ontario | Muskoka TS | ON_MSK_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Burks Falls West | ON_NPBW00_GEN | Northland Power Solar Burks Falls West LP | Burks Falls | 45.6081 | -79.4262 | Ontario.b | Ontario | Muskoka TS | ON_MSK_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Crosby | ON_NPCR00_GEN | Northland Power Solar Crosby LP | Portland | 44.6707 | -76.3044 | Ontario.a | Ontario | Newboro DS | ON_NBO_DSS | 115 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Empire | ON_NPEM00_GEN | Northland Power Solar Empire LP | Cochrane | 49.1258 | -80.9915 | Ontario.b | Ontario | Cochrane West DS | ON_CCW_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Glendale | ON_NPGL00_GEN | Northland Power Solar Glendale LP | Cornwall | 45.0965 | -74.7167 | Ontario.b | Ontario | St. Lawrence TS | ON_STL_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Long Lake | ON_NPLL00_GEN | Northland Power Solar Long Lake LP | Hunta | 49.1402 | -81.2854 | Ontario.b | Ontario | Cochrane West DS | ON_CCW_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Martin's Meadows | ON_NPMM00_GEN | Northland Power Solar Martin's Meadows LP | Cochrane | 49.1433 | -80.9888 | Ontario.b | Ontario | Cochrane West DS | ON_CCW_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power McCann | ON_NPCMC00_GEN | Northland Power Solar Mccann LP | Westport | 44.6824 | -76.2727 | Ontario.a | Ontario | Newboro DS | ON_NBO_DSS | 115 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power North Burgess | ON_NPNB00_GEN | Northland Power Solar North Burgess LP | Perth | 44.8206 | -76.307 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Northland Power Rideau Lakes | ON_NPRL00_GEN | Northland Power Solar Rideau Lakes LP | Portland | 44.6692 | -76.274 | Ontario.a | Ontario | Newboro DS | ON_NBO_DSS | 115 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18.38% | 16.1
| Okikendawt | ON_OKK00_GEN | Okikendawt Hydro LP | Monetville | 46.1238 | -80.0145 | Ontario.b | Ontario | Martindale TS | ON_MTD_DSS | 115 | 2015 | 2055 | hydro_run | hydro_run | 10 | 68.43% | 6.8431 | 65% | 56.94
| Old Woman Falls | ON_OWF00_GEN | Nipiy-Owf Hydrokap LP | Kapuskasing | 49.1651 | -82.7136 | Ontario.b | Ontario | Kapuskasing TS | ON_KAP_DSS | 115 | 2013 | 2053 | hydro_run | hydro_run | 5.5 | 68.43% | 3.7637 | 65% | 31.317
| OPG 7 Gomberg | ON_O7G00_GEN | Ontario Power Generation Inc | Pickering | 43.8123 | -79.074 | Ontario.a | Ontario | Cherrywood TS | ON_CHW_DSS | 230 | 2001 | 2021 | wind_onshore | wind | 1.8 | 21.14% | 0.38056 | 27% | 4.2574
| Orillia 1 | ON_ORI01_GEN | Met Fiera Solar Orillia 1 LP | Hawkestone | 44.5825 | -79.4981 | Ontario.a | Ontario | Orillia TS | ON_ORI_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Orillia 2 | ON_ORI02_GEN | Met Fiera Solar Orillia 2 LP | Hawkestone | 44.5809 | -79.4984 | Ontario.a | Ontario | Orillia TS | ON_ORI_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Orillia 3 | ON_ORI03_GEN | Fiera Solar Orillia 3 LP | Hawkestone | 44.586 | -79.4995 | Ontario.a | Ontario | Orillia TS | ON_ORI_DSS | 230 | 2014 | 2034 | solar | solar | 6.5 | 18.54% | 1.2054 | 18% | 10.2492
| Ottawa Health Sciences Centre | ON_OHS00_GEN | TransAlta | Ottawa | 45.4019 | -75.6557 | Ontario.b | Ontario | OHSC GS | ON_OHS_GSS | 115 | 2014 | 2034 | NG_CG | gasCC | 72 | 85.12% | 61.284 | 4.957% | 31.267
| Otter Rapids | ON_ORP00_GEN | Ontario Power Generation Inc | Smooth Rock Falls | 50.1812 | -81.6373 | Ontario.b | Ontario | Otter Rapids GS | ON_ORP_GSS | 115 | 1961 | 2100 | hydro_daily | hydro_daily | 189 | 68.43% | 129.3343 | 26.95% | 446.157 | 4
| Otto Holden | ON_OTH00_GEN | Ontario Power Generation Inc | Mattawa | 46.3784 | -78.7276 | Ontario.b | Ontario | Otto Holden TS | ON_OTH_DSS | 230 | 1952 | 2100 | hydro_daily | hydro_daily | 265 | 68.43% | 181.3417 | 47.19% | 1095.498 | 8
| Oxley | ON_OXL00_GEN | Henry Verhoeven | Harrow | 42.0066 | -82.8803 | Ontario.a | Ontario | Kingsville TS | ON_KSV_DSS | 115 | 2020 | 2040 | wind_onshore | wind | 6 | 21.14% | 1.2685 | 27% | 14.1912 | [20 empty] | https://www.bullfrogpower.com/green-energy/projects-and-sources/oxley-wind-farm/
| Pearl Street | ON_PST00_GEN | Enwave Energy Corporation | Toronto | 43.6485 | -79.3863 | Ontario.a | Ontario | John TS | ON_JON_DSS | 115 | 2017 | 2037 | NG_CG | gasCC | 3.845 | 85.12% | 3.2727 | 13% | 4.3787
| Pendleton | ON_PDL00_GEN | Pendleton Energy Centre Limited Partnership | Curran | 45.4923 | -74.9956 | Ontario.b | Ontario | St. Isidore TS | ON_STI_DSS | 230 | 2019 | 2039 | solar | solar | 12 | 18.54% | 2.2254 | 18% | 18.9216
| Penn Energy Brantgate | ON_PEBR00_GEN | Brantgate Solar Farm Partnership | Scotland | 43.049 | -80.3883 | Ontario.a | Ontario | Brant TS | ON_BRT_DSS | 115 | 2015 | 2035 | solar | solar | 8 | 18.54% | 1.4836 | 18% | 12.6144
| Penn Energy Edwardsburgh Morrisburg | ON_PEEM00_GEN | Edwardsburgh Solar Farm Partnership | Prescott | 44.7257 | -75.4928 | Ontario.a | Ontario | Brockville TS | ON_BRO_DSS | 115 | 2014 | 2034 | solar | solar | 9.3 | 18.54% | 1.7247 | 18% | 14.6642
| Penn Energy Hamilton Port Hope | ON_PEHP00_GEN | Hamilton Solar Farm Partnership | Baltimore | 44.0246 | -78.1208 | Ontario.a | Ontario | Port Hope TS | ON_PTH_DSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Penn Energy Ridgefield | ON_PERD00_GEN | Ridgefield Solar Farm Partnership | Dunsford | 44.4433 | -78.6864 | Ontario.a | Ontario | Lindsay TS | ON_LND_DSS | 230 | 2015 | 2035 | solar | solar | 8 | 18.54% | 1.4836 | 18% | 12.6144
| Penn Energy Roseplain | ON_PERS00_GEN | Roseplain Solar Farm Partnership | Goodwood | 44.0616 | -79.1816 | Ontario.a | Ontario | Armitage TS | ON_ATG_DSS | 115 | 2015 | 2035 | solar | solar | 6.5 | 18.54% | 1.2054 | 18% | 10.2492
| Penn Energy South Glengarry | ON_PESG00_GEN | South Glengarry Solar Farm Partnership | Williamstown | 45.1066 | -74.6822 | Ontario.b | Ontario | St. Lawrence TS | ON_STL_DSS | 230 | 2014 | 2034 | solar | solar | 9.3 | 18.54% | 1.7247 | 18% | 14.6642
| Penn Energy Vandorp | ON_PEVD00_GEN | Port Hope Solar Farm Partnership | Port Hope | 43.9459 | -78.3877 | Ontario.a | Ontario | Port Hope TS | ON_PTH_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Perpetual Cleanpower Lindsay | ON_PECL00_GEN | Lindsay Solar LP | Lindsay | 44.4307 | -78.694 | Ontario.a | Ontario | Lindsay TS | ON_LND_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Perpetual Cleanpower Oro 4 Line | ON_PECO00_GEN | Oro-Medonte Solar Farm Inc | Hawkestone | 44.5006 | -79.6133 | Ontario.a | Ontario | Orillia TS | ON_ORI_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Peter Sutherland Sr. | ON_PSS00_GEN | Ontario Power Generation / Coral Rapids Power | Smooth Rock Falls | 49.962 | -81.5226 | Ontario.b | Ontario | P Sutherland Sr SYD | ON_PSS_GSS | 115 | 2017 | 2067 | hydro_run | hydro_run | 82 | 68.43% | 56.1133 | 13.74% | 98.726 | 2 | [19 empty] | https://www.opg.com/strengthening-the-economy/our-projects/peter-sutherland-sr/
| Petrolia | ON_PTL00_GEN | Waste Management of Canada Corporation | Petrolia | 42.8721 | -82.1202 | Ontario.a | Ontario | Wanstead TS | ON_WAN_DSS | 115 | 2010 | 2030 | biogas | biomass | 3.2 | 94.51% | 3.0244 | 20% | 5.6064
| Pickering A_01 | ON_PKA01_GEN | Ontario Power Generation Inc | Pickering | 43.8107 | -79.0689 | Ontario.a | Ontario | Pickering A SWS | ON_PKA_SWS | 230 | 1971 | 2100 | nuclear | nuclear | 515 | 92.83% | 478.0844 | 94.05% | 4243.029 | 2
| Pickering A_04 | ON_PKA04_GEN | Ontario Power Generation Inc | Pickering | 43.8107 | -79.0689 | Ontario.a | Ontario | Pickering A SWS | ON_PKA_SWS | 230 | 1971 | 2100 | nuclear | nuclear | 515 | 92.83% | 478.0844 | 62.09% | 2801.085 | 2
| Pickering B_01 | ON_PKB01_GEN | Ontario Power Generation Inc | Pickering | 43.8096 | -79.0639 | Ontario.a | Ontario | Pickering B SWS | ON_PKB_SWS | 115 | 1971 | 2100 | nuclear | nuclear | 518 | 92.83% | 480.8694 | 93.85% | 4258.466 | 4
| Pickering B_02 | ON_PKB02_GEN | Ontario Power Generation Inc | Pickering | 43.8096 | -79.0639 | Ontario.a | Ontario | Pickering B SWS | ON_PKB_SWS | 115 | 1971 | 2100 | nuclear | nuclear | 518 | 92.83% | 480.8694 | 58.61% | 2659.355 | 4
| Pickering B_03 | ON_PKB03_GEN | Ontario Power Generation Inc | Pickering | 43.8096 | -79.0639 | Ontario.a | Ontario | Pickering B SWS | ON_PKB_SWS | 115 | 1971 | 2100 | nuclear | nuclear | 518 | 92.83% | 480.8694 | 95.58% | 4336.899 | 4
| Pickering B_04 | ON_PKB04_GEN | Ontario Power Generation Inc | Pickering | 43.8096 | -79.0639 | Ontario.a | Ontario | Pickering B SWS | ON_PKB_SWS | 115 | 1971 | 2100 | nuclear | nuclear | 518 | 92.83% | 480.8694 | 58.61% | 2659.435 | 4
| Pine Portage | ON_PPT00_GEN | Ontario Power Generation Inc | Nipigon | 49.3074 | -88.3103 | Ontario.b | Ontario | Pine Portage SWS | ON_PPT_SWS | 115 | 1950 | 2100 | hydro_daily | hydro_daily | 151 | 68.43% | 103.3306 | 35.93% | 475.248 | 4
| Plateau I / II | ON_PLT01_GEN | Plateau Wind LP | Dundalk | 44.247 | -80.3944 | Ontario.a | Ontario | Orangeville TS | ON_ORA_DSS | 230 | 2012 | 2032 | wind_onshore | wind | 18 | 21.14% | 3.8056 | 27% | 42.5736
| Plateau III | ON_PLT03_GEN | Plateau Wind LP | Dundalk | 44.1886 | -80.3088 | Ontario.a | Ontario | Orangeville TS | ON_ORA_DSS | 230 | 2012 | 2032 | wind_onshore | wind | 9 | 21.14% | 1.9028 | 27% | 21.2868
| Pointe aux Roches | ON_PAR00_GEN | Pointe-aux-Roches Wind LP | Comber | 42.2841 | -82.5284 | Ontario.a | Ontario | Pte-Aux-Roches WF GS | ON_PAR_GSS | 115 | 2011 | 2031 | wind_onshore | wind | 48.6 | 21.14% | 10.275 | 33.47% | 142.492
| Port Alma | ON_PMA00_GEN | Kruger Energy Port Alma LP | Port Alma | 42.1839 | -82.2851 | Ontario.a | Ontario | Port Alma WF GS | ON_PMA_GSS | 230 | 2008 | 2028 | wind_onshore | wind | 202 | 21.14% | 42.7069 | 32.53% | 575.643
| Port Burwell | ON_PBW00_GEN | Erie Shores Wind Farm LP | Port Burwell | 42.6476 | -80.7695 | Ontario.a | Ontario | Tillsonburg TS | ON_TLL_DSS | 115 | 2006 | 2026 | wind_onshore | wind | 99 | 21.14% | 20.9306 | 21.06% | 182.626
| Port Ryerse | ON_PRY00_GEN | Boralex | Simcoe | 42.7677 | -80.2521 | Ontario.a | Ontario | Norfolk TS | ON_NOR_DSS | 115 | 2016 | 2036 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Portlands_01 | ON_PTE01_GEN | Portlands Energy Centre LP | Toronto | 43.6495 | -79.3311 | Ontario.a | Ontario | Portlands Energy JCT | ON_PTE_JCT | 115 | 2009 | 2029 | NG_CT | gasSC | 194 | 85.12% | 165.1262 | 20% | 339.879
| Portlands_02 | ON_PTE02_GEN | Portlands Energy Centre LP | Toronto | 43.6495 | -79.3311 | Ontario.a | Ontario | Portlands Energy JCT | ON_PTE_JCT | 115 | 2009 | 2029 | NG_CT | gasSC | 194 | 85.12% | 165.1262 | 21.52% | 365.786
| Portlands_03 | ON_PTE03_GEN | Portlands Energy Centre LP | Toronto | 43.6495 | -79.3311 | Ontario.a | Ontario | Portlands Energy JCT | ON_PTE_JCT | 115 | 2009 | 2029 | NG_CT | gasSC | 236 | 85.12% | 200.8752 | 21.59% | 446.414
| Prince | ON_PRC00_GEN | Brookfield Power Wind Prince LP | Heyden | 46.6126 | -84.4792 | Ontario.b | Ontario | Heyden SWS | ON_HYD_SWS | 115 | 2006 | 2026 | wind_onshore | wind | 189 | 21.14% | 39.9584 | 22.6% | 374.125
| Proof Line | ON_PRF00_GEN | Sky Generation LP | Forest | 43.1571 | -82.0184 | Ontario.a | Ontario | Wanstead TS | ON_WAN_DSS | 115 | 2009 | 2029 | wind_onshore | wind | 6.6 | 21.14% | 1.3954 | 27% | 15.6103
| Providence Bay | ON_PVB00_GEN | Schneider Power Providence Bay Inc | Providence Bay | 45.7291 | -82.295 | Ontario.b | Ontario | Manitoulin TS | ON_MNT_DSS | 115 | 2007 | 2027 | wind_onshore | wind | 1.6 | 21.14% | 0.33827 | 27% | 3.7843
| Quixote | ON_QUX00_GEN | Quixote One Wind Energy Corp | Tiverton | 44.2734 | -81.5794 | Ontario.a | Ontario | Bruce A TS | ON_BCA_TSS | 230 | 2015 | 2035 | wind_onshore | wind | 2.3 | 21.14% | 0.48627 | 27% | 5.44
| Ragged Chute | ON_RGD00_GEN | Ragged Chute Energy Inc | Haileybury | 47.2763 | -79.6714 | Ontario.b | Ontario | Dymond TS | ON_DYM_DSS | 230 | 2013 | 2029 | hydro_run | hydro_run | 6.6 | 68.43% | 4.5164 | 65% | 37.5804
| Ragged Rapids | ON_RGP00_GEN | Ontario Power Generation Inc | Bala | 45.018 | -79.6883 | Ontario.b | Ontario | Muskoka TS | ON_MSK_DSS | 230 | 1938 | 2100 | hydro_run | hydro_run | 8 | 68.43% | 5.4745 | 65% | 45.552 | 2
| Ramore | ON_RMR00_GEN | New Ospvf 11 LP | Ramore | 48.4393 | -80.3256 | Ontario.b | Ontario | Ramore TS | ON_RMR_DSS | 115 | 2014 | 2034 | solar | solar | 8 | 18.54% | 1.4836 | 18% | 12.6144
| Ranney Falls | ON_RNF00_GEN | Ontario Power Generation Inc | Campbellford | 44.2921 | -77.802 | Ontario.a | Ontario | Havelock TS | ON_HVL_DSS | 230 | 1922 | 2100 | hydro_run | hydro_run | 10 | 68.43% | 6.8431 | 65% | 56.94 | 3
| Ravensbergen | ON_RVS00_GEN | P. Ravensbergen & Sons Limited | Smithville | 43.1195 | -79.6003 | Ontario.a | Ontario | Niagara West MTS | ON_NIW_DSS | 230 | 2017 | 2037 | NG_CG | gasCC | 2.578 | 85.12% | 2.1943 | 13% | 2.9358
| Ravenswood | ON_RVW00_GEN | Sky Generation LP | Forest | 43.1751 | -81.9812 | Ontario.a | Ontario | Wanstead TS | ON_WAN_DSS | 115 | 2008 | 2028 | wind_onshore | wind | 9.9 | 21.14% | 2.0931 | 27% | 23.4155
| Raylight | ON_RYL00_GEN | Concord Raylight Partnership | Wyebridge | 44.6982 | -79.8423 | Ontario.a | Ontario | Waubaushene TS | ON_WBS_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Rayner | ON_RYN00_GEN | Brookfield Renewable Power Inc | Thessalon | 46.4337 | -83.3838 | Ontario.b | Ontario | Rayner GS | ON_RNR_GSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 42 | 68.43% | 28.7409 | 31.61% | 116.312
| Red Rock Falls | ON_RRF00_GEN | Brookfield Renewable Power Inc | Thessalon | 46.315 | -83.2905 | Ontario.b | Ontario | Red Rock GS | ON_RRC_GSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 37 | 68.43% | 25.3194 | 58.79% | 190.557 | 2
| Regent Park | ON_RGT00_GEN | Regent Park Energy Inc | Toronto | 43.6598 | -79.3611 | Ontario.a | Ontario | Esplanade TS | ON_EPL_DSS | 115 | 2000 | 2100 | NG_CG | gasCC | 4.2 | 85.12% | 3.5749 | 13% | 4.783
| Richardson | ON_RCH00_GEN | Gengrowth LP | Tilbury | 42.2364 | -82.4566 | Ontario.a | Ontario | Tilbury TS | ON_TLB_DSS | 115 | 2010 | 2030 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Rideau Falls | ON_RFL00_GEN | Fortis Generation East LP | Ottawa | 45.4422 | -75.6959 | Ontario.b | Ontario | Lisgar TS | ON_LSG_DSS | 115 | 2010 | 2030 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388
| Ripley | ON_RPL00_GEN | Suncor Acciona | Ripley | 44.0524 | -81.6558 | Ontario.a | Ontario | Majestic TS | ON_MAJ_ISS | 230 | 2007 | 2027 | wind_onshore | wind | 76 | 21.14% | 16.0679 | 24.67% | 164.258
| Robert G. Lake | ON_RGL00_GEN | Trent Rapids Power Corporation | Peterborough | 44.3653 | -78.2928 | Ontario.a | Ontario | Otonabee TS | ON_OTB_DSS | 230 | 2009 | 2049 | hydro_run | hydro_run | 8 | 68.43% | 5.4745 | 65% | 45.552
| Robert O. Pickard | ON_ROP00_GEN | City of Ottawa | Ottawa | 45.4625 | -75.5875 | Ontario.b | Ontario | Bilberry Creek TS | ON_BBC_DSS | 115 | 2000 | 2100 | biomass | biomass | 2.4 | 94.51% | 2.2683 | 20% | 4.2048
| Romney | ON_RMN00_GEN | Romney Energy Centre Limited Partnership | Tilbury | 42.1521 | -82.489 | Ontario.a | Ontario | Leamington TS | ON_LEM_DSS | 230 | 2021 | 2041 | wind_onshore | wind | 60 | 21.14% | 12.6852 | 27% | 141.912
| Rosa Flora Growers Limited | ON_RFG00_GEN | Rosa Flora Growers Limited | Dunnville | 42.9507 | -79.5842 | Ontario.a | Ontario | Dunnville TS | ON_DNV_DSS | 115 | 2015 | 2035 | NG_CG | gasCC | 3.916 | 85.12% | 3.3332 | 13% | 4.4595
| Ruby Farms | ON_RBF00_GEN | Vine Fresh Produce Limited | Strathroy | 42.9548 | -81.6693 | Ontario.a | Ontario | Strathroy TS | ON_SRY_DSS | 115 | 2013 | 2033 | solar | solar | 2 | 18.54% | 0.3709 | 18% | 3.1536
| Ryerse | ON_RYE00_GEN | Skypower Ltd / Sunedison | Port Dover | 42.7841 | -80.2655 | Ontario.a | Ontario | Norfolk TS | ON_NOR_DSS | 115 | 2011 | 2031 | solar | solar | 9.1 | 18.54% | 1.6876 | 18% | 14.3489
| Sandusk | ON_SND00_GEN | Capital Power (PDN) LP | Nanticoke | 42.8392 | -80.0274 | Ontario.a | Ontario | Sandusk GS | ON_SND_GSS | 115 | 2013 | 2033 | wind_onshore | wind | 104.4 | 21.14% | 22.0723 | 32.79% | 299.836
| Sandy Falls | ON_SFL00_GEN | Ontario Power Generation / Umh Energy | Timmins | 48.5113 | -81.4434 | Ontario.b | Ontario | Timmins TS | ON_TMM_DSS | 115 | 2010 | 2060 | hydro_run | hydro_run | 6 | 68.43% | 4.1058 | 65% | 34.164 | 1
| Sarnia 1 | ON_SNS01_GEN | Enbridge Inc | Sarnia | 42.9417 | -82.3394 | Ontario.a | Ontario | Sarnia Scott TS | ON_SNS_TSS | 230 | 2010 | 2030 | solar | solar | 20 | 18.54% | 3.709 | 18% | 31.536
| Sarnia 2 | ON_SNS02_GEN | Enbridge Inc | Sarnia | 42.9498 | -82.3199 | Ontario.a | Ontario | Sarnia Scott TS | ON_SNS_TSS | 230 | 2010 | 2030 | solar | solar | 60 | 18.54% | 11.1269 | 18% | 94.608
| Saunders | ON_SAU00_GEN | Ontario Power Generation Inc | Cornwall | 45.0088 | -74.7905 | Ontario.b | Ontario | St. Lawrence TS | ON_STL_DSS | 230 | 1958 | 2100 | hydro_run | hydro_run | 1086 | 68.43% | 743.1588 | 78.05% | 7424.724 | 16
| Scarfe Lake | ON_SCL00_GEN | 1149377 Ontario Limited | Blind River | 46.2659 | -83.0127 | Ontario.b | Ontario | Blind River TS | ON_BLD_DSS | 115 | 2010 | 2030 | hydro_run | hydro_run | 2.3 | 68.43% | 1.5739 | 65% | 13.0962
| Scott Falls | ON_SCT00_GEN | Brookfield Renewable Power Inc | Wawa | 47.9101 | -84.7447 | Ontario.b | Ontario | DA Watson TS | ON_DAW_DSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 22 | 68.43% | 15.0548 | 30.07% | 57.9447
| Seacliff | ON_SCF00_GEN | Seacliff Energy | Leamington | 42.0279 | -82.5638 | Ontario.a | Ontario | Leamington TS | ON_LEM_DSS | 230 | 2011 | 2031 | biogas | biomass | 1.6 | 94.51% | 1.5122 | 20% | 2.8032
| Serpent | ON_SPT00_GEN | Brookfield Renewable Power Inc | Serpent River | 46.219 | -82.4409 | Ontario.b | Ontario | Spanish DS | ON_SPA_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 7.2 | 68.43% | 4.927 | 65% | 40.9968
| Settlers Landing | ON_SLD00_GEN | Settlers Landing Wind Development Joint Venture | Blackstock | 44.102 | -78.6562 | Ontario.a | Ontario | Wilson TS | ON_WLS_DSS | 230 | 2017 | 2037 | wind_onshore | wind | 8 | 21.14% | 1.6914 | 27% | 18.9216
| Seymour | ON_SEY00_GEN | Ontario Power Generation Inc | Campbellford | 44.3215 | -77.782 | Ontario.a | Ontario | Havelock TS | ON_HVL_DSS | 230 | 1909 | 2100 | hydro_run | hydro_run | 6 | 68.43% | 4.1058 | 65% | 34.164 | 5
| Sidney | ON_SDY00_GEN | Ontario Power Generation Inc | Trenton | 44.1315 | -77.5934 | Ontario.a | Ontario | Sidney TS | ON_SDY_DSS | 115 | 1911 | 2100 | hydro_run | hydro_run | 4 | 68.43% | 2.7372 | 65% | 22.776 | 4
| Sills Island | ON_SLS00_GEN | Ontario Power Generation Inc | Frankford | 44.21 | -77.5975 | Ontario.a | Ontario | Sidney TS | ON_SDY_DSS | 115 | 1900 | 2100 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388 | 2
| Silver Falls | ON_SFS00_GEN | Ontario Power Generation Inc | Thunder Bay | 48.6609 | -89.5974 | Ontario.b | Ontario | Silver Falls GS | ON_SFS_GSS | 115 | 1959 | 2100 | hydro_run | hydro_run | 49 | 68.43% | 33.5311 | 40.54% | 174.003 | 1
| Silvercreek | ON_SVC00_GEN | Silvercreek Nominee Inc | Aylmer | 42.695 | -80.9791 | Ontario.a | Ontario | Silvercreek GS | ON_SVC_GSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Simcoe Solar Energy Centre I | ON_SSE01_GEN | Terraform Ontario Solar LP | Woodville | 44.4761 | -78.9752 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Simcoe Solar Energy Centre III | ON_SSE02_GEN | Terraform Ontario Solar LP | Woodville | 44.4166 | -78.8859 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Skyway 8 | ON_SKY00_GEN | Capstone Infrastructure Corp | Dundalk | 44.0845 | -80.3919 | Ontario.a | Ontario | Orangeville TS | ON_ORA_DSS | 230 | 2014 | 2034 | wind_onshore | wind | 9.5 | 21.14% | 2.0085 | 27% | 22.4694
| Smiths Falls 1 | ON_SMF01_GEN | Aurora Smiths Falls 1 LP | Smiths Falls | 44.8769 | -76.007 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2014 | 2034 | solar | solar | 6 | 18.54% | 1.1127 | 18% | 9.4608
| Smiths Falls 2 | ON_SMF02_GEN | Aurora Smiths Falls 2 LP | Perth | 44.95 | -76.1139 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Smiths Falls 3 | ON_SMF03_GEN | Aurora Smiths Falls 3 LP | Smiths Falls | 44.9279 | -76.1158 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2014 | 2034 | solar | solar | 6.5 | 18.54% | 1.2054 | 18% | 10.2492
| Smiths Falls 4 | ON_SMF04_GEN | Aurora Smiths Falls 4 LP | Perth | 44.9479 | -76.1422 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Smiths Falls 5 | ON_SMF05_GEN | Aurora Smiths Falls 5 LP | Smiths Falls | 44.9207 | -76.1348 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Smiths Falls 6 | ON_SMF06_GEN | Aurora Smiths Falls 6 LP | Smiths Falls | 44.8547 | -75.9818 | Ontario.b | Ontario | Smiths Falls TS | ON_SMF_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Smoky Falls | ON_SKF00_GEN | Ontario Power Generation Inc | Val Rita | 50.0609 | -82.1609 | Ontario.b | Ontario | Smoky Falls GS | ON_SKF_GSS | 230 | 2014 | 2064 | hydro_daily | hydro_daily | 264 | 68.43% | 180.6574 | 26.25% | 607.1 | 3
| Smooth Rock Falls | ON_SRF01_GEN | Gemini-SRF Power Corporation | Smooth Rock Falls | 49.2857 | -81.6376 | Ontario.b | Ontario | Smooth Rock Falls DS | ON_SRF_DSS | 115 | 2010 | 2030 | hydro_run | hydro_run | 7.4 | 68.43% | 5.0639 | 65% | 42.1356
| Smooth Rock Falls Expansion | ON_SRF02_GEN | Gemini-SRF Power Corporation | Smooth Rock Falls | 49.2857 | -81.6376 | Ontario.b | Ontario | Smooth Rock Falls DS | ON_SRF_DSS | 115 | 2017 | 2029 | hydro_run | hydro_run | 2.217 | 68.43% | 1.5171 | 65% | 12.6236
| Snowy Ridge | ON_SNY00_GEN | Snowy Ridge Wind Development Joint Venture | Bethany | 44.1689 | -78.6293 | Ontario.a | Ontario | Dobbin TS | ON_DOB_DSS | 230 | 2016 | 2036 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Solar Spirit 4 | ON_SSP00_GEN | Sune Solar Spirit LP | Corbyville | 44.232 | -77.3566 | Ontario.a | Ontario | Belleville TS | ON_BLV_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Solray Energy Epsom | ON_SEE00_GEN | Marsh Hill III LP | Uxbridge | 44.1479 | -79.0504 | Ontario.a | Ontario | Armitage TS | ON_ATG_DSS | 115 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Solray Energy Sunderland | ON_SES00_GEN | Sunderland Solar Farm LP | Beaverton | 44.2808 | -79.0347 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| South Branch | ON_SBR00_GEN | South Dundas Windfarm LP | Brinston | 44.9437 | -75.371 | Ontario.b | Ontario | Morrisburg TS | ON_MRB_DSS | 115 | 2014 | 2034 | wind_onshore | wind | 30 | 21.14% | 6.3426 | 27% | 70.956
| South Falls | ON_SFA00_GEN | Ontario Power Generation Inc | Bracebridge | 45.0031 | -79.3054 | Ontario.b | Ontario | Bracebridge TS | ON_BRA_DSS | 230 | 1907 | 2100 | hydro_run | hydro_run | 6 | 68.43% | 4.1058 | 65% | 34.164 | 3
| South Kent | ON_SKW00_GEN | South Kent Wind LP | Blenheim | 42.3495 | -82.1071 | Ontario.a | Ontario | SKWP CMS | ON_SKW_GSS | 230 | 2014 | 2034 | wind_onshore | wind | 270 | 21.14% | 57.0835 | 26.82% | 634.436 | [21 empty] | Also called Railbed
| South Side | ON_SSI00_GEN | South Side Wind Farm Limited Partnership | Amherstburg | 42.084 | -83.0425 | Ontario.a | Ontario | Keith TS | ON_KEI_DSS | 230 | 2010 | 2030 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Southgate | ON_SOG00_GEN | Southgate Solar LP | Holstein | 44.102 | -80.7472 | Ontario.a | Ontario | Southgate GS | ON_SOG_GSS | 230 | 2016 | 2036 | solar | solar | 50 | 18.54% | 9.2724 | 15.24% | 66.761
| Sparklelight | ON_SPK00_GEN | Sparklelight LP | Woodville | 44.4631 | -79.0662 | Ontario.a | Ontario | Beaverton TS | ON_BVT_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Spence | ON_SPC00_GEN | Talbot Windfarm LP | Ridgetown | 42.4375 | -81.7961 | Ontario.a | Ontario | Spence SWS | ON_SPC_SWS | 230 | 2010 | 2030 | wind_onshore | wind | 98.9 | 21.14% | 20.9095 | 23.52% | 203.792 | [21 empty] | Also called Talbot
| Springwood | ON_SPR00_GEN | WPD Springwood Wind Inc | Fergus | 43.7838 | -80.404 | Ontario.a | Ontario | Fergus TS | ON_FGS_DSS | 230 | 2014 | 2034 | wind_onshore | wind | 8.2 | 21.14% | 1.7336 | 27% | 19.3946
| SSM 1 | ON_SSM01_GEN | Starwood Energy | Sault Ste. Marie | 46.5236 | -84.4456 | Ontario.b | Ontario | Clergue TS | ON_CGU_DSS | 115 | 2010 | 2030 | solar | solar | 24 | 18.54% | 4.4507 | 18% | 37.8432
| SSM 2/3 | ON_SSM02_GEN | Starwood Energy | Sault Ste. Marie | 46.5473 | -84.2796 | Ontario.b | Ontario | Clergue TS | ON_CGU_DSS | 115 | 2011 | 2031 | solar | solar | 45 | 18.54% | 8.3451 | 18% | 70.956
| St. Clair | ON_STE00_GEN | St. Clair Power LP | Corunna | 42.8973 | -82.3984 | Ontario.a | Ontario | St. Clair E.C. GS | ON_STE_GSS | 230 | 2009 | 2029 | NG_CT | gasSC | 618 | 85.12% | 526.0206 | 14.52% | 785.816
| St. Clair Moore | ON_STM00_GEN | Nextera Energy Inc | Corunna | 42.8692 | -82.4207 | Ontario.a | Ontario | St. Clair E.C. GS | ON_STE_GSS | 230 | 2012 | 2032 | solar | solar | 20 | 18.54% | 3.709 | 18% | 31.536
| St. Clair Sombra | ON_STC00_GEN | Nextera Energy Partners LP | Sombra | 42.7113 | -82.4619 | Ontario.a | Ontario | Lambton TS #2 | ON_LMB_DSS | 230 | 2012 | 2032 | solar | solar | 20 | 18.54% | 3.709 | 18% | 31.536
| St. Columban | ON_SCO00_GEN | St. Columban Energy LP | Seaforth | 43.5505 | -81.2896 | Ontario.a | Ontario | Seaforth TS | ON_SFT_DSS | 115 | 2015 | 2035 | wind_onshore | wind | 33 | 21.14% | 6.9769 | 27% | 78.0516
| St. Isidore A | ON_STI01_GEN | EDF Energies Nouvelles | St. Isidore | 45.4289 | -74.9374 | Ontario.b | Ontario | St. Isidore TS | ON_STI_DSS | 230 | 2010 | 2030 | solar | solar | 12 | 18.54% | 2.2254 | 18% | 18.9216
| St. Isidore B | ON_STI02_GEN | EDF Energies Nouvelles | St. Isidore | 45.3637 | -74.9092 | Ontario.b | Ontario | St. Isidore TS | ON_STI_DSS | 230 | 2011 | 2031 | solar | solar | 12 | 18.54% | 2.2254 | 18% | 18.9216
| Stanley Adamson | ON_STY00_GEN | Trent Energy Inc | Peterborough | 44.3522 | -78.2948 | Ontario.a | Ontario | Otonabee TS | ON_OTB_DSS | 230 | 2013 | 2033 | hydro_run | hydro_run | 3.9 | 68.43% | 2.6688 | 65% | 22.2066
| Stanton Dairy Farm | ON_SDF00_GEN | Stanton Dairy Farm | Iderton | 43.1003 | -81.373 | Ontario.a | Ontario | Clarke TS | ON_CKE_DSS | 115 | 2000 | 2100 | biogas | biomass | 1.3 | 94.51% | 1.2287 | 20% | 2.2776
| Stardale | ON_SDL00_GEN | Innergex Inc | St. Eugene | 45.5035 | -74.5278 | Ontario.b | Ontario | Longueuil TS | ON_LGU_DSS | 230 | 2012 | 2032 | solar | solar | 33.2 | 18.54% | 6.1569 | 18% | 52.3498
| Steephill | ON_SHF00_GEN | Brookfield Renewable Power Inc | Wawa | 48.0778 | -84.7394 | Ontario.b | Ontario | Steephill Falls GS | ON_SHF_GSS | 115 | 2009 | 2029 | hydro_run | hydro_run | 15 | 68.43% | 10.2646 | 37.28% | 48.989
| Stewartville | ON_STW00_GEN | Ontario Power Generation Inc | Arnprior | 45.4071 | -76.5064 | Ontario.b | Ontario | Stewartville TS | ON_STW_DSS | 115 | 1948 | 2100 | hydro_daily | hydro_daily | 186 | 68.43% | 127.2813 | 18.19% | 296.37 | 5
| Stinson | ON_STN00_GEN | Ontario Power Generation Inc | Sudbury | 46.5213 | -80.7104 | Ontario.b | Ontario | Martindale TS | ON_MTD_DSS | 115 | 1925 | 2100 | hydro_run | hydro_run | 5 | 68.43% | 3.4215 | 65% | 28.47 | 2
| Stone Mills | ON_SML00_GEN | Stone Mills Solar Park LP | Centreville | 44.2959 | -76.8975 | Ontario.a | Ontario | Belleville TS | ON_BLV_DSS | 230 | 2012 | 2032 | solar | solar | 11 | 18.54% | 2.0399 | 18% | 17.3448
| Sturgeon Falls | ON_STG00_GEN | H2O Power LP | Atikokan | 48.7443 | -92.2839 | Ontario.b | Ontario | H2O Power Sturgeon Falls GS | ON_H2S_GSS | 230 | 2009 | 2029 | hydro_run | hydro_run | 8.8 | 68.43% | 6.0219 | 65% | 50.1072 | [20 empty] | http://www.h2opower.com/our-locations/
| Sudbury District Energy | ON_SDE00_GEN | Toromont Energy Ltd | Sudbury | 46.4908 | -80.9973 | Ontario.b | Ontario | Martindale TS | ON_MTD_DSS | 115 | 2010 | 2025 | NG_CT | gasSC | 5 | 85.12% | 4.2558 | 12% | 5.256
| Sudbury Hospital | ON_SDH00_GEN | Toromont Energy Ltd | Sudbury | 46.4679 | -80.9963 | Ontario.b | Ontario | Martindale TS | ON_MTD_DSS | 115 | 2010 | 2025 | NG_CT | gasSC | 6.7 | 85.12% | 5.7028 | 12% | 7.043
| Sudbury LFG | ON_SLF00_GEN | Greater Sudbury Utilities | Sudbury | 46.507 | -80.9002 | Ontario.b | Ontario | Martindale TS | ON_MTD_DSS | 115 | 2007 | 2027 | biogas | biomass | 1.6 | 94.51% | 1.5122 | 20% | 2.8032
| Sumac Ridge | ON_SMC00_GEN | WPD Sumac Ridge Wind Incorporated | Blackstock | 44.1002 | -78.6235 | Ontario.a | Ontario | Wilson TS | ON_WLS_DSS | 230 | 2017 | 2037 | wind_onshore | wind | 10.25 | 21.14% | 2.1671 | 27% | 24.2433
| Summerhaven | ON_SUM00_GEN | Summerhaven Wind LP | Nanticoke | 42.87 | -79.9377 | Ontario.a | Ontario | Summerhaven SWS | ON_SUM_SWS | 230 | 2013 | 2033 | wind_onshore | wind | 124.4 | 21.14% | 26.3007 | 20.54% | 223.867
| Sune Bruining 1 | ON_SNBR00_GEN | Sune South Stormont LP | Ingleside | 44.9856 | -75.013 | Ontario.b | Ontario | St. Lawrence TS | ON_STL_DSS | 230 | 2015 | 2035 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Sune Newboro 1 | ON_SNNB01_GEN | Sune Ray LP | Westport | 44.6712 | -76.273 | Ontario.a | Ontario | Newboro DS | ON_NBO_DSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Sune Newboro 4 | ON_SNNB04_GEN | Sune Newboro 4 LP | Westport | 44.649 | -76.3555 | Ontario.a | Ontario | Newboro DS | ON_NBO_DSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Sune Rutley | ON_SNRT00_GEN | Sune Rutley LP | Ingleside | 45.017 | -74.9659 | Ontario.b | Ontario | St. Lawrence TS | ON_STL_DSS | 230 | 2012 | 2032 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Sunningdale 1 | ON_SNG00_GEN | Re Sunningdale LP | Thorndale | 43.0711 | -81.1582 | Ontario.a | Ontario | Highbury TS | ON_HIG_DSS | 115 | 2014 | 2034 | solar | solar | 7 | 18.54% | 1.2981 | 18% | 11.0376
| Sunny Shores | ON_SSH00_GEN | Sunny Shores LP | Wellington | 44.0561 | -77.1519 | Ontario.a | Ontario | Picton TS | ON_PCT_DSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Swanton Line | ON_SWL00_GEN | Gengrowth LP | Merlin | 42.2638 | -82.2682 | Ontario.a | Ontario | Chatham SWS | ON_CHT_SWS | 230 | 2009 | 2029 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
| Swift Rapids | ON_SWT00_GEN | Orillia Power Generation Corp | Coldwater | 44.8569 | -79.5396 | Ontario.b | Ontario | Orillia TS | ON_ORI_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 7.9 | 68.43% | 5.406 | 65% | 44.9826
| Tembec Kapuskasing | ON_TMB00_GEN | Tembec Inc | Kapuskasing | 49.4089 | -82.4248 | Ontario.b | Ontario | Tembec Kapuskasking TS | ON_TMB_GSS | 115 | 2000 | 2100 | biomass | biomass | 15 | 94.51% | 14.1768 | 20% | 26.28
| Thames River | ON_THR00_GEN | Boralex | Merlin | 42.2701 | -82.2539 | Ontario.a | Ontario | Kent TS | ON_KNT_DSS | 115 | 2009 | 2029 | wind_onshore | wind | 90 | 21.14% | 19.0278 | 27% | 212.868 | [20 empty] | https://www.boralex.com/our-projects-and-sites/?refinementList%5Benergy_types%5D%5B0%5D=wind
| Thomas Low | ON_THL00_GEN | Renfrew Power Generation Inc | Renfrew | 45.4796 | -76.6894 | Ontario.b | Ontario | Stewartville TS | ON_STW_DSS | 115 | 2015 | 2032 | hydro_run | hydro_run | 4 | 68.43% | 2.7372 | 65% | 22.776
| Thorold CGS | ON_RFT00_GEN | Thorold Cogen LP | Thorold | 43.1071 | -79.1983 | Ontario.a | Ontario | RFP Thorold TS | ON_RFT_GSS | 115 | 2010 | 2030 | NG_CG | gasCC | 285 | 85.12% | 242.5823 | 16.38% | 408.897
| Thunder Bay Airport | ON_TBA00_GEN | Skypower / Canadian Solar | Thunder Bay | 48.3653 | -89.3208 | Ontario.b | Ontario | Fort William TS | ON_FRW_DSS | 115 | 2011 | 2031 | solar | solar | 8.5 | 18.54% | 1.5763 | 18% | 13.4028
| Thunder Bay Condensing Turbine | ON_RFB00_GEN | Resolute FP Canada Inc | Thunder Bay | 48.3579 | -89.2317 | Ontario.b | Ontario | RFP Thunder Bay TS | ON_RFB_GSS | 115 | 2013 | 2023 | biomass | biomass | 45 | 94.51% | 42.5305 | 4.293% | 16.923
| Tilbury | ON_TLB00_GEN | Enbridge Inc | Tilbury | 42.2741 | -82.4267 | Ontario.a | Ontario | Tilbury TS | ON_TLB_DSS | 115 | 2010 | 2030 | solar | solar | 5 | 18.54% | 0.92724 | 18% | 7.884
| Trail Road | ON_TRD00_GEN | Powertrail Inc | Richmond | 45.2372 | -75.7637 | Ontario.b | Ontario | Manotick DS | ON_MTK_DSS | 115 | 2007 | 2027 | biogas | biomass | 6 | 94.51% | 5.6707 | 20% | 10.512
| Transalta Sarnia | ON_TRA00_GEN | TransAlta | Sarnia | 42.9346 | -82.4381 | Ontario.a | Ontario | TransAlta Energy GS | ON_TRA_GSS | 230 | 2009 | 2026 | NG_CT | gasSC | 510 | 85.12% | 434.0947 | 25.89% | 1156.583 | [20 empty] | https://transalta.com/facilities/plants-operation/sarnia/
| Trent Valley | ON_TRV00_GEN | Sonoco | Trenton | 44.1524 | -77.5835 | Ontario.a | Ontario | Sidney TS | ON_SDY_DSS | 115 | 2011 | 2031 | NG_CT | gasSC | 6.65 | 85.12% | 5.6603 | 12% | 6.9905
| Trethewey Falls | ON_TRF00_GEN | Ontario Power Generation Inc | Bracebridge | 44.9884 | -79.2714 | Ontario.b | Ontario | Bracebridge TS | ON_BRA_DSS | 230 | 1929 | 2100 | hydro_run | hydro_run | 2 | 68.43% | 1.3686 | 65% | 11.388 | 1
| Tunis | ON_TNS00_GEN | Atlantic Power Limited Partnership | Tunis | 48.7725 | -80.7843 | Ontario.b | Ontario | Iroquois Falls DS | ON_IQF_DSS | 115 | 2018 | 2033 | NG_CT | gasSC | 39 | 85.12% | 33.1955 | 12% | 40.9968
| Twin Falls H2O | ON_TFH00_GEN | H2O Power LP | Iroquois Falls | 48.7468 | -80.5817 | Ontario.b | Ontario | Iroquois Falls DS | ON_IQF_DSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 27.5 | 68.43% | 18.8185 | 58.01% | 139.7461 | [20 empty] | http://www.h2opower.com/our-locations/
| Twin Falls Kagiano | ON_TWK00_GEN | Kagiano Power Corp | Marathon | 49.1899 | -86.1172 | Ontario.b | Ontario | Manitouwadge TS | ON_MTW_DSS | 115 | 1994 | 2100 | hydro_run | hydro_run | 5 | 68.43% | 3.4215 | 65% | 28.47
| Umbata Falls | ON_UMB00_GEN | Umbata Falls LP | Marathon | 48.5358 | -86.1442 | Ontario.b | Ontario | Marathon TS | ON_MRT_TSS | 115 | 2008 | 2028 | hydro_run | hydro_run | 24 | 68.43% | 16.4234 | 58.27% | 122.517
| Underwood | ON_UDW00_GEN | Enbridge Renewable Energy Infrastructure LP | Kincardine | 44.3416 | -81.4533 | Ontario.a | Ontario | Underwood GS | ON_UDW_GSS | 230 | 2009 | 2029 | wind_onshore | wind | 181.5 | 21.14% | 38.3728 | 24.13% | 383.668
| Val Caron | ON_VLC00_GEN | Concord Val Caron Partnership | Hanmer | 46.6692 | -80.9214 | Ontario.b | Ontario | Martindale TS | ON_MTD_DSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Valerie Falls | ON_VLF00_GEN | Valerie Falls Ltd Partnership | Atikokan | 48.7918 | -91.705 | Ontario.b | Ontario | Mackenzie TS | ON_MKZ_TSS | 230 | 2000 | 2100 | hydro_run | hydro_run | 10 | 68.43% | 6.8431 | 65% | 56.94
| Vanzwolf | ON_VZW00_GEN | Rainy River First Nations Solar 2 LP | Rainy River | 48.7078 | -94.2516 | Ontario.b | Ontario | Barwick TS | ON_BWK_DSS | 115 | 2015 | 2035 | solar | solar | 5 | 18.54% | 0.92724 | 18% | 7.884
| Wabageshik | ON_WBG00_GEN | Vale Canada Limited | Beaver Lake | 46.3163 | -81.5207 | Ontario.b | Ontario | Whitefish DS | ON_WHF_DSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 3.4 | 68.43% | 2.3266 | 65% | 19.3596
| Wainfleet | ON_WFL00_GEN | Wainfleet Wind Energy Inc | Wainfleet | 42.8978 | -79.3854 | Ontario.a | Ontario | Dunnville TS | ON_DNV_DSS | 115 | 2014 | 2034 | wind_onshore | wind | 9 | 21.14% | 1.9028 | 27% | 21.2868
| Wainwright | ON_WNW00_GEN | New Ospvf 1 LP | Oxdrift | 49.8395 | -92.8467 | Ontario.b | Ontario | Dryden TS | ON_DRY_TSS | 230 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Wainwright Falls | ON_WNF00_GEN | Capstone Infrastructure Corp | Dryden | 49.8217 | -92.8763 | Ontario.b | Ontario | Dryden TS | ON_DRY_TSS | 230 | 2000 | 2100 | hydro_run | hydro_run | 1.1 | 68.43% | 0.75274 | 65% | 6.2634
| Walpole | ON_WLP00_GEN | ABW Solar General Partnership | Hagersville | 42.9359 | -80.1435 | Ontario.a | Ontario | Jarvis TS | ON_JRV_DSS | 230 | 2013 | 2033 | solar | solar | 20 | 18.54% | 3.709 | 18% | 31.536
| Warden Energy Centre | ON_WEC00_GEN | Markham District Energy Inc | Markham | 43.847 | -79.3333 | Ontario.a | Ontario | Markham #1 MTS | ON_MM1_DSS | 230 | 2008 | 2028 | NG_CG | gasCC | 13.7 | 85.12% | 11.661 | 13% | 15.6016
| Wasdell Falls | ON_WSD00_GEN | Wasdell Falls Power Corp | Washago | 44.7808 | -79.2937 | Ontario.b | Ontario | Orillia TS | ON_ORI_DSS | 230 | 2015 | 2055 | hydro_run | hydro_run | 1.6 | 68.43% | 1.0949 | 65% | 9.1104
| Water Street Pumphouse | ON_WSP00_GEN | Peterborough Utilities Commission | Peterborough | 44.3371 | -78.3131 | Ontario.a | Ontario | Otonabee TS | ON_OTB_DSS | 230 | 2013 | 2033 | hydro_run | hydro_run | 1.3 | 68.43% | 0.8896 | 65% | 7.4022
| Waterloo | ON_WTL00_GEN | Region of Waterloo | Waterloo | 43.4375 | -80.5801 | Ontario.a | Ontario | Kitchener MTS #6 | ON_KM6_DSS | 230 | 2007 | 2027 | biogas | biomass | 4.6 | 94.51% | 4.3476 | 20% | 8.0592
| Waubaushene 3 | ON_WBS03_GEN | Aurora Waubaushene 3 LP | Wyebridge | 44.6575 | -79.8048 | Ontario.a | Ontario | Waubaushene TS | ON_WBS_DSS | 230 | 2013 | 2033 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Waubaushene 4 | ON_WBS04_GEN | Aurora Waubaushene 4 LP | Coldwater | 44.7713 | -79.6416 | Ontario.b | Ontario | Orillia TS | ON_ORI_DSS | 230 | 2013 | 2033 | solar | solar | 8 | 18.54% | 1.4836 | 18% | 12.6144
| Waubaushene 5 | ON_WBS05_GEN | Aurora Waubaushene 5 LP | Coldwater | 44.7706 | -79.6018 | Ontario.b | Ontario | Orillia TS | ON_ORI_DSS | 230 | 2013 | 2033 | solar | solar | 3.5 | 18.54% | 0.64907 | 18% | 5.5188
| Wawaitin | ON_WWT00_GEN | Ontario Power Generation / Umh Energy | Timmins | 48.3472 | -81.4806 | Ontario.b | Ontario | Wawaitin GS | ON_WWT_GSS | 115 | 2010 | 2060 | hydro_run | hydro_run | 15 | 68.43% | 10.2646 | 65% | 85.41 | 2
| Wawatay | ON_WWY00_GEN | Biigtigong Dbenjgan | Heron Bay | 48.6604 | -86.2325 | Ontario.b | Ontario | Marathon TS | ON_MRT_TSS | 115 | 2000 | 2100 | hydro_run | hydro_run | 13.5 | 68.43% | 9.2382 | 65% | 76.869 | [20 empty] | http://www.picriverenergy.com/wawatay.php
| Welland | ON_WEL00_GEN | St. Lawrence Seaway Authority | St. Catharines | 43.1547 | -79.1924 | Ontario.a | Ontario | Bunting TS | ON_BUN_DSS | 115 | 2008 | 2028 | hydro_run | hydro_run | 12 | 68.43% | 8.2117 | 65% | 68.328
| Welland Ridge Road | ON_WRR00_GEN | Sune Welland Ridge LP | Welland | 42.9743 | -79.1965 | Ontario.a | Ontario | Crowland TS | ON_CRL_DSS | 115 | 2014 | 2034 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Wells | ON_WLS00_GEN | Brookfield Renewable Power Inc | Thessalon | 46.4315 | -83.3859 | Ontario.b | Ontario | Wells GS | ON_WEL_GSS | 115 | 2009 | 2029 | hydro_daily | hydro_daily | 220 | 68.43% | 150.5478 | 13.26% | 255.642
| West Lincoln | ON_WLN00_GEN | FWRN LP | Smithville | 42.9993 | -79.5035 | Ontario.a | Ontario | West Lincoln GS | ON_WLN_DSS | 115 | 2016 | 2036 | wind_onshore | wind | 253 | 21.14% | 53.4893 | 20.34% | 450.73
| West Lorne | ON_WLR00_GEN | West Lorne Biooil Cogeneration LP | West Lorne | 42.6039 | -81.6116 | Ontario.a | Ontario | Duart TS | ON_DUA_DSS | 230 | 2000 | 2100 | biomass | biomass | 3 | 94.51% | 2.8354 | 20% | 5.256
| West Nipissing | ON_WNP00_GEN | West Nipissing Power Generation | Sturgeon Falls | 46.3695 | -79.9357 | Ontario.b | Ontario | Crystal Falls TS | ON_CRY_DSS | 230 | 2010 | 2030 | hydro_run | hydro_run | 8.7 | 68.43% | 5.9535 | 65% | 49.5378
| West Windsor | ON_WWD00_GEN | West Windsor Power | Windsor | 42.2807 | -83.0876 | Ontario.a | Ontario | West Windsor Power SWS | ON_WWP_SWS | 230 | 2016 | 2031 | NG_CT | gasSC | 122.8 | 85.12% | 104.5232 | 4.362% | 46.918
| Whitby | ON_WBY00_GEN | Calpine | Whitby | 43.8594 | -78.9033 | Ontario.a | Ontario | Whitby GS | ON_WHI_GSS | 230 | 1998 | 2100 | NG_CG | gasCC | 56 | 85.12% | 47.6653 | 82% | 402.237
| White Otter Falls | ON_WOF00_GEN | Nipiy-Wof Hydrokap LP | Kapuskasing | 49.2189 | -82.6888 | Ontario.b | Ontario | Kapuskasing TS | ON_KAP_DSS | 115 | 2013 | 2053 | hydro_run | hydro_run | 5.5 | 68.43% | 3.7637 | 65% | 31.317
| White River | ON_WHT00_GEN | White River Forest Products | White River | 48.594 | -85.3008 | Ontario.b | Ontario | White River DS | ON_WHT_DSS | 115 | 2000 | 2100 | biomass | biomass | 7.5 | 94.51% | 7.0884 | 20% | 13.14
| Whitedog Falls | ON_WDF00_GEN | Ontario Power Generation Inc | Kenora | 50.1145 | -94.8691 | Ontario.b | Ontario | Whitedog Falls GS | ON_WDF_GSS | 115 | 1958 | 2100 | hydro_run | hydro_run | 73 | 68.43% | 49.9545 | 41.08% | 262.687 | 3
| Whittington | ON_WTG00_GEN | WPD Whittington Wind Inc | Orangeville | 44.0045 | -80.1628 | Ontario.a | Ontario | Orangeville TS | ON_ORA_DSS | 230 | 2014 | 2034 | wind_onshore | wind | 6.2 | 21.14% | 1.3108 | 27% | 14.6642
| William Rutley | ON_WRU00_GEN | TransCanada Energy Ltd | Ingleside | 45.0076 | -74.9746 | Ontario.b | Ontario | St. Lawrence TS | ON_STL_DSS | 230 | 2012 | 2032 | solar | solar | 10 | 18.54% | 1.8545 | 18% | 15.768
| Wilson's Falls | ON_WLF00_GEN | Bracebridge Generation Limited | Bracebridge | 45.0624 | -79.3106 | Ontario.b | Ontario | Bracebridge TS | ON_BRA_DSS | 230 | 2012 | 2032 | hydro_run | hydro_run | 2.3 | 68.43% | 1.5739 | 65% | 13.0962
| Windsor Airport | ON_WAP00_GEN | Windsor Solar LP | Windsor | 42.281 | -82.9351 | Ontario.a | Ontario | Windsor Airport GS | ON_WDA_GSS | 115 | 2016 | 2036 | solar | solar | 50 | 18.54% | 9.2724 | 16.64% | 72.9
| Windsor Essex | ON_WSX00_GEN | TransAlta Cogeneration LP | Windsor | 42.2876 | -82.9803 | Ontario.a | Ontario | Windsor Transalta GS | ON_WDT_GSS | 115 | 2016 | 2031 | NG_CG | gasCC | 76 | 85.12% | 64.6886 | 3.869% | 25.759
| WM Ottawa Landfill | ON_WOL00_GEN | Waste Management of Canada Corp | Carp | 45.2816 | -75.9593 | Ontario.b | Ontario | South March TS | ON_SOM_DSS | 230 | 2010 | 2030 | biogas | biomass | 6.4 | 94.51% | 6.0488 | 20% | 11.2128
| Wolfe Island | ON_WIS00_GEN | Melancthon Wolfe Wind LP | Wolfe Island | 44.179 | -76.4725 | Ontario.a | Ontario | Gardiner TS | ON_GAR_DSS | 230 | 2009 | 2029 | wind_onshore | wind | 197.8 | 21.14% | 41.8189 | 26.94% | 466.808
| Woolwich | ON_WLW00_GEN | Woolwich Bio-En Inc | Elmira | 43.6043 | -80.5497 | Ontario.a | Ontario | Elmira TS | ON_EMA_DSS | 115 | 2014 | 2034 | biogas | biomass | 2.9 | 94.51% | 2.7409 | 20% | 5.0808
| Yellow Falls | ON_YFL00_GEN | Yellow Falls Power Limited Partnership | Smooth Rock Falls | 49.1242 | -81.6155 | Ontario.b | Ontario | Smooth Rock Falls DS | ON_SRF_DSS | 115 | 2019 | 2059 | hydro_run | hydro_run | 16 | 68.43% | 10.9489 | 65% | 91.104 | [20 empty] | https://www.boralex.com/our-energy-sources/#hydroelectric
| York Energy Centre_01 | ON_YEC01_GEN | York Energy Centre LP | Newmarket | 44.0757 | -79.5309 | Ontario.a | Ontario | York Energy Centre GS | ON_YEC_GSS | 230 | 2012 | 2032 | NG_CT | gasSC | 232 | 85.12% | 197.4705 | 0.4838% | 9.832
| York Energy Centre_02 | ON_YEC02_GEN | York Energy Centre LP | Newmarket | 44.0757 | -79.5309 | Ontario.a | Ontario | York Energy Centre GS | ON_YEC_GSS | 230 | 2012 | 2032 | NG_CT | gasSC | 232 | 85.12% | 197.4705 | 0.4854% | 9.865
| Zephyr | ON_ZPH00_GEN | Schneider Power | Watford | 42.9238 | -81.9063 | Ontario.a | Ontario | Strathroy TS | ON_SRY_DSS | 115 | 2012 | 2032 | wind_onshore | wind | 10 | 21.14% | 2.1142 | 27% | 23.652
Specific Notes:
All hydro facilities less than 10 MW presumed to be hydro_run, unless otherwise verified
IESO Region included for future updates to CREST based on regional generation
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Unless noted otherwise, the wind generating stations are presumed to be connected to the nearest 69 kV substation
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit Hydro_run facilities treated as single-unit facilities

## Storage
ON | EXISTING STORAGE | [15 empty] | DESIGN | [6 empty] | OPERATIONS
| Project Name | Storage Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | 2018 | 2030 | 2050 | Generation Type | Generation Type - COPPER | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Days | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | kV | [7 empty] | (MW) | (MWh) | (Hours) |  | ($M) | (hours) | (hours) | (%) | (days/y) | ($/year) | ($/MWh)
| Ellwood | ON_ELW00_STO | Hydro Ottawa / CIMA | Ottawa | 45.3715 | -75.6472 | Ontario.b | Ontario | Ellwood MTS | ON_ELW_DSS | 230 | 2016 | 2036 |  |  |  | Storage_Lithium | storage | 4 | 2.76 | 0.75 | Grid |  | 0.75 | 0.75 |  |  |  |  | https://www.cima.ca/en/project/ellwood-energy-storage-substation-connected-battery-energy-storage-system/
| Sault Ste. Marie | ON_SSM00_STO | Convergent Energy & Power | Sault Ste. Marie | 46.5205 | -84.2796 | Ontario.b | Ontario | St. Marys TS | ON_SMY_DSS | 115 | 2016 | 2036 |  |  |  | Storage_Lithium | storage | 7 | 7 | 1 | Grid |  | 1 | 1 |  |  |  |  | https://www.convergentep.com/portfolio/sault-ste-marie-on/
| Stratford | ON_STF00_STO | Hecate / Powin | Stratford | 43.3497 | -81.0147 | Ontario.a | Ontario | Stratford TS | ON_STF_DSS | 230 | 2016 | 2036 |  |  |  | Storage_Lithium | storage | 8.8 | 40.4 | 4.5909 | Grid |  | 4.5909 | 4.5909 |  |  |  |  | https://powin.com/solutions
| Kitchener | ON_KTH00_STO | Hecate / Powin | Kitchener | 43.4455 | -80.4558 | Ontario.a | Ontario | Kitchener MTS#5 | ON_KM5_DSS | 115 | 2016 | 2036 |  |  |  | Storage_Lithium | storage | 4 | 12 | 3 | Grid |  | 3 | 3 |  |  |  |  | https://www.renewableenergyworld.com/2018/09/06/powin-energy-to-deliver-70-mwh-in-energy-storage-projects-to-north-america-italy/#gref
| Newmarket | ON_NMK00_STO | Ameresco Newmarket Energy Storage | Newmarket | 44.064 | -79.4264 | Ontario.a | Ontario | Armitage TS | ON_ATG_DSS | 230 | 2016 | 2036 |  |  |  | Storage_ Solid | storage | 4 | 16 | 4 | Grid |  | 4 | 4 |  |  |  |  | https://www.ameresco.com/portfolio-item/newmarket-battery-energy-storage-system-ontario/
| Elmira | ON_EMA00_STO | Nextera Energy | Elmira | 43.6032 | -80.5528 | Ontario.a | Ontario | Elmira TS | ON_EMA_DSS | 115 | 2016 | 2036 |  |  |  | Storage_Lithium | storage | 2 | 8 | 4 | Grid |  | 4 | 4 |  |  |  |  | https://energycentral.com/c/cp/large-battery-energy-storage-systems
| Parry | ON_PRS00_STO | Nextera Energy | Parry Sound | 45.3025 | -79.9454 | Ontario.b | Ontario | Parry Sound TS | ON_PRS_DSS | 230 | 2016 | 2036 |  |  |  | Storage_Lithium | storage | 2 | 8 | 4 | Grid |  | 4 | 4 |  |  |  |  | https://energycentral.com/c/cp/large-battery-energy-storage-systems
| Baseload | ON_BSL00_STO | Baseload Power Corp | Milton | 43.5244 | -79.9115 | Ontario.a | Ontario | Halton TS | ON_HLT_DSS | 230 | 2016 | 2036 |  |  |  | Storage_ Solid | storage | 2 | 8 | 4 | Grid |  | 4 | 4 |  |  |  |  | https://baseloadpower.ca/project/milton-hydro-baseload-power-flow-battery-project/
| Goderich | ON_GOD00_STO | Nstor | Goderich | 43.7539 | -81.7152 | Ontario.a | Ontario | Goderich TS | ON_GOD_DSS | 115 | 2016 | 2036 |  |  |  | Storage_Air | storage | 1.75 | 7 | 4 | Grid |  | 4 | 4 |  |  |  |  | http://nrstor.com/wp-content/uploads/2019/06/CAES.pdf
Specific Notes:
IESO IPP contract durations presumed to be: storage - 20 years

## HydroExisting
ON | EXISTING STORAGE HYDROELECTRIC | [24 empty] | RESERVOIR
| Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Renewal Year | Dam Type | Penstock | Rated Head | Maximum Head | Minimum Head | Operating Flow (Facility) | Rated Discharge (Unit) | Rated Discharge (Facility) | Upstream Reservoir Area | Upstream Reservoir Storage | Turbine Type | Station Flow | Upper Storage Name | Upper Storage Level | Lower Storage Name | Lower Storage Level | Upper Storage Name | Minimum Level | Maximum Level | Initial Level | Low Reference Level | High Reference Level | Low Volume | High Volume | Live Storage | M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10 | M11 | M12 | Notes
|  |  | (MW) | (%) | (MW) |  | (GWh/year) |  |  |  | (m) | (m) | (m) | (m) | (m3/s) | (m3/s) | (m3/s) | (km2) | (hours) |  | (WSC#) |  | (WSC#) |  | (WSC#) |  | (m) | (m) | (m) | (m) | (m) | (m3) | (m3) | (m3) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s)
| Abitibi Canyon | hydro_daily | 355 | 68.43% | 242.9295 | 30.06% | 934.738 | 5
| Aguasabon | hydro_daily | 52 | 68.43% | 35.584 | 62.93% | 286.643 | 2
| Arnprior Hydro | hydro_daily | 82 | 68.43% | 56.1133 | 21.14% | 151.873 | 2
| Aubrey Falls | hydro_daily | 146 | 68.43% | 99.909 | 13.13% | 167.936
| Chats Falls | hydro_daily | 200 | 68.43% | 136.8617 | 61.93% | 1085.062 | 8
| Chenaux | hydro_daily | 158 | 68.43% | 108.1207 | 49.06% | 679.096 | 8
| Decew Falls 1 | hydro_daily | 144 | 68.43% | 98.5404 | 46.54% | 587.101 | 5
| Des-Joachims | hydro_daily | 475 | 68.43% | 325.0464 | 51.19% | 2129.832 | 8
| Harmon_01 | hydro_daily | 156 | 68.43% | 106.7521 | 25.64% | 540.086 | 2 | [38 empty] | Operated as separate facilities
| Harmon_02 | hydro_daily | 78 | 68.43% | 53.376 | 27.77% | 189.73 | 1 | [38 empty] | Operated as separate facilities
| Hollingsworth | hydro_daily | 23 | 68.43% | 15.7391 | 54.68% | 110.164
| Iroquois Falls Hydro | hydro_daily | 29.7 | 68.43% | 20.324 | 58.01% | 150.9257
| Island Falls | hydro_daily | 44.3 | 68.43% | 30.3149 | 58.01% | 225.1182
| Kipling_01 | hydro_daily | 166 | 68.43% | 113.5952 | 22.82% | 331.843 | 2 | [38 empty] | Operated as separate facilities
| Kipling_02 | hydro_daily | 79 | 68.43% | 54.0604 | 22.58% | 156.239 | 1 | [38 empty] | Operated as separate facilities
| Little Long_01 | hydro_daily | 144 | 68.43% | 98.5404 | 15.83% | 199.71 | 2 | [38 empty] | Operated as separate facilities
| Little Long_02 | hydro_daily | 75 | 68.43% | 51.3231 | 29.53% | 194.017 | 1 | [38 empty] | Operated as separate facilities
| Lower Notch | hydro_daily | 274 | 68.43% | 187.5005 | 13.55% | 325.151 | 2
| MacKay | hydro_daily | 62 | 68.43% | 42.4271 | 46.4% | 251.996
| Mission | hydro_daily | 15 | 68.43% | 10.2646 | 36.33% | 47.742
| Mountain Chute | hydro_daily | 173 | 68.43% | 118.3853 | 20.18% | 305.854 | 2
| Otter Rapids | hydro_daily | 189 | 68.43% | 129.3343 | 26.95% | 446.157 | 4
| Otto Holden | hydro_daily | 265 | 68.43% | 181.3417 | 47.19% | 1095.498 | 8
| Pine Portage | hydro_daily | 151 | 68.43% | 103.3306 | 35.93% | 475.248 | 4
| Rayner | hydro_daily | 42 | 68.43% | 28.7409 | 31.61% | 116.312
| Red Rock Falls | hydro_daily | 37 | 68.43% | 25.3194 | 58.79% | 190.557
| Smoky Falls | hydro_daily | 264 | 68.43% | 180.6574 | 26.25% | 607.1 | 3
| Stewartville | hydro_daily | 186 | 68.43% | 127.2813 | 18.19% | 296.37 | 5
| Twin Falls H2O | hydro_daily | 27.5 | 68.43% | 18.8185 | 58.01% | 139.7461
| Wells | hydro_daily | 220 | 68.43% | 150.5478 | 13.26% | 255.642
General Notes:
Hydroelectric generation type has been estimated based on available information concerning operations, reservoir size and operations, facility location and design flows.
The WSC# refers to the Water Survey of Canada Hydrometric station

## HydroRenewals
ON | HYDROELECTRIC RENEWAL | [7 empty] | EXISTING DESIGN |  |  |  |  | RENEWAL | [7 empty] | COSTS |  | 1.77% | 1.05 |  |  | 7% | 70
| Existing Project Name | Owner | Location | Connecting Node Name | Connecting Node Code | Substation Voltage | Start Year | Turbine Renewal Year | Generation Type | Installed Capacity | Dependable Capacity | Annual Average Energy Plant | Existing #units | Renewal Project Name | Renewal Project Code | COPPER Balancing Area | Distance to Market Grid | Generator Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Additional Annual Energy | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed Cost Existing Project | Fixed Cost Renewed Project | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
[10 empty] | (MW) | (MW) | (GWh/year) |  |  |  |  | (km) |  | (MW) | (MW) | (GWh/year) | ($2017M) | ($2018M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M/year) | ($/kW-year) | ($/year) | ($/year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
NONE
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroGreenfield
ON | HYDROELECTRIC GREENFIELD | [10 empty] | DESIGN | [6 empty] | COSTS |  | 1.77% | 1.05 |  |  | 7% | 70
| Project Name | Project Code | Owner | Location (River) | Latitude | Longitude | Balancing Area | Distance to Market Grid | Connecting Node Name | Connecting Node Code | Substation Voltage | Generation Type | Generation Type - COPPER | Installed Capacity | Effective Capacity | Average Annual Energy - Plant | Capacity Factor | # of units | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Fixed O&M | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Construction Time | Development Time | Notes
[8 empty] | (km) |  |  | (kV) |  |  | (MW) | (MW) | (GWh/year) | (%) |  | ($2013M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($2013M/y) | ($2018M/y) | ($2018/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | (years) | (years)
| 16km Rapids | GF_ON01 | TBD | Groundhog River | 49.0211 | -82.1485 | Ontario.b | 110 | Porcupine TS | ON_PCP_SUB | 500 | hydro_daily | hydro_daily | 23.6 | 23.6 | 148 | 71.59% |  | 148 | 160.7333 | 2.845 | -5.4005 | 158.1779 | 29.6076 | 187.7855 | 13.2613 | 561.9204 | 1.24 | 1.3467 | 57062.9136 | 4.1925 | 3.8 | 7.9925 | 6 | 11
| Allan Rapids | GF_ON02 | TBD | Abitibi River | 51.0503 | -80.9074 | Ontario.b | 160 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 131 | 131 | 308 | 26.84% |  | 678 | 736.3325 | 13.0331 | 15.2023 | 764.5679 | 86.2208 | 850.7887 | 60.0823 | 458.6435 | 4.07 | 4.4202 | 33741.7322 | 2.1746 | 3.8 | 5.9746 | 7 | 13
| Atik Island | GF_ON03 | TBD | Winisk River | 54.7766 | -86.6736 | Ontario.b | 670 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 64.34 | 64.34 | 374 | 66.36% |  | 353 | 383.3707 | 6.7857 | -12.8808 | 377.2756 | 53.3959 | 430.6715 | 30.4138 | 472.7047 | 2.34 | 2.5413 | 39498.3598 | 2.8553 | 3.8 | 6.6553 | 6 | 11
| Biglow Baseload | GF_ON04 | TBD | Albany River | 52.0958 | -82.2226 | Ontario.b | 275 | Pinard TS | ON_PIN_SUB | 500 | hydro_monthly | hydro_monthly | 225 | 225 | 1334 | 67.68% |  | 1135 | 1232.651 | 21.8179 | 25.4493 | 1279.9182 | 122.2968 | 1402.2151 | 99.0238 | 440.1056 | 6.21 | 6.7443 | 29974.5963 | 1.7677 | 3.8 | 5.5677 | 7 | 13 | Baseload facility with live storage
| Biglow Peaking | GF_ON05 | TBD | Albany River | 52.0958 | -82.2226 | Ontario.b | 275 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 480 | 480 | 1601 | 38.08% |  | 2295 | 2492.4528 | 44.1164 | 51.4592 | 2588.0284 | 197.1792 | 2785.2076 | 196.69 | 409.7709 | 11.2 | 12.1636 | 25340.8423 | 1.3224 | 3.8 | 5.1224 | 7 | 13 | Peaking facility
| Black Smith Rapids | GF_ON06 | TBD | Abitibi River | 50.6067 | -81.41 | Ontario.b | 105 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 140 | 140 | 270 | 22.02% |  | 709 | 769.9996 | 13.629 | 15.8974 | 799.526 | 88.876 | 888.402 | 62.7385 | 448.1323 | 4.29 | 4.6591 | 33279.249 | 2.12 | 3.8 | 5.92 | 7 | 13
| Blackbear Island Baseload | GF_ON07 | TBD | Albany River | 51.7237 | -83.1369 | Ontario.b | 260 | Pinard TS | ON_PIN_SUB | 500 | hydro_monthly | hydro_monthly | 240 | 240 | 1420 | 67.54% |  | 1242 | 1348.8568 | 23.8748 | 27.8485 | 1400.5801 | 130.0044 | 1530.5845 | 108.0892 | 450.3715 | 6.53 | 7.0918 | 29549.2321 | 1.7245 | 3.8 | 5.5245 | 7 | 13 | Baseload facility with live storage
| Blackbear Island Peaking | GF_ON08 | TBD | Albany River | 51.7237 | -83.1369 | Ontario.b | 260 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 490 | 490 | 1705 | 39.72% |  | 2377 | 2581.5078 | 45.6927 | 53.2978 | 2680.4983 | 201.9316 | 2882.4299 | 203.5558 | 415.4201 | 11.38 | 12.3591 | 25222.6343 | 1.312 | 3.8 | 5.112 | 7 | 13 | Peaking facility
| Buffaloskin | GF_ON09 | TBD | Albany River | 51.7 | -86 | Ontario.b | 395 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 76 | 76 | 269 | 40.4% |  | 409 | 444.1888 | 7.8621 | -14.9242 | 437.1267 | 59.0053 | 496.1319 | 35.0366 | 461.0079 | 2.67 | 2.8997 | 38154.1629 | 2.6788 | 3.8 | 6.4788 | 6 | 11
| Chard Baseload | GF_ON10 | TBD | Albany River | 51.2927 | -85.0079 | Ontario.b | 315 | Pinard TS | ON_PIN_SUB | 500 | hydro_monthly | hydro_monthly | 210 | 210 | 1220 | 66.32% |  | 1292 | 1403.1586 | 24.8359 | 28.9696 | 1456.9642 | 133.5324 | 1590.4965 | 112.3201 | 534.8577 | 5.88 | 6.3859 | 30409.0107 | 1.815 | 3.8 | 5.615 | 7 | 13 | Baseload facility with live storage
| Chard Peaking | GF_ON11 | TBD | Albany River | 51.2927 | -85.0079 | Ontario.b | 315 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 370 | 370 | 1464 | 45.17% |  | 2027 | 2201.3952 | 38.9647 | 45.45 | 2285.8099 | 181.249 | 2467.0589 | 174.2225 | 470.8717 | 9.15 | 9.9372 | 26857.3792 | 1.4611 | 3.8 | 5.2611 | 7 | 13 | Peaking facility
| Coral Rapids | GF_ON12 | TBD | Abitibi River | 50.2422 | -81.6632 | Ontario.b | 65 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 192 | 192 | 285 | 16.94% |  | 955 | 1037.1645 | 18.3578 | 21.4133 | 1076.9356 | 108.7778 | 1185.7134 | 83.7345 | 436.1173 | 5.49 | 5.9623 | 31053.8447 | 1.8784 | 3.8 | 5.6784 | 7 | 13
| Cypress Falls | GF_ON13 | TBD | Mattagami River | 49.6967 | -81.8917 | Ontario.b | 55 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 42.4 | 42.4 | 137 | 36.89% |  | 229 | 248.7023 | 4.402 | -8.3561 | 244.7482 | 39.8116 | 284.5598 | 20.0955 | 473.95 | 1.69 | 1.8354 | 43287.7595 | 3.3498 | 3.8 | 7.1498 | 6 | 11
| Eskakwa Falls | GF_ON14 | TBD | Albany River | 51.4917 | -88.9183 | Ontario.b | 575 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 46.68 | 46.68 | 246 | 60.16% |  | 419 | 455.0491 | 8.0544 | -15.2891 | 447.8143 | 59.9802 | 507.7945 | 35.8602 | 768.2136 | 1.82 | 1.9766 | 42343.3097 | 3.2286 | 3.8 | 7.0286 | 6 | 11
| Frenchmans Rapids | GF_ON15 | TBD | Albany River | 51.38 | -87.79 | Ontario.b | 495 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 34.9 | 34.9 | 264 | 86.35% |  | 193 | 209.605 | 3.71 | -7.0425 | 206.2725 | 35.4503 | 241.7228 | 17.0703 | 489.1217 | 1.71 | 1.8571 | 53212.6569 | 3.609 | 3.8 | 7.409 | 6 | 11
| Gneiss Rapids | GF_ON16 | TBD | Winisk River | 53.8277 | -87.0286 | Ontario.b | 605 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 20.6 | 20.6 | 115 | 63.73% |  | 118 | 128.1523 | 2.2683 | -4.3058 | 126.1148 | 25.39 | 151.5048 | 10.6992 | 519.3784 | 1.39 | 1.5096 | 73281.0765 | 4.4165 | 3.8 | 8.2165 | 6 | 11
| Grand Rapids | GF_ON17 | TBD | Mattagami River | 50.4029 | -81.8162 | Ontario.b | 75 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 174 | 174 | 707 | 46.38% |  | 911 | 989.3789 | 17.512 | 20.4267 | 1027.3176 | 105.3521 | 1132.6697 | 79.9886 | 459.7046 | 5.08 | 5.5171 | 31707.2608 | 1.9506 | 3.8 | 5.7506 | 7 | 13
| Grey Goose | GF_ON18 | TBD | Moose River | 50.7772 | -81.3957 | Ontario.b | 125 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 140 | 140 | 606 | 49.41% |  | 716 | 777.6018 | 13.7636 | 16.0544 | 807.4198 | 89.4703 | 896.8901 | 63.338 | 452.414 | 4.3 | 4.67 | 33356.823 | 2.12 | 3.8 | 5.92 | 7 | 13
| Hat Island Baseload | GF_ON19 | TBD | Albany River | 51.3433 | -83.8051 | Ontario.b | 250 | Pinard TS | ON_PIN_SUB | 500 | hydro_monthly | hydro_monthly | 250 | 250 | 1396 | 63.74% |  | 1291 | 1402.0726 | 24.8167 | 28.9472 | 1455.8365 | 133.4622 | 1589.2987 | 112.2355 | 448.9421 | 6.74 | 7.3199 | 29279.5332 | 1.6978 | 3.8 | 5.4978 | 7 | 13 | Baseload facility with live storage
| Hat Island Peaking | GF_ON20 | TBD | Albany River | 51.3433 | -83.8051 | Ontario.b | 250 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 490 | 490 | 1676 | 39.05% |  | 2380 | 2584.7659 | 45.7504 | 53.3651 | 2683.8813 | 202.1045 | 2885.9858 | 203.807 | 415.9326 | 11.38 | 12.3591 | 25222.6343 | 1.312 | 3.8 | 5.112 | 7 | 13 | Peaking facility
| Kagiami Falls | GF_ON21 | TBD | Albany River | 51.4501 | -86.7334 | Ontario.b | 430 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 55.1 | 55.1 | 294 | 60.91% |  | 320 | 347.5316 | 6.1513 | -11.6767 | 342.0062 | 49.9564 | 391.9626 | 27.6802 | 502.3633 | 2.47 | 2.6825 | 48684.3768 | 3.0299 | 3.8 | 6.8299 | 6 | 11
| Long Rapids | GF_ON22 | TBD | Missinaibi River | 50.1023 | -83.2092 | Ontario.b | 80 | Hearst TS | ON_HST_SUB | 115 | hydro_daily | hydro_daily | 126 | 126 | 592 | 53.63% |  | 799 | 867.7428 | 15.359 | 17.9154 | 901.0173 | 96.3815 | 997.3988 | 70.4358 | 559.0146 | 3.95 | 4.2898 | 34046.3697 | 2.2073 | 3.8 | 6.0073 | 7 | 13
| Maminiska | GF_ON23 | TBD | Winisk River | 54.8293 | -85.5597 | Ontario.b | 635 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 73 | 73 | 416 | 65.05% |  | 426 | 462.6514 | 8.1889 | 9.5519 | 480.3922 | 62.9068 | 543.299 | 38.3675 | 525.5824 | 4.05 | 4.3984 | 60252.6876 | 2.7205 | 3.8 | 6.5205 | 7 | 13
| Martin Falls | GF_ON24 | TBD | Albany River | 51.5333 | -86.5167 | Ontario.b | 420 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 42.93 | 42.93 | 229 | 60.89% |  | 244 | 264.9928 | 4.6904 | -8.9035 | 260.7797 | 41.5626 | 302.3423 | 21.3513 | 497.3509 | 1.71 | 1.8571 | 43259.2995 | 3.3339 | 3.8 | 7.1339 | 6 | 11
| Newpost Creek Mouth | GF_ON25 | TBD | Newpost Creek | 49.9903 | -81.5305 | Ontario.b | 50 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 26.83 | 26.83 | 31 | 13.19% |  | 149 | 161.8194 | 2.8642 | -5.437 | 159.2466 | 29.7432 | 188.9898 | 13.3464 | 497.4421 | 1.19 | 1.2924 | 48169.3237 | 3.9915 | 3.8 | 7.7915 | 6 | 11
| Nine Mile Rapids | GF_ON26 | TBD | Abitibi River | 50.3812 | -81.586 | Ontario.b | 80 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 295 | 295 | 555 | 21.48% |  | 1472 | 1598.6451 | 28.296 | 33.0056 | 1659.9468 | 145.8864 | 1805.8332 | 127.5271 | 432.2952 | 7.67 | 8.3299 | 28236.9385 | 1.5935 | 3.8 | 5.3935 | 7 | 13
| Nottik Island | GF_ON27 | TBD | Albany River | 51.6611 | -86.3885 | Ontario.b | 415 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 50 | 50 | 264 | 60.27% |  | 281 | 305.1761 | 5.4016 | -10.2536 | 300.3242 | 45.7404 | 346.0646 | 24.4389 | 488.7784 | 1.92 | 2.0852 | 41703.7861 | 3.1448 | 3.8 | 6.9448 | 6 | 11
| Sand And Adjacent Rapids | GF_ON28 | TBD | Abitibi River | 50.8502 | -81.1084 | Ontario.b | 150 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 64.64 | 64.64 | 243 | 42.91% |  | 348 | 377.9406 | 6.6895 | -12.6984 | 371.9317 | 52.8817 | 424.8134 | 30.0001 | 464.1108 | 2.35 | 2.5522 | 39483.0574 | 2.8502 | 3.8 | 6.6502 | 6 | 11
| Sand Rapids | GF_ON29 | TBD | Abitibi River | 50.8502 | -81.1084 | Ontario.b | 140 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 131 | 131 | 308 | 26.84% |  | 671 | 728.7302 | 12.8985 | 15.0454 | 756.6741 | 85.6159 | 842.2901 | 59.4821 | 454.062 | 4.07 | 4.4202 | 33741.7322 | 2.1746 | 3.8 | 5.9746 | 7 | 13
| Seashell Rapids | GF_ON30 | TBD | Winisk River | 53.7015 | -87.0354 | Ontario.b | 590 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 31.9 | 31.9 | 200 | 71.57% |  | 181 | 196.5725 | 3.4793 | -6.6046 | 193.4472 | 33.9396 | 227.3869 | 16.058 | 503.3841 | 1.52 | 1.6508 | 51748.4285 | 3.7354 | 3.8 | 7.5354 | 6 | 11
| Shamattawa | GF_ON31 | TBD | Winisk River | 54.9954 | -85.4144 | Ontario.b | 650 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 76 | 76 | 408 | 61.28% |  | 441 | 478.9419 | 8.4773 | 9.8882 | 497.3074 | 64.4011 | 561.7085 | 39.6676 | 521.942 | 3.6 | 3.9097 | 51443.8151 | 2.6788 | 3.8 | 6.4788 | 7 | 13
| Stooping Baseload | GF_ON32 | TBD | Albany River | 52.2512 | -81.7573 | Ontario.b | 285 | Pinard TS | ON_PIN_SUB | 500 | hydro_monthly | hydro_monthly | 130 | 130 | 792 | 69.55% |  | 703 | 763.4834 | 13.5137 | 15.7629 | 792.7599 | 88.3651 | 881.125 | 62.2246 | 478.651 | 4.05 | 4.3984 | 33834.2015 | 2.181 | 3.8 | 5.981 | 7 | 13 | Baseload facility with live storage
| Stooping Peaking | GF_ON33 | TBD | Albany River | 52.2512 | -81.7573 | Ontario.b | 285 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 285 | 285 | 951 | 38.09% |  | 1427 | 1549.7735 | 27.431 | 31.9966 | 1609.2011 | 142.8457 | 1752.0469 | 123.7287 | 434.1359 | 7.46 | 8.1018 | 28427.4712 | 1.6147 | 3.8 | 5.4147 | 7 | 13 | Peaking facility
| Thunder House Falls & Chute | GF_ON34 | TBD | Missinaibi River | 50.0533 | -83.1833 | Ontario.b | 80 | Hearst TS | ON_HST_SUB | 115 | hydro_daily | hydro_daily | 29.2 | 29.2 | 156 | 60.99% |  | 167 | 181.368 | 3.2102 | -6.0938 | 178.4845 | 32.1358 | 210.6202 | 14.8739 | 509.3802 | 1.68 | 1.8245 | 62484.2686 | 3.8641 | 3.8 | 7.6641 | 6 | 11
| Wabimeig Creek Peaking | GF_ON35 | TBD | Albany River | 51.6459 | -85.6472 | Ontario.b | 375 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 185 | 185 | 601 | 37.09% |  | 946 | 1027.3901 | 18.1848 | 21.2115 | 1066.7865 | 108.0813 | 1174.8678 | 82.9686 | 448.479 | 5.33 | 5.7886 | 31289.5805 | 1.9053 | 3.8 | 5.7053 | 7 | 13 | Peaking facility
| Wabimeig Creek Baseload | GF_ON36 | TBD | Albany River | 51.6459 | -85.6472 | Ontario.b | 375 | Pinard TS | ON_PIN_SUB | 500 | hydro_monthly | hydro_monthly | 100 | 100 | 500 | 57.08% |  | 541 | 587.5455 | 10.3996 | 12.1305 | 610.0755 | 73.9788 | 684.0543 | 48.3076 | 483.0759 | 3.3 | 3.5839 | 35839.1912 | 2.4115 | 3.8 | 6.2115 | 7 | 13 | Baseload facility with live storage
| Winisk PO | GF_ON37 | TBD | Winisk River | 55.2234 | -85.2288 | Ontario.b | 670 | Pinard TS | ON_PIN_SUB | 500 | hydro_daily | hydro_daily | 50.8 | 50.8 | 288 | 64.72% |  | 289 | 313.8644 | 5.5554 | -10.5455 | 308.8743 | 46.6198 | 355.4942 | 25.1048 | 494.1896 | 3.17 | 3.4427 | 67770.3628 | 3.1257 | 3.8 | 6.9257 | 6 | 11
Specific Notes:
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroPS
ON | HYDROELECTRIC PUMPED STORAGE | [15 empty] | Existing Facility | [8 empty] | Reservoir Design | [12 empty] | Costs | 1.77% | 1.06 |  |  | 7% | 70
| Pumped Storage Project | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Installed Capacity | Dependable Capacity | Estimated Round Trip Efficiency | Existing Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Salt/Fresh | Reservoir Types | Reservoir Storage | Storage Requirement | Gross Head | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping) | Turbine Type | Pump Type | Pumping Duration at Peak Output | Generation Duration at Peak Output | Total Footprint | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Cost of Capacity | Unit Cost of Stored Energy | Levelized Cost | Construction Time | Development Time | Notes
[5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) |  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) |  |  |  |  | (m3) | (MWh) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2018/MW) | ($2018/MWh) | ($2018/kW-year) | (years) | (years)
| Marmora Pumped Storage | PS_MAR | Northland Power | Marmora | 44.4818 | 77.6589 | Ontario.a | Havelock | ON_HVL_SUB | 230 | 20 | hydro_pump | hydro_pump | 400 | 400 | 80% | No Existing Project | [8 empty] | Fresh | Man Made | [11 empty] | 900 | 15.93 | 178.6647 | 1094.5947 | 54.9924 | 1149.5871 | 81.1833 | 202.9582 | 18593.5534 | 1.4181 | 0 | 1.4181 |  |  |  | 5 | 8
| Meaford Pumped Storage | PS_MEA | TC Energy | Meaford | 44.6649 | 80.675 | Ontario.a | Meaford | ON_MEA_SUB | 138 | 50 | hydro_pump | hydro_pump | 1000 | 1000 | 80% | No Existing Project | [8 empty] | Fresh | Man Made / Natural | [11 empty] | 2800 | 49.56 | 555.8457 | 3405.4057 | 118.7671 | 3524.1729 | 248.8754 | 248.8754 | 12010.0554 | 0.99838 | 0 | 0.99838 |  |  |  | 5 | 8
Specific Notes:
Loaded Capital Cost presumed to be the equivalent of Implementation Costs, namely they include Capital Overhead and IDC
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## Transmission
ON | EXISTING TRANSMISSION
| Circuit ID | Owner | Operating Region | Number of Circuits | Current | Length | Length | Voltage | Reactance | Smax | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes | Count
[5 empty] | (ad/dc) | (km) | (miles) | (kV) | (ohm) |  | (A) | (A) | (MVA) | (MVA) |  | (MW) | (MW)
| A36N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Murray TS | ON_MRY_DSS | Station 11 SWS | ON_S11_SWS | CNPI. 2014. Transmission Revenue Requirement Application |  | 50
| A37N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Murray TS | ON_MRY_DSS | Station 11 SWS | ON_S11_SWS | CNPI. 2014. Transmission Revenue Requirement Application |  | 54
| CNPI2 | CNPI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Station 11 SWS | ON_S11_SWS | Station 17 TS | ON_S17_DSS | CNPI. 2014. Transmission Revenue Requirement Application | Also called "L2" | 530
| CNPI2 | CNPI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Station 17 TS | ON_S17_DSS | Station 18 TS | ON_S18_DSS | CNPI. 2014. Transmission Revenue Requirement Application | Also called "L2" | 531
| CNPI46 | CNPI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 48 | 48 | Station 18 TS | ON_S18_DSS | INT Peace Bridge | XX_ONUS7_INT | CNPI. 2014. Transmission Revenue Requirement Application | Also called "L46" | 532
| A41T | HONI | Ontario | 1 | ac | 21 | 12.963 | 230 | 10.08 | 3 | [5 empty] | 402 | 435 | Hawthorne TS | ON_HWT_TSS | IPT Outaouais | PP_ONQB2_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 63
| A42T | HONI | Ontario | 1 | ac | 21 | 12.963 | 230 | 10.08 | 3 | [5 empty] | 402 | 435 | Hawthorne TS | ON_HWT_TSS | IPT Outaouais | PP_ONQB2_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 64
| B3N | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 230 | 0.144 | 3 | [5 empty] | 402 | 435 | Sarnia Scott JCT | ON_SNS_JCT | Sarnia Scott TS | ON_SNS_TSS | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 251
| B3N | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 230 | 1.152 | 3 | [5 empty] | 402 | 435 | Sarnia Scott JCT | ON_SNS_JCT | Vidal JCT | ON_VDL_JCT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 252
| B3N | HONI | Ontario | 1 | ac | 0.7 | 0.4321 | 230 | 0.336 | 3 | [5 empty] | 402 | 435 | Vidal JCT | ON_VDL_JCT | Sun Oil Co JCT | ON_SOC_JCT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 253
| B3N | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 230 | 1.152 | 3 | [5 empty] | 590 | 590 | Sun Oil Co JCT | ON_SOC_JCT | INT Bunce Creek | XX_ONUS2_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 254
| BP76 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 480 | 480 | Beck #2 TS | ON_BK2_TSS | INT Niagara | XX_ONUS5_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 367
| BSC105 | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Parks TS | ON_PKS_DSS | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 368
| BSC105 | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 0 | 0 | Parks TS | ON_PKS_DSS | INT Niagara | XX_ONUS5_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 369
| D3K | HONI | Ontario | 1 | ac | 14.5 | 8.9506 | 115 | 6.0486 | 3 | [5 empty] | 98.4491 | 108.4016 | Nine Mile JCT | ON_NIN_JCT | Dymond TS | ON_DYM_DSS | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 608
| D4Z | HONI | Ontario | 1 | ac | 14.5 | 8.9506 | 115 | 6.0486 | 3 | [5 empty] | 98.4491 | 108.4016 | Dymond TS | ON_DYM_DSS | Nine Mile JCT | ON_NIN_JCT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 617
| D4Z | HONI | Ontario | 1 | ac | 15.5 | 9.5679 | 115 | 6.4657 | 3 | [5 empty] | 98.4491 | 108.4016 | Nine Mile JCT | ON_NIN_JCT | IPT Dymond | PP_ONQB7_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 618
| D5A | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Cumberland JCT | ON_CUM_JCT | IPT Masson | PP_ONQB3_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 623
| F3M | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 150 | 150 | H2O Power Fort Frances GS | ON_H2F_GSS | INT Minnesota | XX_ONUS1_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 789
| H4Z | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Otto Holden TS | ON_OTH_DSS | IPT Kipawa | PP_ONQB6_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 889
| H9A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gamble H9A JCT | ON_GAM_JCT | IPT Masson | PP_ONQB3_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 938
| J5D | HONI | Ontario | 1 | ac | 1.8 | 1.1111 | 115 | 0.75086 | 3 | [5 empty] | 570 | 570 | Keith TS | ON_KEI_DSS | INT Waterman | XX_ONUS4_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 990
| K21W | HONI | Ontario | 1 | ac | 63 | 38.8889 | 230 | 30.24 | 3 | [5 empty] | 402 | 435 | Kenora TS | ON_KNO_TSS | IPT Whiteshell | PP_ONMB2_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1014
| K22W | HONI | Ontario | 1 | ac | 63 | 38.8889 | 230 | 30.24 | 3 | [5 empty] | 402 | 435 | Kenora TS | ON_KNO_TSS | IPT Whiteshell | PP_ONMB2_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1015
| L33P | HONI | Ontario | 1 | ac | 4.3 | 2.6543 | 230 | 2.064 | 3 | [5 empty] | 0 | 0 | St. Lawrence TS | ON_STL_DSS | INT Massena Cornwall | XX_ONUS6_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1239
| L34P | HONI | Ontario | 1 | ac | 4.3 | 2.6543 | 230 | 2.064 | 3 | [5 empty] | 0 | 0 | St. Lawrence TS | ON_STL_DSS | INT Massena Cornwall | XX_ONUS6_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1240
| L4D | HONI | Ontario | 1 | ac | 4 | 2.4691 | 345 | 1.7752 | 3 | [5 empty] | 845 | 845 | Lambton TS #2 | ON_LMB_DSS | INT St. Clair | XX_ONUS3_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1247
| L51D | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 230 | 0.528 | 3 | [5 empty] | 0 | 0 | Lambton TS #2 | ON_LMB_DSS | INT St. Clair | XX_ONUS3_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1250
| N4S | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 115 | 1.0011 | 3 | [5 empty] | 98.4491 | 108.4016 | Sarnia Scott TS | ON_SNS_TSS | Vidal JCT | ON_VDL_JCT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1464
| N6S | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 230 | 0.144 | 3 | [5 empty] | 402 | 435 | Sarnia Scott JCT | ON_SNS_JCT | Sarnia Scott TS | ON_SNS_TSS | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1481
| N6S | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 230 | 1.152 | 3 | [5 empty] | 402 | 435 | Sarnia Scott JCT | ON_SNS_JCT | Vidal JCT | ON_VDL_JCT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1482
| N7S | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 230 | 0.144 | 3 | [5 empty] | 402 | 435 | Sarnia Scott JCT | ON_SNS_JCT | Sarnia Scott TS | ON_SNS_TSS | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1489
| P33C | HONI | Ontario | 1 | ac | 8.9 | 5.4938 | 230 | 4.272 | 3 | [5 empty] | 402 | 435 | Chats Falls SWS | ON_CHF_SWS | IPT Chats Falls | PP_ONQB4_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1550
| PA27 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 0 | 0 | Beck #2 TS | ON_BK2_TSS | INT Niagara | XX_ONUS5_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1598
| PA301 | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 345 | 0.17752 | 3 | [5 empty] | 990 | 990 | Beck #2 TS | ON_BK2_TSS | INT Niagara | XX_ONUS5_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1599
| PA302 | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 345 | 0.17752 | 3 | [5 empty] | 0 | 0 | Beck #2 TS | ON_BK2_TSS | INT Niagara | XX_ONUS5_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1600
| Q4C | HONI | Ontario | 1 | ac | 5.8 | 3.5802 | 230 | 2.784 | 3 | [5 empty] | 402 | 435 | Chats Falls SWS | ON_CHF_SWS | IPT Chats Falls | PP_ONQB4_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1712
| SK1 | HONI | Ontario | 1 | ac | 19 | 11.7284 | 115 | 7.9257 | 3 | [5 empty] | 98.4491 | 108.4016 | Forgie JCT | ON_FRG_JCT | IPT Seven Sisters | PP_ONMB1_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1893
| UB3B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 0 | 0 | H2O Power Fort Frances GS | ON_H2F_GSS | INT Minnesota | XX_ONUS1_INT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 1991
| X2Y | HONI | Ontario | 1 | ac | 3.4 | 2.0988 | 115 | 1.4183 | 3 | [5 empty] | 98.4491 | 108.4016 | Chenaux JCT | ON_CHX_JCT | IPT Chenaux | PP_ONQB5_IPT | HONI. 2014. 2015/2016 Transmission Revenue Requirements and Rate Settlement (EB-2014-0140) - Tab 11 Association of Major Power Producers of Ontario (APPrO) |  | 2165
| M29C | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Merivale TS | ON_MER_TSS | Terry Fox JCT | ON_TRF_JCT | Hydro One and Hydro Ottawa. 2019. South Nepean Project - Application and Evidence (EB-2019-0077) |  | 1334
| M29C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Terry Fox JCT | ON_TRF_JCT | Terry Fox MTS | ON_TRF_DSS | Hydro One and Hydro Ottawa. 2019. South Nepean Project - Application and Evidence (EB-2019-0077) |  | 1335
| M29C | HONI | Ontario | 1 | ac | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Terry Fox JCT | ON_TRF_JCT | Almonte TS | ON_ALM_DSS | Hydro One and Hydro Ottawa. 2019. South Nepean Project - Application and Evidence (EB-2019-0077) |  | 1336
| M29C | HONI | Ontario | 1 | ac | 278 | 171.6049 | 230 | 133.44 | 1.4246 | [5 empty] | 190.8966 | 206.5673 | Almonte TS | ON_ALM_DSS | Cherrywood TS | ON_CHW_DSS | Hydro One and Hydro Ottawa. 2019. South Nepean Project - Application and Evidence (EB-2019-0077) |  | 1337
| B40C | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Burlington TS | ON_BUR_DSS | Cumberland TS | ON_CUM_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 263
| B41C | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Burlington TS | ON_BUR_DSS | Cumberland TS | ON_CUM_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 264
| B4V | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Orangeville TS | ON_ORA_DSS | Amaranth JCT | ON_AMA_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 267
| B4V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Amaranth JCT | ON_AMA_JCT | Amaranth TS | ON_AMA_ISS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 268
| B8W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Brant JCT | ON_BRT_JCT | Brant TS | ON_BRT_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 362
| B8W | HONI | Ontario | 1 | ac | 29 | 17.9012 | 115 | 12.0971 | 3 | [5 empty] | 98.4491 | 108.4016 | Brant JCT | ON_BRT_JCT | Toyota Woodstock JCT | ON_TYW_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 363
| B8W | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Toyota Woodstock JCT | ON_TYW_JCT | Toyota Woodstock TS | ON_TYW_ISS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 364
| B8W | HONI | Ontario | 1 | ac | 5.5 | 3.3951 | 115 | 2.2943 | 3 | [5 empty] | 98.4491 | 108.4016 | Toyota Woodstock JCT | ON_TYW_JCT | Commerce Way JCT | ON_CMC_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 365
| B8W | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Commerce Way JCT | ON_CMC_JCT | Commerce Way TS | ON_CMC_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 366
| H29 | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Hurontario SWS | ON_HRN_SWS | Pleasant TS | ON_PLE_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 871
| H30 | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Hurontario SWS | ON_HRN_SWS | Pleasant TS | ON_PLE_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 880
| M31W | HONI | Ontario | 1 | ac | 65 | 40.1235 | 230 | 31.2 | 3 | [5 empty] | 402 | 435 | Salford JCT | ON_SFD_JCT | Carluke JCT | ON_CLK_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1372
| M31W | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1373
| M32W | HONI | Ontario | 1 | ac | 53 | 32.716 | 230 | 25.44 | 3 | [5 empty] | 402 | 435 | Salford JCT | ON_SFD_JCT | Newport JCT | ON_NWP_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1381
| M32W | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Newport JCT | ON_NWP_JCT | Brantford TS | ON_BRF_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1382
| M32W | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Newport JCT | ON_NWP_JCT | Carluke JCT | ON_CLK_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1383
| M32W | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1384
| M33W | HONI | Ontario | 1 | ac | 53 | 32.716 | 230 | 25.44 | 3 | [5 empty] | 402 | 435 | Salford JCT | ON_SFD_JCT | Newport JCT | ON_NWP_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1386
| M33W | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Newport JCT | ON_NWP_JCT | Brantford TS | ON_BRF_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1387
| M33W | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Newport JCT | ON_NWP_JCT | Carluke JCT | ON_CLK_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1388
| M33W | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1389
| NA64M28 | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Alford JCT | ON_ALF_JCT | Mohawk Str 31 EP JCT | ON_MHS_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1500
| V42H | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Goreway JCT | ON_GRW_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2003
| V42H | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Goreway JCT | ON_GRW_JCT | Goreway TS | ON_GRW_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2004
| V42H | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Sithe Goreway JCT | ON_SGW_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2005
| V42H | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Sithe Goreway JCT | ON_SGW_JCT | Bramalea TS | ON_BML_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2006
| V42H | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Bramalea TS | ON_BML_DSS | Cardiff JCT | ON_CDF_JCT | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2007
| V42H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Cardiff JCT | ON_CDF_JCT | Cardiff TS | ON_CDF_DSS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2008
| V42H | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Cardiff JCT | ON_CDF_JCT | Hurontario SWS | ON_HRN_SWS | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2009
| C7BM | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Barrett Chute SWS | ON_BTC_SWS | Arnprior JCT | ON_ARN_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 506
| C7BM | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Arnprior JCT | ON_ARN_JCT | Arnprior TS | ON_ARN_DSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 507
| C7BM | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Arnprior JCT | ON_ARN_JCT | Fitzroy JCT | ON_FTZ_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 508
| C7BM | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Fitzroy JCT | ON_FTZ_JCT | Chats Falls SWS | ON_CHF_SWS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 509
| W6CS | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Arnprior JCT | ON_ARN_JCT | Arnprior TS | ON_ARN_DSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2100
| W6CS | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Arnprior JCT | ON_ARN_JCT | Mississippi JCT | ON_MSP_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2101
| W6CS | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Marchwood JCT | ON_MCW_JCT | Marchwood MTS | ON_MCW_DSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2102
| W6CS | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Marchwood JCT | ON_MCW_JCT | South March SWS | ON_SOM_SWS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2103
| W6CS | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Mississippi JCT | ON_MSP_JCT | Chats Falls SWS | ON_CHF_SWS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2104
| W6CS | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Mississippi JCT | ON_MSP_JCT | Marchwood JCT | ON_MCW_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2105
| W6CS | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Stewartville TS | ON_STW_DSS | Arnprior JCT | ON_ARN_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2106
| W6NL | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Nelson TS | ON_NEL_DSS | Buchanan JCT | ON_BUC_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2107
| W6NL | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 115 | 1.0429 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan JCT | ON_BUC_JCT | Highbury TS | ON_HIG_DSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2108
| W6NL | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Buchanan JCT | ON_BUC_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2109
| W7 | HONI | Ontario | 1 | ac | 28 | 17.284 | 115 | 11.68 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Ingersoll TS | ON_ING_DSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2110
| W8T | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Edgeware JCT | ON_EDG_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2115
| W8T | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Edgeware JCT | ON_EDG_JCT | Lyons JCT | ON_LYO_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2116
| W9L | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 115 | 1.0429 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Highbury TS | ON_HIG_DSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2118
| WT1A | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Lyons JCT | ON_LYO_JCT | Silvercreek JCT | ON_SVC_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2119
| WT1A | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Silvercreek JCT | ON_SVC_JCT | Aylmer TS | ON_AYL_DSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2120
| WT1A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Silvercreek JCT | ON_SVC_JCT | Silvercreek GS | ON_SVC_GSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2121
| WT1T | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Cranberry JCT | ON_CRN_JCT | ESWF JCT | ON_ESW_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2122
| WT1T | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | ESWF JCT | ON_ESW_JCT | ESWF GS | ON_ESW_GSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2123
| WT1T | HONI | Ontario | 1 | ac | 9 | 5.5556 | 115 | 3.7543 | 3 | [5 empty] | 98.4491 | 108.4016 | ESWF JCT | ON_ESW_JCT | Tillsonburg JCT | ON_TLL_JCT | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2124
| WT1T | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Tillsonburg JCT | ON_TLL_JCT | Tillsonburg TS | ON_TLL_DSS | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan |  | 2125
| V43 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Woodbridge JCT | ON_WDB_JCT | Vaughan #3 JCT | ON_VJ3_JCT | Hydro One. 2016. GTA North Regional Infrastructure Plan |  | 2014
| V43 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Vaughan #3 JCT | ON_VJ3_JCT | Vaughan MTS #3 | ON_VM3_DSS | Hydro One. 2016. GTA North Regional Infrastructure Plan |  | 2015
| V43 | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Vaughan #3 JCT | ON_VJ3_JCT | Kleinburg TS | ON_KLE_DSS | Hydro One. 2016. GTA North Regional Infrastructure Plan |  | 2016
| V44 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Woodbridge JCT | ON_WDB_JCT | Vaughan #3 JCT | ON_VJ3_JCT | Hydro One. 2016. GTA North Regional Infrastructure Plan |  | 2026
| V44 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Vaughan #3 JCT | ON_VJ3_JCT | Vaughan MTS #3 | ON_VM3_DSS | Hydro One. 2016. GTA North Regional Infrastructure Plan |  | 2027
| V44 | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Vaughan #3 JCT | ON_VJ3_JCT | Kleinburg TS | ON_KLE_DSS | Hydro One. 2016. GTA North Regional Infrastructure Plan |  | 2028
| R14T | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Tomken JCT | ON_TOM_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1747
| R14T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Tomken JCT | ON_TOM_JCT | Tomken TS | ON_TOM_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1748
| R14T | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Tomken JCT | ON_TOM_JCT | Erindale JCT | ON_ERD_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1749
| R14T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Erindale JCT | ON_ERD_JCT | Erindale TS | ON_ERD_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1750
| R14T | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Erindale JCT | ON_ERD_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1751
| R17T | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Tomken JCT | ON_TOM_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1753
| R17T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Tomken JCT | ON_TOM_JCT | Tomken TS | ON_TOM_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1754
| R17T | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Tomken JCT | ON_TOM_JCT | Erindale JCT | ON_ERD_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1755
| R17T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Erindale JCT | ON_ERD_JCT | Erindale TS | ON_ERD_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1756
| R17T | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Erindale JCT | ON_ERD_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1757
| R19TH | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Tomken JCT | ON_TOM_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1758
| R19TH | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Tomken JCT | ON_TOM_JCT | Tomken TS | ON_TOM_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1759
| R19TH | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Tomken JCT | ON_TOM_JCT | Hanlan JCT | ON_HLA_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1760
| R19TH | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Hanlan JCT | ON_HLA_JCT | Hurontario SWS | ON_HRN_SWS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1761
| R19TH | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Hurontario SWS | ON_HRN_SWS | Jim Yarrow MTS | ON_JMY_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1762
| R19TH | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Hanlan JCT | ON_HLA_JCT | Erindale JCT | ON_ERD_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1763
| R19TH | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Erindale JCT | ON_ERD_JCT | Erindale TS | ON_ERD_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1764
| R19TH | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Erindale JCT | ON_ERD_JCT | Churchill Meadows JCT | ON_CHU_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1765
| R19TH | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Churchill Meadows JCT | ON_CHU_JCT | Churchill Meadows TS | ON_CHU_ISS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1766
| R19TH | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Churchill Meadows JCT | ON_CHU_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1767
| R21TH | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Tomken JCT | ON_TOM_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1775
| R21TH | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Tomken JCT | ON_TOM_JCT | Tomken TS | ON_TOM_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1776
| R21TH | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Tomken JCT | ON_TOM_JCT | Hanlan JCT | ON_HLA_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1777
| R21TH | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Hanlan JCT | ON_HLA_JCT | Hurontario SWS | ON_HRN_SWS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1778
| R21TH | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Hurontario SWS | ON_HRN_SWS | Jim Yarrow MTS | ON_JMY_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1779
| R21TH | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Hanlan JCT | ON_HLA_JCT | Erindale JCT | ON_ERD_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1780
| R21TH | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Erindale JCT | ON_ERD_JCT | Churchill Meadows JCT | ON_CHU_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1781
| R21TH | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Erindale JCT | ON_ERD_JCT | Erindale TS | ON_ERD_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1782
| R21TH | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Churchill Meadows JCT | ON_CHU_JCT | Churchill Meadows TS | ON_CHU_ISS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1783
| R21TH | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Churchill Meadows JCT | ON_CHU_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1784
| T36B | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Burlington TS | ON_BUR_DSS | Palermo TxB JCT | ON_PAL_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1942
| T36B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Palermo TxB JCT | ON_PAL_JCT | Palermo TS | ON_PAL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1943
| T36B | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Palermo TxB JCT | ON_PAL_JCT | Glenorchy JCT | ON_GLO_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1944
| T36B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Glenorchy JCT | ON_GLO_JCT | Glenorchy MTS #1 | ON_GLO_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1945
| T36B | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Glenorchy JCT | ON_GLO_JCT | Lantz JCT | ON_LNZ_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1946
| T36B | HONI | Ontario | 2 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Lantz JCT | ON_LNZ_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1947
| T37B | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Burlington TS | ON_BUR_DSS | Palermo TxB JCT | ON_PAL_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1948
| T37B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Palermo TxB JCT | ON_PAL_JCT | Palermo TS | ON_PAL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1949
| T37B | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Palermo TxB JCT | ON_PAL_JCT | Glenorchy JCT | ON_GLO_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1950
| T37B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Glenorchy JCT | ON_GLO_JCT | Glenorchy MTS #1 | ON_GLO_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1951
| T37B | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Glenorchy JCT | ON_GLO_JCT | Lantz JCT | ON_LNZ_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1952
| T37B | HONI | Ontario | 2 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Lantz JCT | ON_LNZ_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1953
| T38B | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Burlington TS | ON_BUR_DSS | Tremaine JCT | ON_TRM_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1954
| T38B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Tremaine JCT | ON_TRM_JCT | Tremaine TS | ON_TRM_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1955
| T38B | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Tremaine JCT | ON_TRM_JCT | Lantz JCT | ON_LNZ_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1956
| T38B | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Lantz JCT | ON_LNZ_JCT | Trafalgar DESN JCT | ON_TFL_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1957
| T38B | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Lantz JCT | ON_LNZ_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1958
| T38B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Trafalgar DESN JCT | ON_TFL_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1959
| T38B | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Trafalgar DESN JCT | ON_TFL_JCT | Hornby JCT | ON_HBY_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1960
| T38B | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Hornby JCT | ON_HBY_JCT | Meadowvale TS | ON_MDV_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1961
| T38B | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Hornby JCT | ON_HBY_JCT | TCE Halton Hills JCT | ON_TCE_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1962
| T38B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | TCE Halton Hills JCT | ON_TCE_JCT | Halton Hills GS | ON_HHL_GSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1963
| T38B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | TCE Halton Hills JCT | ON_TCE_JCT | Halton Hills MTS | ON_HHL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1964
| T38B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | TCE Halton Hills JCT | ON_TCE_JCT | Halton TS | ON_HLT_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1965
| T39B | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Burlington TS | ON_BUR_DSS | Tremaine JCT | ON_TRM_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1966
| T39B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Tremaine JCT | ON_TRM_JCT | Tremaine TS | ON_TRM_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1967
| T39B | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Tremaine JCT | ON_TRM_JCT | Lantz JCT | ON_LNZ_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1968
| T39B | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Lantz JCT | ON_LNZ_JCT | Trafalgar DESN JCT | ON_TFL_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1969
| T39B | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Lantz JCT | ON_LNZ_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1970
| T39B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Trafalgar DESN JCT | ON_TFL_JCT | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1971
| T39B | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Trafalgar DESN JCT | ON_TFL_JCT | Hornby JCT | ON_HBY_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1972
| T39B | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Hornby JCT | ON_HBY_JCT | Meadowvale TS | ON_MDV_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1973
| T39B | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Hornby JCT | ON_HBY_JCT | TCE Halton Hills JCT | ON_TCE_JCT | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1974
| T39B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | TCE Halton Hills JCT | ON_TCE_JCT | Halton Hills GS | ON_HHL_GSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1975
| T39B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | TCE Halton Hills JCT | ON_TCE_JCT | Halton Hills MTS | ON_HHL_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1976
| T39B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | TCE Halton Hills JCT | ON_TCE_JCT | Halton TS | ON_HLT_DSS | Hydro One. 2016. GTA West Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1977
| R13K | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Manby TS | ON_MBY_DSS | Vansco JCT | ON_VNO_JCT | Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1745
| R13K | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Vansco JCT | ON_VNO_JCT | Horner TS | ON_HOR_DSS | Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1746
| R2K | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Manby TS | ON_MBY_DSS | Vansco JCT | ON_VNO_JCT | Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1788
| R2K | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Vansco JCT | ON_VNO_JCT | Horner TS | ON_HOR_DSS | Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1789
| Q1N | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Dresser JCT | ON_DRS_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1615
| Q3N | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Portal JCT | ON_POR_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1697
| Q3N | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 115 | 0.12514 | 3 | [5 empty] | 98.4491 | 108.4016 | Portal JCT | ON_POR_JCT | Stanley TS | ON_SLY_DSS | Hydro One. 2016. Needs Assessment Report Niagara |  | 1698
| Q3N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Portal JCT | ON_POR_JCT | Dresser JCT | ON_DRS_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1699
| Q3N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dresser JCT | ON_DRS_JCT | Trei-bacher JCT | ON_TRB_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1700
| Q3N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dresser JCT | ON_DRS_JCT | Niagara JCT | ON_NIA_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1701
| Q3N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Niagara JCT | ON_NIA_JCT | Murray TS | ON_MRY_DSS | Hydro One. 2016. Needs Assessment Report Niagara |  | 1702
| Q3NC | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Canal JCT | ON_CNL_JCT | Portal JCT | ON_POR_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1703
| Q4N | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Portal JCT | ON_POR_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1713
| Q4N | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 115 | 0.12514 | 3 | [5 empty] | 98.4491 | 108.4016 | Portal JCT | ON_POR_JCT | Stanley TS | ON_SLY_DSS | Hydro One. 2016. Needs Assessment Report Niagara |  | 1714
| Q4N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Portal JCT | ON_POR_JCT | Dresser JCT | ON_DRS_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1715
| Q4N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dresser JCT | ON_DRS_JCT | Trei-bacher JCT | ON_TRB_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1716
| Q4N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dresser JCT | ON_DRS_JCT | Niagara JCT | ON_NIA_JCT | Hydro One. 2016. Needs Assessment Report Niagara |  | 1717
| Q4N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Niagara JCT | ON_NIA_JCT | Murray TS | ON_MRY_DSS | Hydro One. 2016. Needs Assessment Report Niagara |  | 1718
| A1T | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Allanburg TS | ON_ALL_TSS | Michigan JCT | ON_MIC_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 29
| A1T | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Michigan JCT | ON_MIC_JCT | Crowland JCT | ON_CRL_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 30
| A1T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Crowland JCT | ON_CRL_JCT | ASW Steel JCT | ON_ASW_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 31
| A1T | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | Michigan JCT | ON_MIC_JCT | Montrose JCT | ON_MTR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 32
| A1T | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Montrose JCT | ON_MTR_JCT | Toronto Power T#56 JCT | ON_TOT_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 33
| A1T | HONI | Ontario | 2 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Toronto Power T#56 JCT | ON_TOT_JCT | Niagara A1T T#49 JCT | ON_NIT_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 34
| A36N | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Allanburg TS | ON_ALL_TSS | Kalar JCT | ON_KLR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 47
| A36N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kalar JCT | ON_KLR_JCT | Kalar MTS | ON_KLR_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 48
| A36N | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Kalar JCT | ON_KLR_JCT | Murray TS | ON_MRY_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 49
| A37N | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Allanburg TS | ON_ALL_TSS | Kalar JCT | ON_KLR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 51
| A37N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kalar JCT | ON_KLR_JCT | Kalar MTS | ON_KLR_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 52
| A37N | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Kalar JCT | ON_KLR_JCT | Murray TS | ON_MRY_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 53
| A6C | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | BF Goodrich JCT | ON_BFG_JCT | Oxy Vinyls TS | ON_OXY_ISS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 114
| A7C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Allanburg TS | ON_ALL_TSS | Hurricane JCT | ON_HRC_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 125
| A7C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Hurricane JCT | ON_HRC_JCT | BF Goodrich JCT | ON_BFG_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 126
| A7C | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | BF Goodrich JCT | ON_BFG_JCT | Cytec Welland TS | ON_CYT_ISS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 127
| A7C | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | BF Goodrich JCT | ON_BFG_JCT | Oxy Vinyls TS | ON_OXY_ISS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 128
| A7C | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Hurricane JCT | ON_HRC_JCT | Michigan JCT | ON_MIC_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 129
| A7C | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Michigan JCT | ON_MIC_JCT | Crowland TS | ON_CRL_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 130
| C1P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Crowland TS | ON_CRL_DSS | Tunnel JCT | ON_TUN_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 405
| C1P | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Tunnel JCT | ON_TUN_JCT | Vale Inco JCT | ON_VLI_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 406
| C1P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vale Inco JCT | ON_VLI_JCT | Port Colborne TS | ON_PTC_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 407
| C2P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Crowland TS | ON_CRL_DSS | Tunnel JCT | ON_TUN_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 456
| C2P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Tunnel JCT | ON_TUN_JCT | Panabrasives TS | ON_PNB_ISS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 457
| C2P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Tunnel JCT | ON_TUN_JCT | JBL JCT | ON_JBL_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 458
| C2P | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | JBL JCT | ON_JBL_JCT | JBL SWS | ON_JBL_SWS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 459
| C2P | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | JBL JCT | ON_JBL_JCT | Vale Inco JCT | ON_VLI_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 460
| C2P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vale Inco JCT | ON_VLI_JCT | Port Colborne TS | ON_PTC_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 461
| C2P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vale Inco JCT | ON_VLI_JCT | Vale Port Colborne | ON_VLP_ISS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 462
| D10S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | DeCew Falls SWS | ON_DEC_SWS | Hooper's JCT | ON_HOO_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 540
| D10S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hooper's JCT | ON_HOO_JCT | Vansickle TS | ON_VNS_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 541
| D10S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vansickle TS | ON_VNS_DSS | Louth JCT | ON_LOU_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 542
| D10S | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Louth JCT | ON_LOU_JCT | Carlton TS | ON_CLT_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 543
| D10S | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 115 | 2.7114 | 3 | [5 empty] | 98.4491 | 108.4016 | Louth JCT | ON_LOU_JCT | Glendale TS | ON_GND_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 544
| D9HS | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | DeCew Falls SWS | ON_DEC_SWS | Hooper's JCT | ON_HOO_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 692
| D9HS | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hooper's JCT | ON_HOO_JCT | Vansickle TS | ON_VNS_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 693
| D9HS | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vansickle TS | ON_VNS_DSS | Louth JCT | ON_LOU_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 694
| D9HS | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Louth JCT | ON_LOU_JCT | Carlton TS | ON_CLT_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 695
| D9HS | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 115 | 2.7114 | 3 | [5 empty] | 98.4491 | 108.4016 | Louth JCT | ON_LOU_JCT | Glendale TS | ON_GND_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 696
| M11S | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | G.M. St. Cath TS | ON_GMS_ISS | McKinnon's JCT | ON_MCK_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1276
| M34H | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Middleport TS | ON_MPT_TSS | Carluke JCT | ON_CLK_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1390
| M34H | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Southcote JCT | ON_SCT_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1391
| M34H | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Southcote JCT | ON_SCT_JCT | Neale JCT | ON_NEA_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1392
| M34H | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Neale JCT | ON_NEA_JCT | Hannon JCT | ON_HNN_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1393
| M34H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Hannon JCT | ON_HNN_JCT | Beach TS | ON_BCH_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1394
| M572T | HONI | Ontario | 1 | ac | 12 | 7.4074 | 500 | 4.74 | 3 | [5 empty] | 2550 | 3225 | Milton SWS | ON_MIL_SWS | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1404
| M573T | HONI | Ontario | 1 | ac | 12 | 7.4074 | 500 | 4.74 | 3 | [5 empty] | 2550 | 3225 | Milton SWS | ON_MIL_SWS | Trafalgar TS | ON_TFL_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1405
| NF3M11 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Toronto Power TS | ON_TOP_DSS | Drummond Road JCT | ON_DRU_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1509
| Q10M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | McKinnon's JCT | ON_MCK_JCT | G.M. St. Cath TS | ON_GMS_ISS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1601
| Q11S | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Warner Road JCT | ON_WNR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1602
| Q11S | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Warner Road JCT | ON_WNR_JCT | NOTL MTS #2 | ON_NM2_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1603
| Q11S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Warner Road JCT | ON_WNR_JCT | NOTL York MTS #1 JCT | ON_NJ1_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1604
| Q11S | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | NOTL York MTS #1 JCT | ON_NJ1_JCT | McKinnon's JCT | ON_MCK_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1605
| Q11S | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | McKinnon's JCT | ON_MCK_JCT | Glendale JCT | ON_GND_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1606
| Q11S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Glendale JCT | ON_GND_JCT | Glendale TS | ON_GND_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1607
| Q11S | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Glendale JCT | ON_GND_JCT | Bunting TS | ON_BUN_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1608
| Q12S | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Warner Road JCT | ON_WNR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1609
| Q12S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Warner Road JCT | ON_WNR_JCT | NOTL York MTS #1 JCT | ON_NJ1_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1610
| Q12S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | NOTL York MTS #1 JCT | ON_NJ1_JCT | NOTL York MTS #1 | ON_NM1_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1611
| Q12S | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | NOTL York MTS #1 JCT | ON_NJ1_JCT | Glendale JCT | ON_GND_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1612
| Q12S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Glendale JCT | ON_GND_JCT | Glendale TS | ON_GND_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1613
| Q12S | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Glendale JCT | ON_GND_JCT | Bunting TS | ON_BUN_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1614
| Q23BM | HONI | Ontario | 1 | ac | 47 | 29.0123 | 230 | 22.56 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Niagara West JCT | ON_NIW_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1618
| Q23BM | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Niagara West JCT | ON_NIW_JCT | Niagara West MTS | ON_NIW_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1619
| Q23BM | HONI | Ontario | 1 | ac | 21 | 12.963 | 230 | 10.08 | 3 | [5 empty] | 402 | 435 | Niagara West JCT | ON_NIW_JCT | Hannon JCT | ON_HNN_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1620
| Q23BM | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Hannon JCT | ON_HNN_JCT | Neale JCT | ON_NEA_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1621
| Q23BM | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Neale JCT | ON_NEA_JCT | Burlington TS | ON_BUR_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1622
| Q23BM | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Neale JCT | ON_NEA_JCT | Southcote JCT | ON_SCT_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1623
| Q23BM | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Southcote JCT | ON_SCT_JCT | Mount Hope JCT | ON_MTH_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1624
| Q23BM | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Mount Hope JCT | ON_MTH_JCT | Carluke JCT | ON_CLK_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1625
| Q23BM | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1626
| Q25BM | HONI | Ontario | 1 | ac | 47 | 29.0123 | 230 | 22.56 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Niagara West JCT | ON_NIW_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1637
| Q25BM | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Niagara West JCT | ON_NIW_JCT | Niagara West MTS | ON_NIW_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1638
| Q25BM | HONI | Ontario | 1 | ac | 21 | 12.963 | 230 | 10.08 | 3 | [5 empty] | 402 | 435 | Niagara West JCT | ON_NIW_JCT | Hannon JCT | ON_HNN_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1639
| Q25BM | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Hannon JCT | ON_HNN_JCT | Neale JCT | ON_NEA_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1640
| Q25BM | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Neale JCT | ON_NEA_JCT | Burlington TS | ON_BUR_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1641
| Q25BM | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Neale JCT | ON_NEA_JCT | Southcote JCT | ON_SCT_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1642
| Q25BM | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Southcote JCT | ON_SCT_JCT | Mount Hope JCT | ON_MTH_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1643
| Q25BM | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Mount Hope JCT | ON_MTH_JCT | Carluke JCT | ON_CLK_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1644
| Q25BM | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1645
| Q26M | HONI | Ontario | 2 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Abit Cons NAN91 JCT | ON_ACS_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1646
| Q26M | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Abit Cons NAN91 JCT | ON_ACS_JCT | Crossline JCT | ON_CSL_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1647
| Q26M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Crossline JCT | ON_CSL_JCT | Allanburg TS | ON_ALL_TSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1648
| Q26M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Crossline JCT | ON_CSL_JCT | Allanburg West JCT | ON_ALW_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1649
| Q26M | HONI | Ontario | 1 | ac | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Allanburg West JCT | ON_ALW_JCT | Middleport TS | ON_MPT_TSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1650
| Q29HM | HONI | Ontario | 1 | ac | 68 | 41.9753 | 230 | 32.64 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Hannon JCT | ON_HNN_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1653
| Q29HM | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Hannon JCT | ON_HNN_JCT | Beach TS | ON_BCH_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1654
| Q29HM | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Beach TS | ON_BCH_DSS | Dofasco Kenilworth TS | ON_DKW_ISS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1655
| Q29HM | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Hannon JCT | ON_HNN_JCT | Nebo JCT | ON_NEB_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1656
| Q29HM | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Nebo JCT | ON_NEB_JCT | Nebo TS | ON_NEB_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1657
| Q29HM | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Nebo JCT | ON_NEB_JCT | Neale JCT | ON_NEA_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1658
| Q29HM | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Neale JCT | ON_NEA_JCT | Southcote JCT | ON_SCT_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1659
| Q29HM | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Southcote JCT | ON_SCT_JCT | Carluke JCT | ON_CLK_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1660
| Q29HM | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1661
| Q5G | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Holland Road JCT | ON_HLR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1729
| Q5G | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Holland Road JCT | ON_HLR_JCT | Beamsville TS | ON_BMS_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1730
| Q5G | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Beamsville TS | ON_BMS_DSS | West Lincoln JCT | ON_WLN_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1731
| Q6A | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Crossline JCT | ON_CSL_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1732
| T2N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Toronto Power TS | ON_TOP_DSS | Drummond Road JCT | ON_DRU_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1932
| D1A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | DeCew Falls SWS | ON_DEC_SWS | Hooper's JCT | ON_HOO_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 551
| D1A | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Hooper's JCT | ON_HOO_JCT | St. Johns Valley JCT | ON_STJ_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 552
| D1A | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Johns Valley JCT | ON_STJ_JCT | Gibson JCT | ON_GIB_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 553
| D1A | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Gibson JCT | ON_GIB_JCT | Thorold TS | ON_THL_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 554
| D1A | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Gibson JCT | ON_GIB_JCT | Fibre JCT | ON_FBR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 555
| D1A | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Fibre JCT | ON_FBR_JCT | Holland Road JCT | ON_HLR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 556
| D1A | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Holland Road JCT | ON_HLR_JCT | Allanburg TS | ON_ALL_TSS | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 557
| D1A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Holland Road JCT | ON_HLR_JCT | RFP Thorold TS | ON_RFT_GSS | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 558
| D3A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | DeCew Falls SWS | ON_DEC_SWS | Hooper's JCT | ON_HOO_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 587
| D3A | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Hooper's JCT | ON_HOO_JCT | St. Johns Valley JCT | ON_STJ_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 588
| D3A | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Johns Valley JCT | ON_STJ_JCT | Gibson JCT | ON_GIB_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 589
| D3A | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Gibson JCT | ON_GIB_JCT | Thorold TS | ON_THL_DSS | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 590
| D3A | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Gibson JCT | ON_GIB_JCT | Fibre JCT | ON_FBR_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 591
| D3A | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Fibre JCT | ON_FBR_JCT | Allanburg TS | ON_ALL_TSS | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 592
| D3A | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Allanburg TS | ON_ALL_TSS | Michigan JCT | ON_MIC_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 593
| D3A | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Michigan JCT | ON_MIC_JCT | ASW Steel JCT | ON_ASW_JCT | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 594
| D3A | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | ASW Steel JCT | ON_ASW_JCT | ASW Steel TS | ON_ASW_ISS | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 595
| Q24HM | HONI | Ontario | 1 | ac | 68 | 41.9753 | 230 | 32.64 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Hannon JCT | ON_HNN_JCT | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1627
| Q24HM | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Hannon JCT | ON_HNN_JCT | Beach TS | ON_BCH_DSS | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1628
| Q24HM | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Beach TS | ON_BCH_DSS | Dofasco Kenilworth TS | ON_DKW_ISS | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1629
| Q24HM | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Hannon JCT | ON_HNN_JCT | Nebo JCT | ON_NEB_JCT | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1630
| Q24HM | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Nebo JCT | ON_NEB_JCT | Nebo TS | ON_NEB_DSS | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1631
| Q24HM | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Nebo JCT | ON_NEB_JCT | Neale JCT | ON_NEA_JCT | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1632
| Q24HM | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Neale JCT | ON_NEA_JCT | Southcote JCT | ON_SCT_JCT | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1633
| Q24HM | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Southcote JCT | ON_SCT_JCT | Trinity JCT | ON_TRN_JCT | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1634
| Q24HM | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Trinity JCT | ON_TRN_JCT | Carluke JCT | ON_CLK_JCT | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1635
| Q24HM | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Hydro One. 2017. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1636
| N5K | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Sarnia Scott TS | ON_SNS_TSS | Kimball JCT | ON_KIM_JCT | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan |  | 1469
| N5K | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Kimball JCT | ON_KIM_JCT | Wallaceburg TS | ON_WLB_DSS | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan |  | 1470
| N5K | HONI | Ontario | 1 | ac | 26 | 16.0494 | 115 | 10.8457 | 3 | [5 empty] | 98.4491 | 108.4016 | Wallaceburg TS | ON_WLB_DSS | Kent TS | ON_KNT_DSS | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan |  | 1471
| N6C | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Sarnia Scott TS | ON_SNS_TSS | St. Andrews TS | ON_STA_DSS | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan |  | 1477
| K12 | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 115 | 1.0429 | 3 | [5 empty] | 98.4491 | 108.4016 | Karn TS | ON_KRN_TSS | Woodstock TS | ON_WDK_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 995
| K12 | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Woodstock TS | ON_WDK_DSS | Commerce Way TS | ON_CMC_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 996
| K7 | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 115 | 1.0429 | 3 | [5 empty] | 98.4491 | 108.4016 | Karn TS | ON_KRN_TSS | Woodstock TS | ON_WDK_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1099
| K7 | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Woodstock TS | ON_WDK_DSS | Commerce Way TS | ON_CMC_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1100
| M31W | HONI | Ontario | 1 | ac | 32 | 19.7531 | 230 | 15.36 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Salford JCT | ON_SFD_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1368
| M31W | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Salford JCT | ON_SFD_JCT | Ingersoll JCT | ON_ING_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1369
| M31W | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Ingersoll JCT | ON_ING_JCT | Ingersoll TS | ON_ING_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1370
| M31W | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Ingersoll JCT | ON_ING_JCT | Karn TS | ON_KRN_TSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1371
| M32W | HONI | Ontario | 1 | ac | 32 | 19.7531 | 230 | 15.36 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Salford JCT | ON_SFD_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1377
| M32W | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Salford JCT | ON_SFD_JCT | Ingersoll JCT | ON_ING_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1378
| M32W | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Ingersoll JCT | ON_ING_JCT | Ingersoll TS | ON_ING_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1379
| M32W | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Ingersoll JCT | ON_ING_JCT | Karn TS | ON_KRN_TSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1380
| M33W | HONI | Ontario | 1 | ac | 32 | 19.7531 | 230 | 15.36 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Salford JCT | ON_SFD_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1385
| N21W | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Bostwick Road JCT | ON_BOS_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1446
| N21W | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Bostwick Road JCT | ON_BOS_JCT | Wonderland TS | ON_WND_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1447
| N22W | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Bostwick Road JCT | ON_BOS_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1456
| N22W | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Bostwick Road JCT | ON_BOS_JCT | Wonderland TS | ON_WND_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1457
| S2N | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Sydenham JCT | ON_SYD_JCT | Strathroy TS | ON_SRY_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1851
| T11T | HONI | Ontario | 1 | ac | 17 | 10.4938 | 115 | 7.0914 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Thomas TS | ON_STT_DSS | Lyons JCT | ON_LYO_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1903
| T11T | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Lyons JCT | ON_LYO_JCT | Cranberry JCT | ON_CRN_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 1904
| W12 | HONI | Ontario | 1 | ac | 28 | 17.284 | 115 | 11.68 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Ingersoll TS | ON_ING_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2059
| W2S | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Sydenham JCT | ON_SYD_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2067
| W2S | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Sydenham JCT | ON_SYD_JCT | Strathroy TS | ON_SRY_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2068
| W36 | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Oxford Street JCT | ON_OXS_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2069
| W36 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Oxford Street JCT | ON_OXS_JCT | Clarke TS | ON_CKE_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2070
| W36 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Oxford Street JCT | ON_OXS_JCT | Talbot TS | ON_TBT_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2071
| W37 | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Dundas Street JCT | ON_DST_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2072
| W37 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas Street JCT | ON_DST_JCT | Clarke TS | ON_CKE_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2073
| W37 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas Street JCT | ON_DST_JCT | Talbot TS | ON_TBT_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2074
| W3T | HONI | Ontario | 1 | ac | 5.5 | 3.3951 | 115 | 2.2943 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Kettle Creek JCT | ON_KET_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2080
| W3T | HONI | Ontario | 1 | ac | 9 | 5.5556 | 115 | 3.7543 | 3 | [5 empty] | 98.4491 | 108.4016 | Kettle Creek JCT | ON_KET_JCT | St. Thomas TS | ON_STT_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2081
| W3T | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Kettle Creek JCT | ON_KET_JCT | W3_4T STR B JCT | ON_W34_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2082
| W42L | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Longwood TS | ON_LGW_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2083
| W43L | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Longwood TS | ON_LGW_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2084
| W44LC | HONI | Ontario | 1 | ac | 14 | 8.642 | 230 | 6.72 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Edgeware TS | ON_EDG_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2085
| W44LC | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Cowal JCT | ON_COW_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2086
| W44LC | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Cowal JCT | ON_COW_JCT | Duart JCT | ON_DUA_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2087
| W44LC | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Cowal JCT | ON_COW_JCT | Longwood TS | ON_LGW_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2090
| W45LS | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Buchanan TS | ON_BUC_DSS | Cowal JCT | ON_COW_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2091
| W45LS | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Cowal JCT | ON_COW_JCT | Duart JCT | ON_DUA_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2092
| W45LS | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Duart JCT | ON_DUA_JCT | Spence SWS | ON_SPC_SWS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2094
| W45LS | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Cowal JCT | ON_COW_JCT | Longwood TS | ON_LGW_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2095
| W4T | HONI | Ontario | 1 | ac | 5.5 | 3.3951 | 115 | 2.2943 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Kettle Creek JCT | ON_KET_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2096
| W4T | HONI | Ontario | 1 | ac | 9 | 5.5556 | 115 | 3.7543 | 3 | [5 empty] | 98.4491 | 108.4016 | Kettle Creek JCT | ON_KET_JCT | St. Thomas TS | ON_STT_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2097
| W4T | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Kettle Creek JCT | ON_KET_JCT | W3_4T STR B JCT | ON_W34_JCT | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2098
| W5N | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Buchanan TS | ON_BUC_DSS | Nelson TS | ON_NEL_DSS | Hydro One. 2017. London Area Regional Infrastructure Plan |  | 2099
| E1C | HONI | Ontario | 1 | ac | 60 | 37.037 | 115 | 25.0286 | 3 | [5 empty] | 98.4491 | 108.4016 | Golden Patricia JCT | ON_GLP_JCT | Cat Lake MTS | ON_CTL_DSS | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan |  | 701
| B5C | HONI | Ontario | 1 | ac | 12.4 | 7.6543 | 115 | 5.1726 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Harper's JCT | ON_HRP_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 300
| B5C | HONI | Ontario | 1 | ac | 20.3 | 12.5309 | 115 | 8.468 | 3 | [5 empty] | 98.4491 | 108.4016 | Harper's JCT | ON_HRP_JCT | Puslinch JCT | ON_PUS_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 301
| B5C | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Harper's JCT | ON_HRP_JCT | Westover JCT | ON_WSV_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 302
| B5C | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Westover JCT | ON_WSV_JCT | Westover A JCT | ON_WVA_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 303
| B5C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Westover A JCT | ON_WVA_JCT | Enbridge Westover N TS | ON_EWN_ISS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 304
| B5C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Westover A JCT | ON_WVA_JCT | Enbridge Westover S TS | ON_EWS_ISS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 305
| B5C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Puslinch JCT | ON_PUS_JCT | Puslinch DS | ON_PUS_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 306
| B5C | HONI | Ontario | 1 | ac | 4.4 | 2.716 | 115 | 1.8354 | 3 | [5 empty] | 98.4491 | 108.4016 | Puslinch JCT | ON_PUS_JCT | Arlen MTS JCT | ON_ARL_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 307
| B5C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Arlen MTS JCT | ON_ARL_JCT | Arlen MTS | ON_ARL_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 308
| B5C | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Arlen MTS JCT | ON_ARL_JCT | Hanlon JCT | ON_HLO_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 309
| B5C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hanlon JCT | ON_HLO_JCT | Hanlon TS | ON_HLO_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 310
| B5C | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Hanlon JCT | ON_HLO_JCT | Cedar TS | ON_CED_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 311
| D10H | HONI | Ontario | 1 | ac | 2.3 | 1.4198 | 115 | 0.95943 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler TS | ON_DET_TSS | Leong JCT | ON_LEO_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 533
| D10H | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Leong JCT | ON_LEO_JCT | Waterloo JCT | ON_WTL_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 534
| D10H | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Waterloo JCT | ON_WTL_JCT | Rush MTS | ON_RSH_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 535
| D10H | HONI | Ontario | 1 | ac | 18.3 | 11.2963 | 115 | 7.6337 | 3 | [5 empty] | 98.4491 | 108.4016 | Waterloo JCT | ON_WTL_JCT | Wallenstein JCT | ON_WST_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 536
| D10H | HONI | Ontario | 1 | ac | 8.1 | 5 | 115 | 3.3789 | 3 | [5 empty] | 98.4491 | 108.4016 | Wallenstein JCT | ON_WST_JCT | Elmira TS | ON_EMA_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 537
| D10H | HONI | Ontario | 1 | ac | 29 | 17.9012 | 115 | 12.0971 | 3 | [5 empty] | 98.4491 | 108.4016 | Wallenstein JCT | ON_WST_JCT | Palmerston TS | ON_PLM_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 538
| D11K | HONI | Ontario | 1 | ac | 4.7 | 2.9012 | 115 | 1.9606 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler TS | ON_DET_TSS | Kitchener #1&4 JCT | ON_KJ1_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 545
| D11K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener #1&4 JCT | ON_KJ1_JCT | Kitchener MTS #1 | ON_KM1_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 546
| D11K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener #1&4 JCT | ON_KJ1_JCT | Kitchener MTS #4 | ON_KM4_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 547
| D12K | HONI | Ontario | 1 | ac | 4.7 | 2.9012 | 115 | 1.9606 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler TS | ON_DET_TSS | Kitchener #1&4 JCT | ON_KJ1_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 548
| D12K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener #1&4 JCT | ON_KJ1_JCT | Kitchener MTS #1 | ON_KM1_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 549
| D12K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener #1&4 JCT | ON_KJ1_JCT | Kitchener MTS #4 | ON_KM4_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 550
| D1W | HONI | Ontario | 1 | ac | 17.9 | 11.0494 | 115 | 7.4669 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler JCT | ON_DET_JCT | Wolverton JCT | ON_WLV_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 560
| D1W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Wolverton JCT | ON_WLV_JCT | Wolverton DS | ON_WLV_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 561
| D4W | HONI | Ontario | 1 | ac | 12.1 | 7.4691 | 230 | 5.808 | 3 | [5 empty] | 402 | 435 | Detweiler TS | ON_DET_TSS | Kitchener #9 JCT | ON_KJ9_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 614
| D4W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Kitchener #9 JCT | ON_KJ9_JCT | Kitchener MTS #9 | ON_KM9_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 615
| D4W | HONI | Ontario | 1 | ac | 66.9 | 41.2963 | 230 | 32.112 | 3 | [5 empty] | 402 | 435 | Kitchener #9 JCT | ON_KJ9_JCT | Buchanan TS | ON_BUC_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 616
| D5W | HONI | Ontario | 1 | ac | 12.1 | 7.4691 | 230 | 5.808 | 3 | [5 empty] | 402 | 435 | Detweiler TS | ON_DET_TSS | Kitchener #9 JCT | ON_KJ9_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 631
| D5W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Kitchener #9 JCT | ON_KJ9_JCT | Kitchener MTS #9 | ON_KM9_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 632
| D5W | HONI | Ontario | 1 | ac | 66.9 | 41.2963 | 230 | 32.112 | 3 | [5 empty] | 402 | 435 | Kitchener #9 JCT | ON_KJ9_JCT | Buchanan TS | ON_BUC_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 633
| D6V | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 230 | 2.16 | 3 | [5 empty] | 402 | 435 | Detweiler TS | ON_DET_TSS | Waterloo North MTS 3 JCT | ON_WTN_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 652
| D6V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Waterloo North MTS 3 JCT | ON_WTN_JCT | Waterloo North MTS 3 | ON_WTN_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 653
| D6V | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Waterloo North MTS 3 JCT | ON_WTN_JCT | Scheifele JCT | ON_SCF_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 654
| D6V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Scheifele JCT | ON_SCF_JCT | Scheifele MTS | ON_SCF_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 655
| D6V | HONI | Ontario | 1 | ac | 18.8 | 11.6049 | 230 | 9.024 | 3 | [5 empty] | 402 | 435 | Scheifele JCT | ON_SCF_JCT | Guelph North JCT | ON_GUE_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 656
| D6V | HONI | Ontario | 1 | ac | 12.7 | 7.8395 | 230 | 6.096 | 3 | [5 empty] | 402 | 435 | Guelph North JCT | ON_GUE_JCT | Campbell TS | ON_CBL_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 657
| D6V | HONI | Ontario | 1 | ac | 6.4 | 3.9506 | 230 | 3.072 | 3 | [5 empty] | 402 | 435 | Campbell TS | ON_CBL_DSS | Speed River JCT | ON_SPR_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 658
| D6V | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Speed River JCT | ON_SPR_JCT | Cedar TS | ON_CED_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 659
| D6V | HONI | Ontario | 1 | ac | 9.4 | 5.8025 | 230 | 4.512 | 3 | [5 empty] | 402 | 435 | Guelph North JCT | ON_GUE_JCT | Fergus JCT | ON_FGS_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 660
| D6V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Fergus JCT | ON_FGS_JCT | Fergus TS | ON_FGS_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 661
| D6V | HONI | Ontario | 1 | ac | 27.5 | 16.9753 | 230 | 13.2 | 3 | [5 empty] | 402 | 435 | Fergus JCT | ON_FGS_JCT | Orangeville TS | ON_ORA_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 662
| D7F | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 115 | 0.45886 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler TS | ON_DET_TSS | Detweiler JCT | ON_DET_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 664
| D7F | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler JCT | ON_DET_JCT | Kitchener #6 JCT | ON_KJ6_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 665
| D7F | HONI | Ontario | 1 | ac | 5.5 | 3.3951 | 115 | 2.2943 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener #6 JCT | ON_KJ6_JCT | Siebert JCT | ON_SBT_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 666
| D7F | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 115 | 1.0011 | 3 | [5 empty] | 98.4491 | 108.4016 | Siebert JCT | ON_SBT_JCT | Kitchener MTS #7 | ON_KM7_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 667
| D7F | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 115 | 1.0011 | 3 | [5 empty] | 98.4491 | 108.4016 | Siebert JCT | ON_SBT_JCT | Kitchener #2&3 JCT | ON_KJ2_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 668
| D7F | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener #2&3 JCT | ON_KJ2_JCT | Kitchener MTS #3 | ON_KM3_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 669
| D7F | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener MTS #7 | ON_KM7_DSS | Freeport SWS | ON_FPT_SWS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 670
| D7V | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 230 | 2.16 | 3 | [5 empty] | 402 | 435 | Detweiler TS | ON_DET_TSS | Waterloo North MTS 3 JCT | ON_WTN_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 671
| D7V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Waterloo North MTS 3 JCT | ON_WTN_JCT | Waterloo North MTS 3 | ON_WTN_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 672
| D7V | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Waterloo North MTS 3 JCT | ON_WTN_JCT | Scheifele JCT | ON_SCF_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 673
| D7V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Scheifele JCT | ON_SCF_JCT | Scheifele MTS | ON_SCF_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 674
| D7V | HONI | Ontario | 1 | ac | 18.8 | 11.6049 | 230 | 9.024 | 3 | [5 empty] | 402 | 435 | Scheifele JCT | ON_SCF_JCT | Guelph North JCT | ON_GUE_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 675
| D7V | HONI | Ontario | 1 | ac | 12.7 | 7.8395 | 230 | 6.096 | 3 | [5 empty] | 402 | 435 | Guelph North JCT | ON_GUE_JCT | Campbell TS | ON_CBL_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 676
| D7V | HONI | Ontario | 1 | ac | 6.4 | 3.9506 | 230 | 3.072 | 3 | [5 empty] | 402 | 435 | Campbell TS | ON_CBL_DSS | Speed River JCT | ON_SPR_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 677
| D7V | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Speed River JCT | ON_SPR_JCT | Cedar TS | ON_CED_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 678
| D7V | HONI | Ontario | 1 | ac | 9.4 | 5.8025 | 230 | 4.512 | 3 | [5 empty] | 402 | 435 | Guelph North JCT | ON_GUE_JCT | Fergus JCT | ON_FGS_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 679
| D7V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Fergus JCT | ON_FGS_JCT | Fergus TS | ON_FGS_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 680
| D7V | HONI | Ontario | 1 | ac | 27.5 | 16.9753 | 230 | 13.2 | 3 | [5 empty] | 402 | 435 | Fergus JCT | ON_FGS_JCT | Orangeville TS | ON_ORA_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 681
| D8S | HONI | Ontario | 1 | ac | 2.3 | 1.4198 | 115 | 0.95943 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler TS | ON_DET_TSS | Leong JCT | ON_LEO_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 682
| D8S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Leong JCT | ON_LEO_JCT | Rush MTS | ON_RSH_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 683
| D8S | HONI | Ontario | 1 | ac | 56 | 34.5679 | 115 | 23.36 | 3 | [5 empty] | 98.4491 | 108.4016 | Leong JCT | ON_LEO_JCT | St. Marys TS | ON_SMY_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 684
| D9F | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 115 | 0.45886 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler TS | ON_DET_TSS | Detweiler JCT | ON_DET_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 685
| D9F | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Detweiler JCT | ON_DET_JCT | Kitchener #6 JCT | ON_KJ6_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 686
| D9F | HONI | Ontario | 1 | ac | 5.5 | 3.3951 | 115 | 2.2943 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener #6 JCT | ON_KJ6_JCT | Siebert JCT | ON_SBT_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 687
| D9F | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 115 | 1.0011 | 3 | [5 empty] | 98.4491 | 108.4016 | Siebert JCT | ON_SBT_JCT | Kitchener MTS #7 | ON_KM7_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 688
| D9F | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 115 | 1.0011 | 3 | [5 empty] | 98.4491 | 108.4016 | Siebert JCT | ON_SBT_JCT | Kitchener #2&3 JCT | ON_KJ2_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 689
| D9F | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener #2&3 JCT | ON_KJ2_JCT | Kitchener MTS #3 | ON_KM3_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 690
| D9F | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener MTS #7 | ON_KM7_DSS | Freeport SWS | ON_FPT_SWS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 691
| F11C | HONI | Ontario | 1 | ac | 4.8 | 2.963 | 115 | 2.0023 | 3 | [5 empty] | 98.4491 | 108.4016 | Freeport SWS | ON_FPT_SWS | Kitchener Graber JCT | ON_KGB_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 763
| F11C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener Graber JCT | ON_KGB_JCT | Kitchener MTS #5 | ON_KM5_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 764
| F11C | HONI | Ontario | 1 | ac | 8.6 | 5.3086 | 115 | 3.5874 | 3 | [5 empty] | 98.4491 | 108.4016 | Freeport SWS | ON_FPT_SWS | Speedsville JCT | ON_SPS_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 765
| F11C | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 115 | 0.45886 | 3 | [5 empty] | 98.4491 | 108.4016 | Speedsville JCT | ON_SPS_JCT | Preston TS | ON_PRE_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 766
| F11C | HONI | Ontario | 1 | ac | 15.3 | 9.4444 | 115 | 6.3823 | 3 | [5 empty] | 98.4491 | 108.4016 | Speedsville JCT | ON_SPS_JCT | Speed River JCT | ON_SPR_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 767
| F11C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Speed River JCT | ON_SPR_JCT | Cedar TS | ON_CED_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 768
| F12C | HONI | Ontario | 1 | ac | 4.8 | 2.963 | 115 | 2.0023 | 3 | [5 empty] | 98.4491 | 108.4016 | Freeport SWS | ON_FPT_SWS | Kitchener Graber JCT | ON_KGB_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 769
| F12C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kitchener Graber JCT | ON_KGB_JCT | Kitchener MTS #5 | ON_KM5_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 770
| F12C | HONI | Ontario | 1 | ac | 8.6 | 5.3086 | 115 | 3.5874 | 3 | [5 empty] | 98.4491 | 108.4016 | Freeport SWS | ON_FPT_SWS | Speedsville JCT | ON_SPS_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 771
| F12C | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 115 | 0.45886 | 3 | [5 empty] | 98.4491 | 108.4016 | Speedsville JCT | ON_SPS_JCT | Preston TS | ON_PRE_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 772
| F12C | HONI | Ontario | 1 | ac | 15.3 | 9.4444 | 115 | 6.3823 | 3 | [5 empty] | 98.4491 | 108.4016 | Speedsville JCT | ON_SPS_JCT | Speed River JCT | ON_SPR_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 773
| F12C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Speed River JCT | ON_SPR_JCT | Cedar TS | ON_CED_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 774
| M20D | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 230 | 0.528 | 3 | [5 empty] | 402 | 435 | Detweiler JCT | ON_DET_JCT | Detweiler TS | ON_DET_TSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1288
| M20D | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Detweiler JCT | ON_DET_JCT | Kitchener MTS #6 | ON_KM6_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1289
| M20D | HONI | Ontario | 1 | ac | 17 | 10.4938 | 230 | 8.16 | 3 | [5 empty] | 402 | 435 | Detweiler JCT | ON_DET_JCT | Kitchener #8 JCT | ON_KJ8_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1290
| M20D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Kitchener #8 JCT | ON_KJ8_JCT | Kitchener MTS #8 | ON_KM8_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1291
| M20D | HONI | Ontario | 1 | ac | 24.6 | 15.1852 | 230 | 11.808 | 3 | [5 empty] | 402 | 435 | Kitchener #8 JCT | ON_KJ8_JCT | Galt JCT | ON_GTT_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1292
| M20D | HONI | Ontario | 1 | ac | 17.2 | 10.6173 | 230 | 8.256 | 3 | [5 empty] | 402 | 435 | Galt JCT | ON_GTT_JCT | Preston JCT | ON_PRE_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1293
| M20D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Preston JCT | ON_PRE_JCT | Galt TS | ON_GTT_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1294
| M20D | HONI | Ontario | 1 | ac | 4.3 | 2.6543 | 230 | 2.064 | 3 | [5 empty] | 402 | 435 | Preston JCT | ON_PRE_JCT | Cambridge #1 JCT | ON_CMB_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1295
| M20D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Cambridge #1 JCT | ON_CMB_JCT | Energy Inc(Cam) MTS#1 | ON_ENI_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1296
| M20D | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Cambridge #1 JCT | ON_CMB_JCT | Preston TS | ON_PRE_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1297
| M20D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Galt JCT | ON_GTT_JCT | Galt South JCT | ON_GTS_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1298
| M21D | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 230 | 0.528 | 3 | [5 empty] | 402 | 435 | Detweiler JCT | ON_DET_JCT | Detweiler TS | ON_DET_TSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1302
| M21D | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Detweiler JCT | ON_DET_JCT | Kitchener MTS #6 | ON_KM6_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1303
| M21D | HONI | Ontario | 1 | ac | 17 | 10.4938 | 230 | 8.16 | 3 | [5 empty] | 402 | 435 | Detweiler JCT | ON_DET_JCT | Kitchener #8 JCT | ON_KJ8_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1304
| M21D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Kitchener #8 JCT | ON_KJ8_JCT | Kitchener MTS #8 | ON_KM8_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1305
| M21D | HONI | Ontario | 1 | ac | 24.6 | 15.1852 | 230 | 11.808 | 3 | [5 empty] | 402 | 435 | Kitchener #8 JCT | ON_KJ8_JCT | Galt North JCT | ON_GTN_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1306
| M21D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Galt North JCT | ON_GTN_JCT | Galt JCT | ON_GTT_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1307
| M21D | HONI | Ontario | 1 | ac | 15.2 | 9.3827 | 230 | 7.296 | 3 | [5 empty] | 402 | 435 | Galt JCT | ON_GTT_JCT | Ameristeel Cambridge JCT | ON_AMC_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1308
| M21D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Ameristeel Cambridge JCT | ON_AMC_JCT | Ameristeel Cambridge TS | ON_AMC_ISS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1309
| M21D | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Ameristeel Cambridge JCT | ON_AMC_JCT | Preston JCT | ON_PRE_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1310
| M21D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Preston JCT | ON_PRE_JCT | Galt TS | ON_GTT_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1311
| M21D | HONI | Ontario | 1 | ac | 4.3 | 2.6543 | 230 | 2.064 | 3 | [5 empty] | 402 | 435 | Preston JCT | ON_PRE_JCT | Cambridge #1 JCT | ON_CMB_JCT | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1312
| M21D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Cambridge #1 JCT | ON_CMB_JCT | Energy Inc(Cam) MTS#1 | ON_ENI_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1313
| M21D | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Cambridge #1 JCT | ON_CMB_JCT | Preston TS | ON_PRE_DSS | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG) |  | 1314
| H24S | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | AP North Bay JCT | ON_APB_JCT | Grant JCT | ON_GRT_JCT | Hydro One. 2019. 2019 Wood Replacement Program Circuit H24S - General Area Map |  | 846
| H24S | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Grant JCT | ON_GRT_JCT | Crystal Falls TS | ON_CRY_DSS | Hydro One. 2019. 2019 Wood Replacement Program Circuit H24S - General Area Map |  | 847
| H24S | HONI | Ontario | 1 | ac | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Grant JCT | ON_GRT_JCT | Martindale TS | ON_MTD_DSS | Hydro One. 2019. 2019 Wood Replacement Program Circuit H24S - General Area Map |  | 848
| B1 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Beach Road JCT | ON_BCR_JCT | Beach TS | ON_BCH_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 156
| B10 | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Gage JCT | ON_GAG_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 157
| B10 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gage JCT | ON_GAG_JCT | Gage TS | ON_GAG_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 158
| B10 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gage JCT | ON_GAG_JCT | Birmingham TS | ON_BRM_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 159
| B11 | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Gage JCT | ON_GAG_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 160
| B11 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gage JCT | ON_GAG_JCT | Gage TS | ON_GAG_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 161
| B11 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gage JCT | ON_GAG_JCT | Birmingham TS | ON_BRM_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 162
| B12 | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Dundas #2 JCT | ON_DD2_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 163
| B12 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas #2 JCT | ON_DD2_JCT | Dundas #2 TS | ON_DD2_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 164
| B12 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas #2 JCT | ON_DD2_JCT | Horning Mountain JCT | ON_HGM_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 165
| B12 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Horning Mountain JCT | ON_HGM_JCT | Newton TS | ON_NWT_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 166
| B12 | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Horning Mountain JCT | ON_HGM_JCT | Alford JCT | ON_ALF_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 167
| B12 | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Alford JCT | ON_ALF_JCT | Mohawk Str 31 EP JCT | ON_MHS_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 168
| B12 | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Alford JCT | ON_ALF_JCT | Powerline JCT | ON_PWL_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 169
| B12 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Powerline JCT | ON_PWL_JCT | Powerline MTS | ON_PWL_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 170
| B12 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Powerline JCT | ON_PWL_JCT | Brant TS | ON_BRT_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 171
| B13 | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Dundas #2 JCT | ON_DD2_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 172
| B13 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas #2 JCT | ON_DD2_JCT | Dundas #2 TS | ON_DD2_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 173
| B13 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas #2 JCT | ON_DD2_JCT | Horning Mountain JCT | ON_HGM_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 174
| B13 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Horning Mountain JCT | ON_HGM_JCT | Newton TS | ON_NWT_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 175
| B13 | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Horning Mountain JCT | ON_HGM_JCT | Alford JCT | ON_ALF_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 176
| B13 | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Alford JCT | ON_ALF_JCT | Powerline JCT | ON_PWL_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 177
| B13 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Powerline JCT | ON_PWL_JCT | Powerline MTS | ON_PWL_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 178
| B13 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Powerline JCT | ON_PWL_JCT | Brant TS | ON_BRT_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 179
| B3 | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Dundas JCT | ON_DDS_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 238
| B3 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas JCT | ON_DDS_JCT | Dundas TS | ON_DDS_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 239
| B3 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas JCT | ON_DDS_JCT | McMaster JCT | ON_MCM_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 240
| B3 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | McMaster JCT | ON_MCM_JCT | McMaster TS | ON_MCM_ISS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 241
| B3 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | McMaster JCT | ON_MCM_JCT | Horning Mountain JCT | ON_HGM_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 242
| B3 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Horning Mountain JCT | ON_HGM_JCT | Newton TS | ON_NWT_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 243
| B3 | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Horning Mountain JCT | ON_HGM_JCT | Glanford JCT | ON_GLF_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 244
| B3 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Glanford JCT | ON_GLF_JCT | Mohawk TS | ON_MOH_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 245
| B4 | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Dundas JCT | ON_DDS_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 255
| B4 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas JCT | ON_DDS_JCT | Dundas TS | ON_DDS_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 256
| B4 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dundas JCT | ON_DDS_JCT | McMaster JCT | ON_MCM_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 257
| B4 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | McMaster JCT | ON_MCM_JCT | McMaster TS | ON_MCM_ISS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 258
| B4 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | McMaster JCT | ON_MCM_JCT | Horning Mountain JCT | ON_HGM_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 259
| B4 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Horning Mountain JCT | ON_HGM_JCT | Newton TS | ON_NWT_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 260
| B4 | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Horning Mountain JCT | ON_HGM_JCT | Glanford JCT | ON_GLF_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 261
| B4 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Glanford JCT | ON_GLF_JCT | Mohawk TS | ON_MOH_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 262
| B6C | HONI | Ontario | 1 | ac | 12.4 | 7.6543 | 115 | 5.1726 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Harper's JCT | ON_HRP_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 331
| B6C | HONI | Ontario | 1 | ac | 20.3 | 12.5309 | 115 | 8.468 | 3 | [5 empty] | 98.4491 | 108.4016 | Harper's JCT | ON_HRP_JCT | Puslinch JCT | ON_PUS_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 332
| B6C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Puslinch JCT | ON_PUS_JCT | Puslinch DS | ON_PUS_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 333
| B6C | HONI | Ontario | 1 | ac | 4.4 | 2.716 | 115 | 1.8354 | 3 | [5 empty] | 98.4491 | 108.4016 | Puslinch JCT | ON_PUS_JCT | Arlen MTS JCT | ON_ARL_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 334
| B6C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Arlen MTS JCT | ON_ARL_JCT | Arlen MTS | ON_ARL_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 335
| B6C | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Arlen MTS JCT | ON_ARL_JCT | Hanlon JCT | ON_HLO_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 336
| B6C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hanlon JCT | ON_HLO_JCT | Hanlon TS | ON_HLO_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 337
| B6C | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Hanlon JCT | ON_HLO_JCT | Cedar TS | ON_CED_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 338
| B7 | HONI | Ontario | 1 | ac | 16 | 9.8765 | 115 | 6.6743 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Bronte TS | ON_BRN_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 350
| B8 | HONI | Ontario | 1 | ac | 16 | 9.8765 | 115 | 6.6743 | 3 | [5 empty] | 98.4491 | 108.4016 | Burlington TS | ON_BUR_DSS | Bronte TS | ON_BRN_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 351
| C12 | HONI | Ontario | 1 | ac | 18 | 11.1111 | 115 | 7.5086 | 3 | [5 empty] | 98.4491 | 108.4016 | Caledonia TS | ON_CAL_DSS | Hartford JCT | ON_HRT_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 379
| C12 | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Hartford JCT | ON_HRT_JCT | Vanessa JCT | ON_VNA_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 380
| C12 | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vanessa JCT | ON_VNA_JCT | Bloomsburg JCT | ON_BLO_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 381
| C12 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bloomsburg JCT | ON_BLO_JCT | Bloomsburg DS | ON_BLO_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 382
| C12 | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 115 | 0.62571 | 3 | [5 empty] | 98.4491 | 108.4016 | Bloomsburg JCT | ON_BLO_JCT | Norfolk TS | ON_NOR_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 383
| C9 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Caledonia TS | ON_CAL_DSS | Caledonia Q35M JCT | ON_CAQ_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 522
| C9 | HONI | Ontario | 1 | ac | 18 | 11.1111 | 115 | 7.5086 | 3 | [5 empty] | 98.4491 | 108.4016 | Caledonia Q35M JCT | ON_CAQ_JCT | Hartford JCT | ON_HRT_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 523
| C9 | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Hartford JCT | ON_HRT_JCT | Vanessa JCT | ON_VNA_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 524
| C9 | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vanessa JCT | ON_VNA_JCT | Bloomsburg JCT | ON_BLO_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 525
| C9 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bloomsburg JCT | ON_BLO_JCT | Bloomsburg DS | ON_BLO_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 526
| C9 | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 115 | 0.62571 | 3 | [5 empty] | 98.4491 | 108.4016 | Bloomsburg JCT | ON_BLO_JCT | Norfolk TS | ON_NOR_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 527
| H9W | HONI | Ontario | 1 | ac | 45 | 27.7778 | 115 | 18.7714 | 3 | [5 empty] | 98.4491 | 108.4016 | Beach TS | ON_BCH_DSS | West Lincoln JCT | ON_WLN_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 955
| H9W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | West Lincoln JCT | ON_WLN_JCT | West Lincoln GS | ON_WLN_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 956
| HL3 | HONI | Ontario | 1 | ac | 3.7 | 2.284 | 115 | 1.5434 | 3 | [5 empty] | 98.4491 | 108.4016 | Beach TS | ON_BCH_DSS | Birmingham TS | ON_BRM_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 965
| HL3 | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Birmingham TS | ON_BRM_DSS | Specialty Bar JCT | ON_SPB_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 966
| HL3 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Specialty Bar JCT | ON_SPB_JCT | Specialty Bar TS | ON_SPB_ISS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 967
| HL3 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Specialty Bar JCT | ON_SPB_JCT | Stirton TS | ON_STR_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 968
| HL3 | HONI | Ontario | 1 | ac | 2.7 | 1.6667 | 115 | 1.1263 | 3 | [5 empty] | 98.4491 | 108.4016 | Stirton TS | ON_STR_DSS | Elgin TS | ON_ELG_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 969
| HL3 | HONI | Ontario | 1 | ac | 3.2 | 1.9753 | 115 | 1.3349 | 3 | [5 empty] | 98.4491 | 108.4016 | Elgin TS | ON_ELG_DSS | Newton TS | ON_NWT_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 970
| HL4 | HONI | Ontario | 1 | ac | 3.7 | 2.284 | 115 | 1.5434 | 3 | [5 empty] | 98.4491 | 108.4016 | Beach TS | ON_BCH_DSS | Birmingham TS | ON_BRM_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 971
| HL4 | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Birmingham TS | ON_BRM_DSS | Specialty Bar JCT | ON_SPB_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 972
| HL4 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Specialty Bar JCT | ON_SPB_JCT | Specialty Bar TS | ON_SPB_ISS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 973
| HL4 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Specialty Bar JCT | ON_SPB_JCT | Stirton TS | ON_STR_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 974
| HL4 | HONI | Ontario | 1 | ac | 2.7 | 1.6667 | 115 | 1.1263 | 3 | [5 empty] | 98.4491 | 108.4016 | Stirton TS | ON_STR_DSS | Elgin TS | ON_ELG_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 975
| HL4 | HONI | Ontario | 1 | ac | 3.2 | 1.9753 | 115 | 1.3349 | 3 | [5 empty] | 98.4491 | 108.4016 | Elgin TS | ON_ELG_DSS | Newton TS | ON_NWT_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 976
| K1G | HONI | Ontario | 1 | ac | 1.7 | 1.0494 | 115 | 0.70914 | 3 | [5 empty] | 98.4491 | 108.4016 | Kenilworth TS | ON_KNL_DSS | Gage TS | ON_GAG_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1005
| K2G | HONI | Ontario | 1 | ac | 1.7 | 1.0494 | 115 | 0.70914 | 3 | [5 empty] | 98.4491 | 108.4016 | Kenilworth TS | ON_KNL_DSS | Gage TS | ON_GAG_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1030
| M27B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Middleport TS | ON_MPT_TSS | Carluke JCT | ON_CLK_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1324
| M27B | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Southcote JCT | ON_SCT_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1325
| M27B | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Southcote JCT | ON_SCT_JCT | Horning JCT | ON_HNG_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1326
| M27B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Horning JCT | ON_HNG_JCT | Horning TS | ON_HNG_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1327
| M27B | HONI | Ontario | 1 | ac | 16 | 9.8765 | 230 | 7.68 | 3 | [5 empty] | 402 | 435 | Horning JCT | ON_HNG_JCT | Burlington TS | ON_BUR_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1328
| M28B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Middleport TS | ON_MPT_TSS | Carluke JCT | ON_CLK_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1329
| M28B | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Southcote JCT | ON_SCT_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1330
| M28B | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Southcote JCT | ON_SCT_JCT | Horning JCT | ON_HNG_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1331
| M28B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Horning JCT | ON_HNG_JCT | Horning TS | ON_HNG_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1332
| M28B | HONI | Ontario | 1 | ac | 16 | 9.8765 | 230 | 7.68 | 3 | [5 empty] | 402 | 435 | Horning JCT | ON_HNG_JCT | Burlington TS | ON_BUR_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1333
| N21J | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Nanticoke TS | ON_NTK_TSS | Stelco JCT | ON_STO_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1443
| N21J | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Stelco JCT | ON_STO_JCT | Jarvis TS | ON_JRV_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1444
| N21J | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Stelco JCT | ON_STO_JCT | Nanticoke Creek JCT | ON_NTC_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1445
| N22J | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Nanticoke TS | ON_NTK_TSS | Stelco JCT | ON_STO_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1453
| N22J | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Stelco JCT | ON_STO_JCT | Jarvis TS | ON_JRV_DSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1454
| N22J | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Stelco JCT | ON_STO_JCT | Nanticoke Creek JCT | ON_NTC_JCT | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1455
| N580M | HONI | Ontario | 1 | ac | 35 | 21.6049 | 500 | 13.825 | 3 | [5 empty] | 2550 | 3225 | Nanticoke TS | ON_NTK_TSS | Middleport TS | ON_MPT_TSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1466
| N581M | HONI | Ontario | 1 | ac | 35 | 21.6049 | 500 | 13.825 | 3 | [5 empty] | 2550 | 3225 | Nanticoke TS | ON_NTK_TSS | Middleport TS | ON_MPT_TSS | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1467
| D6 | HONI | Ontario | 1 | ac | 43 | 26.5432 | 230 | 20.64 | 3 | [5 empty] | 402 | 435 | Chalk River TS | ON_CKR_ISS | Petawawa JCT | ON_PET_JCT | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 634
| D6 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Craig JCT | ON_CRG_JCT | Craig DS | ON_CRG_DSS | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 635
| D6 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Craig JCT | ON_CRG_JCT | Petawawa DS | ON_PET_DSS | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 636
| D6 | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Deep River DS | ON_DPR_DSS | Chalk River TS | ON_CKR_ISS | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 637
| D6 | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Des Joachims JCT | ON_DEJ_JCT | Des Joachims DS | ON_DEJ_DSS | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 638
| D6 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Des Joachims JCT | ON_DEJ_JCT | Tee Lake JCT | ON_TEE_JCT | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 639
| D6 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Forest Lea JCT | ON_FRL_JCT | Forest Lea DS | ON_FRL_DSS | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 640
| D6 | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Forest Lea JCT | ON_FRL_JCT | Pembroke TS | ON_PEM_DSS | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 641
| D6 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Petawawa JCT | ON_PET_JCT | Craig JCT | ON_CRG_JCT | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 642
| D6 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Petawawa JCT | ON_PET_JCT | Forest Lea JCT | ON_FRL_JCT | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 643
| D6 | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Tee Lake JCT | ON_TEE_JCT | Deep River DS | ON_DPR_DSS | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 644
| D6 | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Tee Lake JCT | ON_TEE_JCT | NPD #2 STR10 JCT | ON_NPD_JCT | Hydro One. 2019. Des Joachims Transformer Station to Pembroke Transformer Station: Transmission Line Refurbishment |  | 645
| ALGOMA1 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Third Line TS | ON_TDL_DSS | Patrick St TS | ON_PTS_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region | Also called "No. 1 Algoma" | 152
| ALGOMA2 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Third Line TS | ON_TDL_DSS | Patrick St TS | ON_PTS_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region | Also called "No. 2 Algoma" | 153
| ALGOMA3 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Third Line TS | ON_TDL_DSS | Patrick St TS | ON_PTS_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region | Also called "No. 3 Algoma" | 154
| ANDREWS1 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Gartshore TS | ON_GSO_DSS | Andrews TS | ON_AND_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 155
| CLERGUE1 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Patrick St TS | ON_PTS_DSS | Clergue TS | ON_CGU_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 528
| CLERGUE2 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Patrick St TS | ON_PTS_DSS | Clergue TS | ON_CGU_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 529
| GL1SM | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Third Line TS | ON_TDL_DSS | St. Marys MTS | ON_STM_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 793
| GL1TA | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Third Line TS | ON_TDL_DSS | Tarentorus MTS | ON_TRT_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 794
| GL2SM | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Third Line TS | ON_TDL_DSS | St. Marys MTS | ON_STM_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 795
| GL2TA | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Third Line TS | ON_TDL_DSS | Tarentorus MTS | ON_TRT_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 796
| GARTSHO1 | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Mackay TS | ON_MKY_DSS | Gartshore TS | ON_GSO_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 797
| GARTSHO2 | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Mackay TS | ON_MKY_DSS | Gartshore TS | ON_GSO_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 798
| GARTSHO3 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gartshore TS | ON_GSO_DSS | Gartshore GS | ON_GSO_GSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 799
| HARRIS1 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Magpie TS | ON_MGP_DSS | Harris GS | ON_HRS_GSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 957
| HBUS | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Rabbit Lake SWS | ON_RBL_SWS | Kenora DS | ON_KNO_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 958
| HIGHFAL1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami JCT | ON_ANJ_JCT | Wawa TS | ON_WAW_TSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 959
| HIGHFAL1 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami TS | ON_ANJ_DSS | DA Watson TS | ON_DAW_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 960
| HIGHFAL1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami TS | ON_ANJ_DSS | Anjigami JCT | ON_ANJ_JCT | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 961
| HIGHFAL2 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami JCT | ON_ANJ_JCT | Wawa TS | ON_WAW_TSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 962
| HIGHFAL2 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami TS | ON_ANJ_DSS | DA Watson TS | ON_DAW_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 963
| HIGHFAL2 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami TS | ON_ANJ_DSS | Anjigami JCT | ON_ANJ_JCT | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 964
| HLNGWTH1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami TS | ON_ANJ_DSS | Anjigami JCT #2 | ON_ANJ_JCT | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 977
| HLNGWTH1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami JCT #2 | ON_AN2_JCT | Hollingsworth TS | ON_HGW_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 978
| HLNGWTH1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Anjigami JCT #2 | ON_AN2_JCT | Wawa TS | ON_WAW_TSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 979
| HOGG1 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gartshore TS | ON_GSO_DSS | Hogg GS | ON_HOG_GSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 980
| K24G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Goulais JCT | ON_GLA_JCT | Goulais SWS | ON_GLA_SWS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1024
| K24G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Heyden JCT | ON_HYD_JCT | Heyden SWS | ON_HYD_SWS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1025
| K24G | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Heyden JCT | ON_HYD_JCT | Goulais JCT | ON_GLA_JCT | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1026
| K24G | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Heyden JCT | ON_HYD_JCT | Third Line TS | ON_TDL_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1027
| K24G | HONI | Ontario | 1 | ac | 78 | 48.1481 | 230 | 37.44 | 3 | [5 empty] | 402 | 435 | Mackay TS | ON_MKY_DSS | Heyden JCT | ON_HYD_JCT | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1028
| LEIGHBY1 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Patrick St TS | ON_PTS_DSS | Wallace Terrace TS | ON_WTC_ISS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1274
| LEIGHBY1 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Wallace Terrace TS | ON_WTC_ISS | Flakeboard TS | ON_FKB_ISS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1275
| MAGPIE1 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | DA Watson TS | ON_DAW_DSS | Magpie SWS | ON_MGP_SWS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1436
| MISSION1 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Magpie SWS | ON_MGP_SWS | Mission Falls GS | ON_MSF_GSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1437
| NAV1 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Third Line TS | ON_TDL_DSS | Northern Ave TS | ON_NAV_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region | Circuit ID name invented | 1508
| P21G | HONI | Ontario | 1 | ac | 135 | 83.3333 | 230 | 64.8 | 2.294 | [5 empty] | 307.3907 | 332.6242 | Third Line TS | ON_TDL_DSS | Mississagi TS | ON_MSS_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1516
| P22G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Echo River JCT | ON_ERV_JCT | Echo River DS | ON_ERV_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1528
| P22G | HONI | Ontario | 1 | ac | 100 | 61.7284 | 230 | 48 | 2.796 | [5 empty] | 374.6673 | 405.4236 | Echo River JCT | ON_ERV_JCT | Mississagi TS | ON_MSS_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1529
| P22G | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Third Line TS | ON_TDL_DSS | Echo River JCT | ON_ERV_JCT | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1530
| SAULT3 | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Batchawana TS | ON_BWA_DSS | Goulais Bay TS | ON_GLB_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region | Also called "No.3 Sault" | 1897
| SAULT4 | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Goulais Bay TS | ON_GLB_DSS | Third Line TS | ON_TDL_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region | Also called "No.3 Sault" | 1898
| SAULT5 | HONI | Ontario | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Mackay TS | ON_MKY_DSS | Batchawana TS | ON_BWA_DSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region | Also called "No.3 Sault" | 1899
| STEEPHL1 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Magpie SWS | ON_MGP_SWS | Wesdome Gold Mines JCT | ON_WGM_JCT | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1900
| STEEPHL1 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Wesdome Gold Mines JCT | ON_WGM_JCT | Wesdome Gold Mines TS | ON_WGM_ISS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1901
| STEEPHL1 | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Wesdome Gold Mines JCT | ON_WGM_JCT | Steephill Falls GS | ON_SHF_GSS | Hydro One. 2019. Needs Assessment Report East Lake Superior Region |  | 1902
| V43 | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Goreway TS | ON_GRW_DSS | Goreway JCT | ON_GRW_JCT | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region |  | 2010
| V43 | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Goreway JCT | ON_GRW_JCT | Claireville TS | ON_CLV_TSS | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region |  | 2011
| C10A | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Seaton MTS | ON_SEN_DSS | Hydro One. 2020. GTA East Regional Infrastructure Plan |  | 370
| C10A | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Seaton MTS | ON_SEN_DSS | Duffin JCT | ON_DFN_JCT | Hydro One. 2020. GTA East Regional Infrastructure Plan |  | 371
| T28C | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Duffin JCT | ON_DFN_JCT | Seaton MTS | ON_SEN_DSS | Hydro One. 2020. GTA East Regional Infrastructure Plan |  | 372
| T28C | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Seaton MTS | ON_SEN_DSS | Cherrywood TS | ON_CHW_DSS | Hydro One. 2020. GTA East Regional Infrastructure Plan |  | 373
| T25B | HONI | Ontario | 1 | ac | 115 | 70.9877 | 230 | 55.2 | 2.5498 | [5 empty] | 341.6769 | 369.725 | Clarington TS | ON_CLG_TSS | Belleville TS | ON_BLV_DSS | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region |  | 1923
| T31H | HONI | Ontario | 1 | ac | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Clarington TS | ON_CLG_TSS | Havelock TS | ON_HVL_DSS | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region |  | 1939
| T32H | HONI | Ontario | 1 | ac | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Clarington TS | ON_CLG_TSS | Havelock TS | ON_HVL_DSS | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region |  | 1940
| C10A | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Duffin JCT | ON_DFN_JCT | Agincourt JCT | ON_AGN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 374
| C10A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Agincourt JCT | ON_AGN_JCT | Agincourt TS | ON_AGN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 375
| C10A | HONI | Ontario | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Agincourt JCT | ON_AGN_JCT | Cavanagh MTS | ON_CVN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 376
| C10A | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Agincourt JCT | ON_AGN_JCT | Leaside JCT | ON_LES_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 377
| C11R | HONI | Ontario | 1 | ac | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Leaside JCT | ON_LES_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 378
| C14L | HONI | Ontario | 1 | ac | 16 | 9.8765 | 230 | 7.68 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Scarboro JCT | ON_SCB_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 384
| C14L | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 230 | 2.16 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Bermondsey TS | ON_BMD_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 385
| C14L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Scarboro TS | ON_SCB_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 386
| C14L | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Warden TS | ON_WDN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 387
| C14L | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 230 | 1.68 | 3 | [5 empty] | 402 | 435 | Bermondsey TS | ON_BMD_DSS | Leaside TS | ON_LES_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 388
| C15L | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Sheppard TS | ON_SHP_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 389
| C15L | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Sheppard TS | ON_SHP_DSS | Scarboro JCT | ON_SCB_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 390
| C15L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Scarboro TS | ON_SCB_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 391
| C15L | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Leaside TS | ON_LES_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 392
| C16L | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Sheppard TS | ON_SHP_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 393
| C16L | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Sheppard TS | ON_SHP_DSS | Leaside TS | ON_LES_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 394
| C17L | HONI | Ontario | 1 | ac | 16 | 9.8765 | 230 | 7.68 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Scarboro JCT | ON_SCB_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 395
| C17L | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Warden TS | ON_WDN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 396
| C17L | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 230 | 2.16 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Bermondsey TS | ON_BMD_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 397
| C17L | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 230 | 1.68 | 3 | [5 empty] | 402 | 435 | Bermondsey TS | ON_BMD_DSS | Leaside TS | ON_LES_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 398
| C20R | HONI | Ontario | 1 | ac | 14.5 | 8.9506 | 230 | 6.96 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Agincourt JCT | ON_AGN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 408
| C20R | HONI | Ontario | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Agincourt JCT | ON_AGN_JCT | Cavanagh MTS | ON_CVN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 409
| C20R | HONI | Ontario | 1 | ac | 5.5 | 3.3951 | 230 | 2.64 | 3 | [5 empty] | 402 | 435 | Agincourt JCT | ON_AGN_JCT | Leslie JCT | ON_LSL_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 410
| C20R | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Leslie JCT | ON_LSL_JCT | Fairchild TS | ON_FCD_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 411
| C20R | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Fairchild TS | ON_FCD_DSS | Bathurst JCT | ON_BTH_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 412
| C20R | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Bathurst JCT | ON_BTH_JCT | Finch JCT | ON_FIN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 413
| C20R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Finch JCT | ON_FIN_JCT | Finch TS | ON_FIN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 414
| C20R | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Finch JCT | ON_FIN_JCT | Richview TS | ON_RCV_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 415
| C2L | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Ellesmere JCT | ON_ELM_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 451
| C2L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Ellesmere JCT | ON_ELM_JCT | Ellesmere TS | ON_ELM_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 452
| C2L | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Ellesmere JCT | ON_ELM_JCT | Scarboro JCT | ON_SCB_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 453
| C2L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Scarboro TS | ON_SCB_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 454
| C2L | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Leaside TS | ON_LES_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 455
| C35P | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Markham #2 JCT | ON_MJ2_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 465
| C35P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Markham #2 JCT | ON_MJ2_JCT | Markham #2 MTS | ON_MM2_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 466
| C35P | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Markham #2 JCT | ON_MJ2_JCT | Markham #3 JCT | ON_MJ3_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 467
| C35P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Markham #3 JCT | ON_MJ3_JCT | Markham #3 MTS | ON_MM3_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 468
| C35P | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 230 | 1.2 | 3 | [5 empty] | 402 | 435 | Markham #3 JCT | ON_MJ3_JCT | Parkway TS | ON_PKW_TSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 469
| C36P | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Markham #2 JCT | ON_MJ2_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 470
| C36P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Markham #2 JCT | ON_MJ2_JCT | Markham #2 MTS | ON_MM2_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 471
| C36P | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Markham #2 JCT | ON_MJ2_JCT | Markham #3 JCT | ON_MJ3_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 472
| C36P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Markham #3 JCT | ON_MJ3_JCT | Markham #3 MTS | ON_MM3_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 473
| C36P | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 230 | 1.2 | 3 | [5 empty] | 402 | 435 | Markham #3 JCT | ON_MJ3_JCT | Parkway TS | ON_PKW_TSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 474
| C3L | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Ellesmere JCT | ON_ELM_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 477
| C3L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Ellesmere JCT | ON_ELM_JCT | Ellesmere TS | ON_ELM_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 478
| C3L | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Ellesmere JCT | ON_ELM_JCT | Scarboro JCT | ON_SCB_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 479
| C3L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Scarboro TS | ON_SCB_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 480
| C3L | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Scarboro JCT | ON_SCB_JCT | Leaside TS | ON_LES_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 481
| C4R | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Malvern TS | ON_MLV_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 484
| C4R | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Malvern TS | ON_MLV_DSS | Agincourt JCT | ON_AGN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 485
| C4R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Agincourt JCT | ON_AGN_JCT | Agincourt TS | ON_AGN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 486
| C4R | HONI | Ontario | 1 | ac | 5.5 | 3.3951 | 230 | 2.64 | 3 | [5 empty] | 402 | 435 | Agincourt JCT | ON_AGN_JCT | Leslie TS | ON_LSL_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 487
| C4R | HONI | Ontario | 1 | ac | 13.5 | 8.3333 | 230 | 6.48 | 3 | [5 empty] | 402 | 435 | Leslie TS | ON_LSL_DSS | Finch JCT | ON_FIN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 488
| C4R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Finch JCT | ON_FIN_JCT | Finch TS | ON_FIN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 489
| C4R | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Finch JCT | ON_FIN_JCT | Richview TS | ON_RCV_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 490
| C550VP | HONI | Ontario | 1 | ac | 17.5 | 10.8025 | 500 | 6.9125 | 3 | [5 empty] | 2550 | 3225 | Cherrywood TS | ON_CHW_DSS | Parkway JCT | ON_PKW_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 491
| C550VP | HONI | Ontario | 1 | ac | 25 | 15.4321 | 500 | 9.875 | 3 | [5 empty] | 2550 | 3225 | Parkway JCT | ON_PKW_JCT | Claireville TS | ON_CLV_TSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 492
| C550VP | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 500 | 0.0395 | 3 | [5 empty] | 2550 | 3225 | Parkway JCT | ON_PKW_JCT | Parkway TS | ON_PKW_TSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 493
| C551V | HONI | Ontario | 1 | ac | 42.5 | 26.2346 | 500 | 16.7875 | 3 | [5 empty] | 2550 | 3225 | Cherrywood TS | ON_CHW_DSS | Claireville TS | ON_CLV_TSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 494
| C552V | HONI | Ontario | 1 | ac | 42.5 | 26.2346 | 500 | 16.7875 | 3 | [5 empty] | 2550 | 3225 | Cherrywood TS | ON_CHW_DSS | Claireville TS | ON_CLV_TSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 495
| C553VP | HONI | Ontario | 1 | ac | 17.5 | 10.8025 | 500 | 6.9125 | 3 | [5 empty] | 2550 | 3225 | Cherrywood TS | ON_CHW_DSS | Parkway JCT | ON_PKW_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 496
| C553VP | HONI | Ontario | 1 | ac | 25 | 15.4321 | 500 | 9.875 | 3 | [5 empty] | 2550 | 3225 | Parkway JCT | ON_PKW_JCT | Claireville TS | ON_CLV_TSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 497
| C553VP | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 500 | 0.0395 | 3 | [5 empty] | 2550 | 3225 | Parkway JCT | ON_PKW_JCT | Parkway TS | ON_PKW_TSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 498
| C5R | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Malvern TS | ON_MLV_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 502
| C5R | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 230 | 2.16 | 3 | [5 empty] | 402 | 435 | Malvern TS | ON_MLV_DSS | Agincourt JCT | ON_AGN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 503
| C5R | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 230 | 2.16 | 3 | [5 empty] | 402 | 435 | Agincourt JCT | ON_AGN_JCT | Leslie TS | ON_LSL_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 504
| C5R | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Leslie TS | ON_LSL_DSS | Richview TS | ON_RCV_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 505
| D6Y | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Duplex TS | ON_DPX_DSS | Glengrove TS | ON_GLG_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 663
| L4S | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Bermondsey JCT | ON_BMD_JCT | Scarboro TS | ON_SCB_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 1249
| L5S | HONI | Ontario | 1 | ac | 4.5 | 2.7778 | 115 | 1.8771 | 3 | [5 empty] | 98.4491 | 108.4016 | Bermondsey JCT | ON_BMD_JCT | Scarboro TS | ON_SCB_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 1255
| T28C | HONI | Ontario | 1 | ac | 22 | 13.5802 | 230 | 10.56 | 3 | [5 empty] | 402 | 435 | Clarington TS | ON_CLG_TSS | Duffin JCT | ON_DFN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 1925
| V43 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Woodbridge JCT | ON_WDB_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 2012
| V43 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Woodbridge JCT | ON_WDB_JCT | Woodbridge TS | ON_WDB_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 2013
| V44 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Woodbridge JCT | ON_WDB_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 2024
| V44 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Woodbridge JCT | ON_WDB_JCT | Woodbridge TS | ON_WDB_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan |  | 2025
| P21R | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Parkway TS | ON_PKW_TSS | Markham #1 JCT | ON_MJ1_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1517
| P21R | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Markham #1 JCT | ON_MJ1_JCT | Markham #1 MTS | ON_MM1_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1518
| P21R | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Markham #1 JCT | ON_MJ1_JCT | IBM Markham JCT | ON_IBM_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1519
| P21R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | IBM Markham JCT | ON_IBM_JCT | IBM Markham TS | ON_IBM_ISS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1520
| P21R | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | IBM Markham JCT | ON_IBM_JCT | Leslie East JCT | ON_LSE_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1521
| P21R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Leslie East JCT | ON_LSE_JCT | Leslie TS | ON_LSL_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1522
| P21R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Leslie East JCT | ON_LSE_JCT | Leslie West JCT | ON_LSW_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1523
| P21R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Leslie West JCT | ON_LSW_JCT | Leslie TS | ON_LSL_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1524
| P21R | HONI | Ontario | 1 | ac | 13.5 | 8.3333 | 230 | 6.48 | 3 | [5 empty] | 402 | 435 | Leslie West JCT | ON_LSW_JCT | Finch JCT | ON_FIN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1525
| P21R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Finch JCT | ON_FIN_JCT | Finch TS | ON_FIN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1526
| P21R | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Finch JCT | ON_FIN_JCT | Richview TS | ON_RCV_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1527
| P22R | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Parkway TS | ON_PKW_TSS | Markham #1 JCT | ON_MJ1_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1531
| P22R | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Markham #1 JCT | ON_MJ1_JCT | Markham #1 MTS | ON_MM1_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1532
| P22R | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Markham #1 JCT | ON_MJ1_JCT | IBM Markham JCT | ON_IBM_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1533
| P22R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | IBM Markham JCT | ON_IBM_JCT | IBM Markham TS | ON_IBM_ISS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1534
| P22R | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | IBM Markham JCT | ON_IBM_JCT | Bathurst JCT | ON_BTH_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1535
| P22R | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Bathurst JCT | ON_BTH_JCT | Bathurst TS | ON_BTH_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1536
| P22R | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Bathurst JCT | ON_BTH_JCT | Finch JCT | ON_FIN_JCT | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1537
| P22R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Finch JCT | ON_FIN_JCT | Finch TS | ON_FIN_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1538
| P22R | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Finch JCT | ON_FIN_JCT | Richview TS | ON_RCV_DSS | Hydro One. 2020. Toronto Regional Infrastructure Plan.; Hydro One. 2016. Metro Toronto Regional Infrastructure Plan |  | 1539
| K2Z | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Lauzon JCT | ON_LAU_JCT | Lauzon TS | ON_LAU_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1032
| K2Z | HONI | Ontario | 1 | ac | 18.5 | 11.4198 | 115 | 7.7171 | 3 | [5 empty] | 98.4491 | 108.4016 | Lauzon JCT | ON_LAU_JCT | Woodslee JCT | ON_WDS_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1033
| K2Z | HONI | Ontario | 1 | ac | 13.9 | 8.5802 | 115 | 5.7983 | 3 | [5 empty] | 98.4491 | 108.4016 | Woodslee JCT | ON_WDS_JCT | Gosfield GS JCT | ON_GOS_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1034
| K2Z | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gosfield GS JCT | ON_GOS_JCT | Gosfield GS | ON_GOS_GSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1035
| K2Z | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gosfield GS JCT | ON_GOS_JCT | Kingsville TS | ON_KSV_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1036
| K2Z | HONI | Ontario | 1 | ac | 15.8 | 9.7531 | 115 | 6.5909 | 3 | [5 empty] | 98.4491 | 108.4016 | Lauzon JCT | ON_LAU_JCT | Rourke Line JCT | ON_RLN_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1037
| K2Z | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Rourke Line JCT | ON_RLN_JCT | Belle River JCT | ON_BLR_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1038
| K2Z | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Rourke Line JCT | ON_RLN_JCT | Belle River TS | ON_BLR_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1039
| K2Z | HONI | Ontario | 1 | ac | 21.9 | 13.5185 | 115 | 9.1354 | 3 | [5 empty] | 98.4491 | 108.4016 | Belle River JCT | ON_BLR_JCT | Tilbury JCT | ON_TLB_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1040
| K2Z | HONI | Ontario | 1 | ac | 21.9 | 13.5185 | 115 | 9.1354 | 3 | [5 empty] | 98.4491 | 108.4016 | Woodslee JCT | ON_WDS_JCT | Tilbury JCT | ON_TLB_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1041
| K2Z | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Tilbury JCT | ON_TLB_JCT | Tilbury West JCT | ON_TLW_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1042
| K2Z | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Tilbury West JCT | ON_TLW_JCT | Tilbury TS | ON_TLB_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1043
| K2Z | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Tilbury West JCT | ON_TLW_JCT | Tilbury West DS | ON_TLW_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1044
| K2Z | HONI | Ontario | 1 | ac | 27.7 | 17.0988 | 115 | 11.5549 | 3 | [5 empty] | 98.4491 | 108.4016 | Tilbury JCT | ON_TLB_JCT | Kent JCT | ON_KNT_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1045
| K2Z | HONI | Ontario | 1 | ac | 5.2 | 3.2099 | 115 | 2.1691 | 3 | [5 empty] | 98.4491 | 108.4016 | Kent JCT | ON_KNT_JCT | Kent TS | ON_KNT_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1046
| K6Z | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Lauzon JCT | ON_LAU_JCT | Lauzon TS | ON_LAU_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1092
| K6Z | HONI | Ontario | 1 | ac | 15.8 | 9.7531 | 115 | 6.5909 | 3 | [5 empty] | 98.4491 | 108.4016 | Lauzon JCT | ON_LAU_JCT | Rourke Line JCT | ON_RLN_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1093
| K6Z | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Rourke Line JCT | ON_RLN_JCT | Belle River JCT | ON_BLR_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1094
| K6Z | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Rourke Line JCT | ON_RLN_JCT | Belle River TS | ON_BLR_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1095
| K6Z | HONI | Ontario | 1 | ac | 16.2 | 10 | 115 | 6.7577 | 3 | [5 empty] | 98.4491 | 108.4016 | Belle River JCT | ON_BLR_JCT | Pte-Aux-Roches WF JCT | ON_PAR_JCT | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1096
| K6Z | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pte-Aux-Roches WF JCT | ON_PAR_JCT | Pte-Aux-Roches WF GS | ON_PAR_GSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1097
| K6Z | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pte-Aux-Roches WF JCT | ON_PAR_JCT | Kingsville TS | ON_KSV_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1098
| L28C | HONI | Ontario | 1 | ac | 3.1 | 1.9136 | 230 | 1.488 | 3 | [5 empty] | 402 | 435 | Lynwood JCT | ON_LYN_JCT | Kent TS | ON_KNT_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1208
| L28C | HONI | Ontario | 1 | ac | 4.6 | 2.8395 | 230 | 2.208 | 3 | [5 empty] | 402 | 435 | Lynwood JCT | ON_LYN_JCT | Chatham SWS | ON_CHT_SWS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1209
| L29C | HONI | Ontario | 1 | ac | 3.1 | 1.9136 | 230 | 1.488 | 3 | [5 empty] | 402 | 435 | Lynwood JCT | ON_LYN_JCT | Kent TS | ON_KNT_DSS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1215
| L29C | HONI | Ontario | 1 | ac | 4.6 | 2.8395 | 230 | 2.208 | 3 | [5 empty] | 402 | 435 | Lynwood JCT | ON_LYN_JCT | Chatham SWS | ON_CHT_SWS | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.; IMO. 2002. Connection Assessment & Approval Process. Preliminary Assessment Report For the Proposal by Hydro One Networks Inc to Install a 230/115 kV Auto-transformer at Kent TS |  | 1216
| J1B | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 115 | 0.12514 | 3 | [5 empty] | 98.4491 | 108.4016 | Keith TS | ON_KEI_DSS | Brighton Interface JCT | ON_BTN_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 981
| J20B | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 230 | 0.144 | 3 | [5 empty] | 402 | 435 | Keith TS | ON_KEI_DSS | Brighton Interface JCT | ON_BTN_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 982
| J2N | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 115 | 0.12514 | 3 | [5 empty] | 98.4491 | 108.4016 | Keith TS | ON_KEI_DSS | West Windsor Power SWS | ON_WWP_SWS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 983
| J3E | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Keith TS | ON_KEI_DSS | Crawford JCT | ON_CRW_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 984
| J3E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Crawford JCT | ON_CRW_JCT | Crawford TS | ON_CRW_DSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 985
| J3E | HONI | Ontario | 1 | ac | 6.2 | 3.8272 | 115 | 2.5863 | 3 | [5 empty] | 98.4491 | 108.4016 | Crawford JCT | ON_CRW_JCT | Essex TS | ON_ESX_DSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 986
| J4E | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Crawford JCT | ON_CRW_JCT | Crawford TS | ON_CRW_DSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 987
| J4E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Crawford JCT | ON_CRW_JCT | Essex TS | ON_ESX_DSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 988
| J4E | HONI | Ontario | 1 | ac | 6.2 | 3.8272 | 115 | 2.5863 | 3 | [5 empty] | 98.4491 | 108.4016 | Keith TS | ON_KEI_DSS | Crawford JCT | ON_CRW_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 989
| Z1E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Essex TS | ON_ESX_DSS | Windsor Transalta JCT | ON_WDT_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2197
| Z1E | HONI | Ontario | 1 | ac | 0.2 | 0.12346 | 115 | 0.083429 | 3 | [5 empty] | 98.4491 | 108.4016 | Windsor Transalta JCT | ON_WDT_JCT | Windsor Transalta GS | ON_WDT_GSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2198
| Z1E | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Windsor Transalta JCT | ON_WDT_JCT | Walker JCT | ON_WLK_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2199
| Z1E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Walker JCT | ON_WLK_JCT | Walker TS | ON_WLK_DSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2200
| Z1E | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Walker JCT | ON_WLK_JCT | Jefferson JCT | ON_JFF_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2201
| Z1E | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Jefferson JCT | ON_JFF_JCT | Ford Essex JCT | ON_FDE_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2202
| Z1E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Ford Essex JCT | ON_FDE_JCT | Ford Essex TS | ON_FDE_ISS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2203
| Z1E | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Jefferson JCT | ON_JFF_JCT | Windsor Airport JCT | ON_WDA_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2204
| Z1E | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Windsor Airport JCT | ON_WDA_JCT | Windsor Airport GS | ON_WDA_GSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2205
| Z1E | HONI | Ontario | 1 | ac | 1.6 | 0.98765 | 115 | 0.66743 | 3 | [5 empty] | 98.4491 | 108.4016 | Windsor Airport JCT | ON_WDA_JCT | Lauzon TS | ON_LAU_DSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2206
| Z7E | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Essex TS | ON_ESX_DSS | Walker JCT | ON_WLK_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2207
| Z7E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Walker JCT | ON_WLK_JCT | Walker TS | ON_WLK_DSS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2208
| Z7E | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Walker JCT | ON_WLK_JCT | Jefferson JCT | ON_JFF_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2209
| Z7E | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Jefferson JCT | ON_JFF_JCT | Ford Essex JCT | ON_FDE_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2210
| Z7E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Ford Essex JCT | ON_FDE_JCT | Ford Essex TS | ON_FDE_ISS | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2211
| Z7E | HONI | Ontario | 1 | ac | 1.6 | 0.98765 | 115 | 0.66743 | 3 | [5 empty] | 98.4491 | 108.4016 | Jefferson JCT | ON_JFF_JCT | Lauzon TS | ON_LAU_JCT | IESO. 2005. Connection Assessment & Approval Process Essex TS |  | 2212
| C21J | HONI | Ontario | 1 | ac | 47.9 | 29.5679 | 230 | 22.992 | 3 | [5 empty] | 402 | 435 | Leamington JCT | ON_LEM_JCT | Chatham SWS | ON_CHT_SWS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 416
| C21J | HONI | Ontario | 1 | ac | 17.4 | 10.7407 | 230 | 8.352 | 3 | [5 empty] | 402 | 435 | Malden JCT | ON_MLD_JCT | Sandwich JCT | ON_SNW_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 417
| C21J | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Keith TS | ON_KEI_DSS | Malden JCT | ON_MLD_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 418
| C21J | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Malden JCT | ON_MLD_JCT | Malden TS | ON_MLD_DSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 419
| C21J | HONI | Ontario | 1 | ac | 21 | 12.963 | 230 | 10.08 | 3 | [5 empty] | 402 | 435 | Sandwich JCT | ON_SNW_JCT | Leamington JCT | ON_LEM_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 420
| C21J | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Leamington JCT | ON_LEM_JCT | Leamington TS | ON_LEM_DSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 421
| C22J | HONI | Ontario | 1 | ac | 17.4 | 10.7407 | 230 | 8.352 | 3 | [5 empty] | 402 | 435 | Malden JCT | ON_MLD_JCT | Sandwich JCT | ON_SNW_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 422
| C22J | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Leamington JCT | ON_LEM_JCT | Leamington TS | ON_LEM_DSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 423
| C22J | HONI | Ontario | 1 | ac | 47.9 | 29.5679 | 230 | 22.992 | 3 | [5 empty] | 402 | 435 | Leamington JCT | ON_LEM_JCT | Chatham SWS | ON_CHT_SWS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 424
| C22J | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Keith TS | ON_KEI_DSS | Malden JCT | ON_MLD_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 425
| C22J | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Malden JCT | ON_MLD_JCT | Malden TS | ON_MLD_DSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 426
| C22J | HONI | Ontario | 1 | ac | 21 | 12.963 | 230 | 10.08 | 3 | [5 empty] | 402 | 435 | Sandwich JCT | ON_SNW_JCT | Leamington JCT | ON_LEM_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 427
| C23Z | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Chatham SWS | ON_CHT_SWS | Dillon RWEC GS JCT | ON_DIL_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 428
| C23Z | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Dillon RWEC GS JCT | ON_DIL_JCT | Dillon RWEC GS | ON_DIL_GSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 429
| C23Z | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Dillon RWEC GS JCT | ON_DIL_JCT | KEPA Wind Farm JCT | ON_KEP_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 430
| C23Z | HONI | Ontario | 1 | ac | 14 | 8.642 | 230 | 6.72 | 3 | [5 empty] | 402 | 435 | KEPA Wind Farm JCT | ON_KEP_JCT | Port Alma WF GS | ON_PMA_GSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 431
| C23Z | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | KEPA Wind Farm JCT | ON_KEP_JCT | Comber WF JCT | ON_COM_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 432
| C23Z | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Comber WF JCT | ON_COM_JCT | Comber WF GS | ON_COM_GSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 433
| C23Z | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Comber WF JCT | ON_COM_JCT | Belle River JCT #2 | ON_BLR_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 434
| C23Z | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Belle River JCT #2 | ON_BL2_JCT | Belle River GS | ON_BLR_GSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 435
| C23Z | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Belle River JCT #2 | ON_BL2_JCT | Sandwich JCT | ON_SNW_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 436
| C23Z | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Sandwich JCT | ON_SNW_JCT | Lauzon TS | ON_LAU_DSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 437
| C24Z | HONI | Ontario | 1 | ac | 22 | 13.5802 | 230 | 10.56 | 3 | [5 empty] | 402 | 435 | Chatham SWS | ON_CHT_SWS | KEPA Wind Farm JCT | ON_KEP_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 438
| C24Z | HONI | Ontario | 1 | ac | 14 | 8.642 | 230 | 6.72 | 3 | [5 empty] | 402 | 435 | KEPA Wind Farm JCT | ON_KEP_JCT | Port Alma WF GS | ON_PMA_GSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 439
| C24Z | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | KEPA Wind Farm JCT | ON_KEP_JCT | Comber WF JCT | ON_COM_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 440
| C24Z | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Comber WF JCT | ON_COM_JCT | Comber WF GS | ON_COM_GSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 441
| C24Z | HONI | Ontario | 1 | ac | 27 | 16.6667 | 230 | 12.96 | 3 | [5 empty] | 402 | 435 | Comber WF JCT | ON_COM_JCT | Sandwich JCT | ON_SNW_JCT | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 442
| C24Z | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Sandwich JCT | ON_SNW_JCT | Lauzon TS | ON_LAU_DSS | IESO. 2006.10-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities to Meet Future Electricity Needs in Ontario.; Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan |  | 443
| B88H | HONI | Ontario | 1 | ac | 19.5 | 12.037 | 230 | 9.36 | 3 | [5 empty] | 402 | 435 | Brown Hill TS | ON_BRW_DSS | York Energy Centre JCT | ON_YEC_JCT | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 352
| B88H | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Holland Marsh JCT | ON_HLM_JCT | Holland TS | ON_HLD_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 353
| B88H | HONI | Ontario | 1 | ac | 8.5 | 5.2469 | 230 | 4.08 | 3 | [5 empty] | 402 | 435 | Holland TS | ON_HLD_DSS | Armitage TS | ON_ATG_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 354
| B88H | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | York Energy Centre JCT | ON_YEC_JCT | Holland Marsh JCT | ON_HLM_JCT | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 355
| B88H | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | York Energy Centre JCT | ON_YEC_JCT | York Energy Centre GS | ON_YEC_GSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 356
| B89H | HONI | Ontario | 1 | ac | 19.5 | 12.037 | 230 | 9.36 | 3 | [5 empty] | 402 | 435 | Brown Hill TS | ON_BRW_DSS | York Energy Centre JCT | ON_YEC_JCT | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 357
| B89H | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Holland Marsh JCT | ON_HLM_JCT | Holland TS | ON_HLD_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 358
| B89H | HONI | Ontario | 1 | ac | 8.5 | 5.2469 | 230 | 4.08 | 3 | [5 empty] | 402 | 435 | Holland TS | ON_HLD_DSS | Armitage TS | ON_ATG_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 359
| B89H | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | York Energy Centre JCT | ON_YEC_JCT | Holland Marsh JCT | ON_HLM_JCT | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 360
| B89H | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | York Energy Centre JCT | ON_YEC_JCT | York Energy Centre GS | ON_YEC_GSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 361
| M80B | HONI | Ontario | 1 | ac | 0.11 | 0.067901 | 230 | 0.0528 | 3 | [5 empty] | 402 | 435 | Beaver JCT | ON_BVR_JCT | Beaverton TS | ON_BVT_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1425
| M80B | HONI | Ontario | 1 | ac | 30.92 | 19.0864 | 230 | 14.8416 | 3 | [5 empty] | 402 | 435 | Beaver JCT | ON_BVR_JCT | Brown Hill TS | ON_BRW_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1426
| M80B | HONI | Ontario | 1 | ac | 28.23 | 17.4259 | 230 | 13.5504 | 3 | [5 empty] | 402 | 435 | Beaverton JCT | ON_BVT_JCT | Lindsay TS | ON_LND_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1427
| M80B | HONI | Ontario | 1 | ac | 2.49 | 1.537 | 230 | 1.1952 | 3 | [5 empty] | 402 | 435 | Beaverton JCT | ON_BVT_JCT | Beaver JCT | ON_BVR_JCT | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1428
| M80B | HONI | Ontario | 1 | ac | 73.64 | 45.4568 | 230 | 35.3472 | 3 | [5 empty] | 402 | 435 | Minden TS | ON_MND_DSS | Beaverton JCT | ON_BVT_JCT | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1429
| M81B | HONI | Ontario | 1 | ac | 0.11 | 0.067901 | 230 | 0.0528 | 3 | [5 empty] | 402 | 435 | Beaver JCT | ON_BVR_JCT | Beaverton TS | ON_BVT_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1430
| M81B | HONI | Ontario | 1 | ac | 30.92 | 19.0864 | 230 | 14.8416 | 3 | [5 empty] | 402 | 435 | Beaver JCT | ON_BVR_JCT | Brown Hill TS | ON_BRW_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1431
| M81B | HONI | Ontario | 1 | ac | 28.23 | 17.4259 | 230 | 13.5504 | 3 | [5 empty] | 402 | 435 | Beaverton JCT | ON_BVT_JCT | Lindsay TS | ON_LND_DSS | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1432
| M81B | HONI | Ontario | 1 | ac | 2.49 | 1.537 | 230 | 1.1952 | 3 | [5 empty] | 402 | 435 | Beaverton JCT | ON_BVT_JCT | Beaver JCT | ON_BVR_JCT | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1433
| M81B | HONI | Ontario | 1 | ac | 73.64 | 45.4568 | 230 | 35.3472 | 3 | [5 empty] | 402 | 435 | Minden TS | ON_MND_DSS | Beaverton JCT | ON_BVT_JCT | IESO. 2009. System Impact Assessment Report Connection Assessment & Approval Process (Final) York Energy Centre GS |  | 1434
| K6F | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Ainsworth JCT | ON_AIN_JCT | Barwick JCT | ON_BWK_JCT | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1077
| K6F | HONI | Ontario | 1 | ac | 33.4 | 20.6173 | 115 | 13.9326 | 3 | [5 empty] | 98.4491 | 108.4016 | Ainsworth JCT | ON_AIN_JCT | Nestor Falls JCT | ON_NES_JCT | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1078
| K6F | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Barwick JCT | ON_BWK_JCT | Barwick TS | ON_BWK_DSS | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1079
| K6F | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Fort Frances JCT | ON_FRF_JCT | Ainsworth JCT | ON_AIN_JCT | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1080
| K6F | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Fort Frances TS | ON_FRF_TSS | Fort Frances JCT | ON_FRF_JCT | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1081
| K6F | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | K6F-10 SW JCT | ON_K6F_JCT | Sioux Narrows JCT | ON_SXN_JCT | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1082
| K6F | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Margach JCT | ON_MGH_JCT | Margach DS | ON_MGH_DSS | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1083
| K6F | HONI | Ontario | 1 | ac | 8.6 | 5.3086 | 115 | 3.5874 | 3 | [5 empty] | 98.4491 | 108.4016 | Margach JCT | ON_MGH_JCT | Rabbit Lake SWS | ON_RBL_SWS | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1084
| K6F | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Nestor Falls JCT | ON_NES_JCT | Nestor Falls DS | ON_NES_DSS | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1085
| K6F | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | K6F-10 SW JCT | ON_K6F_JCT | Nestor Falls JCT | ON_NES_JCT | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1086
| K6F | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Sioux Narrows JCT | ON_SXN_JCT | Sioux Narrows DS | ON_SXN_DSS | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1087
| K6F | HONI | Ontario | 1 | ac | 47.9 | 29.5679 | 115 | 19.9811 | 3 | [5 empty] | 98.4491 | 108.4016 | Sioux Narrows JCT | ON_SXN_JCT | Margach JCT | ON_MGH_JCT | IESO. 2010. System Impact Assessment Report Connection Assessment & Approval Process (Final Report) Barwick TS |  | 1088
| D2L | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Dymond TS | ON_DYM_DSS | New Liskeard JCT | ON_NLK_JCT | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 572
| D2L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | New Liskeard JCT | ON_NLK_JCT | New Liskeard JCT #2 | ON_NLK2_JCT | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 573
| D2L | HONI | Ontario | 1 | ac | 40.15 | 24.784 | 115 | 16.7483 | 3 | [5 empty] | 98.4491 | 108.4016 | New Liskeard JCT | ON_NLK_JCT | Upper Notch JCT | ON_UPN_JCT | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 574
| D2L | HONI | Ontario | 2 | ac | 21.29 | 13.142 | 115 | 8.881 | 3 | [5 empty] | 98.4491 | 108.4016 | Upper Notch JCT | ON_UPN_JCT | Cassels 2 JCT | ON_CS2_JCT | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 575
| D2L | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cassels 2 JCT | ON_CS2_JCT | Cassels JCT | ON_CSS_JCT | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 576
| D2L | HONI | Ontario | 2 | ac | 11.7 | 7.2222 | 115 | 4.8806 | 3 | [5 empty] | 98.4491 | 108.4016 | Cassels 2 JCT | ON_CS2_JCT | Herridge Lake JCT | ON_HRL_JCT | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 578
| D2L | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Herridge Lake JCT | ON_HRL_JCT | Herridge Lake DS | ON_HRL_DSS | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 579
| D2L | HONI | Ontario | 2 | ac | 26.8 | 16.5432 | 115 | 11.1794 | 3 | [5 empty] | 98.4491 | 108.4016 | Herridge Lake JCT | ON_HRL_JCT | Marten River JCT | ON_MRV_JCT | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 580
| D2L | HONI | Ontario | 2 | ac | 34.32 | 21.1852 | 115 | 14.3163 | 3 | [5 empty] | 98.4491 | 108.4016 | Marten River JCT | ON_MRV_JCT | D2L STR 409 JCT | ON_D2L_JCT | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 581
| D2L | HONI | Ontario | 1 | ac | 0.05 | 0.030864 | 115 | 0.020857 | 3 | [5 empty] | 98.4491 | 108.4016 | D2L STR 409 JCT | ON_D2L_JCT | Crystal Falls SWS | ON_CRY_SWS | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 582
| X74P | HONI | Ontario | 1 | ac | 205.8 | 127.037 | 230 | 98.784 | 1.7371 | [5 empty] | 232.7708 | 251.8789 | Hanmer TS | ON_HNM_TSS | Mississagi TS | ON_MSS_DSS | IESO. 2011. System Impact Assessment Report Connection Assessment & Approval Process - Liskeard Projects |  | 2196
| N5M | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Nanticoke TS | ON_NTK_TSS | Grand JCT | ON_GRD_JCT | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1472
| N5M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Grand JCT | ON_GRD_JCT | Grand GS | ON_GRD_GSS | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1473
| N5M | HONI | Ontario | 1 | ac | 12.1 | 7.4691 | 230 | 5.808 | 3 | [5 empty] | 402 | 435 | Grand JCT | ON_GRD_JCT | Caledonia JCT | ON_CAL_JCT | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1474
| N5M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Caledonia JCT | ON_CAL_JCT | Caledonia TS | ON_CAL_DSS | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1475
| N5M | HONI | Ontario | 1 | ac | 12.2 | 7.5309 | 230 | 5.856 | 3 | [5 empty] | 402 | 435 | Caledonia JCT | ON_CAL_JCT | Middleport TS | ON_MPT_TSS | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1476
| N6M | HONI | Ontario | 1 | ac | 32.1 | 19.8148 | 230 | 15.408 | 3 | [5 empty] | 402 | 435 | Nanticoke TS | ON_NTK_TSS | Caledonia JCT | ON_CAL_JCT | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1478
| N6M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Caledonia JCT | ON_CAL_JCT | Caledonia TS | ON_CAL_DSS | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1479
| N6M | HONI | Ontario | 1 | ac | 12.2 | 7.5309 | 230 | 5.856 | 3 | [5 empty] | 402 | 435 | Caledonia JCT | ON_CAL_JCT | Middleport TS | ON_MPT_TSS | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1480
| S39M | HONI | Ontario | 1 | ac | 28 | 17.284 | 230 | 13.44 | 3 | [5 empty] | 402 | 435 | Summerhaven SWS | ON_SUM_SWS | Caledonia JCT | ON_CAL_JCT | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1856
| S39M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Caledonia JCT | ON_CAL_JCT | Caledonia TS | ON_CAL_DSS | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1857
| S39M | HONI | Ontario | 1 | ac | 12.2 | 7.5309 | 230 | 5.856 | 3 | [5 empty] | 402 | 435 | Caledonia JCT | ON_CAL_JCT | Middleport TS | ON_MPT_TSS | IESO. 2012. System Impact Assessment Report Addendum Connection Assessment & Approval Process Final Report - Grand Renewable Energy Park |  | 1858
| C5E | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cecil TS | ON_CEC_DSS | Manhole A OPF | ON_MHA_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 499
| C5E | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Manhole A OPF | ON_MHA_DSS | Terauley TS | ON_TER_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 500
| C5E | HONI | Ontario | 1 | ac | 3.6 | 2.2222 | 115 | 1.5017 | 3 | [5 empty] | 98.4491 | 108.4016 | Terauley TS | ON_TER_DSS | Esplanade TS | ON_EPL_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 501
| C7E | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cecil TS | ON_CEC_DSS | Manhole A OPF | ON_MHA_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 519
| C7E | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Manhole A OPF | ON_MHA_DSS | Terauley TS | ON_TER_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 520
| C7E | HONI | Ontario | 1 | ac | 3.6 | 2.2222 | 115 | 1.5017 | 3 | [5 empty] | 98.4491 | 108.4016 | Terauley TS | ON_TER_DSS | Esplanade TS | ON_EPL_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 521
| H10EJ | HONI | Ontario | 1 | ac | 1.8 | 1.1111 | 115 | 0.75086 | 3 | [5 empty] | 98.4491 | 108.4016 | Hearn SWS | ON_HEA_SWS | Don Fleet JCT | ON_DFL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 800
| H10EJ | HONI | Ontario | 1 | ac | 1.8 | 1.1111 | 115 | 0.75086 | 3 | [5 empty] | 98.4491 | 108.4016 | Don Fleet JCT | ON_DFL_JCT | Esplanade TS | ON_EPL_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 801
| H11L | HONI | Ontario | 1 | ac | 0.8 | 0.49383 | 115 | 0.33371 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Todmorden JCT | ON_TOD_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 802
| H11L | HONI | Ontario | 1 | ac | 4.2 | 2.5926 | 115 | 1.752 | 3 | [5 empty] | 98.4491 | 108.4016 | Todmorden JCT | ON_TOD_JCT | Lumsden JCT | ON_LUM_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 803
| H11L | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 115 | 0.62571 | 3 | [5 empty] | 98.4491 | 108.4016 | Lumsden JCT | ON_LUM_JCT | Main TS | ON_MAI_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 804
| H11L | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Main TS | ON_MAI_DSS | Brookside OPF | ON_BRK_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 805
| H11L | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Brookside OPF | ON_BRK_DSS | Waverly OPF | ON_WAV_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 806
| H11L | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Waverly OPF | ON_WAV_DSS | Hearn SWS | ON_HEA_SWS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 807
| H1L | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Bloor Street JCT | ON_BLS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 811
| H1L | HONI | Ontario | 1 | ac | 1.8 | 1.1111 | 115 | 0.75086 | 3 | [5 empty] | 98.4491 | 108.4016 | Bloor Street JCT | ON_BLS_JCT | Gerrard TS | ON_GER_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 812
| H1L | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gerrard TS | ON_GER_DSS | Carlaw TS | ON_CLW_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 813
| H1L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gerrard TS | ON_GER_DSS | Mill Street JCT | ON_MLS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 814
| H1L | HONI | Ontario | 1 | ac | 2.9 | 1.7901 | 115 | 1.2097 | 3 | [5 empty] | 98.4491 | 108.4016 | Mill Street JCT | ON_MLS_JCT | Basin TS | ON_BSN_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 815
| H1L | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 115 | 0.12514 | 3 | [5 empty] | 98.4491 | 108.4016 | Basin TS | ON_BSN_DSS | Hearn SWS | ON_HEA_SWS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 816
| H2JK | HONI | Ontario | 2 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Hearn SWS | ON_HEA_SWS | Basin TS | ON_BSN_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 872
| H2JK | HONI | Ontario | 2 | ac | 1.4 | 0.8642 | 115 | 0.584 | 3 | [5 empty] | 98.4491 | 108.4016 | Basin TS | ON_BSN_DSS | Don Fleet JCT | ON_DFL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 873
| H2JK | HONI | Ontario | 1 | ac | 1.8 | 1.1111 | 115 | 0.75086 | 3 | [5 empty] | 98.4491 | 108.4016 | Don Fleet JCT | ON_DFL_JCT | Esplanade TS | ON_EPL_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 874
| H2JK | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Esplanade TS | ON_EPL_DSS | John TS | ON_JON_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 875
| H2JK | HONI | Ontario | 1 | ac | 2.7 | 1.6667 | 115 | 1.1263 | 3 | [5 empty] | 98.4491 | 108.4016 | John TS | ON_JON_DSS | Strachan TS | ON_STH_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 876
| H2JK | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Strachan TS | ON_STH_DSS | Riverside JCT | ON_RVS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 877
| H2JK | HONI | Ontario | 1 | ac | 6.9 | 4.2593 | 115 | 2.8783 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverside JCT | ON_RVS_JCT | Manby TS | ON_MBY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 878
| H3L | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Bloor Street JCT | ON_BLS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 883
| H3L | HONI | Ontario | 2 | ac | 1.8 | 1.1111 | 115 | 0.75086 | 3 | [5 empty] | 98.4491 | 108.4016 | Bloor Street JCT | ON_BLS_JCT | Gerrard TS | ON_GER_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 884
| H3L | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gerrard TS | ON_GER_DSS | Carlaw TS | ON_CLW_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 885
| H3L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gerrard TS | ON_GER_DSS | Mill Street JCT | ON_MLS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 886
| H3L | HONI | Ontario | 1 | ac | 2.9 | 1.7901 | 115 | 1.2097 | 3 | [5 empty] | 98.4491 | 108.4016 | Mill Street JCT | ON_MLS_JCT | Basin TS | ON_BSN_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 887
| H3L | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 115 | 0.12514 | 3 | [5 empty] | 98.4491 | 108.4016 | Basin TS | ON_BSN_DSS | Hearn SWS | ON_HEA_SWS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 888
| H6LC | HONI | Ontario | 1 | ac | 2.9 | 1.7901 | 115 | 1.2097 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Bloor Street JCT | ON_BLS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 892
| H6LC | HONI | Ontario | 1 | ac | 1.7 | 1.0494 | 115 | 0.70914 | 3 | [5 empty] | 98.4491 | 108.4016 | Bloor Street JCT | ON_BLS_JCT | Gerrard JCT | ON_GER_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 893
| H6LC | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Gerrard JCT | ON_GER_JCT | Cecil TS | ON_CEC_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 894
| H6LC | HONI | Ontario | 1 | ac | 1.4 | 0.8642 | 115 | 0.584 | 3 | [5 empty] | 98.4491 | 108.4016 | Gerrard JCT | ON_GER_JCT | Don Fleet JCT | ON_DFL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 895
| H6LC | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 115 | 0.62571 | 3 | [5 empty] | 98.4491 | 108.4016 | Don Fleet JCT | ON_DFL_JCT | Hearn SWS | ON_HEA_SWS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 896
| H7L | HONI | Ontario | 1 | ac | 0.8 | 0.49383 | 115 | 0.33371 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Todmorden JCT | ON_TOD_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 901
| H7L | HONI | Ontario | 1 | ac | 4.2 | 2.5926 | 115 | 1.752 | 3 | [5 empty] | 98.4491 | 108.4016 | Todmorden JCT | ON_TOD_JCT | Lumsden JCT | ON_LUM_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 902
| H7L | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 115 | 0.62571 | 3 | [5 empty] | 98.4491 | 108.4016 | Lumsden JCT | ON_LUM_JCT | Main TS | ON_MAI_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 903
| H7L | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Main TS | ON_MAI_DSS | Brookside OPF | ON_BRK_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 904
| H7L | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Brookside OPF | ON_BRK_DSS | Waverly OPF | ON_WAV_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 905
| H7L | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Waverly OPF | ON_WAV_DSS | Hearn SWS | ON_HEA_SWS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 906
| H8LC | HONI | Ontario | 1 | ac | 2.9 | 1.7901 | 115 | 1.2097 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Bloor Street JCT | ON_BLS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 920
| H8LC | HONI | Ontario | 1 | ac | 1.7 | 1.0494 | 115 | 0.70914 | 3 | [5 empty] | 98.4491 | 108.4016 | Bloor Street JCT | ON_BLS_JCT | Gerrard JCT | ON_GER_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 921
| H8LC | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Gerrard JCT | ON_GER_JCT | Cecil TS | ON_CEC_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 922
| H8LC | HONI | Ontario | 1 | ac | 1.4 | 0.8642 | 115 | 0.584 | 3 | [5 empty] | 98.4491 | 108.4016 | Gerrard JCT | ON_GER_JCT | Don Fleet JCT | ON_DFL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 923
| H8LC | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 115 | 0.62571 | 3 | [5 empty] | 98.4491 | 108.4016 | Don Fleet JCT | ON_DFL_JCT | Hearn SWS | ON_HEA_SWS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 924
| H9EJ | HONI | Ontario | 1 | ac | 1.8 | 1.1111 | 115 | 0.75086 | 3 | [5 empty] | 98.4491 | 108.4016 | Hearn SWS | ON_HEA_SWS | Don Fleet JCT | ON_DFL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 939
| H9EJ | HONI | Ontario | 1 | ac | 1.8 | 1.1111 | 115 | 0.75086 | 3 | [5 empty] | 98.4491 | 108.4016 | Don Fleet JCT | ON_DFL_JCT | Esplanade TS | ON_EPL_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 940
| H10EJ | HONI | Ontario | 1 | ac | 1.2 | 0.74074 | 115 | 0.50057 | 3 | [5 empty] | 98.4491 | 108.4016 | Esplanade TS | ON_EPL_DSS | Copeland MTS | ON_COP_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 941
| H9EJ | HONI | Ontario | 1 | ac | 1.2 | 0.74074 | 115 | 0.50057 | 3 | [5 empty] | 98.4491 | 108.4016 | Esplanade TS | ON_EPL_DSS | Copeland MTS | ON_COP_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 942
| H10EJ | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Copeland MTS | ON_COP_DSS | John TS | ON_JON_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 943
| H9EJ | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Copeland MTS | ON_COP_DSS | John TS | ON_JON_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 944
| K10SB | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 115 | 2.7114 | 3 | [5 empty] | 98.4491 | 108.4016 | Richview JCT | ON_RCV_JCT | Manby TS | ON_MBY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 992
| K11W | HONI | Ontario | 1 | ac | 5.9 | 3.642 | 115 | 2.4611 | 3 | [5 empty] | 98.4491 | 108.4016 | Manby TS | ON_MBY_DSS | Runnymede TS | ON_RNY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 993
| K11W | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Runnymede TS | ON_RNY_DSS | Wiltshire TS | ON_WLT_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 994
| K12W | HONI | Ontario | 1 | ac | 5.9 | 3.642 | 115 | 2.4611 | 3 | [5 empty] | 98.4491 | 108.4016 | Manby TS | ON_MBY_DSS | Runnymede TS | ON_RNY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 997
| K12W | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Runnymede TS | ON_RNY_DSS | Wiltshire TS | ON_WLT_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 998
| K13J | HONI | Ontario | 1 | ac | 6.9 | 4.2593 | 115 | 2.8783 | 3 | [5 empty] | 98.4491 | 108.4016 | Manby TS | ON_MBY_DSS | Riverside JCT | ON_RVS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 999
| K13J | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverside JCT | ON_RVS_JCT | Strachan TS | ON_STH_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1000
| K13J | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 115 | 1.0429 | 3 | [5 empty] | 98.4491 | 108.4016 | Strachan TS | ON_STH_DSS | John TS | ON_JON_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1001
| K14J | HONI | Ontario | 1 | ac | 6.9 | 4.2593 | 115 | 2.8783 | 3 | [5 empty] | 98.4491 | 108.4016 | Manby TS | ON_MBY_DSS | Riverside JCT | ON_RVS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1002
| K14J | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverside JCT | ON_RVS_JCT | Strachan TS | ON_STH_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1003
| K14J | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 115 | 1.0429 | 3 | [5 empty] | 98.4491 | 108.4016 | Strachan TS | ON_STH_DSS | John TS | ON_JON_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1004
| K1W | HONI | Ontario | 1 | ac | 8.7 | 5.3704 | 115 | 3.6291 | 3 | [5 empty] | 98.4491 | 108.4016 | Manby TS | ON_MBY_DSS | St. Clair Avenue JCT | ON_STC_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1006
| K1W | HONI | Ontario | 1 | ac | 4.6 | 2.8395 | 115 | 1.9189 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Clair Avenue JCT | ON_STC_JCT | Fairbank TS | ON_FBK_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1007
| K1W | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 115 | 0.37543 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Clair Avenue JCT | ON_STC_JCT | Wiltshire TS | ON_WLT_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1008
| K21C | HONI | Ontario | 2 | ac | 5.8 | 3.5802 | 230 | 2.784 | 3 | [5 empty] | 402 | 435 | Manby TS | ON_MBY_DSS | Applewood JCT | ON_APP_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1012
| K21C | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 230 | 0.432 | 3 | [5 empty] | 402 | 435 | Applewood JCT | ON_APP_JCT | Cooksville TS | ON_CKV_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1013
| K23C | HONI | Ontario | 1 | ac | 6.2 | 3.8272 | 230 | 2.976 | 3 | [5 empty] | 402 | 435 | Manby TS | ON_MBY_DSS | Applewood JCT | ON_APP_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1016
| K23C | HONI | Ontario | 1 | ac | 1.4 | 0.8642 | 230 | 0.672 | 3 | [5 empty] | 402 | 435 | Applewood JCT | ON_APP_JCT | Cooksville TS | ON_CKV_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1017
| K3W | HONI | Ontario | 1 | ac | 8.7 | 5.3704 | 115 | 3.6291 | 3 | [5 empty] | 98.4491 | 108.4016 | Manby TS | ON_MBY_DSS | St. Clair Avenue JCT | ON_STC_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1058
| K3W | HONI | Ontario | 1 | ac | 4.6 | 2.8395 | 115 | 1.9189 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Clair Avenue JCT | ON_STC_JCT | Fairbank TS | ON_FBK_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1059
| K3W | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 115 | 0.37543 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Clair Avenue JCT | ON_STC_JCT | Wiltshire TS | ON_WLT_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1060
| K6J | HONI | Ontario | 1 | ac | 2.7 | 1.6667 | 115 | 1.1263 | 3 | [5 empty] | 98.4491 | 108.4016 | John TS | ON_JON_DSS | Strachan TS | ON_STH_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1089
| K6J | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Strachan TS | ON_STH_DSS | Riverside JCT | ON_RVS_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1090
| K6J | HONI | Ontario | 1 | ac | 6.9 | 4.2593 | 115 | 2.8783 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverside JCT | ON_RVS_JCT | Manby TS | ON_MBY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1091
| L12C | HONI | Ontario | 1 | ac | 1.59 | 0.98148 | 115 | 0.66326 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Balfour JCT | ON_BAL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1106
| L12C | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Balfour JCT | ON_BAL_JCT | Charles TS | ON_CHL_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1107
| L12C | HONI | Ontario | 1 | ac | 2.6 | 1.6049 | 115 | 1.0846 | 3 | [5 empty] | 98.4491 | 108.4016 | Charles TS | ON_CHL_DSS | Cecil TS | ON_CEC_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1108
| L13W | HONI | Ontario | 1 | ac | 1.17 | 0.72222 | 115 | 0.48806 | 3 | [5 empty] | 98.4491 | 108.4016 | Wiltshire TS | ON_WLT_DSS | Dufferin JCT | ON_DUF_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1109
| L13W | HONI | Ontario | 1 | ac | 1.29 | 0.7963 | 115 | 0.53811 | 3 | [5 empty] | 98.4491 | 108.4016 | Dufferin JCT | ON_DUF_JCT | Dufferin TS | ON_DUF_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1110
| L13W | HONI | Ontario | 1 | ac | 2.7 | 1.6667 | 115 | 1.1263 | 3 | [5 empty] | 98.4491 | 108.4016 | Dufferin JCT | ON_DUF_JCT | Bridgman JCT | ON_BRG_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1111
| L13W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridgman JCT | ON_BRG_JCT | Bridgman TS | ON_BRG_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1112
| L13W | HONI | Ontario | 1 | ac | 2.12 | 1.3086 | 115 | 0.88434 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridgman JCT | ON_BRG_JCT | Balfour JCT | ON_BAL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1113
| L13W | HONI | Ontario | 1 | ac | 4.14 | 2.5556 | 115 | 1.727 | 3 | [5 empty] | 98.4491 | 108.4016 | Balfour JCT | ON_BAL_JCT | Leaside TS | ON_LES_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1114
| L14W | HONI | Ontario | 1 | ac | 3.99 | 2.463 | 115 | 1.6644 | 3 | [5 empty] | 98.4491 | 108.4016 | Wiltshire TS | ON_WLT_DSS | Bridgman JCT | ON_BRG_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1115
| L14W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridgman JCT | ON_BRG_JCT | Bridgman TS | ON_BRG_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1116
| L14W | HONI | Ontario | 1 | ac | 2.47 | 1.5247 | 115 | 1.0303 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridgman JCT | ON_BRG_JCT | Birch JCT | ON_BIR_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1117
| L14W | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Birch JCT | ON_BIR_JCT | Bayview JCT | ON_BYV_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1118
| L14W | HONI | Ontario | 1 | ac | 1.59 | 0.98148 | 115 | 0.66326 | 3 | [5 empty] | 98.4491 | 108.4016 | Bayview JCT | ON_BYV_JCT | Leaside TS | ON_LES_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1119
| L15W | HONI | Ontario | 1 | ac | 2.12 | 1.3086 | 115 | 0.88434 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridgman JCT | ON_BRG_JCT | Balfour JCT | ON_BAL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1120
| L15W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridgman JCT | ON_BRG_JCT | Bridgman TS | ON_BRG_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1121
| L15W | HONI | Ontario | 1 | ac | 2.55 | 1.5741 | 115 | 1.0637 | 3 | [5 empty] | 98.4491 | 108.4016 | Balfour JCT | ON_BAL_JCT | Bayview JCT | ON_BYV_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1122
| L15W | HONI | Ontario | 1 | ac | 1.59 | 0.98148 | 115 | 0.66326 | 3 | [5 empty] | 98.4491 | 108.4016 | Bayview JCT | ON_BYV_JCT | Leaside TS | ON_LES_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1123
| L16D | HONI | Ontario | 1 | ac | 4.7 | 2.9012 | 115 | 1.9606 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Duplex TS | ON_DPX_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1124
| L18W | HONI | Ontario | 1 | ac | 1.17 | 0.72222 | 115 | 0.48806 | 3 | [5 empty] | 98.4491 | 108.4016 | Wiltshire TS | ON_WLT_DSS | Bartlett JCT | ON_BTL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1125
| L18W | HONI | Ontario | 1 | ac | 1.29 | 0.7963 | 115 | 0.53811 | 3 | [5 empty] | 98.4491 | 108.4016 | Bartlett JCT | ON_BTL_JCT | Dufferin TS | ON_DUF_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1126
| L18W | HONI | Ontario | 1 | ac | 2.72 | 1.679 | 115 | 1.1346 | 3 | [5 empty] | 98.4491 | 108.4016 | Bartlett JCT | ON_BTL_JCT | Bridgman JCT | ON_BRG_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1127
| L18W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridgman JCT | ON_BRG_JCT | Bridgman TS | ON_BRG_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1128
| L18W | HONI | Ontario | 1 | ac | 2.47 | 1.5247 | 115 | 1.0303 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridgman JCT | ON_BRG_JCT | Birch JCT | ON_BIR_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1129
| L18W | HONI | Ontario | 1 | ac | 2.79 | 1.7222 | 115 | 1.1638 | 3 | [5 empty] | 98.4491 | 108.4016 | Birch JCT | ON_BIR_JCT | Bayview JCT | ON_BYV_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1130
| L18W | HONI | Ontario | 1 | ac | 1.59 | 0.98148 | 115 | 0.66326 | 3 | [5 empty] | 98.4491 | 108.4016 | Bayview JCT | ON_BYV_JCT | Leaside TS | ON_LES_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1131
| L2Y | HONI | Ontario | 1 | ac | 5.7 | 3.5185 | 115 | 2.3777 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Glengrove TS | ON_GLG_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1238
| L4C | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Charles TS | ON_CHL_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1246
| L5D | HONI | Ontario | 1 | ac | 4.8 | 2.963 | 115 | 2.0023 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Duplex TS | ON_DPX_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1251
| L9C | HONI | Ontario | 1 | ac | 1.59 | 0.98148 | 115 | 0.66326 | 3 | [5 empty] | 98.4491 | 108.4016 | Leaside TS | ON_LES_DSS | Balfour JCT | ON_BAL_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1271
| L9C | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Balfour JCT | ON_BAL_JCT | Charles TS | ON_CHL_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1272
| L9C | HONI | Ontario | 1 | ac | 2.6 | 1.6049 | 115 | 1.0846 | 3 | [5 empty] | 98.4491 | 108.4016 | Charles TS | ON_CHL_DSS | Cecil TS | ON_CEC_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1273
| NAR43M21 | HONI | Ontario | 1 | ac | 4.2 | 2.5926 | 115 | 1.752 | 3 | [5 empty] | 98.4491 | 108.4016 | Lumsden JCT | ON_LUM_JCT | Todmorden JCT | ON_TOD_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1504
| R13K | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Manby TS | ON_MBY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1744
| R15K | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Manby TS | ON_MBY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1752
| R1K | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Manby TS | ON_MBY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1768
| R24C | HONI | Ontario | 1 | ac | 12.9 | 7.963 | 230 | 6.192 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Applewood JCT | ON_APP_JCT | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1785
| R24C | HONI | Ontario | 1 | ac | 1.2 | 0.74074 | 230 | 0.576 | 3 | [5 empty] | 402 | 435 | Applewood JCT | ON_APP_JCT | Cooksville TS | ON_CKV_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1786
| R2K | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Richview TS | ON_RCV_DSS | Manby TS | ON_MBY_DSS | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices |  | 1787
| V71P | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Toronto Star JCT | ON_TOS_JCT | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2031
| V71P | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 230 | 0.432 | 3 | [5 empty] | 402 | 435 | Toronto Star JCT | ON_TOS_JCT | Vaughan MTS #2 | ON_VM2_DSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2032
| V71P | HONI | Ontario | 1 | ac | 7.1 | 4.3827 | 230 | 3.408 | 3 | [5 empty] | 402 | 435 | Toronto Star JCT | ON_TOS_JCT | Vaughan #1 JCT | ON_VJ1_JCT | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2033
| V71P | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 230 | 0.192 | 3 | [5 empty] | 402 | 435 | Vaughan #1 JCT | ON_VJ1_JCT | Vaughan MTS #1 | ON_VM1_DSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2034
| V71P | HONI | Ontario | 1 | ac | 7.1 | 4.3827 | 230 | 3.408 | 3 | [5 empty] | 402 | 435 | Vaughan #1 JCT | ON_VJ1_JCT | Richmond Hill JCT | ON_RJ1_JCT | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2035
| V71P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Richmond Hill JCT | ON_RJ1_JCT | Richmond Hill MTS #1 | ON_RM1_DSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2036
| V71P | HONI | Ontario | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Richmond Hill JCT | ON_RJ1_JCT | Richmond Hill #2 JCT | ON_RJ2_JCT | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2037
| V71P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Richmond Hill #2 JCT | ON_RJ2_JCT | Richmond Hill MTS #2 | ON_RM2_DSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2038
| V71P | HONI | Ontario | 1 | ac | 7.3 | 4.5062 | 230 | 3.504 | 3 | [5 empty] | 402 | 435 | Richmond Hill #2 JCT | ON_RJ2_JCT | Parkway TS | ON_PKW_TSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2039
| V75P | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Toronto Star JCT | ON_TOS_JCT | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2045
| V75P | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 230 | 0.432 | 3 | [5 empty] | 402 | 435 | Toronto Star JCT | ON_TOS_JCT | Vaughan MTS #2 | ON_VM2_DSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2046
| V75P | HONI | Ontario | 1 | ac | 7.1 | 4.3827 | 230 | 3.408 | 3 | [5 empty] | 402 | 435 | Toronto Star JCT | ON_TOS_JCT | Vaughan #1 JCT | ON_VJ1_JCT | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2047
| V75P | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 230 | 0.192 | 3 | [5 empty] | 402 | 435 | Vaughan #1 JCT | ON_VJ1_JCT | Vaughan MTS #1 | ON_VM1_DSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2048
| V75P | HONI | Ontario | 1 | ac | 7.1 | 4.3827 | 230 | 3.408 | 3 | [5 empty] | 402 | 435 | Vaughan #1 JCT | ON_VJ1_JCT | Richmond Hill JCT | ON_RJ1_JCT | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2049
| V75P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Richmond Hill JCT | ON_RJ1_JCT | Richmond Hill MTS #1 | ON_RM1_DSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2050
| V75P | HONI | Ontario | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Richmond Hill JCT | ON_RJ1_JCT | Richmond Hill #2 JCT | ON_RJ2_JCT | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2051
| V75P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Richmond Hill #2 JCT | ON_RJ2_JCT | Richmond Hill MTS #2 | ON_RM2_DSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2052
| V75P | HONI | Ontario | 1 | ac | 7.3 | 4.5062 | 230 | 3.504 | 3 | [5 empty] | 402 | 435 | Richmond Hill #2 JCT | ON_RJ2_JCT | Parkway TS | ON_PKW_TSS | IESO. 2015. York Region Integrated Regional Resource Plan |  | 2053
| 79M1 | HONI | Ontario | 1 | ac | 11.1 | 6.8519 | 115 | 4.6303 | 3 | [5 empty] | 98.4491 | 108.4016 | Gamble H9A JCT | ON_GAM_JCT | Rockland JCT | ON_RKL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 17
| 79M1 | HONI | Ontario | 1 | ac | 1.2 | 0.74074 | 115 | 0.50057 | 3 | [5 empty] | 98.4491 | 108.4016 | Rockland JCT | ON_RKL_JCT | Rockland DS | ON_RKL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 18
| 79M1 | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Rockland JCT | ON_RKL_JCT | Rockland East DS JCT | ON_RKE_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 19
| 79M1 | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Rockland East DS JCT | ON_RKE_JCT | Rockland East DS | ON_RKE_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 20
| 79M1 | HONI | Ontario | 1 | ac | 2.3 | 1.4198 | 115 | 0.95943 | 3 | [5 empty] | 98.4491 | 108.4016 | Rockland East DS JCT | ON_RKE_JCT | Clarence DS | ON_CLC_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 21
| 79M1 | HONI | Ontario | 1 | ac | 7.1 | 4.3827 | 115 | 2.9617 | 3 | [5 empty] | 98.4491 | 108.4016 | Clarence DS | ON_CLC_DSS | Wendover JCT | ON_WEN_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 22
| 79M1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Wendover JCT | ON_WEN_JCT | Wendover DS | ON_WEN_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 23
| 79M1 | HONI | Ontario | 1 | ac | 35.2 | 21.7284 | 115 | 14.6834 | 3 | [5 empty] | 98.4491 | 108.4016 | Wendover JCT | ON_WEN_JCT | Cassburn JCT | ON_CSB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 24
| 79M1 | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Cassburn JCT | ON_CSB_JCT | Hawkesbury MTS #1 | ON_HWK_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 25
| A2 | HONI | Ontario | 1 | ac | 2.6 | 1.6049 | 115 | 1.0846 | 3 | [5 empty] | 98.4491 | 108.4016 | Hawthorne TS | ON_HWT_TSS | Blackburn JCT | ON_BLB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 35
| A2 | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Blackburn JCT | ON_BLB_JCT | Cyrville Rd JCT | ON_CYR_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 36
| A2 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cyrville Rd JCT | ON_CYR_JCT | Cyrville MTS | ON_CYV_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 37
| A2 | HONI | Ontario | 1 | ac | 1.6 | 0.98765 | 115 | 0.66743 | 3 | [5 empty] | 98.4491 | 108.4016 | Cyrville Rd JCT | ON_CYR_JCT | Cyrville JCT | ON_CYV_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 38
| A2 | HONI | Ontario | 1 | ac | 6.2 | 3.8272 | 115 | 2.5863 | 3 | [5 empty] | 98.4491 | 108.4016 | Cyrville JCT | ON_CYV_JCT | Bilberry Creek JCT | ON_BBC_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 39
| A2 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bilberry Creek JCT | ON_BBC_JCT | Bilberry Creek TS | ON_BBC_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 40
| A2 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Cyrville JCT | ON_CYV_JCT | National Research JCT | ON_NRS_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 41
| A2 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | National Research JCT | ON_NRS_JCT | NRC TS | ON_NRC_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 42
| A3RM | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Hawthorne TS | ON_HWT_TSS | Ellwood JCT | ON_ELD_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 56
| A3RM | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Ellwood JCT | ON_ELD_JCT | Billings JCT | ON_BIL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 57
| A3RM | HONI | Ontario | 1 | ac | 3.9 | 2.4074 | 115 | 1.6269 | 3 | [5 empty] | 98.4491 | 108.4016 | Ellwood JCT | ON_ELD_JCT | Riverdale JCT | ON_RVD_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 58
| A3RM | HONI | Ontario | 1 | ac | 4.8 | 2.963 | 115 | 2.0023 | 3 | [5 empty] | 98.4491 | 108.4016 | Billings JCT | ON_BIL_JCT | Merivale MTS | ON_MER_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 59
| A3RM | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Merivale MTS | ON_MER_DSS | Merivale TS | ON_MER_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 60
| A3RM | HONI | Ontario | 1 | ac | 2.3 | 1.4198 | 115 | 0.95943 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverdale JCT | ON_RVD_JCT | Riverdale TS | ON_RVD_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 61
| A3RM | HONI | Ontario | 1 | ac | 3.3 | 2.037 | 115 | 1.3766 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverdale TS | ON_RVD_DSS | Slater TS | ON_SLT_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 62
| A4K | HONI | Ontario | 1 | ac | 2.6 | 1.6049 | 115 | 1.0846 | 3 | [5 empty] | 98.4491 | 108.4016 | Hawthorne TS | ON_HWT_TSS | Blackburn JCT | ON_BLB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 71
| A4K | HONI | Ontario | 1 | ac | 0.4 | 0.24691 | 115 | 0.16686 | 3 | [5 empty] | 98.4491 | 108.4016 | Blackburn JCT | ON_BLB_JCT | Cyrville Rd JCT | ON_CYR_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 72
| A4K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cyrville Rd JCT | ON_CYR_JCT | Cyrville MTS | ON_CYV_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 73
| A4K | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 115 | 1.0011 | 3 | [5 empty] | 98.4491 | 108.4016 | Cyrville Rd JCT | ON_CYR_JCT | Cyrville JCT | ON_CYV_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 74
| A4K | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Cyrville JCT | ON_CYV_JCT | Moulton JCT | ON_MOU_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 75
| A4K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Moulton JCT | ON_MOU_JCT | Moulton MTS | ON_MOU_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 76
| A4K | HONI | Ontario | 1 | ac | 2.2 | 1.358 | 115 | 0.91771 | 3 | [5 empty] | 98.4491 | 108.4016 | Moulton JCT | ON_MOU_JCT | Overbrook TS | ON_OVB_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 77
| A4K | HONI | Ontario | 1 | ac | 4.1 | 2.5309 | 115 | 1.7103 | 3 | [5 empty] | 98.4491 | 108.4016 | Overbrook TS | ON_OVB_DSS | King Edward TS | ON_KNE_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 78
| A5RK | HONI | Ontario | 1 | ac | 2.6 | 1.6049 | 115 | 1.0846 | 3 | [5 empty] | 98.4491 | 108.4016 | Hawthorne TS | ON_HWT_TSS | Blackburn JCT | ON_BLB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 103
| A5RK | HONI | Ontario | 1 | ac | 2.9 | 1.7901 | 115 | 1.2097 | 3 | [5 empty] | 98.4491 | 108.4016 | Blackburn JCT | ON_BLB_JCT | Russell TS | ON_RSS_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 104
| A5RK | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Russell TS | ON_RSS_DSS | Riverdale JCT | ON_RVD_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 105
| A5RK | HONI | Ontario | 1 | ac | 2.3 | 1.4198 | 115 | 0.95943 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverdale JCT | ON_RVD_JCT | Riverdale TS | ON_RVD_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 106
| A5RK | HONI | Ontario | 1 | ac | 3.8 | 2.3457 | 115 | 1.5851 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverdale TS | ON_RVD_DSS | Slater TS | ON_SLT_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 107
| A5RK | HONI | Ontario | 1 | ac | 2.1 | 1.2963 | 115 | 0.876 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverdale JCT | ON_RVD_JCT | A5RK STR O7 JCT | ON_A5R_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 108
| A5RK | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | A5RK STR O7 JCT | ON_A5R_JCT | Overbrook TS | ON_OVB_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 109
| A5RK | HONI | Ontario | 1 | ac | 4.1 | 2.5309 | 115 | 1.7103 | 3 | [5 empty] | 98.4491 | 108.4016 | Overbrook TS | ON_OVB_DSS | King Edward TS | ON_KNE_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 110
| A6C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Allanburg TS | ON_ALL_TSS | Hurricane JCT | ON_HRC_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 111
| A6C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Hurricane JCT | ON_HRC_JCT | BF Goodrich JCT | ON_BFG_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 112
| A6C | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | BF Goodrich JCT | ON_BFG_JCT | Cytec Welland TS | ON_CYT_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 113
| A6C | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Hurricane JCT | ON_HRC_JCT | Michigan JCT | ON_MIC_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 115
| A6C | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Michigan JCT | ON_MIC_JCT | Crowland TS | ON_CRL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 116
| A6R | HONI | Ontario | 1 | ac | 2.6 | 1.6049 | 115 | 1.0846 | 3 | [5 empty] | 98.4491 | 108.4016 | Hawthorne TS | ON_HWT_TSS | Blackburn JCT | ON_BLB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 119
| A6R | HONI | Ontario | 1 | ac | 2.9 | 1.7901 | 115 | 1.2097 | 3 | [5 empty] | 98.4491 | 108.4016 | Blackburn JCT | ON_BLB_JCT | Russell TS | ON_RSS_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 120
| A6R | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Russell TS | ON_RSS_DSS | Riverdale JCT | ON_RVD_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 121
| A6R | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Riverdale JCT | ON_RVD_JCT | OHSC JCT | ON_OHS_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 122
| A6R | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | OHSC JCT | ON_OHS_JCT | OHSC GS | ON_OHS_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 123
| A6R | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | OHSC JCT | ON_OHS_JCT | Riverdale TS | ON_RVD_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 124
| A8M | HONI | Ontario | 1 | ac | 4.8 | 2.963 | 115 | 2.0023 | 3 | [5 empty] | 98.4491 | 108.4016 | Billings JCT | ON_BIL_JCT | Merivale TS | ON_MER_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 143
| A8M | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Billings JCT | ON_BIL_JCT | Uplands JCT | ON_UPL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 144
| A8M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Uplands JCT | ON_UPL_JCT | National Aeronautical TS | ON_NAE_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 145
| A8M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Uplands JCT | ON_UPL_JCT | Uplands MTS #2 | ON_UPL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 146
| A8M | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Billings JCT | ON_BIL_JCT | Hawthorne TS | ON_HWT_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 147
| B31L | HONI | Ontario | 1 | ac | 47.1 | 29.0741 | 230 | 22.608 | 3 | [5 empty] | 402 | 435 | Raisin River JCT | ON_RSR_JCT | B5D-B31L SWS JCT | ON_B5D_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 247
| B31L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | B5D-B31L SWS JCT | ON_B5D_JCT | IPT Beauharnois | PP_ONQB1_IPT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 248
| B5D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | B5D-B31L SWS JCT | ON_B5D_JCT | IPT Beauharnois | PP_ONQB1_IPT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 312
| B5D | HONI | Ontario | 1 | ac | 39.1 | 24.1358 | 230 | 18.768 | 3 | [5 empty] | 402 | 435 | St. Isidore TS | ON_STI_DSS | B5D-B31L SWS JCT | ON_B5D_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 313
| B5D | HONI | Ontario | 1 | ac | 30.7 | 18.9506 | 230 | 14.736 | 3 | [5 empty] | 402 | 435 | Longueuil JCT | ON_LGU_JCT | St. Isidore TS | ON_STI_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 314
| B5D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Longueuil JCT | ON_LGU_JCT | Longueuil TS | ON_LGU_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 315
| B5D | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Longueuil JCT | ON_LGU_JCT | Ivaco TS | ON_IVO_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 316
| C7BM | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Fitzroy JCT | ON_FTZ_JCT | Bellman JCT | ON_BLL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 510
| C7BM | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Bellman JCT | ON_BLL_JCT | NQL1 B JCT | ON_NQL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 511
| C7BM | HONI | Ontario | 1 | ac | 2.8 | 1.7284 | 115 | 1.168 | 3 | [5 empty] | 98.4491 | 108.4016 | NQL1 B JCT | ON_NQL_JCT | Centre Point JCT | ON_CTP_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 512
| C7BM | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | NQL1 B JCT | ON_NQL_JCT | Manordale JCT | ON_MDL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 513
| C7BM | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Manordale JCT | ON_MDL_JCT | Manordale MTS | ON_MDL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 514
| C7BM | HONI | Ontario | 1 | ac | 3.9 | 2.4074 | 115 | 1.6269 | 3 | [5 empty] | 98.4491 | 108.4016 | NQL1 B JCT | ON_NQL_JCT | Merivale TS | ON_MER_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 515
| C7BM | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Centre Point JCT | ON_CTP_JCT | Centre Point MTS | ON_CTP_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 516
| C7BM | HONI | Ontario | 1 | ac | 0.8 | 0.49383 | 115 | 0.33371 | 3 | [5 empty] | 98.4491 | 108.4016 | Centre Point JCT | ON_CTP_JCT | Woodroffe TS | ON_WDR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 517
| C7BM | HONI | Ontario | 1 | ac | 2.9 | 1.7901 | 115 | 1.2097 | 3 | [5 empty] | 98.4491 | 108.4016 | Woodroffe TS | ON_WDR_DSS | Lincoln Heights TS | ON_LNH_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 518
| D5A | HONI | Ontario | 1 | ac | 11 | 6.7901 | 230 | 5.28 | 3 | [5 empty] | 402 | 435 | Hawthorne TS | ON_HWT_TSS | Orleans JCT #2 | ON_OR2_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 620
| D5A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Orleans JCT #2 | ON_OR2_JCT | Orleans TS | ON_ORL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 621
| D5A | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 230 | 3.12 | 3 | [5 empty] | 402 | 435 | Orleans JCT #2 | ON_OR2_JCT | Cumberland JCT | ON_CUM_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 622
| D5A | HONI | Ontario | 1 | ac | 47.3 | 29.1975 | 230 | 22.704 | 3 | [5 empty] | 402 | 435 | Cumberland JCT | ON_CUM_JCT | St. Isidore TS | ON_STI_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 624
| D5A | HONI | Ontario | 1 | ac | 30.7 | 18.9506 | 230 | 14.736 | 3 | [5 empty] | 402 | 435 | St. Isidore TS | ON_STI_DSS | Longueuil JCT | ON_LGU_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 625
| D5A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Longueuil JCT | ON_LGU_JCT | Longueuil TS | ON_LGU_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 626
| D5A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Longueuil JCT | ON_LGU_JCT | Ivaco TS | ON_IVO_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 627
| F10MV | HONI | Ontario | 1 | ac | 4.2 | 2.5926 | 115 | 1.752 | 3 | [5 empty] | 98.4491 | 108.4016 | Merivale TS | ON_MER_TSS | City View JCT | ON_CTV_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 758
| F10MV | HONI | Ontario | 1 | ac | 4.9 | 3.0247 | 115 | 2.044 | 3 | [5 empty] | 98.4491 | 108.4016 | City View JCT | ON_CTV_JCT | Woodroffe TS | ON_WDR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 761
| F10MV | HONI | Ontario | 1 | ac | 2.9 | 1.7901 | 115 | 1.2097 | 3 | [5 empty] | 98.4491 | 108.4016 | Woodroffe TS | ON_WDR_DSS | Lincoln Heights TS | ON_LNH_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 762
| H9A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bilberry Creek JCT | ON_BBC_JCT | Bilberry Creek TS | ON_BBC_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 925
| H9A | HONI | Ontario | 1 | ac | 4.4 | 2.716 | 115 | 1.8354 | 3 | [5 empty] | 98.4491 | 108.4016 | Bilberry Creek JCT | ON_BBC_JCT | Orleans JCT | ON_ORL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 926
| H9A | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 115 | 0.62571 | 3 | [5 empty] | 98.4491 | 108.4016 | Orleans JCT #2 | ON_OR2_JCT | Borromee JCT | ON_BOR_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 927
| H9A | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 115 | 2.7114 | 3 | [5 empty] | 98.4491 | 108.4016 | Borromee JCT | ON_BOR_JCT | Navan DS | ON_NVN_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 928
| H9A | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Borromee JCT | ON_BOR_JCT | Wilhaven JCT | ON_WLH_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 929
| H9A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Wilhaven JCT | ON_WLH_JCT | Wilhaven DS | ON_WLH_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 930
| H9A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Wilhaven JCT | ON_WLH_JCT | Cumberland JCT | ON_CUM_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 931
| H9A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Orleans JCT #2 | ON_OR2_JCT | Orleans TS | ON_ORL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 932
| H9A | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | Hawthorne TS | ON_HWT_TSS | Orleans JCT #2 | ON_OR2_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 933
| H9A | HONI | Ontario | 3 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cumberland DS JCT | ON_CUS_JCT | Cumberland DS | ON_CUS_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 934
| H9A | HONI | Ontario | 1 | ac | 6.9 | 4.2593 | 115 | 2.8783 | 3 | [5 empty] | 98.4491 | 108.4016 | Cumberland DS JCT | ON_CUS_JCT | Orleans JCT | ON_ORL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 935
| H9A | HONI | Ontario | 1 | ac | 3.4 | 2.0988 | 115 | 1.4183 | 3 | [5 empty] | 98.4491 | 108.4016 | Cumberland JCT | ON_CUM_JCT | Gamble H9A JCT | ON_GAM_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 936
| H9A | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Cumberland DS JCT | ON_CUS_JCT | Gamble H9A JCT | ON_GAM_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 937
| L24A | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | St. Lawrence TS | ON_STL_DSS | Raisin River JCT | ON_RSR_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1192
| L24A | HONI | Ontario | 1 | ac | 55 | 33.9506 | 230 | 26.4 | 3 | [5 empty] | 402 | 435 | Raisin River JCT | ON_RSR_JCT | Hawthorne TS | ON_HWT_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1193
| L2M | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Osgoode JCT | ON_OSG_JCT | Russell DS | ON_RSL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1234
| L2M | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Osgoode JCT | ON_OSG_JCT | Limebank JCT | ON_LBK_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1235
| L2M | HONI | Ontario | 3 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Limebank JCT | ON_LBK_JCT | Limebank MTS | ON_LBK_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1236
| L2M | HONI | Ontario | 1 | ac | 7.8 | 4.8148 | 115 | 3.2537 | 3 | [5 empty] | 98.4491 | 108.4016 | Limebank JCT | ON_LBK_JCT | Merivale TS | ON_MER_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1237
| M1R | HONI | Ontario | 2 | ac | 12.6 | 7.7778 | 115 | 5.256 | 3 | [5 empty] | 98.4491 | 108.4016 | Merivale TS | ON_MER_TSS | South Gloucester JCT | ON_SGL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1277
| M1R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | South Gloucester JCT | ON_SGL_JCT | South Gloucester DS | ON_SGL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1278
| M1R | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | South Gloucester JCT | ON_SGL_JCT | Greely JCT | ON_GRE_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1279
| M1R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Greely JCT | ON_GRE_JCT | Greely DS | ON_GRE_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1280
| M1R | HONI | Ontario | 1 | ac | 8.3 | 5.1235 | 115 | 3.4623 | 3 | [5 empty] | 98.4491 | 108.4016 | Greely JCT | ON_GRE_JCT | Russell DS | ON_RSL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1281
| M30A | HONI | Ontario | 1 | ac | 7.8 | 4.8148 | 230 | 3.744 | 3 | [5 empty] | 402 | 435 | Merivale TS | ON_MER_TSS | Albion JCT | ON_ALB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1354
| M30A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Albion JCT | ON_ALB_JCT | Albion TS | ON_ALB_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1355
| M30A | HONI | Ontario | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Albion JCT | ON_ALB_JCT | Ellwood MTS JCT | ON_ELW_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1356
| M30A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Ellwood MTS JCT | ON_ELW_JCT | Ellwood MTS | ON_ELW_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1357
| M30A | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Ellwood MTS JCT | ON_ELW_JCT | Hawthorne TS | ON_HWT_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1358
| M31A | HONI | Ontario | 1 | ac | 7.8 | 4.8148 | 230 | 3.744 | 3 | [5 empty] | 402 | 435 | Merivale TS | ON_MER_TSS | Albion JCT | ON_ALB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1363
| M31A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Albion JCT | ON_ALB_JCT | Albion TS | ON_ALB_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1364
| M31A | HONI | Ontario | 1 | ac | 0.2 | 0.12346 | 230 | 0.096 | 3 | [5 empty] | 402 | 435 | Albion JCT | ON_ALB_JCT | Ellwood MTS JCT | ON_ELW_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1365
| M31A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Ellwood MTS JCT | ON_ELW_JCT | Ellwood MTS | ON_ELW_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1366
| M31A | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Ellwood MTS JCT | ON_ELW_JCT | Hawthorne TS | ON_HWT_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1367
| M32S | HONI | Ontario | 1 | ac | 6.1 | 3.7654 | 230 | 2.928 | 3 | [5 empty] | 402 | 435 | Merivale TS | ON_MER_TSS | Nepean TS | ON_NEP_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1374
| M32S | HONI | Ontario | 1 | ac | 9.1 | 5.6173 | 230 | 4.368 | 3 | [5 empty] | 402 | 435 | Nepean TS | ON_NEP_DSS | South March TS | ON_SOM_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1375
| M32S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | South March TS | ON_SOM_DSS | Kanata MTS #1 | ON_KAN_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1376
| M4G | HONI | Ontario | 1 | ac | 1.6 | 0.98765 | 115 | 0.66743 | 3 | [5 empty] | 98.4491 | 108.4016 | Merivale TS | ON_MER_TSS | Nepean Epworth JCT | ON_NPE_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1396
| M4G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Nepean Epworth JCT | ON_NPE_JCT | Nepean Epworth MTS | ON_NPE_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1397
| M4G | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Nepean Epworth JCT | ON_NPE_JCT | Ottawa JCT | ON_OTT_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1398
| M4G | HONI | Ontario | 1 | ac | 3.9 | 2.4074 | 115 | 1.6269 | 3 | [5 empty] | 98.4491 | 108.4016 | Ottawa JCT | ON_OTT_JCT | Carling TS | ON_CAR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1399
| M4G | HONI | Ontario | 1 | ac | 5.2 | 3.2099 | 115 | 2.1691 | 3 | [5 empty] | 98.4491 | 108.4016 | Carling TS | ON_CAR_DSS | Lisgar TS | ON_LSG_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1400
| M4G | HONI | Ontario | 1 | ac | 1.2 | 0.74074 | 115 | 0.50057 | 3 | [5 empty] | 98.4491 | 108.4016 | Lisgar TS | ON_LSG_DSS | Slater TS | ON_SLT_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1401
| M5G | HONI | Ontario | 1 | ac | 1.6 | 0.98765 | 115 | 0.66743 | 3 | [5 empty] | 98.4491 | 108.4016 | Merivale TS | ON_MER_TSS | Nepean Epworth JCT | ON_NPE_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1407
| M5G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Nepean Epworth JCT | ON_NPE_JCT | Nepean Epworth MTS | ON_NPE_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1408
| M5G | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Nepean Epworth JCT | ON_NPE_JCT | Ottawa JCT | ON_OTT_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1409
| M5G | HONI | Ontario | 1 | ac | 3.9 | 2.4074 | 115 | 1.6269 | 3 | [5 empty] | 98.4491 | 108.4016 | Ottawa JCT | ON_OTT_JCT | Carling TS | ON_CAR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1410
| M5G | HONI | Ontario | 1 | ac | 5.2 | 3.2099 | 115 | 2.1691 | 3 | [5 empty] | 98.4491 | 108.4016 | Carling TS | ON_CAR_DSS | Lisgar TS | ON_LSG_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1411
| S7M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | South March SWS | ON_SOM_SWS | Marchwood JCT | ON_MCW_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1876
| S7M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Marchwood JCT | ON_MCW_JCT | Marchwood MTS | ON_MCW_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1877
| S7M | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Marchwood JCT | ON_MCW_JCT | Bridlewood JCT | ON_BRI_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1878
| S7M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridlewood JCT | ON_BRI_JCT | Bridlewood MTS | ON_BRI_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1879
| S7M | HONI | Ontario | 1 | ac | 5.3 | 3.2716 | 115 | 2.2109 | 3 | [5 empty] | 98.4491 | 108.4016 | Bridlewood JCT | ON_BRI_JCT | X523A STR 654 JCT | ON_X52_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1880
| S7M | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 115 | 1.0011 | 3 | [5 empty] | 98.4491 | 108.4016 | X523A STR 654 JCT | ON_X52_JCT | Didsbury Road JCT | ON_DID_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1881
| S7M | HONI | Ontario | 1 | ac | 5.3 | 3.2716 | 115 | 2.2109 | 3 | [5 empty] | 98.4491 | 108.4016 | X523A STR 654 JCT | ON_X52_JCT | S7M STR 673N JCT | ON_S7M_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1882
| S7M | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | S7M STR 673N JCT | ON_S7M_JCT | Merivale TS | ON_MER_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1883
| S7M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | S7M STR 673N JCT | ON_S7M_JCT | S7M STR R14-R15 JCT | ON_S7R_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1884
| S7M | HONI | Ontario | 1 | ac | 4.7 | 2.9012 | 115 | 1.9606 | 3 | [5 empty] | 98.4491 | 108.4016 | S7M STR R14-R15 JCT | ON_S7R_JCT | Fallowfield JCT | ON_FLF_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1885
| S7M | HONI | Ontario | 1 | ac | 6.1 | 3.7654 | 115 | 2.5446 | 3 | [5 empty] | 98.4491 | 108.4016 | S7M STR R14-R15 JCT | ON_S7R_JCT | Manordale JCT | ON_MDL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1886
| S7M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Fallowfield JCT | ON_FLF_JCT | Fallowfield MTS | ON_FLF_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1887
| S7M | HONI | Ontario | 1 | ac | 2.7 | 1.6667 | 115 | 1.1263 | 3 | [5 empty] | 98.4491 | 108.4016 | Fallowfield JCT | ON_FLF_JCT | Manotick JCT | ON_MTK_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1888
| S7M | HONI | Ontario | 1 | ac | 8.1 | 5 | 115 | 3.3789 | 3 | [5 empty] | 98.4491 | 108.4016 | Manotick JCT | ON_MTK_JCT | Manotick DS | ON_MTK_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1889
| S7M | HONI | Ontario | 1 | ac | 5.2 | 3.2099 | 115 | 2.1691 | 3 | [5 empty] | 98.4491 | 108.4016 | Manotick JCT | ON_MTK_JCT | Richmond MTS | ON_RMD_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1890
| V12M | HONI | Ontario | 1 | ac | 7.3 | 4.5062 | 115 | 3.0451 | 3 | [5 empty] | 98.4491 | 108.4016 | Merivale TS | ON_MER_TSS | Val Tetreau JCT | ON_VLT_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process (2nd Draft Report) - South Nepean MTS & South Nepean Transmission Reinforcement |  | 1992
| 56M1 | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Nipigon JCT | ON_NIP_JCT | Red Rock JCT | ON_RRK_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 11
| 56M1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Red Rock JCT | ON_RRK_JCT | Red Rock DS | ON_RRK_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 12
| 57M1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Nipigon JCT | ON_NIP_JCT | Nipigon DS | ON_NIP_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 13
| 57M1 | HONI | Ontario | 1 | ac | 4.7 | 2.9012 | 115 | 1.9606 | 3 | [5 empty] | 98.4491 | 108.4016 | Reserve JCT | ON_RSV_JCT | Nipigon JCT | ON_NIP_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 14
| A1B | HONI | Ontario | 1 | ac | 4.6 | 2.8395 | 115 | 1.9189 | 3 | [5 empty] | 98.4491 | 108.4016 | Aguasabon SWS | ON_AGU_SWS | Terrace Bay SWS | ON_TRB_SWS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 26
| A1B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | AV Terrace Bay JCT | ON_AVT_JCT | AV Terrace Bay TS | ON_AVT_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 27
| A1B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | AV Terrace Bay JCT | ON_AVT_JCT | Terrace Bay SWS | ON_TRB_SWS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 28
| A21L | HONI | Ontario | 1 | ac | 191.8 | 118.3951 | 230 | 92.064 | 1.8197 | [5 empty] | 243.8412 | 263.8581 | Mackenzie TS | ON_MKZ_TSS | Lakehead TS | ON_LKH_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 43
| A22L | HONI | Ontario | 1 | ac | 191.8 | 118.3951 | 230 | 92.064 | 1.8197 | [5 empty] | 243.8412 | 263.8581 | Mackenzie TS | ON_MKZ_TSS | Lakehead TS | ON_LKH_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 44
| A3M | HONI | Ontario | 1 | ac | 11.2 | 6.9136 | 115 | 4.672 | 3 | [5 empty] | 98.4491 | 108.4016 | Mackenzie TS | ON_MKZ_TSS | Moose Lake TS | ON_MSL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 55
| A4L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | AP Nipigon JCT | ON_APN_JCT | AP Nipigon GS | ON_APN_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 79
| A4L | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | AP Nipigon JCT | ON_APN_JCT | Beardmore JCT | ON_BRD_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 80
| A4L | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Alexander SWS | ON_ALX_SWS | AP Nipigon JCT | ON_APN_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 81
| A4L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Beardmore JCT | ON_BRD_JCT | Beardmore DS #2 | ON_BRD_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 82
| A4L | HONI | Ontario | 1 | ac | 1.4 | 0.8642 | 115 | 0.584 | 3 | [5 empty] | 98.4491 | 108.4016 | Beardmore JCT | ON_BRD_JCT | Namewaminikan JCT | ON_NAM_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 83
| A4L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Jellicoe DS #3 JCT | ON_JLL_JCT | Jellicoe DS #3 | ON_JLL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 84
| A4L | HONI | Ontario | 1 | ac | 42.1 | 25.9877 | 115 | 17.5617 | 3 | [5 empty] | 98.4491 | 108.4016 | Jellicoe DS #3 JCT | ON_JLL_JCT | Roxmark JCT | ON_RXK_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 85
| A4L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Namewaminikan JCT | ON_NAM_JCT | Namewaminikan GS | ON_NAM_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 86
| A4L | HONI | Ontario | 1 | ac | 34.9 | 21.5432 | 115 | 14.5583 | 3 | [5 empty] | 98.4491 | 108.4016 | Namewaminikan JCT | ON_NAM_JCT | Jellicoe DS #3 JCT | ON_JLL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 87
| A4L | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Roxmark JCT | ON_RXK_JCT | Roxmark Mine TS | ON_RXM_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 88
| A4L | HONI | Ontario | 1 | ac | 9 | 5.5556 | 115 | 3.7543 | 3 | [5 empty] | 98.4491 | 108.4016 | Roxmark JCT | ON_RXK_JCT | Longlac TS | ON_LLC_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 89
| A4M | HONI | Ontario | 1 | ac | 11.2 | 6.9136 | 115 | 4.672 | 3 | [5 empty] | 98.4491 | 108.4016 | Mackenzie TS | ON_MKZ_TSS | Moose Lake TS | ON_MSL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 90
| A5A | HONI | Ontario | 1 | ac | 83 | 51.2346 | 115 | 34.6229 | 3 | [5 empty] | 98.4491 | 108.4016 | Alexander SWS | ON_ALX_SWS | Minnova JCT | ON_MNV_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 93
| A5A | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Minnova JCT | ON_MNV_JCT | Schreiber JCT | ON_SCH_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 94
| A5A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Schreiber JCT | ON_SCH_JCT | Schreiber Winnipeg DS | ON_SCW_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 95
| A5A | HONI | Ontario | 1 | ac | 9.2 | 5.679 | 115 | 3.8377 | 3 | [5 empty] | 98.4491 | 108.4016 | Schreiber JCT | ON_SCH_JCT | Aguasabon SWS | ON_AGU_SWS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 96
| A6P | HONI | Ontario | 1 | ac | 90.8 | 56.0494 | 115 | 37.8766 | 2.9798 | [5 empty] | 97.7854 | 107.6708 | Alexander SWS | ON_ALX_SWS | Reserve JCT | ON_RSV_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 117
| A6P | HONI | Ontario | 1 | ac | 15.8 | 9.7531 | 115 | 6.5909 | 3 | [5 empty] | 98.4491 | 108.4016 | Reserve JCT | ON_RSV_JCT | Port Arthur TS #1 | ON_PTA_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 118
| A7L | HONI | Ontario | 1 | ac | 15.8 | 9.7531 | 115 | 6.5909 | 3 | [5 empty] | 98.4491 | 108.4016 | Alexander SWS | ON_ALX_SWS | Reserve JCT | ON_RSV_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 131
| A7L | HONI | Ontario | 1 | ac | 91.2 | 56.2963 | 115 | 38.0434 | 2.9711 | [5 empty] | 97.5023 | 107.3591 | Reserve JCT | ON_RSV_JCT | Lakehead TS | ON_LKH_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 132
| A8L | HONI | Ontario | 1 | ac | 98.2 | 60.6173 | 115 | 40.9634 | 2.8297 | [5 empty] | 92.8612 | 102.2488 | Alexander SWS | ON_ALX_SWS | Lakehead TS | ON_LKH_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 142
| B6M | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Caland Ore JCT | ON_CLO_JCT | Sapawe JCT | ON_SPW_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 339
| B6M | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Kashabowie JCT | ON_KSH_JCT | Shebandowan JCT | ON_SHB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 340
| B6M | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | Moose Lake TS | ON_MSL_DSS | Caland Ore JCT | ON_CLO_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 341
| B6M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Murillo JCT | ON_MRL_JCT | Murillo DS | ON_MRL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 342
| B6M | HONI | Ontario | 1 | ac | 14.5 | 8.9506 | 115 | 6.0486 | 3 | [5 empty] | 98.4491 | 108.4016 | Murillo JCT | ON_MRL_JCT | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 343
| B6M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Sapawe JCT | ON_SPW_JCT | Sapawe DS | ON_SPW_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 344
| B6M | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Sapawe JCT | ON_SPW_JCT | Kashabowie JCT | ON_KSH_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 345
| B6M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Shabaqua JCT | ON_SBQ_JCT | Shabaqua DS | ON_SBQ_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 346
| B6M | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Shabaqua JCT | ON_SBQ_JCT | Stanley JCT | ON_SLY_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 347
| B6M | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Shebandowan JCT | ON_SHB_JCT | Shabaqua JCT | ON_SBQ_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 348
| B6M | HONI | Ontario | 1 | ac | 21 | 12.963 | 115 | 8.76 | 3 | [5 empty] | 98.4491 | 108.4016 | Stanley JCT | ON_SLY_JCT | Murillo JCT | ON_MRL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 349
| E2R | HONI | Ontario | 1 | ac | 22 | 13.5802 | 115 | 9.1771 | 3 | [5 empty] | 98.4491 | 108.4016 | Balmer JCT | ON_BLM_JCT | Red Lake TS | ON_RDL_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 721
| E2R | HONI | Ontario | 1 | ac | 22 | 13.5802 | 115 | 9.1771 | 3 | [5 empty] | 98.4491 | 108.4016 | Ear Falls TS | ON_EAF_DSS | Pakwash JCT | ON_PAK_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 722
| E2R | HONI | Ontario | 1 | ac | 22 | 13.5802 | 115 | 9.1771 | 3 | [5 empty] | 98.4491 | 108.4016 | Pakwash JCT | ON_PAK_JCT | Balmer JCT | ON_BLM_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 723
| E4D | HONI | Ontario | 1 | ac | 30.2 | 18.642 | 115 | 12.5977 | 3 | [5 empty] | 98.4491 | 108.4016 | Ear Falls TS | ON_EAF_DSS | Scout Lake JCT | ON_SCL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 730
| E4D | HONI | Ontario | 1 | ac | 68.2 | 42.0988 | 115 | 28.4491 | 3 | [5 empty] | 98.4491 | 108.4016 | Scout Lake JCT | ON_SCL_JCT | Dryden TS | ON_DRY_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 731
| E4D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Scout Lake JCT | ON_SCL_JCT | Perrault Falls DS | ON_PER_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 732
| K23D | HONI | Ontario | 1 | ac | 53.2 | 32.8395 | 230 | 25.536 | 3 | [5 empty] | 402 | 435 | Kenora TS | ON_KNO_TSS | TCPL Vermillion Bay JCT | ON_TCV_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1018
| K23D | HONI | Ontario | 1 | ac | 58.6 | 36.1728 | 230 | 28.128 | 3 | [5 empty] | 402 | 435 | TCPL Vermillion Bay JCT | ON_TCV_JCT | Dryden TS | ON_DRY_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1019
| K23D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | TCPL Vermillion Bay JCT | ON_TCV_JCT | TCPL Vermillion Bay TS | ON_TCV_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1020
| M1S | HONI | Ontario | 1 | ac | 5.8 | 3.5802 | 115 | 2.4194 | 3 | [5 empty] | 98.4491 | 108.4016 | Mill Creek JCT | ON_MLC_JCT | H2O Power Calm Lake GS | ON_H2C_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1282
| M1S | HONI | Ontario | 1 | ac | 8.3 | 5.1235 | 115 | 3.4623 | 3 | [5 empty] | 98.4491 | 108.4016 | Mill Creek JCT | ON_MLC_JCT | H2O Power Sturgeon Falls GS | ON_H2S_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1283
| M1S | HONI | Ontario | 1 | ac | 9.5 | 5.8642 | 115 | 3.9629 | 3 | [5 empty] | 98.4491 | 108.4016 | Moose Lake TS | ON_MSL_DSS | Valerie Falls JCT | ON_VFS_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1284
| M1S | HONI | Ontario | 1 | ac | 38.8 | 23.9506 | 115 | 16.1851 | 3 | [5 empty] | 98.4491 | 108.4016 | Valerie Falls JCT | ON_VFS_JCT | Mill Creek JCT | ON_MLC_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1285
| M23L | HONI | Ontario | 1 | ac | 10.2 | 6.2963 | 230 | 4.896 | 3 | [5 empty] | 402 | 435 | Greenwich WF GS JCT | ON_GRH_JCT | Greenwich WF GS | ON_GRH_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1318
| M23L | HONI | Ontario | 1 | ac | 44.9 | 27.716 | 230 | 21.552 | 3 | [5 empty] | 402 | 435 | Greenwich WF GS JCT | ON_GRH_JCT | Lakehead TS | ON_LKH_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1319
| M23L | HONI | Ontario | 1 | ac | 229.4 | 141.6049 | 230 | 110.112 | 1.6171 | [5 empty] | 216.6878 | 234.4756 | Marathon TS | ON_MRT_TSS | Greenwich WF GS JCT | ON_GRH_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1320
| M24L | HONI | Ontario | 1 | ac | 10.2 | 6.2963 | 230 | 4.896 | 3 | [5 empty] | 402 | 435 | Greenwich WF GS JCT | ON_GRH_JCT | Greenwich WF GS | ON_GRH_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1321
| M24L | HONI | Ontario | 1 | ac | 44.9 | 27.716 | 230 | 21.552 | 3 | [5 empty] | 402 | 435 | Greenwich WF GS JCT | ON_GRH_JCT | Lakehead TS | ON_LKH_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1322
| M24L | HONI | Ontario | 1 | ac | 229.4 | 141.6049 | 230 | 110.112 | 1.6171 | [5 empty] | 216.6878 | 234.4756 | Marathon TS | ON_MRT_TSS | Greenwich WF GS JCT | ON_GRH_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1323
| M2D | HONI | Ontario | 1 | ac | 80 | 49.3827 | 115 | 33.3714 | 3 | [5 empty] | 98.4491 | 108.4016 | Ignace JCT | ON_IGN_JCT | Dryden TS | ON_DRY_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1338
| M2D | HONI | Ontario | 1 | ac | 77 | 47.5309 | 115 | 32.12 | 3 | [5 empty] | 98.4491 | 108.4016 | Moose Lake TS | ON_MSL_DSS | Ignace JCT | ON_IGN_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1339
| M2W | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Marathon TS | ON_MRT_TSS | Pic DS | ON_PIC_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1347
| M2W | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Pic JCT | ON_PIC_JCT | Marathon TS | ON_MRT_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1349
| N93A | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Atikokan TGS | ON_ATK_GSS | Marmion Lake JCT | ON_MRM_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1494
| N93A | HONI | Ontario | 1 | ac | 8.9 | 5.4938 | 230 | 4.272 | 3 | [5 empty] | 402 | 435 | Marmion Lake JCT | ON_MRM_JCT | Mackenzie TS | ON_MKZ_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1495
| P25W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Aubrey Falls JCT | ON_AUB_JCT | Aubrey Falls GS | ON_AUB_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1540
| P25W | HONI | Ontario | 1 | ac | 56.6 | 34.9383 | 230 | 27.168 | 3 | [5 empty] | 402 | 435 | Aubrey Falls JCT | ON_AUB_JCT | Mississagi TS | ON_MSS_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1541
| P25W | HONI | Ontario | 1 | ac | 147.8 | 91.2346 | 230 | 70.944 | 2.1609 | [5 empty] | 289.5646 | 313.3349 | Wawa TS | ON_WAW_TSS | Aubrey Falls JCT | ON_AUB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1542
| P26W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Aubrey Falls JCT | ON_AUB_JCT | Aubrey Falls GS | ON_AUB_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1543
| P26W | HONI | Ontario | 1 | ac | 56.6 | 34.9383 | 230 | 27.168 | 3 | [5 empty] | 402 | 435 | Aubrey Falls JCT | ON_AUB_JCT | Mississagi TS | ON_MSS_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1544
| P26W | HONI | Ontario | 1 | ac | 147.8 | 91.2346 | 230 | 70.944 | 2.1609 | [5 empty] | 289.5646 | 313.3349 | Wawa TS | ON_WAW_TSS | Aubrey Falls JCT | ON_AUB_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1545
| P3B | HONI | Ontario | 1 | ac | 14.6 | 9.0123 | 115 | 6.0903 | 3 | [5 empty] | 98.4491 | 108.4016 | Port Arthur TS #1 | ON_PTA_DSS | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1551
| P5M | HONI | Ontario | 1 | ac | 33 | 20.3704 | 115 | 13.7657 | 3 | [5 empty] | 98.4491 | 108.4016 | Port Arthur TS #1 | ON_PTA_DSS | Conmee JCT | ON_CNM_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1570
| P7B | HONI | Ontario | 1 | ac | 15.4 | 9.5062 | 115 | 6.424 | 3 | [5 empty] | 98.4491 | 108.4016 | P7B STR 320 JCT | ON_P7B_JCT | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1572
| P7B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Port Arthur TS #1 | ON_PTA_DSS | P7B STR 320 JCT | ON_P7B_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1573
| Q4B | HONI | Ontario | 1 | ac | 5.4 | 3.3333 | 115 | 2.2526 | 3 | [5 empty] | 98.4491 | 108.4016 | Abitibi JCT | ON_AB1_JCT | James Street JCT | ON_JMS_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1704
| Q4B | HONI | Ontario | 1 | ac | 1.6 | 0.98765 | 115 | 0.66743 | 3 | [5 empty] | 98.4491 | 108.4016 | James Street JCT | ON_JMS_JCT | RFP Thunder Bay TS | ON_RFB_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1705
| Q4B | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 115 | 0.45886 | 3 | [5 empty] | 98.4491 | 108.4016 | James Street JCT | ON_JMS_JCT | St. Paul JCT | ON_STP_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1706
| Q4B | HONI | Ontario | 1 | ac | 2.1 | 1.2963 | 115 | 0.876 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Paul JCT | ON_STP_JCT | RFP Kraft TS | ON_RFK_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1707
| Q4B | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 115 | 1.0429 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Paul JCT | ON_STP_JCT | Walsh Street JCT | ON_WAL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1708
| Q4B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Thunder Bay SWS | ON_THU_SWS | Abitibi JCT | ON_AB1_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1709
| Q4B | HONI | Ontario | 1 | ac | 4.6 | 2.8395 | 115 | 1.9189 | 3 | [5 empty] | 98.4491 | 108.4016 | Walsh Street JCT | ON_WAL_JCT | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1710
| Q4B | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 115 | 0.37543 | 3 | [5 empty] | 98.4491 | 108.4016 | Walsh Street JCT | ON_WAL_JCT | Fort William TS | ON_FRW_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1711
| Q5B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Abitibi JCT | ON_AB1_JCT | Erco JCT | ON_ERC_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1719
| Q5B | HONI | Ontario | 1 | ac | 5.4 | 3.3333 | 115 | 2.2526 | 3 | [5 empty] | 98.4491 | 108.4016 | Abitibi JCT | ON_AB1_JCT | James Street JCT | ON_JMS_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1720
| Q5B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Erco JCT | ON_ERC_JCT | Q5B STR A6 JCT | ON_Q5B_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1721
| Q5B | HONI | Ontario | 1 | ac | 1.6 | 0.98765 | 115 | 0.66743 | 3 | [5 empty] | 98.4491 | 108.4016 | James Street JCT | ON_JMS_JCT | RFP Thunder Bay TS | ON_RFB_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1722
| Q5B | HONI | Ontario | 1 | ac | 1.1 | 0.67901 | 115 | 0.45886 | 3 | [5 empty] | 98.4491 | 108.4016 | James Street JCT | ON_JMS_JCT | St. Paul JCT | ON_STP_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1723
| Q5B | HONI | Ontario | 1 | ac | 2.1 | 1.2963 | 115 | 0.876 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Paul JCT | ON_STP_JCT | RFP Kraft TS | ON_RFK_ISS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1724
| Q5B | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 115 | 1.0429 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Paul JCT | ON_STP_JCT | Walsh Street JCT | ON_WAL_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1725
| Q5B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Thunder Bay SWS | ON_THU_SWS | Abitibi JCT | ON_AB1_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1726
| Q5B | HONI | Ontario | 1 | ac | 4.6 | 2.8395 | 115 | 1.9189 | 3 | [5 empty] | 98.4491 | 108.4016 | Walsh Street JCT | ON_WAL_JCT | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1727
| Q5B | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 115 | 0.37543 | 3 | [5 empty] | 98.4491 | 108.4016 | Walsh Street JCT | ON_WAL_JCT | Fort William TS | ON_FRW_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1728
| Q8B | HONI | Ontario | 1 | ac | 9.7 | 5.9877 | 115 | 4.0463 | 3 | [5 empty] | 98.4491 | 108.4016 | Thunder Bay SWS | ON_THU_SWS | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1742
| Q9B | HONI | Ontario | 1 | ac | 9.7 | 5.9877 | 115 | 4.0463 | 3 | [5 empty] | 98.4491 | 108.4016 | Thunder Bay SWS | ON_THU_SWS | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1743
| R1LB | HONI | Ontario | 1 | ac | 21.1 | 13.0247 | 115 | 8.8017 | 3 | [5 empty] | 98.4491 | 108.4016 | Lakehead TS | ON_LKH_TSS | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1769
| R1LB | HONI | Ontario | 1 | ac | 122.6 | 75.679 | 115 | 51.1417 | 2.4445 | [5 empty] | 80.2181 | 88.3275 | Pine Portage SWS | ON_PPT_SWS | Lakehead TS | ON_LKH_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1770
| R2LB | HONI | Ontario | 1 | ac | 21.6 | 13.3333 | 115 | 9.0103 | 3 | [5 empty] | 98.4491 | 108.4016 | Lakehead TS | ON_LKH_TSS | Birch TS | ON_BIR_DSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1790
| R2LB | HONI | Ontario | 1 | ac | 118.9 | 73.3951 | 115 | 49.5983 | 2.4944 | [5 empty] | 81.8558 | 90.1308 | Pine Portage SWS | ON_PPT_SWS | Lakehead TS | ON_LKH_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1791
| R9A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Alexander SWS | ON_ALX_SWS | Alexander GS | ON_ALX_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1792
| R9A | HONI | Ontario | 1 | ac | 21.1 | 13.0247 | 115 | 8.8017 | 3 | [5 empty] | 98.4491 | 108.4016 | Pine Portage SWS | ON_PPT_SWS | Alexander SWS | ON_ALX_SWS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1793
| S1C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Conmee JCT | ON_CNM_JCT | Lac Des Iles JCT | ON_LDI_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1794
| S1C | HONI | Ontario | 1 | ac | 65 | 40.1235 | 115 | 27.1143 | 3 | [5 empty] | 98.4491 | 108.4016 | Lac Des Iles JCT | ON_LDI_JCT | Lac Des Iles Min SWS | ON_LDI_SWS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1795
| S1C | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Lac Des Iles JCT | ON_LDI_JCT | Silver Falls GS | ON_SFS_GSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1796
| T1M | HONI | Ontario | 1 | ac | 5.6 | 3.4568 | 115 | 2.336 | 3 | [5 empty] | 98.4491 | 108.4016 | Angler Switch JCT | ON_ANG_JCT | Pic JCT | ON_PIC_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1915
| T1M | HONI | Ontario | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Terrace Bay SWS | ON_TRB_SWS | Angler Switch JCT | ON_ANG_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 1919
| W21M | HONI | Ontario | 1 | ac | 168.3 | 103.8889 | 230 | 80.784 | 1.9835 | [5 empty] | 265.7929 | 287.6117 | Wawa TS | ON_WAW_TSS | Marathon TS | ON_MRT_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 2061
| W22M | HONI | Ontario | 1 | ac | 168.3 | 103.8889 | 230 | 80.784 | 1.9835 | [5 empty] | 265.7929 | 287.6117 | Wawa TS | ON_WAW_TSS | Marathon TS | ON_MRT_TSS | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 2062
| W23K | HONI | Ontario | 1 | ac | 74.2 | 45.8025 | 230 | 35.616 | 3 | [5 empty] | 402 | 435 | Wawa TS | ON_WAW_TSS | MacKay JCT | ON_MKY_JCT | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum - Ontario 230 kV East-West Tie |  | 2063
| B18H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Burlington TS | ON_BUR_DSS | Beach Road JCT | ON_BCR_JCT | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 188
| B18H | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Beach Road JCT | ON_BCR_JCT | Beach TS | ON_BCH_DSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 189
| B18H | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 230 | 1.68 | 3 | [5 empty] | 402 | 435 | Beach Road JCT | ON_BCR_JCT | Lake TS | ON_LAK_DSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 190
| B20H | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Beach Road JCT | ON_BCR_JCT | Beach TS | ON_BCH_DSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 198
| B20H | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 230 | 1.68 | 3 | [5 empty] | 402 | 435 | Beach Road JCT | ON_BCR_JCT | Lake TS | ON_LAK_DSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 199
| H35D | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Beach TS | ON_BCH_DSS | Dofasco Bay Front TS | ON_DBF_ISS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 881
| H36D | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Beach TS | ON_BCH_DSS | Dofasco Bay Front TS | ON_DBF_ISS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 882
| H5K | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Beach TS | ON_BCH_DSS | Kenilworth TS | ON_KNL_DSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 890
| H6K | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Beach TS | ON_BCH_DSS | Kenilworth TS | ON_KNL_DSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 891
| M570V | HONI | Ontario | 1 | ac | 38 | 23.4568 | 500 | 15.01 | 3 | [5 empty] | 2550 | 3225 | Milton SWS | ON_MIL_SWS | Claireville TS | ON_CLV_TSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1402
| M571V | HONI | Ontario | 1 | ac | 38 | 23.4568 | 500 | 15.01 | 3 | [5 empty] | 2550 | 3225 | Milton SWS | ON_MIL_SWS | Claireville TS | ON_CLV_TSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1403
| M585M | HONI | Ontario | 1 | ac | 65 | 40.1235 | 500 | 25.675 | 3 | [5 empty] | 2550 | 3225 | Middleport TS | ON_MPT_TSS | Milton SWS | ON_MIL_SWS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1406
| N37S | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Nanticoke TS | ON_NTK_TSS | Summerhaven SWS | ON_SUM_SWS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 1463
| V586M | HONI | Ontario | 1 | ac | 38 | 23.4568 | 500 | 15.01 | 3 | [5 empty] | 2550 | 3225 | Claireville TS | ON_CLV_TSS | Milton SWS | ON_MIL_SWS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2029
| V586M | HONI | Ontario | 1 | ac | 65 | 40.1235 | 500 | 25.675 | 3 | [5 empty] | 2550 | 3225 | Milton SWS | ON_MIL_SWS | Middleport TS | ON_MPT_TSS | IESO. 2019. Hamilton Sub-Region Integrated Regional Resource Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing |  | 2030
| NA12M6 | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Buttonville TS | ON_BUT_DSS | Gormley JCT | ON_GML_JCT | IESO. 2020. York Region: Integrated Regional Resource Plan |  | 1496
| NA41M31 | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Old Armitage JCT | ON_OLA_JCT | Gormley JCT | ON_GML_JCT | IESO. 2020. York Region: Integrated Regional Resource Plan |  | 1497
| NA41M31 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Armitage TS | ON_ATG_DSS | Old Armitage JCT | ON_OLA_JCT | IESO. 2020. York Region: Integrated Regional Resource Plan |  | 1498
| S5M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Donaldson Cres JCT | ON_DNC_JCT | McCrea JCT | ON_MCC_JCT | Independent Electricity Market Operator. 2003. Connection Assessment & Approval Process. Assessment Summary Falconbridge Limited Nickel Rim Mine Substation |  | 1866
| S5M | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Martindale TS | ON_MTD_DSS | Donaldson Cres JCT | ON_DNC_JCT | Independent Electricity Market Operator. 2003. Connection Assessment & Approval Process. Assessment Summary Falconbridge Limited Nickel Rim Mine Substation |  | 1867
| S5M | HONI | Ontario | 1 | ac | 7.9 | 4.8765 | 115 | 3.2954 | 3 | [5 empty] | 98.4491 | 108.4016 | McCrea JCT | ON_MCC_JCT | Onaping JCT | ON_ONP_JCT | Independent Electricity Market Operator. 2003. Connection Assessment & Approval Process. Assessment Summary Falconbridge Limited Nickel Rim Mine Substation |  | 1868
| S6F | HONI | Ontario | 1 | ac | 2.4 | 1.4815 | 115 | 1.0011 | 3 | [5 empty] | 98.4491 | 108.4016 | Falconbridge JCT | ON_FLB_JCT | Falconbridge 61 JCT | ON_FL6_JCT | Independent Electricity Market Operator. 2003. Connection Assessment & Approval Process. Assessment Summary Falconbridge Limited Nickel Rim Mine Substation |  | 1873
| S6F | HONI | Ontario | 1 | ac | 8.7 | 5.3704 | 115 | 3.6291 | 3 | [5 empty] | 98.4491 | 108.4016 | Martindale TS | ON_MTD_DSS | Falconbridge JCT | ON_FLB_JCT | Independent Electricity Market Operator. 2003. Connection Assessment & Approval Process. Assessment Summary Falconbridge Limited Nickel Rim Mine Substation |  | 1874
| T2R | HONI | Ontario | 1 | ac | 23 | 14.1975 | 115 | 9.5943 | 3 | [5 empty] | 98.4491 | 108.4016 | Blezard Valley JCT | ON_BLZ_JCT | Falconbridge T2R TS | ON_FLB_ISS | Independent Electricity Market Operator. 2003. Connection Assessment & Approval Process. Assessment Summary Falconbridge Limited Nickel Rim Mine Substation |  | 1934
| L23N | HONI | Ontario | 1 | ac | 5.8 | 3.5802 | 230 | 2.784 | 3 | [5 empty] | 402 | 435 | Sarnia Scott TS | ON_SNS_TSS | Talford JCT | ON_TLF_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1187
| L23N | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 230 | 0.432 | 3 | [5 empty] | 402 | 435 | Talford JCT | ON_TLF_JCT | Dupont JCT | ON_DUP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1188
| L23N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Dupont JCT | ON_DUP_JCT | Nova St Clair R TS | ON_NSC_ISS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1189
| L23N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Dupont JCT | ON_DUP_JCT | Shell Sarnia TS | ON_SHL_ISS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1190
| L23N | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Talford JCT | ON_TLF_JCT | Lambton TS #2 | ON_LMB_DSS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1191
| L25V | HONI | Ontario | 1 | ac | 9.4 | 5.8025 | 230 | 4.512 | 3 | [5 empty] | 402 | 435 | Lambton TS #2 | ON_LMB_DSS | Nova Moore JCT | ON_NVM_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1198
| L25V | HONI | Ontario | 1 | ac | 0.27 | 0.16667 | 230 | 0.1296 | 3 | [5 empty] | 402 | 435 | Nova Moore JCT | ON_NVM_JCT | Nova Moore TS | ON_NVM_ISS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1199
| L25V | HONI | Ontario | 1 | ac | 0.27 | 0.16667 | 230 | 0.1296 | 3 | [5 empty] | 402 | 435 | Nova Moore JCT | ON_NVM_JCT | Nova SWS | ON_NOV_SWS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1200
| L27V | HONI | Ontario | 1 | ac | 9.4 | 5.8025 | 230 | 4.512 | 3 | [5 empty] | 402 | 435 | Lambton TS #2 | ON_LMB_DSS | Nova Moore JCT | ON_NVM_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1202
| L27V | HONI | Ontario | 1 | ac | 0.27 | 0.16667 | 230 | 0.1296 | 3 | [5 empty] | 402 | 435 | Nova Moore JCT | ON_NVM_JCT | Nova Moore TS | ON_NVM_ISS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1203
| L27V | HONI | Ontario | 1 | ac | 0.27 | 0.16667 | 230 | 0.1296 | 3 | [5 empty] | 402 | 435 | Nova Moore JCT | ON_NVM_JCT | Nova SWS | ON_NOV_SWS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1204
| L27V | HONI | Ontario | 1 | ac | 4.2 | 2.5926 | 230 | 2.016 | 3 | [5 empty] | 402 | 435 | Nova SWS | ON_NOV_SWS | Nova Corunna TS | ON_NVC_ISS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 1205
| V43N | HONI | Ontario | 1 | ac | 3.4 | 2.0988 | 230 | 1.632 | 3 | [5 empty] | 402 | 435 | St. Clair E.C. JCT | ON_STE_JCT | Talford JCT | ON_TLF_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 2019
| V43N | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 230 | 0.432 | 3 | [5 empty] | 402 | 435 | Talford JCT | ON_TLF_JCT | Nova SWS | ON_NOV_SWS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 2020
| V43N | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 230 | 0.432 | 3 | [5 empty] | 402 | 435 | Talford JCT | ON_TLF_JCT | Dupont JCT | ON_DUP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 2021
| V43N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Dupont JCT | ON_DUP_JCT | Nova St Clair R TS | ON_NSC_ISS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 2022
| V43N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Dupont JCT | ON_DUP_JCT | Shell Sarnia TS | ON_SHL_ISS | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area |  | 2023
| L21K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Haig JCT | ON_HAI_JCT | Applewood JCT | ON_APP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1169
| L21K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Haig JCT | ON_HAI_JCT | Applewood JCT | ON_APP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1170
| L21K | HONI | Ontario | 1 | ac | 3.4 | 2.0988 | 230 | 1.632 | 3 | [5 empty] | 402 | 435 | Lakeview SWS | ON_LKV_SWS | Haig JCT | ON_HAI_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1171
| L22K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Haig JCT | ON_HAI_JCT | Applewood JCT | ON_APP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1181
| L22K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Haig JCT | ON_HAI_JCT | Applewood JCT | ON_APP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1182
| L22K | HONI | Ontario | 1 | ac | 3.4 | 2.0988 | 230 | 1.632 | 3 | [5 empty] | 402 | 435 | Lakeview SWS | ON_LKV_SWS | Haig JCT | ON_HAI_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1183
| L23CK | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Haig JCT | ON_HAI_JCT | Applewood JCT | ON_APP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1184
| L23CK | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Haig JCT | ON_HAI_JCT | Applewood JCT | ON_APP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1185
| L23CK | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 230 | 1.68 | 3 | [5 empty] | 402 | 435 | Lakeview SWS | ON_LKV_SWS | Haig JCT | ON_HAI_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1186
| L24CR | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Haig JCT | ON_HAI_JCT | Applewood JCT | ON_APP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1194
| L24CR | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Haig JCT | ON_HAI_JCT | Applewood JCT | ON_APP_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1195
| L24CR | HONI | Ontario | 1 | ac | 3.7 | 2.284 | 230 | 1.776 | 3 | [5 empty] | 402 | 435 | Lakeview SWS | ON_LKV_SWS | Haig JCT | ON_HAI_JCT | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the Proposed Enhancement of Cooksville TS & and Retermination of the 230 kV Circuits at Applewood Junction |  | 1196
| B4B | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Blind River TS | ON_BLD_DSS | Algoma TS | ON_ALG_TSS | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 265
| S2B | HONI | Ontario | 1 | ac | 152 | 93.8272 | 115 | 63.4057 | 2.1214 | [5 empty] | 69.6155 | 76.6531 | Baldwin JCT | ON_BDW_JCT | Massey JCT | ON_MSY_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1808
| S2B | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Blind River TS JCT | ON_BLD_JCT | Algoma TS | ON_ALG_TSS | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1809
| S2B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Blind River TS JCT | ON_BLD_JCT | Blind River TS | ON_BLD_DSS | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1810
| S2B | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Cameron Falls JCT | ON_CAM_JCT | Spanish JCT | ON_SPA_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1811
| S2B | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Carmeuse Lime JCT | ON_CML_JCT | Blind River TS JCT | ON_BLD_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1812
| S2B | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Creighton JCT | ON_CRE_JCT | Vermillion JCT | ON_VEM_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1815
| S2B | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Cutler JCT | ON_CUT_JCT | Serpent River JCT | ON_SER_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1816
| S2B | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Eacom Nairn Centre JCT | ON_EAC_JCT | Espanola JCT | ON_ESP_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1818
| S2B | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Eddy Tap JCT | ON_EDT_JCT | Espanola A JCT | ON_EPA_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1820
| S2B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Espanola A JCT | ON_EPA_JCT | Espanola TS | ON_ESP_DSS | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1821
| S2B | HONI | Ontario | 1 | ac | 47 | 29.0123 | 115 | 19.6057 | 3 | [5 empty] | 98.4491 | 108.4016 | Espanola A JCT | ON_EPA_JCT | McLeans Mountain JCT | ON_MCL_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1822
| S2B | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Espanola JCT | ON_ESP_JCT | Eddy Tap JCT | ON_EDT_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1823
| S2B | HONI | Ontario | 1 | ac | 28 | 17.284 | 115 | 11.68 | 3 | [5 empty] | 98.4491 | 108.4016 | Espanola JCT | ON_ESP_JCT | Baldwin JCT | ON_BDW_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1824
| S2B | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Ethel Lake JCT | ON_ETH_JCT | Turbine JCT | ON_TUR_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1827
| S2B | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 115 | 2.7114 | 3 | [5 empty] | 98.4491 | 108.4016 | Massey JCT | ON_MSY_JCT | Cameron Falls JCT | ON_CAM_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1829
| S2B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Massey JCT | ON_MSY_JCT | Massey DS | ON_MSY_DSS | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1830
| S2B | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | McLeans Mountain JCT | ON_MCL_JCT | McLeans Mountain GS | ON_MCL_GSS | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1832
| S2B | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | Serpent River JCT | ON_SER_JCT | Carmeuse Lime JCT | ON_CML_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1834
| S2B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Spanish JCT | ON_SPA_JCT | Spanish DS | ON_SPA_DSS | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1835
| S2B | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Spanish JCT | ON_SPA_JCT | Cutler JCT | ON_CUT_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1836
| S2B | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Vermillion JCT | ON_VEM_JCT | Ethel Lake JCT | ON_ETH_JCT | McLean's Mountain Wind Limited Partnership. 2013. Application for Amendment to Form of Transmission Connection Agreement - McLean's Mountain Wind Limited Partnership |  | 1839
| A8G | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosedene JCT | ON_RSD_JCT | Railway JCT | ON_RLW_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 133
| A8G | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Railway JCT | ON_RLW_JCT | Glanford JCT | ON_GLF_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 134
| A8G | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Glanford JCT | ON_GLF_JCT | Beach JCT | ON_BCH_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 135
| A8G | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Beach JCT | ON_BCH_JCT | Gage TS | ON_GAG_DSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 136
| M20D | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Galt South JCT | ON_GTS_JCT | Trinity JCT | ON_TRN_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1299
| M20D | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Trinity JCT | ON_TRN_JCT | Carluke JCT | ON_CLK_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1300
| M20D | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1301
| M21D | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Trinity JCT | ON_TRN_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1315
| M21D | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Trinity JCT | ON_TRN_JCT | Carluke JCT | ON_CLK_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1316
| M21D | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1317
| Q28A | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Abit Cons NAN91 JCT | ON_ACS_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1651
| Q28A | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Abit Cons NAN91 JCT | ON_ACS_JCT | Allanburg TS | ON_ALL_TSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1652
| Q2AH | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 SWS | ON_BK1_SWS | Beck #1 Q2AH JCT | ON_BKQ_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1662
| Q2AH | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Beck #1 Q2AH JCT | ON_BKQ_JCT | Holland Road JCT | ON_HLR_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1663
| Q2AH | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Holland Road JCT | ON_HLR_JCT | Allanburg TS | ON_ALL_TSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1664
| Q2AH | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Holland Road JCT | ON_HLR_JCT | St. Johns Valley JCT | ON_STJ_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1665
| Q2AH | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Johns Valley JCT | ON_STJ_JCT | Louth JCT | ON_LOU_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1666
| Q2AH | HONI | Ontario | 1 | ac | 12.5 | 7.716 | 115 | 5.2143 | 3 | [5 empty] | 98.4491 | 108.4016 | Louth JCT | ON_LOU_JCT | Cherry JCT | ON_CHR_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1667
| Q2AH | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cherry JCT | ON_CHR_JCT | Vineland DS | ON_VNL_DSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1668
| Q2AH | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Cherry JCT | ON_CHR_JCT | Beamsville TS | ON_BMS_DSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1669
| Q2AH | HONI | Ontario | 1 | ac | 14 | 8.642 | 115 | 5.84 | 3 | [5 empty] | 98.4491 | 108.4016 | Beamsville TS | ON_BMS_DSS | Winona JCT | ON_WNA_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1670
| Q2AH | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Winona JCT | ON_WNA_JCT | Winona TS | ON_WNA_DSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1671
| Q2AH | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Winona JCT | ON_WNA_JCT | Saltfleet JCT | ON_SLT_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1672
| Q2AH | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Saltfleet JCT | ON_SLT_JCT | Beach TS | ON_BCH_DSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1673
| Q2AH | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Johns Valley JCT | ON_STJ_JCT | Pelham JCT | ON_PEL_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1674
| Q2AH | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Pelham JCT | ON_PEL_JCT | Rosedene JCT | ON_RSD_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1675
| Q2AH | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Rosedene JCT | ON_RSD_JCT | St. Anns JCT | ON_STN_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1676
| Q2AH | HONI | Ontario | 1 | ac | 22 | 13.5802 | 115 | 9.1771 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Anns JCT | ON_STN_JCT | Dunnville TS | ON_DNV_DSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1677
| Q2AH | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | St. Anns JCT | ON_STN_JCT | Caistor JCT | ON_CST_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1678
| Q2AH | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Caistor JCT | ON_CST_JCT | IPPL Smithville TS | ON_SMV_ISS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1679
| Q2AH | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Caistor JCT | ON_CST_JCT | Railway JCT | ON_RLW_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1680
| Q2AH | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Railway JCT | ON_RLW_JCT | Glanford JCT | ON_GLF_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1681
| Q30M | HONI | Ontario | 1 | ac | 17 | 10.4938 | 230 | 8.16 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Allanburg Q30M JCT | ON_ALQ_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1682
| Q30M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Allanburg Q30M JCT | ON_ALQ_JCT | Allanburg TS | ON_ALL_TSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1683
| Q30M | HONI | Ontario | 1 | ac | 64 | 39.5062 | 230 | 30.72 | 3 | [5 empty] | 402 | 435 | Allanburg Q30M JCT | ON_ALQ_JCT | Mount Hope JCT | ON_MTH_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1684
| Q30M | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Mount Hope JCT | ON_MTH_JCT | Carluke JCT | ON_CLK_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1685
| Q30M | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Carluke JCT | ON_CLK_JCT | Middleport TS | ON_MPT_TSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1686
| Q35M | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Abit Cons NAN91 JCT | ON_ACS_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1687
| Q35M | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Abit Cons NAN91 JCT | ON_ACS_JCT | Crossline JCT | ON_CSL_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1688
| Q35M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Crossline JCT | ON_CSL_JCT | Allanburg TS | ON_ALL_TSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1689
| Q35M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Crossline JCT | ON_CSL_JCT | Allanburg West JCT | ON_ALW_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1690
| Q35M | HONI | Ontario | 1 | ac | 17 | 10.4938 | 230 | 8.16 | 3 | [5 empty] | 402 | 435 | Allanburg West JCT | ON_ALW_JCT | St. Anns JCT | ON_STN_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1691
| Q35M | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | St. Anns JCT | ON_STN_JCT | Caledonia Q35M JCT | ON_CAQ_JCT | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1692
| Q35M | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Caledonia Q35M JCT | ON_CAQ_JCT | Middleport TS | ON_MPT_TSS | Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000) |  | 1693
| 15M1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kenora MTS JCT | ON_KNM_JCT | Kenora MTS | ON_KNM_DSS |  |  | 1
| 15M1 | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Rabbit Lake SWS | ON_RBL_SWS | Kenora MTS JCT | ON_KNM_JCT |  |  | 2
| 29M1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Agimak DS JCT | ON_AGM_JCT | Agimak DS | ON_AGM_DSS |  |  | 3
| 29M1 | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Camp Lake JCT | ON_CPL_JCT | Agimak DS JCT | ON_AGM_JCT |  |  | 4
| 29M1 | HONI | Ontario | 1 | ac | 45 | 27.7778 | 115 | 18.7714 | 3 | [5 empty] | 98.4491 | 108.4016 | Camp Lake JCT | ON_CPL_JCT | Valora JCT | ON_VLA_JCT |  |  | 5
| 29M1 | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Ignace DS JCT | ON_IGD_JCT | Camp Lake JCT | ON_CPL_JCT |  |  | 6
| 29M1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Ignace JCT | ON_IGN_JCT | Ignace DS JCT | ON_IGD_JCT |  |  | 7
| 29M1 | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Valora JCT | ON_VLA_JCT | Mattabi JCT | ON_MTB_JCT |  |  | 8
| 29M1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Valora JCT | ON_VLA_JCT | Valora DS | ON_VLA_DSS |  |  | 9
| 3024F2 | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Tisdale JCT | ON_TSD_JCT | Pamour JCT | ON_PAM_JCT |  |  | 10
| 61M18 | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Goderich TS | ON_GOD_DSS | Constance DS | ON_CNC_DSS |  |  | 15
| 61M18 | HONI | Ontario | 1 | ac | 17 | 10.4938 | 115 | 7.0914 | 3 | [5 empty] | 98.4491 | 108.4016 | Constance DS | ON_CNC_DSS | Seaforth TS | ON_SFT_DSS |  |  | 16
| A23P | HONI | Ontario | 1 | ac | 65 | 40.1235 | 230 | 31.2 | 3 | [5 empty] | 402 | 435 | Algoma TS | ON_ALG_TSS | Mississagi TS | ON_MSS_DSS |  |  | 45
| A24P | HONI | Ontario | 1 | ac | 65 | 40.1235 | 230 | 31.2 | 3 | [5 empty] | 402 | 435 | Algoma TS | ON_ALG_TSS | Mississagi TS | ON_MSS_DSS |  |  | 46
| A4H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cochrane West JCT | ON_CCW_JCT | Cochrane West DS | ON_CCW_DSS |  |  | 65
| A4H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cochrane West JCT | ON_CCW_JCT | Cochrane West MTS | ON_COC_DSS |  |  | 66
| A4H | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Fournier JCT | ON_FOU_JCT | Power JCT | ON_POW_JCT |  |  | 67
| A4H | HONI | Ontario | 1 | ac | 45 | 27.7778 | 115 | 18.7714 | 3 | [5 empty] | 98.4491 | 108.4016 | Fournier JCT | ON_FOU_JCT | Ansonville TS | ON_ANS_TSS |  |  | 68
| A4H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hunta SWS | ON_HTA_SWS | Fournier JCT | ON_FOU_JCT |  |  | 69
| A4H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Power JCT | ON_POW_JCT | Cochrane West JCT | ON_CCW_JCT |  |  | 70
| A565L | HONI | Ontario | 1 | ac | 135 | 83.3333 | 500 | 53.325 | 2.294 | [5 empty] | 1949.8662 | 2466.0073 | Ashfield SWS | ON_ASH_SWS | Longwood TS | ON_LGW_DSS |  |  | 91
| A592K | HONI | Ontario | 1 | ac | 1 | 0.61728 | 500 | 0.395 | 3 | [5 empty] | 2550 | 3225 | Ashfield SWS | ON_ASH_SWS | K2 Wind GS | ON_K2W_GSS |  |  | 92
| A5H | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | AP Tunis JCT | ON_APT_JCT | Iroq Falls 115 JCT | ON_IRF_JCT |  |  | 97
| A5H | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Fournier JCT | ON_FOU_JCT | AP Tunis JCT | ON_APT_JCT |  |  | 98
| A5H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hunta SWS | ON_HTA_SWS | Fournier JCT | ON_FOU_JCT |  |  | 99
| A5H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Iroq Falls 115 JCT | ON_IRF_JCT | Iroquois Fls DS JCT | ON_IQF_JCT |  |  | 100
| A5H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Iroquois Fls DS JCT | ON_IQF_JCT | Iroquois Falls DS | ON_IQF_DSS |  |  | 101
| A5H | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Iroquois Fls DS JCT | ON_IQF_JCT | Ansonville TS | ON_ANS_TSS |  |  | 102
| A8K | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | A8K-19EO JCT | ON_A19_JCT | Monteith SWS JCT | ON_MTT_JCT |  |  | 137
| A8K | HONI | Ontario | 1 | ac | 45 | 27.7778 | 115 | 18.7714 | 3 | [5 empty] | 98.4491 | 108.4016 | A8K-47EO JCT | ON_A47_JCT | Kirkland Lake TS | ON_KLL_DSS |  |  | 138
| A8K | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Ansonville TS | ON_ANS_TSS | A8K-19EO JCT | ON_A19_JCT |  |  | 139
| A8K | HONI | Ontario | 1 | ac | 75 | 46.2963 | 115 | 31.2857 | 3 | [5 empty] | 98.4491 | 108.4016 | Monteith SWS JCT | ON_MTT_JCT | A8K-47EO JCT | ON_A47_JCT |  |  | 140
| A8K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Monteith SWS JCT | ON_MTT_JCT | Monteith SWS | ON_MTT_SWS |  |  | 141
| A9K | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | Ansonville TS | ON_ANS_TSS | Monteith DS JCT | ON_MON_JCT |  |  | 148
| A9K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Monteith DS JCT | ON_MON_JCT | Monteith DS | ON_MON_DSS |  |  | 149
| A9K | HONI | Ontario | 1 | ac | 60 | 37.037 | 115 | 25.0286 | 3 | [5 empty] | 98.4491 | 108.4016 | Monteith DS JCT | ON_MON_JCT | Ramore TS | ON_RMR_DSS |  |  | 150
| A9K | HONI | Ontario | 1 | ac | 60 | 37.037 | 115 | 25.0286 | 3 | [5 empty] | 98.4491 | 108.4016 | Ramore TS | ON_RMR_DSS | Kirkland Lake TS | ON_KLL_DSS |  |  | 151
| B15C | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Cooksville TS | ON_CKV_DSS | Lorne Park TS | ON_LNP_DSS |  |  | 180
| B15C | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Lorne Park TS | ON_LNP_DSS | Ford JCT | ON_FRD_JCT |  |  | 181
| B15C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Ford JCT | ON_FRD_JCT | Ford Oakville TS | ON_FDO_ISS |  |  | 182
| B15C | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Ford JCT | ON_FRD_JCT | Oakville TS #2 | ON_OAK_DSS |  |  | 183
| B16C | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Cooksville TS | ON_CKV_DSS | Lorne Park TS | ON_LNP_DSS |  |  | 184
| B16C | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Lorne Park TS | ON_LNP_DSS | Ford JCT | ON_FRD_JCT |  |  | 185
| B16C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Ford JCT | ON_FRD_JCT | Ford Oakville TS | ON_FDO_ISS |  |  | 186
| B16C | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Ford JCT | ON_FRD_JCT | Oakville TS #2 | ON_OAK_DSS |  |  | 187
| B1S | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Ardoch JCT | ON_ARD_JCT | Ardoch DS | ON_ARD_DSS |  |  | 191
| B1S | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Ardoch JCT | ON_ARD_JCT | Northbrook JCT | ON_NBK_JCT |  |  | 192
| B1S | HONI | Ontario | 1 | ac | 38 | 23.4568 | 115 | 15.8514 | 3 | [5 empty] | 98.4491 | 108.4016 | Barrett Chute SWS | ON_BTC_SWS | Ardoch JCT | ON_ARD_JCT |  |  | 193
| B1S | HONI | Ontario | 1 | ac | 38 | 23.4568 | 115 | 15.8514 | 3 | [5 empty] | 98.4491 | 108.4016 | Lodgeroom DS | ON_LGR_DSS | Sidney TS | ON_SDY_DSS |  |  | 194
| B1S | HONI | Ontario | 1 | ac | 32 | 19.7531 | 115 | 13.3486 | 3 | [5 empty] | 98.4491 | 108.4016 | Northbrook DS | ON_NBK_DSS | Lodgeroom DS | ON_LGR_DSS |  |  | 195
| B1S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Northbrook JCT | ON_NBK_JCT | Northbrook DS | ON_NBK_DSS |  |  | 196
| B20H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Burlington TS | ON_BUR_DSS | Beach Road JCT | ON_BCR_JCT |  |  | 197
| B20P | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Bruce A TS | ON_BCA_TSS | Bruce HWP B TS | ON_BCW_ISS |  |  | 200
| B24P | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Bruce A TS | ON_BCA_TSS | Bruce HWP B TS | ON_BCW_ISS |  |  | 201
| B20P | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Bruce A TS | ON_BCA_TSS | Douglas Point TS | ON_DGP_DSS |  |  | 202
| B22D | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Bruce A TS | ON_BCA_TSS | Majestic JCT | ON_MAJ_JCT |  |  | 203
| B22D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Majestic JCT | ON_MAJ_JCT | Majestic TS | ON_MAJ_ISS |  |  | 204
| B22D | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Majestic JCT | ON_MAJ_JCT | Armow JCT | ON_ARM_JCT |  |  | 205
| B22D | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Armow JCT | ON_ARM_JCT | Armow GS | ON_ARM_GSS |  |  | 206
| B22D | HONI | Ontario | 1 | ac | 50 | 30.8642 | 230 | 24 | 3 | [5 empty] | 402 | 435 | Armow JCT | ON_ARM_JCT | Wingham JCT | ON_WNG_JCT |  |  | 207
| B22D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Wingham JCT | ON_WNG_JCT | Wingham TS | ON_WNG_DSS |  |  | 208
| B22D | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Wingham JCT | ON_WNG_JCT | Seaforth TS | ON_SFT_DSS |  |  | 209
| B22D | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Seaforth TS | ON_SFT_DSS | Festival MTS #1 JCT | ON_FST_JCT |  |  | 210
| B22D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Festival MTS #1 JCT | ON_FST_JCT | Festival MTS #1 | ON_FST_DSS |  |  | 211
| B22D | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Festival MTS #1 JCT | ON_FST_JCT | Stratford JCT | ON_STF_JCT |  |  | 212
| B22D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Stratford JCT | ON_STF_JCT | Stratford TS | ON_STF_DSS |  |  | 213
| B22D | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Stratford JCT | ON_STF_JCT | Detweiler TS | ON_DET_TSS |  |  | 214
| B23C | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | B23C H26C Tie JCT | ON_B23_JCT | Cherrywood TS | ON_CHW_DSS |  |  | 215
| B23C | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Belleville TS | ON_BLV_DSS | Pancake JCT | ON_PNC_JCT |  |  | 216
| B23C | HONI | Ontario | 1 | ac | 120 | 74.0741 | 230 | 57.6 | 2.4793 | [5 empty] | 332.22 | 359.4918 | Pancake JCT | ON_PNC_JCT | Wilson JCT | ON_WLS_JCT |  |  | 217
| B23C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Whitby JCT | ON_WHB_JCT | Whitby TS | ON_WHB_DSS |  |  | 218
| B23C | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Whitby JCT | ON_WHB_JCT | B23C H26C Tie JCT | ON_B23_JCT |  |  | 219
| B23C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Wilson JCT | ON_WLS_JCT | Wilson TS | ON_WLS_DSS |  |  | 220
| B23C | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Wilson JCT | ON_WLS_JCT | Whitby JCT | ON_WHB_JCT |  |  | 221
| B23D | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Bruce A TS | ON_BCA_TSS | Majestic JCT | ON_MAJ_JCT |  |  | 222
| B23D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Majestic JCT | ON_MAJ_JCT | Majestic TS | ON_MAJ_ISS |  |  | 223
| B23D | HONI | Ontario | 1 | ac | 56 | 34.5679 | 230 | 26.88 | 3 | [5 empty] | 402 | 435 | Majestic JCT | ON_MAJ_JCT | Wingham JCT | ON_WNG_JCT |  |  | 224
| B23D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Wingham JCT | ON_WNG_JCT | Wingham TS | ON_WNG_DSS |  |  | 225
| B23D | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Wingham JCT | ON_WNG_JCT | Seaforth TS | ON_SFT_DSS |  |  | 226
| B23D | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Seaforth TS | ON_SFT_DSS | Zurich JCT | ON_ZUR_JCT |  |  | 227
| B23D | HONI | Ontario | 1 | ac | 27 | 16.6667 | 230 | 12.96 | 3 | [5 empty] | 402 | 435 | Zurich JCT | ON_ZUR_JCT | Zurich GS | ON_ZUR_DSS |  |  | 228
| B23D | HONI | Ontario | 1 | ac | 38 | 23.4568 | 230 | 18.24 | 3 | [5 empty] | 402 | 435 | Zurich JCT | ON_ZUR_JCT | Festival MTS #1 JCT | ON_FST_JCT |  |  | 229
| B23D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Festival MTS #1 JCT | ON_FST_JCT | Festival MTS #1 | ON_FST_DSS |  |  | 230
| B23D | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Festival MTS #1 JCT | ON_FST_JCT | Stratford JCT | ON_STF_JCT |  |  | 231
| B23D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Stratford JCT | ON_STF_JCT | Stratford TS | ON_STF_DSS |  |  | 232
| B23D | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Stratford JCT | ON_STF_JCT | Detweiler TS | ON_DET_TSS |  |  | 233
| B24P | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Bruce A TS | ON_BCA_TSS | Douglas Point TS | ON_DGP_DSS |  |  | 234
| B27S | HONI | Ontario | 1 | ac | 75 | 46.2963 | 230 | 36 | 3 | [5 empty] | 402 | 435 | Bruce A TS | ON_BCA_TSS | Owen Sound JCT | ON_OWS_JCT |  |  | 235
| B27S | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Owen Sound JCT | ON_OWS_JCT | Owen Sound TS | ON_OWS_DSS |  |  | 236
| B28S | HONI | Ontario | 1 | ac | 75 | 46.2963 | 230 | 36 | 3 | [5 empty] | 402 | 435 | Bruce A TS | ON_BCA_TSS | Owen Sound TS | ON_OWS_DSS |  |  | 237
| B31L | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | St. Lawrence TS | ON_STL_DSS | Raisin River JCT | ON_RSR_JCT |  |  | 246
| B3E | HONI | Ontario | 1 | ac | 57 | 35.1852 | 115 | 23.7771 | 3 | [5 empty] | 98.4491 | 108.4016 | Blind River TS | ON_BLD_DSS | Elliot Lake JCT | ON_ELL_JCT |  |  | 249
| B3E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Elliot Lake JCT | ON_ELL_JCT | Elliot Lake TS | ON_ELL_DSS |  |  | 250
| B4E | HONI | Ontario | 1 | ac | 57 | 35.1852 | 115 | 23.7771 | 3 | [5 empty] | 98.4491 | 108.4016 | Blind River TS | ON_BLD_DSS | Elliot Lake TS | ON_ELL_DSS |  |  | 266
| B4V | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Amaranth JCT | ON_AMA_JCT | GV3 WF JCT | ON_GV3_JCT |  |  | 269
| B4V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | GV3 WF JCT | ON_GV3_JCT | GV3 WF GS | ON_GV3_GSS |  |  | 270
| B4V | HONI | Ontario | 1 | ac | 28 | 17.284 | 230 | 13.44 | 3 | [5 empty] | 402 | 435 | GV3 WF JCT | ON_GV3_JCT | Southgate JCT | ON_SOG_JCT |  |  | 271
| B4V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Southgate JCT | ON_SOG_JCT | Southgate GS | ON_SOG_GSS |  |  | 272
| B4V | HONI | Ontario | 1 | ac | 28 | 17.284 | 230 | 13.44 | 3 | [5 empty] | 402 | 435 | Southgate JCT | ON_SOG_JCT | Hanover TS | ON_HNV_DSS |  |  | 273
| B4V | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Hanover TS | ON_HNV_DSS | Underwood JCT | ON_UDW_JCT |  |  | 274
| B4V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Underwood JCT | ON_UDW_JCT | Underwood GS | ON_UDW_GSS |  |  | 275
| B4V | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Underwood JCT | ON_UDW_JCT | Bruce A TS | ON_BCA_TSS |  |  | 276
| B501M | HONI | Ontario | 1 | ac | 16 | 9.8765 | 500 | 6.32 | 3 | [5 empty] | 2550 | 3225 | Bruce B SWS | ON_BCB_SWS | Willow Creek JCT | ON_WLC_JCT |  |  | 277
| B501M | HONI | Ontario | 1 | ac | 160 | 98.7654 | 500 | 63.2 | 2.0508 | [5 empty] | 1743.1823 | 2204.6129 | Willow Creek JCT | ON_WLC_JCT | Milton SWS | ON_MIL_SWS |  |  | 278
| B502M | HONI | Ontario | 1 | ac | 16 | 9.8765 | 500 | 6.32 | 3 | [5 empty] | 2550 | 3225 | Bruce A TS | ON_BCA_TSS | Willow Creek JCT | ON_WLC_JCT |  |  | 279
| B502M | HONI | Ontario | 1 | ac | 160 | 98.7654 | 500 | 63.2 | 2.0508 | [5 empty] | 1743.1823 | 2204.6129 | Willow Creek JCT | ON_WLC_JCT | Milton SWS | ON_MIL_SWS |  |  | 280
| B540C | HONI | Ontario | 1 | ac | 45 | 27.7778 | 500 | 17.775 | 3 | [5 empty] | 2550 | 3225 | Bowmanville SWS | ON_BOW_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 281
| B541C | HONI | Ontario | 1 | ac | 45 | 27.7778 | 500 | 17.775 | 3 | [5 empty] | 2550 | 3225 | Bowmanville SWS | ON_BOW_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 282
| B542C | HONI | Ontario | 1 | ac | 45 | 27.7778 | 500 | 17.775 | 3 | [5 empty] | 2550 | 3225 | Bowmanville SWS | ON_BOW_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 283
| B543TC | HONI | Ontario | 1 | ac | 20 | 12.3457 | 500 | 7.9 | 3 | [5 empty] | 2550 | 3225 | Bowmanville SWS | ON_BOW_SWS | Clarington JCT | ON_CLG_JCT |  |  | 284
| B543TC | HONI | Ontario | 1 | ac | 25 | 15.4321 | 500 | 9.875 | 3 | [5 empty] | 2550 | 3225 | Clarington JCT | ON_CLG_JCT | Cherrywood TS | ON_CHW_DSS |  |  | 285
| B543TC | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 500 | 0.0395 | 3 | [5 empty] | 2550 | 3225 | Clarington JCT | ON_CLG_JCT | Clarington TS | ON_CLG_TSS |  |  | 286
| B560V | HONI | Ontario | 1 | ac | 16 | 9.8765 | 500 | 6.32 | 3 | [5 empty] | 2550 | 3225 | Bruce A TS | ON_BCA_TSS | Willow Creek JCT | ON_WLC_JCT |  |  | 287
| B560V | HONI | Ontario | 1 | ac | 160 | 98.7654 | 500 | 63.2 | 2.0508 | [5 empty] | 1743.1823 | 2204.6129 | Willow Creek JCT | ON_WLC_JCT | Milton SWS | ON_MIL_SWS |  |  | 288
| B560V | HONI | Ontario | 1 | ac | 38 | 23.4568 | 500 | 15.01 | 3 | [5 empty] | 2550 | 3225 | Milton SWS | ON_MIL_SWS | Claireville TS | ON_CLV_TSS |  |  | 289
| B561M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 500 | 0.0395 | 3 | [5 empty] | 2550 | 3225 | Bruce B SWS | ON_BCB_SWS | Bruce JCT | ON_BCC_JCT |  |  | 290
| B561M | HONI | Ontario | 1 | ac | 16 | 9.8765 | 500 | 6.32 | 3 | [5 empty] | 2550 | 3225 | Bruce JCT | ON_BCC_JCT | Willow Creek JCT | ON_WLC_JCT |  |  | 291
| B561M | HONI | Ontario | 1 | ac | 160 | 98.7654 | 500 | 63.2 | 2.0508 | [5 empty] | 1743.1823 | 2204.6129 | Willow Creek JCT | ON_WLC_JCT | Milton SWS | ON_MIL_SWS |  |  | 292
| B562E | HONI | Ontario | 1 | ac | 16 | 9.8765 | 500 | 6.32 | 3 | [5 empty] | 2550 | 3225 | Bruce A TS | ON_BCA_TSS | Willow Creek JCT | ON_WLC_JCT |  |  | 293
| B562E | HONI | Ontario | 1 | ac | 150 | 92.5926 | 500 | 59.25 | 2.14 | [5 empty] | 1818.9793 | 2300.4738 | Willow Creek JCT | ON_WLC_JCT | Evergreen SWS | ON_EVG_SWS |  |  | 294
| B563A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 500 | 0.0395 | 3 | [5 empty] | 2550 | 3225 | Bruce B SWS | ON_BCB_SWS | Bruce JCT | ON_BCC_JCT |  |  | 295
| B563A | HONI | Ontario | 1 | ac | 16 | 9.8765 | 500 | 6.32 | 3 | [5 empty] | 2550 | 3225 | Bruce JCT | ON_BCC_JCT | Willow Creek JCT | ON_WLC_JCT |  |  | 296
| B563A | HONI | Ontario | 1 | ac | 45 | 27.7778 | 500 | 17.775 | 3 | [5 empty] | 2550 | 3225 | Willow Creek JCT | ON_WLC_JCT | Ashfield SWS | ON_ASH_SWS |  |  | 297
| B569B | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 500 | 0.1975 | 3 | [5 empty] | 2550 | 3225 | Bruce A TS | ON_BCA_TSS | Bruce JCT | ON_BCC_JCT |  |  | 298
| B569B | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 500 | 0.1975 | 3 | [5 empty] | 2550 | 3225 | Bruce JCT | ON_BCC_JCT | Bruce B SWS | ON_BCB_SWS |  |  | 299
| B5QK | HONI | Ontario | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Barrett Chute SWS | ON_BTC_SWS | Sharbot JCT | ON_SHR_JCT |  |  | 317
| B5QK | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Harrowsmith JCT | ON_HRR_JCT | Railton JCT | ON_RLT_JCT |  |  | 318
| B5QK | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Harrowsmith JCT | ON_HRR_JCT | Harrowsmith DS | ON_HRR_DSS |  |  | 319
| B5QK | HONI | Ontario | 2 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Hinchinbrooke DS | ON_HNB_DSS | Harrowsmith JCT | ON_HRR_JCT |  |  | 320
| B5QK | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Railton JCT | ON_RLT_JCT | Cataraqui TS | ON_CTQ_TSS |  |  | 321
| B5QK | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Railton JCT | ON_RLT_JCT | Frontenac TS | ON_FRO_DSS |  |  | 322
| B5QK | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Sharbot JCT | ON_SHR_JCT | Sharbot DS | ON_SHR_DSS |  |  | 323
| B5QK | HONI | Ontario | 1 | ac | 32 | 19.7531 | 115 | 13.3486 | 3 | [5 empty] | 98.4491 | 108.4016 | Sharbot JCT | ON_SHR_JCT | Hinchinbrooke DS | ON_HNB_DSS |  |  | 324
| B5V | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Orangeville TS | ON_ORA_DSS | Amaranth JCT | ON_AMA_JCT |  |  | 325
| B5V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Amaranth JCT | ON_AMA_JCT | Amaranth TS | ON_AMA_ISS |  |  | 326
| B5V | HONI | Ontario | 1 | ac | 68 | 41.9753 | 230 | 32.64 | 3 | [5 empty] | 402 | 435 | Amaranth JCT | ON_AMA_JCT | Hanover TS | ON_HNV_DSS |  |  | 327
| B5V | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Hanover TS | ON_HNV_DSS | Underwood JCT | ON_UDW_JCT |  |  | 328
| B5V | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Underwood JCT | ON_UDW_JCT | Underwood GS | ON_UDW_GSS |  |  | 329
| B5V | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Underwood JCT | ON_UDW_JCT | Bruce A TS | ON_BCA_TSS |  |  | 330
| C18R | HONI | Ontario | 1 | ac | 24 | 14.8148 | 230 | 11.52 | 3 | [5 empty] | 402 | 435 | Cherrywood TS | ON_CHW_DSS | Fairchild TS | ON_FCD_DSS |  |  | 399
| C18R | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Fairchild TS | ON_FCD_DSS | Bathurst JCT | ON_BTH_JCT |  |  | 400
| C18R | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 230 | 0.72 | 3 | [5 empty] | 402 | 435 | Bathurst JCT | ON_BTH_JCT | Bathurst TS | ON_BTH_DSS |  |  | 401
| C18R | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Bathurst JCT | ON_BTH_JCT | Richview TS | ON_RCV_DSS |  |  | 402
| C1A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Alexander SWS | ON_ALX_SWS | Alexander GS | ON_ALX_GSS |  |  | 403
| C1A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cameron Falls GS | ON_CAM_GSS | Alexander SWS | ON_ALX_SWS |  |  | 404
| C25H | HONI | Ontario | 1 | ac | 175 | 108.0247 | 230 | 84 | 1.9331 | [5 empty] | 259.0372 | 280.3015 | Chats Falls SWS | ON_CHF_SWS | Havelock TS | ON_HVL_DSS |  |  | 444
| C27P | HONI | Ontario | 1 | ac | 75 | 46.2963 | 230 | 36 | 3 | [5 empty] | 402 | 435 | Bannockburn JCT | ON_BNK_JCT | Dobbin TS | ON_DOB_DSS |  |  | 445
| C27P | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Chats Falls SWS | ON_CHF_SWS | Galetta JCT | ON_GAL_JCT |  |  | 446
| C27P | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Galetta JCT | ON_GAL_JCT | Arnprior GS | ON_ARN_GSS |  |  | 447
| C27P | HONI | Ontario | 1 | ac | 135 | 83.3333 | 230 | 64.8 | 2.294 | [5 empty] | 307.3907 | 332.6242 | Galetta JCT | ON_GAL_JCT | Bannockburn JCT | ON_BNK_JCT |  |  | 448
| C2A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Alexander SWS | ON_ALX_SWS | Alexander GS | ON_ALX_GSS |  |  | 449
| C2A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cameron Falls GS | ON_CAM_GSS | Alexander SWS | ON_ALX_SWS |  |  | 450
| C31 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | SKWP CMS JCT | ON_SKW_JCT | SKWP CMS | ON_SKW_GSS |  |  | 463
| C31 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Chatham SWS | ON_CHT_SWS | SKWP CMS JCT | ON_SKW_JCT |  |  | 464
| C3A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Alexander SWS | ON_ALX_SWS | Alexander GS | ON_ALX_GSS |  |  | 475
| C3A | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cameron Falls GS | ON_CAM_GSS | Alexander SWS | ON_ALX_SWS |  |  | 476
| C3S | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Chats Falls SWS | ON_CHF_SWS | South March TS | ON_SOM_DSS |  |  | 482
| C3S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | South March TS | ON_SOM_DSS | Kanata MTS #1 | ON_KAN_DSS |  |  | 483
| D10H | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Palmerston TS | ON_PLM_DSS | Hanover TS | ON_HNV_DSS |  |  | 539
| D1M | HONI | Ontario | 1 | ac | 160 | 98.7654 | 230 | 76.8 | 2.0508 | [5 empty] | 274.8076 | 297.3664 | Des Joachims TS | ON_DEJ_TSS | Minden TS | ON_MND_DSS |  |  | 559
| D26A | HONI | Ontario | 1 | ac | 175 | 108.0247 | 230 | 84 | 1.9331 | [5 empty] | 259.0372 | 280.3015 | Dryden TS | ON_DRY_TSS | Mackenzie TS | ON_MKZ_TSS |  |  | 562
| D2H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pinard TS | ON_PIN_TSS | Pinard JCT #2 | ON_PI2_JCT |  |  | 563
| D2H | HONI | Ontario | 2 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pinard JCT #2 | ON_PI2_JCT | Hwy 634 JCT | ON_H63_JCT |  |  | 564
| D2H | HONI | Ontario | 2 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Hwy 634 JCT | ON_H63_JCT | Island Falls JCT | ON_ISF_JCT |  |  | 565
| D2H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Island Falls JCT | ON_ISF_JCT | Island Falls GS | ON_ISF_GSS |  |  | 566
| D2H | HONI | Ontario | 2 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Island Falls JCT | ON_ISF_JCT | Greenwater Pr Pk JCT | ON_GWP_JCT |  |  | 567
| D2H | HONI | Ontario | 2 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Greenwater Pr Pk JCT | ON_GWP_JCT | Calder JCT | ON_CLD_JCT |  |  | 568
| D2H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Calder JCT | ON_CLD_JCT | Calder TS | ON_CLD_ISS |  |  | 569
| D2H | HONI | Ontario | 2 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Calder JCT | ON_CLD_JCT | Hunta JCT | ON_HTA_JCT |  |  | 570
| D2H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hunta JCT | ON_HTA_JCT | Hunta SWS | ON_HTA_SWS |  |  | 571
| D2L | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Cassels JCT | ON_CSS_JCT | Temagami DS | ON_TMG_DSS |  |  | 577
| D2M | HONI | Ontario | 1 | ac | 95 | 58.642 | 230 | 45.6 | 2.8922 | [5 empty] | 387.5583 | 419.3728 | Des Joachims TS | ON_DEJ_TSS | Otter Creek JCT | ON_OTC_JCT |  |  | 583
| D2M | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Otter Creek JCT | ON_OTC_JCT | Wallace JCT | ON_WLL_JCT |  |  | 584
| D2M | HONI | Ontario | 1 | ac | 65 | 40.1235 | 230 | 31.2 | 3 | [5 empty] | 402 | 435 | Otter Creek JCT | ON_OTC_JCT | Minden TS | ON_MND_DSS |  |  | 585
| D2M | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Wallace JCT | ON_WLL_JCT | Wallace TS | ON_WLL_DSS |  |  | 586
| D3H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pinard TS | ON_PIN_TSS | Pinard JCT #2 | ON_PI2_JCT |  |  | 596
| D3H | HONI | Ontario | 2 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pinard JCT #2 | ON_PI2_JCT | Hwy 634 JCT | ON_H63_JCT |  |  | 597
| D3H | HONI | Ontario | 2 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Hwy 634 JCT | ON_H63_JCT | Island Falls JCT | ON_ISF_JCT |  |  | 598
| D3H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Island Falls JCT | ON_ISF_JCT | Island Falls GS | ON_ISF_GSS |  |  | 599
| D3H | HONI | Ontario | 2 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Island Falls JCT | ON_ISF_JCT | Greenwater Pr Pk JCT | ON_GWP_JCT |  |  | 600
| D3H | HONI | Ontario | 2 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Greenwater Pr Pk JCT | ON_GWP_JCT | Calder JCT | ON_CLD_JCT |  |  | 601
| D3H | HONI | Ontario | 2 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Calder JCT | ON_CLD_JCT | Hunta JCT | ON_HTA_JCT |  |  | 602
| D3H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hunta JCT | ON_HTA_JCT | Hunta SWS | ON_HTA_SWS |  |  | 603
| D3K | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Dane JCT | ON_DAN_JCT | Notre Development TS | ON_NOT_ISS |  |  | 604
| D3K | HONI | Ontario | 1 | ac | 60 | 37.037 | 115 | 25.0286 | 3 | [5 empty] | 98.4491 | 108.4016 | Dane JCT | ON_DAN_JCT | Nine Mile JCT | ON_NIN_JCT |  |  | 605
| D3K | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gull Lake South JCT | ON_GLS_JCT | Dane JCT | ON_DAN_JCT |  |  | 606
| D3K | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Kirkland Lake TS | ON_KLL_DSS | Gull Lake South JCT | ON_GLS_JCT |  |  | 607
| D3M | HONI | Ontario | 1 | ac | 160 | 98.7654 | 230 | 76.8 | 2.0508 | [5 empty] | 274.8076 | 297.3664 | Des Joachims TS | ON_DEJ_TSS | Minden TS | ON_MND_DSS |  |  | 609
| D4 | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pinard JCT #2 | ON_PI2_JCT | Abitibi Canyon GS | ON_ABC_GSS |  |  | 610
| D4 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pinard TS | ON_PIN_TSS | Pinard JCT #2 | ON_PI2_JCT |  |  | 611
| D4M | HONI | Ontario | 1 | ac | 95 | 58.642 | 230 | 45.6 | 2.8922 | [5 empty] | 387.5583 | 419.3728 | Des Joachims TS | ON_DEJ_TSS | Otter Creek JCT | ON_OTC_JCT |  |  | 612
| D4M | HONI | Ontario | 1 | ac | 65 | 40.1235 | 230 | 31.2 | 3 | [5 empty] | 402 | 435 | Otter Creek JCT | ON_OTC_JCT | Minden TS | ON_MND_DSS |  |  | 613
| D501P | HONI | Ontario | 1 | ac | 220 | 135.8025 | 500 | 86.9 | 1.6623 | [5 empty] | 1412.9675 | 1786.9883 | Pinard TS | ON_PIN_TSS | Porcupine TS | ON_PCP_TSS |  |  | 619
| D5D | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Dryden JCT B | ON_DRY_JCT | Domtar Dryden TS | ON_DTD_ISS |  |  | 628
| D5D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dryden TS | ON_DRY_TSS | Dryden JCT B | ON_DRY_JCT |  |  | 629
| D5H | HONI | Ontario | 1 | ac | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Des Joachims TS | ON_DEJ_TSS | Otto Holden TS | ON_OTH_DSS |  |  | 630
| D6T | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Abitibi Canyon JCT #2 | ON_AB2_JCT | P Sutherland Sr JCT | ON_PSS_JCT |  |  | 646
| D6T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Otter Rapids SWS | ON_ORP_SWS | Otter Rapids GS | ON_ORP_GSS |  |  | 647
| D6T | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | P Sutherland Sr JCT | ON_PSS_JCT | Otter Rapids SWS | ON_ORP_SWS |  |  | 648
| D6T | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | P Sutherland Sr JCT | ON_PSS_JCT | P Sutherland Sr SYD | ON_PSS_GSS |  |  | 649
| D6T | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pinard JCT #2 | ON_PI2_JCT | Abitibi Canyon JCT #2 | ON_AB2_JCT |  |  | 650
| D6T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pinard TS | ON_PIN_TSS | Pinard JCT #2 | ON_PI2_JCT |  |  | 651
| E1C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Crow River DS | ON_CRR_DSS | Placer JCT | ON_PLC_JCT |  |  | 697
| E1C | HONI | Ontario | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Ear Falls TS | ON_EAF_DSS | Selco JCT | ON_SLC_JCT |  |  | 698
| E1C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Etruscan JCT | ON_ETR_JCT | Etruscan Enterprise TS | ON_ETR_ISS |  |  | 699
| E1C | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Etruscan JCT | ON_ETR_JCT | Pickle Lake SWS | ON_PKL_SWS |  |  | 700
| E1C | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Golden Patricia JCT | ON_GLP_JCT | Etruscan JCT | ON_ETR_JCT |  |  | 702
| E1C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pickle Lake SWS | ON_PKL_SWS | Crow River DS | ON_CRR_DSS |  |  | 703
| E1C | HONI | Ontario | 1 | ac | 187.5 | 115.7407 | 115 | 78.2143 | 1.8471 | [5 empty] | 60.616 | 66.7439 | Placer JCT | ON_PLC_JCT | Musselwhite SWS | ON_MSW_SWS |  |  | 704
| E1C | HONI | Ontario | 1 | ac | 70 | 43.2099 | 115 | 29.2 | 3 | [5 empty] | 98.4491 | 108.4016 | Selco JCT | ON_SLC_JCT | Slate Falls JCT | ON_SLF_JCT |  |  | 705
| E1C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Slate Falls JCT | ON_SLF_JCT | Slate Falls DS | ON_SLF_DSS |  |  | 706
| E1C | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Slate Falls JCT | ON_SLF_JCT | Golden Patricia JCT | ON_GLP_JCT |  |  | 707
| E1W | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Essa TS | ON_ESA_TSS | Minesing JCT | ON_MNS_JCT |  |  | 708
| E20S | HONI | Ontario | 1 | ac | 24 | 14.8148 | 230 | 11.52 | 3 | [5 empty] | 402 | 435 | Essa TS | ON_ESA_TSS | Stayner TS | ON_STY_DSS |  |  | 709
| E21S | HONI | Ontario | 1 | ac | 24 | 14.8148 | 230 | 11.52 | 3 | [5 empty] | 402 | 435 | Essa TS | ON_ESA_TSS | Stayner TS | ON_STY_DSS |  |  | 710
| E26 | HONI | Ontario | 1 | ac | 45 | 27.7778 | 230 | 21.6 | 3 | [5 empty] | 402 | 435 | Essa TS | ON_ESA_TSS | Waubaushene JCT | ON_WBS_JCT |  |  | 711
| E26 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Parry Sound JCT | ON_PRS_JCT | Parry Sound TS | ON_PRS_DSS |  |  | 712
| E26 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Waubaushene JCT | ON_WBS_JCT | Waubaushene TS | ON_WBS_DSS |  |  | 713
| E26 | HONI | Ontario | 1 | ac | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Waubaushene JCT | ON_WBS_JCT | Parry Sound JCT | ON_PRS_JCT |  |  | 714
| E27 | HONI | Ontario | 1 | ac | 45 | 27.7778 | 230 | 21.6 | 3 | [5 empty] | 402 | 435 | Essa TS | ON_ESA_TSS | Waubaushene JCT | ON_WBS_JCT |  |  | 715
| E27 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Parry Sound JCT | ON_PRS_JCT | Parry Sound TS | ON_PRS_DSS |  |  | 716
| E27 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Waubaushene JCT | ON_WBS_JCT | Waubaushene TS | ON_WBS_DSS |  |  | 717
| E27 | HONI | Ontario | 1 | ac | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Waubaushene JCT | ON_WBS_JCT | Parry Sound JCT | ON_PRS_JCT |  |  | 718
| E2Q | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Elliot Lake TS | ON_ELL_DSS | Quirke Lake JCT | ON_QUL_JCT |  |  | 719
| E2Q | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Quirke Lake JCT | ON_QUL_JCT | Denison Mines TS | ON_DNM_ISS |  |  | 720
| E34M | HONI | Ontario | 1 | ac | 23 | 14.1975 | 230 | 11.04 | 3 | [5 empty] | 402 | 435 | Almonte TS | ON_ALM_DSS | Didsbury Road JCT | ON_DID_JCT |  |  | 724
| E34M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Didsbury Road JCT | ON_DID_JCT | Terry Fox JCT | ON_TRF_JCT |  |  | 725
| E34M | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Terry Fox JCT | ON_TRF_JCT | Terry Fox MTS | ON_TRF_DSS |  |  | 726
| E34M | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Terry Fox JCT | ON_TRF_JCT | Merivale TS | ON_MER_TSS |  |  | 727
| E3B | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Essa TS | ON_ESA_TSS | Barrie TS | ON_BAR_DSS |  |  | 728
| E4B | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Essa TS | ON_ESA_TSS | Barrie TS | ON_BAR_DSS |  |  | 729
| E510V | HONI | Ontario | 1 | ac | 65 | 40.1235 | 500 | 25.675 | 3 | [5 empty] | 2550 | 3225 | Essa TS | ON_ESA_TSS | Claireville TS | ON_CLV_TSS |  |  | 733
| E511V | HONI | Ontario | 1 | ac | 65 | 40.1235 | 500 | 25.675 | 3 | [5 empty] | 2550 | 3225 | Essa TS | ON_ESA_TSS | Claireville TS | ON_CLV_TSS |  |  | 734
| E564L | HONI | Ontario | 1 | ac | 36 | 22.2222 | 500 | 14.22 | 3 | [5 empty] | 2550 | 3225 | Evergreen SWS | ON_EVG_SWS | Longwood TS | ON_LGW_DSS |  |  | 735
| E578P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 500 | 0.0395 | 3 | [5 empty] | 2550 | 3225 | Evergreen SWS | ON_EVG_SWS | Parkhill TS | ON_PKH_ISS |  |  | 736
| E6L | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Seaforth TS | ON_SFT_DSS | Egmondville SWS | ON_EGM_SWS |  |  | 737
| E8F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Essex TS | ON_ESX_DSS | Chrysler WAP MTS | ON_CHY_ISS |  |  | 738
| E8F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Chrysler WAP MTS | ON_CHY_ISS | G.M. Windsor MTS | ON_GMW_ISS |  |  | 739
| E8F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | G.M. Windsor MTS | ON_GMW_ISS | Ford Annex MTS | ON_FDA_ISS |  |  | 740
| E8F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Ford Annex MTS | ON_FDA_ISS | Ford Windsor MTS | ON_FDW_ISS |  |  | 741
| E8F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Ford Windsor MTS | ON_FDW_ISS | East Windsor GS | ON_EWI_GSS |  |  | 742
| E8V | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Alliston JCT | ON_ALS_JCT | Alliston TS | ON_ALS_DSS |  |  | 743
| E8V | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Alliston JCT | ON_ALS_JCT | Everett JCT | ON_EVT_JCT |  |  | 744
| E8V | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Essa TS | ON_ESA_TSS | Alliston JCT | ON_ALS_JCT |  |  | 745
| E8V | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Everett JCT | ON_EVT_JCT | Everett TS | ON_EVT_DSS |  |  | 746
| E8V | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Everett JCT | ON_EVT_JCT | Orangeville TS | ON_ORA_DSS |  |  | 747
| E9F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Essex TS | ON_ESX_DSS | Chrysler WAP MTS | ON_CHY_ISS |  |  | 748
| E9F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Chrysler WAP MTS | ON_CHY_ISS | G.M. Windsor MTS | ON_GMW_ISS |  |  | 749
| E9F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | G.M. Windsor MTS | ON_GMW_ISS | Ford Annex MTS | ON_FDA_ISS |  |  | 750
| E9F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Ford Annex MTS | ON_FDA_ISS | Ford Windsor MTS | ON_FDW_ISS |  |  | 751
| E9F | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Ford Windsor MTS | ON_FDW_ISS | East Windsor GS | ON_EWI_GSS |  |  | 752
| E9V | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Alliston JCT | ON_ALS_JCT | Alliston TS | ON_ALS_DSS |  |  | 753
| E9V | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Alliston JCT | ON_ALS_JCT | Everett JCT | ON_EVT_JCT |  |  | 754
| E9V | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Essa TS | ON_ESA_TSS | Alliston JCT | ON_ALS_JCT |  |  | 755
| E9V | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Everett JCT | ON_EVT_JCT | Everett TS | ON_EVT_DSS |  |  | 756
| E9V | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Everett JCT | ON_EVT_JCT | Orangeville TS | ON_ORA_DSS |  |  | 757
| F10MV | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | City View JCT | ON_CTV_JCT | Val Tetreau JCT | ON_VLT_JCT |  |  | 759
| F10MV | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Val Tetreau JCT | ON_VLT_JCT | Hinchey TS | ON_HIN_DSS |  |  | 760
| F1B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Burleigh JCT | ON_BUL_JCT | Burleigh DS | ON_BUL_DSS |  |  | 775
| F1B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Burleigh JCT | ON_BUL_JCT | Hwy #11 JCT | ON_H11_JCT |  |  | 776
| F1B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Burleigh JCT | ON_BUL_JCT | Fort Frances JCT | ON_FRF_JCT |  |  | 777
| F1B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Fort Frances TS | ON_FRF_TSS | Fort Frances MTS | ON_FRM_DSS |  |  | 778
| F1B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Fort Frances JCT | ON_FRF_JCT | Fort Frances TS | ON_FRF_TSS |  |  | 779
| F1E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | AP Calstock GS JCT | ON_APC_JCT | AP Calstock GS | ON_APC_GSS |  |  | 780
| F1E | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | AP Calstock GS JCT | ON_APC_JCT | Nagagami GS JCT | ON_NAG_JCT |  |  | 781
| F1E | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Kapuskasing TS | ON_KAP_DSS | AP Calstock GS JCT | ON_APC_JCT |  |  | 782
| F1E | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Kapuskasing TS | ON_KAP_DSS | Spruce Falls TS | ON_SPF_TSS |  |  | 783
| F1E | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Nagagami GS JCT | ON_NAG_JCT | Hearst TS | ON_HST_DSS |  |  | 784
| F1E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Nagagami GS JCT | ON_NAG_JCT | Nagagami GS | ON_NAG_DSS |  |  | 785
| F25A | HONI | Ontario | 1 | ac | 140 | 86.4198 | 230 | 67.2 | 2.2396 | [5 empty] | 300.1058 | 324.7413 | Fort Frances TS | ON_FRF_TSS | Mackenzie TS | ON_MKZ_TSS |  |  | 786
| F2B | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Fort Frances TS | ON_FRF_TSS | H2O Power Fort Frances GS | ON_H2F_GSS |  |  | 787
| F3M | HONI | Ontario | 1 | ac | 0.9 | 0.55556 | 115 | 0.37543 | 3 | [5 empty] | 98.4491 | 108.4016 | Fort Frances TS | ON_FRF_TSS | H2O Power Fort Frances GS | ON_H2F_GSS |  |  | 788
| FA16G3K | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Matachewan JCT | ON_MWN_JCT | Indian Chute JCT | ON_INC_JCT |  |  | 790
| FS23M1 | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Elliot Lake TS | ON_ELL_DSS | Quirke Lake JCT | ON_QUL_JCT |  |  | 791
| FS9M6 | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Martindale TS | ON_MTD_DSS | Dominion Drive DS | ON_DMD_DSS |  |  | 792
| H12P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hearn SWS | ON_HEA_SWS | Portlands Energy JCT | ON_PTE_JCT |  |  | 808
| H13P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hearn SWS | ON_HEA_SWS | Portlands Energy JCT | ON_PTE_JCT |  |  | 809
| H14P | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hearn SWS | ON_HEA_SWS | Portlands Energy JCT | ON_PTE_JCT |  |  | 810
| H22D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Harmon JCT | ON_HRJ_JCT | Harmon GS | ON_HRJ_GSS |  |  | 817
| H22D | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Harmon JCT | ON_HRJ_JCT | Kipling JCT | ON_KPG_JCT |  |  | 818
| H22D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Kipling JCT | ON_KPG_JCT | Kipling GS | ON_KPG_GSS |  |  | 819
| H22D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Little Long JCT | ON_LLG_JCT | Little Long 2 JCT | ON_LLG2_JCT |  |  | 820
| H22D | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Little Long JCT | ON_LLG_JCT | Smoky Falls JCT | ON_SKF_JCT |  |  | 821
| H22D | HONI | Ontario | 1 | ac | 50 | 30.8642 | 230 | 24 | 3 | [5 empty] | 402 | 435 | Pinard TS | ON_PIN_TSS | Little Long JCT | ON_LLG_JCT |  |  | 822
| H22D | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Smoky Falls JCT | ON_SKF_JCT | Harmon JCT | ON_HRJ_JCT |  |  | 823
| H22D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Smoky Falls JCT | ON_SKF_JCT | Smoky Falls GS | ON_SKF_GSS |  |  | 824
| H23B | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Belleville TS | ON_BLV_DSS | Pancake JCT | ON_PNC_JCT |  |  | 825
| H23B | HONI | Ontario | 1 | ac | 65 | 40.1235 | 230 | 31.2 | 3 | [5 empty] | 402 | 435 | Hinchinbrooke SWS | ON_HNB_SWS | Pancake JCT | ON_PNC_JCT |  |  | 826
| H23S | HONI | Ontario | 1 | ac | 45 | 27.7778 | 230 | 21.6 | 3 | [5 empty] | 402 | 435 | Otto Holden TS | ON_OTH_DSS | Widdifield SWS | ON_WFD_SWS |  |  | 827
| H23S | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Pedley JCT | ON_PED_JCT | Crystal Falls TS | ON_CRY_DSS |  |  | 828
| H23S | HONI | Ontario | 1 | ac | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Pedley JCT | ON_PED_JCT | Martindale TS | ON_MTD_DSS |  |  | 829
| H23S | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Widdifield SWS | ON_WFD_SWS | Pedley JCT | ON_PED_JCT |  |  | 830
| H24C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Atlantic Packaging JCT | ON_ATP_JCT | Atlantic Packaging TS | ON_ATP_ISS |  |  | 831
| H24C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Atlantic Packaging JCT | ON_ATP_JCT | Gerdau A. Whitby TS | ON_GAW_ISS |  |  | 832
| H24C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Columbus JCT | ON_CLB_JCT | Lasco JCT | ON_LAS_JCT |  |  | 833
| H24C | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Columbus JCT | ON_CLB_JCT | Whitby JCT | ON_WHB_JCT |  |  | 834
| H24C | HONI | Ontario | 1 | ac | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Havelock TS | ON_HVL_DSS | Marine JCT | ON_MAR_JCT |  |  | 835
| H24C | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Lasco JCT | ON_LAS_JCT | Thornton JCT | ON_THO_JCT |  |  | 836
| H24C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Lasco JCT | ON_LAS_JCT | Atlantic Packaging JCT | ON_ATP_JCT |  |  | 837
| H24C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Marine JCT | ON_MAR_JCT | Otonabee TS | ON_OTB_DSS |  |  | 838
| H24C | HONI | Ontario | 1 | ac | 85 | 52.4691 | 230 | 40.8 | 3 | [5 empty] | 402 | 435 | Marine JCT | ON_MAR_JCT | Oshawa Area JCT | ON_OSH_JCT |  |  | 839
| H24C | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Oshawa Area JCT | ON_OSH_JCT | Columbus JCT | ON_CLB_JCT |  |  | 840
| H24C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Oshawa G.M. JCT | ON_OGM_JCT | Oshawa G.M. TS | ON_OGM_ISS |  |  | 841
| H24C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Thornton JCT | ON_THO_JCT | Thornton TS | ON_THO_DSS |  |  | 842
| H24C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Thornton JCT | ON_THO_JCT | Oshawa G.M. JCT | ON_OGM_JCT |  |  | 843
| H24C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Whitby JCT | ON_WHB_JCT | Whitby TS | ON_WHB_DSS |  |  | 844
| H24C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Whitby JCT | ON_WHB_JCT | Cherrywood TS | ON_CHW_DSS |  |  | 845
| H24S | HONI | Ontario | 1 | ac | 45 | 27.7778 | 230 | 21.6 | 3 | [5 empty] | 402 | 435 | Otto Holden TS | ON_OTH_DSS | Widdifield SWS | ON_WFD_SWS |  |  | 849
| H24S | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Widdifield SWS | ON_WFD_SWS | Trout Lake TS | ON_TRL_DSS |  |  | 850
| H24S | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Widdifield SWS | ON_WFD_SWS | AP North Bay JCT | ON_APB_JCT |  |  | 851
| H26C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Atlantic Packaging JCT | ON_ATP_JCT | Atlantic Packaging TS | ON_ATP_ISS |  |  | 852
| H26C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Atlantic Packaging JCT | ON_ATP_JCT | Whitby GS JCT | ON_WHI_JCT |  |  | 853
| H26C | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | B23C H26C Tie JCT | ON_B23_JCT | Cherrywood TS | ON_CHW_DSS |  |  | 854
| H26C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Columbus JCT | ON_CLB_JCT | Lasco JCT | ON_LAS_JCT |  |  | 855
| H26C | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Columbus JCT | ON_CLB_JCT | Whitby JCT | ON_WHB_JCT |  |  | 856
| H26C | HONI | Ontario | 1 | ac | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Havelock TS | ON_HVL_DSS | Marine JCT | ON_MAR_JCT |  |  | 857
| H26C | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Lasco JCT | ON_LAS_JCT | Thornton JCT | ON_THO_JCT |  |  | 858
| H26C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Lasco JCT | ON_LAS_JCT | Atlantic Packaging JCT | ON_ATP_JCT |  |  | 859
| H26C | HONI | Ontario | 1 | ac | 85 | 52.4691 | 230 | 40.8 | 3 | [5 empty] | 402 | 435 | Marine JCT | ON_MAR_JCT | Oshawa Area JCT | ON_OSH_JCT |  |  | 860
| H26C | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Oshawa Area JCT | ON_OSH_JCT | Columbus JCT | ON_CLB_JCT |  |  | 861
| H26C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Oshawa G.M. JCT | ON_OGM_JCT | Oshawa G.M. TS | ON_OGM_ISS |  |  | 862
| H26C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Thornton JCT | ON_THO_JCT | Thornton TS | ON_THO_DSS |  |  | 863
| H26C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Thornton JCT | ON_THO_JCT | Oshawa G.M. JCT | ON_OGM_JCT |  |  | 864
| H26C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Whitby GS JCT | ON_WHI_JCT | Gerdau A. Whitby TS | ON_GAW_ISS |  |  | 865
| H26C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Whitby GS JCT | ON_WHI_JCT | Whitby GS | ON_WHI_GSS |  |  | 866
| H26C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Whitby JCT | ON_WHB_JCT | Whitby TS | ON_WHB_DSS |  |  | 867
| H26C | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Whitby JCT | ON_WHB_JCT | B23C H26C Tie JCT | ON_B23_JCT |  |  | 868
| H27H | HONI | Ontario | 1 | ac | 73 | 45.0617 | 230 | 35.04 | 3 | [5 empty] | 402 | 435 | Bannockburn JCT | ON_BNK_JCT | Hinchinbrooke SWS | ON_HNB_SWS |  |  | 869
| H27H | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Havelock TS | ON_HVL_DSS | Bannockburn JCT | ON_BNK_JCT |  |  | 870
| H2N | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Hearst TS | ON_HST_DSS | Calstock DS | ON_CSK_DSS |  |  | 879
| H6T | HONI | Ontario | 1 | ac | 60 | 37.037 | 115 | 25.0286 | 3 | [5 empty] | 98.4491 | 108.4016 | Hunta SWS | ON_HTA_SWS | Tisdale JCT | ON_TSD_JCT |  |  | 897
| H6T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Laforest Road JCT | ON_LFR_JCT | Laforest Road DS | ON_LFR_DSS |  |  | 898
| H6T | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Laforest Road JCT | ON_LFR_JCT | Timmins TS | ON_TMM_DSS |  |  | 899
| H6T | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Tisdale JCT | ON_TSD_JCT | Laforest Road JCT | ON_LFR_JCT |  |  | 900
| H7T | HONI | Ontario | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Hunta SWS | ON_HTA_SWS | Warkus JCT | ON_WKS_JCT |  |  | 907
| H7T | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Warkus JCT | ON_WKS_JCT | Kidd Minesite TS | ON_KMN_ISS |  |  | 908
| H7T | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Warkus JCT | ON_WKS_JCT | Timmins TS | ON_TMM_DSS |  |  | 909
| H82V | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Woodbridge JCT | ON_WDB_JCT |  |  | 910
| H82V | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Holland JCT | ON_HLD_JCT | Holland TS | ON_HLD_DSS |  |  | 911
| H82V | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Vaughan #4 JCT | ON_VJ4_JCT | Vaughan MTS #4 | ON_VM4_DSS |  |  | 912
| H82V | HONI | Ontario | 1 | ac | 22 | 13.5802 | 230 | 10.56 | 3 | [5 empty] | 402 | 435 | Vaughan #4 JCT | ON_VJ4_JCT | Holland JCT | ON_HLD_JCT |  |  | 913
| H82V | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Woodbridge JCT | ON_WDB_JCT | Vaughan #4 JCT | ON_VJ4_JCT |  |  | 914
| H83V | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Woodbridge JCT | ON_WDB_JCT |  |  | 915
| H83V | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Holland JCT | ON_HLD_JCT | Holland TS | ON_HLD_DSS |  |  | 916
| H83V | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Vaughan #4 JCT | ON_VJ4_JCT | Vaughan MTS #4 | ON_VM4_DSS |  |  | 917
| H83V | HONI | Ontario | 1 | ac | 22 | 13.5802 | 230 | 10.56 | 3 | [5 empty] | 402 | 435 | Vaughan #4 JCT | ON_VJ4_JCT | Holland JCT | ON_HLD_JCT |  |  | 918
| H83V | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Woodbridge JCT | ON_WDB_JCT | Vaughan #4 JCT | ON_VJ4_JCT |  |  | 919
| H9K | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Carmichael Falls JCT | ON_CMF_JCT | Spruce Falls JCT | ON_SPF_JCT |  |  | 945
| H9K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Fauquier JCT | ON_FAU_JCT | Fauquier DS | ON_FAU_DSS |  |  | 946
| H9K | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Fauquier JCT | ON_FAU_JCT | Carmichael Falls JCT | ON_CMF_JCT |  |  | 947
| H9K | HONI | Ontario | 2 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | H9K STR 127A JCT | ON_H9K_JCT | Smooth Rock Falls JCT | ON_SRF_JCT |  |  | 948
| H9K | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hunta H9K JCT | ON_HHK_JCT | H9K STR 127A JCT | ON_H9K_JCT |  |  | 949
| H9K | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hunta SWS | ON_HTA_SWS | Hunta H9K JCT | ON_HHK_JCT |  |  | 950
| H9K | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kapuskasing TS | ON_KAP_DSS | Tembec Kapuskasking TS | ON_TMB_GSS |  |  | 951
| H9K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Smooth Rock Falls JCT | ON_SRF_JCT | Smooth Rock Falls DS | ON_SRF_DSS |  |  | 952
| H9K | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Smooth Rock Falls JCT | ON_SRF_JCT | Fauquier JCT | ON_FAU_JCT |  |  | 953
| H9K | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Spruce Falls JCT | ON_SPF_JCT | Kapuskasing TS | ON_KAP_DSS |  |  | 954
| K1 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Kirkland Lake TS | ON_KLL_DSS | Gull Lake North JCT | ON_GLN_JCT |  |  | 991
| K2 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Gull Lake North JCT | ON_GLN_JCT | Gull Lake South JCT | ON_GLS_JCT |  |  | 1009
| K2 | HONI | Ontario | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Gull Lake South JCT | ON_GLS_JCT | Holloway Holt JCT | ON_HLH_JCT |  |  | 1010
| K2 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Kirkland Lake TS | ON_KLL_DSS | Gull Lake North JCT | ON_GLN_JCT |  |  | 1011
| K24F | HONI | Ontario | 1 | ac | 120 | 74.0741 | 230 | 57.6 | 2.4793 | [5 empty] | 332.22 | 359.4918 | Kenora TS | ON_KNO_TSS | Rainy River Gold JCT | ON_RRG_JCT |  |  | 1021
| K24F | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Rainy River Gold JCT | ON_RRG_JCT | Fort Frances TS | ON_FRF_TSS |  |  | 1022
| K24F | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Rainy River Gold JCT | ON_RRG_JCT | Rainy River Gold SWS | ON_RRG_SWS |  |  | 1023
| K25BUS | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Sandusk SWS | ON_SND_SWS | Sandusk GS | ON_SND_GSS |  |  | 1029
| K2M | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Rabbit Lake SWS | ON_RBL_SWS | Norman JCT | ON_NOM_JCT |  |  | 1031
| K3 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kapuskasing TS | ON_KAP_DSS | Kapuskasing R JCT | ON_KAP_JCT |  |  | 1047
| K38S | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Kapuskasing TS | ON_KAP_DSS | Spruce Falls JCT | ON_SPF_JCT |  |  | 1048
| K38S | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | O'Brien JCT | ON_OBR_JCT | Tembec Kapuskasking TS | ON_TMB_GSS |  |  | 1049
| K38S | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Spruce Falls JCT | ON_SPF_JCT | O'Brien JCT | ON_OBR_JCT |  |  | 1050
| K3D | HONI | Ontario | 1 | ac | 75 | 46.2963 | 115 | 31.2857 | 3 | [5 empty] | 98.4491 | 108.4016 | Dryden TS | ON_DRY_TSS | Sam Lake DS | ON_SML_DSS |  |  | 1051
| K3D | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Eton JCT | ON_ETO_JCT | Dryden TS | ON_DRY_TSS |  |  | 1052
| K3D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Eton JCT | ON_ETO_JCT | Eton DS | ON_ETO_DSS |  |  | 1053
| K3D | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | K3D-10 SW JCT | ON_K3D_JCT | Vermilion Bay JCT | ON_VEB_JCT |  |  | 1054
| K3D | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Rabbit Lake SWS | ON_RBL_SWS | K3D-10 SW JCT | ON_K3D_JCT |  |  | 1055
| K3D | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Vermilion Bay JCT | ON_VEB_JCT | Eton JCT | ON_ETO_JCT |  |  | 1056
| K3D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vermilion Bay JCT | ON_VEB_JCT | Vermilion Bay DS | ON_VEB_DSS |  |  | 1057
| K4 | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | 93K4-89 JCT | ON_93K_JCT | Matachewan JCT | ON_MWN_JCT |  |  | 1061
| K4 | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Extender Min. JCT | ON_EXT_JCT | Elk Lake JCT | ON_ELK_JCT |  |  | 1062
| K4 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Kirkland Lake TS | ON_KLL_DSS | Macassa Mill JCT | ON_MAM_JCT |  |  | 1063
| K4 | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Macassa #3 JCT | ON_MAC_JCT | 93K4-89 JCT | ON_93K_JCT |  |  | 1064
| K4 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Macassa Mill JCT | ON_MAM_JCT | Macassa #3 JCT | ON_MAC_JCT |  |  | 1065
| K4 | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Matachewan JCT | ON_MWN_JCT | Extender Min. JCT | ON_EXT_JCT |  |  | 1066
| K4 | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Matachewan JCT | ON_MWN_JCT | Young-Davidson TS | ON_YOD_ISS |  |  | 1067
| K40M | HONI | Ontario | 1 | ac | 12.2 | 7.5309 | 230 | 5.856 | 3 | [5 empty] | 402 | 435 | Middleport TS | ON_MPT_TSS | Caledonia JCT | ON_CAL_JCT |  |  | 1068
| K40M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Caledonia JCT | ON_CAL_JCT | Caledonia TS | ON_CAL_DSS |  |  | 1069
| K40M | HONI | Ontario | 1 | ac | 26 | 16.0494 | 230 | 12.48 | 3 | [5 empty] | 402 | 435 | Caledonia JCT | ON_CAL_JCT | Sandusk JCT | ON_SND_JCT |  |  | 1070
| K40M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Sandusk JCT | ON_SND_JCT | Sandusk SWS | ON_SND_SWS |  |  | 1071
| K4W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Minaki JCT | ON_MIN_JCT | Minaki DS | ON_MIN_DSS |  |  | 1072
| K4W | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Minaki JCT | ON_MIN_JCT | Whitedog Falls SWS | ON_WDF_SWS |  |  | 1073
| K4W | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Rabbit Lake SWS | ON_RBL_SWS | Minaki JCT | ON_MIN_JCT |  |  | 1074
| K5W | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Minaki JCT | ON_MIN_JCT | Whitedog Falls SWS | ON_WDF_SWS |  |  | 1075
| K5W | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Rabbit Lake SWS | ON_RBL_SWS | Minaki JCT | ON_MIN_JCT |  |  | 1076
| K7B | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Vansco JCT | ON_VNO_JCT | Manby TS | ON_MBY_DSS |  |  | 1101
| K7K | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Kenora TS | ON_KNO_TSS | Rabbit Lake SWS | ON_RBL_SWS |  |  | 1102
| K7K | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kenora TS | ON_KNO_TSS | Weyerhaeuser Kenora TS | ON_WYK_ISS |  |  | 1103
| K8B | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Vansco JCT | ON_VNO_JCT | Manby TS | ON_MBY_DSS |  |  | 1104
| K9S | HONI | Ontario | 1 | ac | 6.5 | 4.0123 | 115 | 2.7114 | 3 | [5 empty] | 98.4491 | 108.4016 | Richview JCT | ON_RCV_JCT | Manby TS | ON_MBY_DSS |  |  | 1105
| L1MB | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | Brockville TS | ON_BRO_DSS | Brockville Chem. JCT | ON_BRC_JCT |  |  | 1132
| L1MB | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Brockville Chem. JCT | ON_BRC_JCT | Dyno Nobel TS | ON_DYN_ISS |  |  | 1133
| L1MB | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Brockville Chem. JCT | ON_BRC_JCT | Cardinal JCT | ON_CDL_JCT |  |  | 1134
| L1MB | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cardinal JCT | ON_CDL_JCT | Enbridge PL Card TS | ON_ENC_ISS |  |  | 1135
| L1MB | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cardinal JCT | ON_CDL_JCT | Casco JCT | ON_CSC_JCT |  |  | 1136
| L1MB | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Casco JCT | ON_CSC_JCT | Cardinal Power GS | ON_CDP_GSS |  |  | 1137
| L1MB | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Casco JCT | ON_CSC_JCT | Morrisburg JCT | ON_MRB_JCT |  |  | 1138
| L1MB | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Morrisburg JCT | ON_MRB_JCT | Morrisburg TS | ON_MRB_DSS |  |  | 1139
| L1MB | HONI | Ontario | 1 | ac | 26 | 16.0494 | 115 | 10.8457 | 3 | [5 empty] | 98.4491 | 108.4016 | Morrisburg JCT | ON_MRB_JCT | Lunenburg JCT | ON_LUN_JCT |  |  | 1140
| L1MB | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | Lunenburg JCT | ON_LUN_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1141
| L1S | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Coniston TS | ON_CTN_DSS | Sudbury JCT | ON_SUD_JCT |  |  | 1142
| L1S | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Crystal Falls SWS | ON_CRY_SWS | Verner JCT | ON_VER_JCT |  |  | 1143
| L1S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Milman Foundry JCT | ON_MLF_JCT | Milman Foundry TS | ON_MLF_ISS |  |  | 1144
| L1S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Milman Foundry JCT | ON_MLF_JCT | Milman Foundry TS | ON_MLF_ISS |  |  | 1145
| L1S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Sudbury JCT | ON_SUD_JCT | Milman Foundry JCT | ON_MLF_JCT |  |  | 1146
| L1S | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Sudbury JCT | ON_SUD_JCT | Martindale TS | ON_MTD_DSS |  |  | 1147
| L1S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Verner JCT | ON_VER_JCT | Verner Pole 45 JCT | ON_VPL_JCT |  |  | 1148
| L1S | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Verner JCT | ON_VER_JCT | Warren DS | ON_WRR_DSS |  |  | 1149
| L1S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Verner Pole 45 JCT | ON_VPL_JCT | Verner DS | ON_VER_DSS |  |  | 1150
| L1S | HONI | Ontario | 1 | ac | 45 | 27.7778 | 115 | 18.7714 | 3 | [5 empty] | 98.4491 | 108.4016 | Warren DS | ON_WRR_DSS | Coniston TS | ON_CTN_DSS |  |  | 1151
| L20D | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Harmon JCT | ON_HRJ_JCT | Kipling JCT | ON_KPG_JCT |  |  | 1152
| L20D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Kipling JCT | ON_KPG_JCT | Kipling 2 GS | ON_KPG2_GSS |  |  | 1153
| L20D | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Little Long JCT | ON_LLG_JCT | Smoky Falls JCT | ON_SKF_JCT |  |  | 1154
| L20D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Little Long JCT | ON_LLG_JCT | Little Long SWS | ON_LLG_SWS |  |  | 1155
| L20D | HONI | Ontario | 2 | ac | 50 | 30.8642 | 230 | 24 | 3 | [5 empty] | 402 | 435 | Pinard TS | ON_PIN_TSS | Little Long JCT | ON_LLG_JCT |  |  | 1156
| L20D | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Smoky Falls JCT | ON_SKF_JCT | Harmon JCT | ON_HRJ_JCT |  |  | 1157
| L20D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Smoky Falls JCT | ON_SKF_JCT | Smoky Falls GS | ON_SKF_GSS |  |  | 1158
| L20H | HONI | Ontario | 1 | ac | 38 | 23.4568 | 230 | 18.24 | 3 | [5 empty] | 402 | 435 | Hinchinbrooke SWS | ON_HNB_SWS | Crosby JCT | ON_CRO_JCT |  |  | 1159
| L20H | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Crosby JCT | ON_CRO_JCT | Crosby TS | ON_CRO_DSS |  |  | 1160
| L20H | HONI | Ontario | 2 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Crosby JCT | ON_CRO_JCT | Easton JCT | ON_EAS_JCT |  |  | 1161
| L20H | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Easton JCT | ON_EAS_JCT | Brockville TS | ON_BRO_DSS |  |  | 1162
| L20H | HONI | Ontario | 1 | ac | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Easton JCT | ON_EAS_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1163
| L21H | HONI | Ontario | 1 | ac | 38 | 23.4568 | 230 | 18.24 | 3 | [5 empty] | 402 | 435 | Hinchinbrooke SWS | ON_HNB_SWS | Crosby JCT | ON_CRO_JCT |  |  | 1164
| L21H | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Crosby JCT | ON_CRO_JCT | Crosby TS | ON_CRO_DSS |  |  | 1165
| L21H | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Crosby JCT | ON_CRO_JCT | Easton Yule JCT | ON_EAY_JCT |  |  | 1166
| L21H | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Easton Yule JCT | ON_EAY_JCT | Smiths Falls TS | ON_SMF_DSS |  |  | 1167
| L21H | HONI | Ontario | 1 | ac | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Easton Yule JCT | ON_EAY_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1168
| L21S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | AP Kapuskasing JCT | ON_APK_JCT | Kapuskasing TS | ON_KAP_DSS |  |  | 1172
| L21S | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Knob JCT | ON_KNB_JCT | AP Kapuskasing JCT | ON_APK_JCT |  |  | 1173
| L21S | HONI | Ontario | 1 | ac | 50 | 30.8642 | 230 | 24 | 3 | [5 empty] | 402 | 435 | Little Long SWS | ON_LLG_SWS | Knob JCT | ON_KNB_JCT |  |  | 1174
| L22H | HONI | Ontario | 1 | ac | 73 | 45.0617 | 230 | 35.04 | 3 | [5 empty] | 402 | 435 | Hinchinbrooke SWS | ON_HNB_SWS | Easton JCT | ON_EAS_JCT |  |  | 1175
| L22H | HONI | Ontario | 1 | ac | 0.3 | 0.18519 | 230 | 0.144 | 3 | [5 empty] | 402 | 435 | Easton JCT | ON_EAS_JCT | Easton Yule JCT | ON_EAY_JCT |  |  | 1176
| L22H | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Easton JCT | ON_EAS_JCT | Brockville TS | ON_BRO_DSS |  |  | 1177
| L22H | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Easton Yule JCT | ON_EAY_JCT | Smiths Falls TS | ON_SMF_DSS |  |  | 1178
| L22H | HONI | Ontario | 1 | ac | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Easton Yule JCT | ON_EAY_JCT | Raisin River JCT | ON_RSR_JCT |  |  | 1179
| L22H | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Raisin River JCT | ON_RSR_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1180
| L24L | HONI | Ontario | 1 | ac | 80 | 49.3827 | 230 | 38.4 | 3 | [5 empty] | 402 | 435 | Lambton TS #2 | ON_LMB_DSS | Longwood TS | ON_LGW_DSS |  |  | 1197
| L26L | HONI | Ontario | 1 | ac | 80 | 49.3827 | 230 | 38.4 | 3 | [5 empty] | 402 | 435 | Lambton TS #2 | ON_LMB_DSS | Longwood TS | ON_LGW_DSS |  |  | 1201
| L28C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Lambton TS #2 | ON_LMB_DSS | GSPC JCT | ON_GSP_JCT |  |  | 1206
| L28C | HONI | Ontario | 1 | ac | 54 | 33.3333 | 230 | 25.92 | 3 | [5 empty] | 402 | 435 | GSPC JCT | ON_GSP_JCT | Lynwood JCT | ON_LYN_JCT |  |  | 1207
| L29C | HONI | Ontario | 1 | ac | 33 | 20.3704 | 230 | 15.84 | 3 | [5 empty] | 402 | 435 | Lambton TS #2 | ON_LMB_DSS | East Lake St. Clair JCT | ON_ESC_JCT |  |  | 1210
| L29C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | East Lake St. Clair JCT | ON_ESC_JCT | East Lake St. Clair GS | ON_ESC_GSS |  |  | 1211
| L29C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | East Lake St. Clair JCT | ON_ESC_JCT | North Kent 1 JCT | ON_NOK_JCT |  |  | 1212
| L29C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | North Kent 1 JCT | ON_NOK_JCT | North Kent 1 GS | ON_NOK_GSS |  |  | 1213
| L29C | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | North Kent 1 JCT | ON_NOK_JCT | Lynwood JCT | ON_LYN_JCT |  |  | 1214
| L2M | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | Brockville TS | ON_BRO_DSS | Brockville Chem. JCT | ON_BRC_JCT |  |  | 1217
| L2M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Brockville Chem. JCT | ON_BRC_JCT | Dyno Nobel TS | ON_DYN_ISS |  |  | 1218
| L2M | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Brockville Chem. JCT | ON_BRC_JCT | Casco JCT | ON_CSC_JCT |  |  | 1219
| L2M | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Casco JCT | ON_CSC_JCT | Cardinal Power GS | ON_CDP_GSS |  |  | 1220
| L2M | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Casco JCT | ON_CSC_JCT | Morrisburg JCT | ON_MRB_JCT |  |  | 1221
| L2M | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Morrisburg JCT | ON_MRB_JCT | Morrisburg TS | ON_MRB_DSS |  |  | 1222
| L2M | HONI | Ontario | 1 | ac | 26 | 16.0494 | 115 | 10.8457 | 3 | [5 empty] | 98.4491 | 108.4016 | Morrisburg JCT | ON_MRB_JCT | Lunenburg JCT | ON_LUN_JCT |  |  | 1223
| L2M | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Lunenburg JCT | ON_LUN_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1224
| L2M | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Lunenburg JCT | ON_LUN_JCT | Newington JCT | ON_NWG_JCT |  |  | 1225
| L2M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Newington JCT | ON_NWG_JCT | Newington DS | ON_NWG_DSS |  |  | 1226
| L2M | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Newington JCT | ON_NWG_JCT | Chesterville S. JCT | ON_CLS_JCT |  |  | 1227
| L2M | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Chesterville S. JCT | ON_CLS_JCT | Chesterville TS | ON_CHS_DSS |  |  | 1228
| L2M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Chesterville N. JCT | ON_CLN_JCT | Chesterville S. JCT | ON_CLS_JCT |  |  | 1229
| L2M | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Chesterville N. JCT | ON_CLN_JCT | Chesterville TS | ON_CHS_DSS |  |  | 1230
| L2M | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Chesterville N. JCT | ON_CLN_JCT | Marionville JCT | ON_MRN_JCT |  |  | 1231
| L2M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Marionville JCT | ON_MRN_JCT | Marionville DS | ON_MRN_DSS |  |  | 1232
| L2M | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Marionville JCT | ON_MRN_JCT | Osgoode JCT | ON_OSG_JCT |  |  | 1233
| L37G | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Lambton TS #2 | ON_LMB_DSS | Greenfield Interface JCT | ON_GRF_JCT |  |  | 1241
| L37G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Greenfield Interface JCT | ON_GRF_JCT | Greenfield Energy GS | ON_GRF_GSS |  |  | 1242
| L38G | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Lambton TS #2 | ON_LMB_DSS | Greenfield Interface JCT | ON_GRF_JCT |  |  | 1243
| L38G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Greenfield Interface JCT | ON_GRF_JCT | Greenfield Energy GS | ON_GRF_GSS |  |  | 1244
| L3P | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Lakehead TS | ON_LKH_TSS | Port Arthur TS #1 | ON_PTA_DSS |  |  | 1245
| L4P | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Lakehead TS | ON_LKH_TSS | Port Arthur TS #1 | ON_PTA_DSS |  |  | 1248
| L5H | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Commanda JCT | ON_CMM_JCT | North Bay TS | ON_NBY_DSS |  |  | 1252
| L5H | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Crystal Falls SWS | ON_CRY_SWS | Commanda JCT | ON_CMM_JCT |  |  | 1253
| L5H | HONI | Ontario | 1 | ac | 70 | 43.2099 | 115 | 29.2 | 3 | [5 empty] | 98.4491 | 108.4016 | North Bay TS | ON_NBY_DSS | Otto Holden TS | ON_OTH_DSS |  |  | 1254
| L7S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Seaforth TS | ON_SFT_DSS | Seaforth L7S JCT | ON_SFL_JCT |  |  | 1256
| L7S | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | Seaforth L7S JCT | ON_SFL_JCT | Goshen JCT | ON_GSH_JCT |  |  | 1257
| L7S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Goshen JCT | ON_GSH_JCT | Goshen GS | ON_GSH_GSS |  |  | 1258
| L7S | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | Goshen JCT | ON_GSH_JCT | Kirkton JCT | ON_KRK_JCT |  |  | 1259
| L7S | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Kirkton JCT | ON_KRK_JCT | Biddulph JCT | ON_BID_JCT |  |  | 1260
| L7S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Biddulph JCT | ON_BID_JCT | Centralia TS | ON_CEN_DSS |  |  | 1261
| L7S | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Centralia TS | ON_CEN_DSS | McGillivray R&BP TS | ON_MCG_ISS |  |  | 1262
| L7S | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Biddulph JCT | ON_BID_JCT | Grand Bend East JCT | ON_GRB_JCT |  |  | 1263
| L7S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Grand Bend East JCT | ON_GRB_JCT | Grand Bend East DS | ON_GRB_DSS |  |  | 1264
| L7S | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Grand Bend East JCT | ON_GRB_JCT | Lake Huron WTP TS | ON_LAH_ISS |  |  | 1265
| L7S | HONI | Ontario | 1 | ac | 18 | 11.1111 | 115 | 7.5086 | 3 | [5 empty] | 98.4491 | 108.4016 | Kirkton JCT | ON_KRK_JCT | Devizes JCT | ON_DVZ_JCT |  |  | 1266
| L7S | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Devizes JCT | ON_DVZ_JCT | Enbridge Bryanston TS | ON_ENB_ISS |  |  | 1267
| L7S | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Devizes JCT | ON_DVZ_JCT | Portland JCT | ON_PTL_JCT |  |  | 1268
| L7S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Portland JCT | ON_PTL_JCT | St. Marys Cement TS | ON_SMC_ISS |  |  | 1269
| L7S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Portland JCT | ON_PTL_JCT | St. Marys TS | ON_SMY_DSS |  |  | 1270
| M1T | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Gold Centre JCT | ON_GLC_JCT | Timmins TS | ON_TMM_DSS |  |  | 1286
| M1T | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Monteith SWS | ON_MTT_SWS | Echo Bay Aquarius JCT | ON_ECH_JCT |  |  | 1287
| M2W | HONI | Ontario | 1 | ac | 35 | 21.6049 | 115 | 14.6 | 3 | [5 empty] | 98.4491 | 108.4016 | Animki JCT | ON_ANM_JCT | White River DS | ON_WHT_DSS |  |  | 1340
| M2W | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Black River JCT | ON_BKR_JCT | Umbata Falls JCT | ON_UBF_JCT |  |  | 1341
| M2W | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Hemlo Mine JCT | ON_HML_JCT | Animki JCT | ON_ANM_JCT |  |  | 1342
| M2W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Manitouwadge JCT | ON_MTG_JCT | Manitouwadge JCT B | ON_MTW_JCT |  |  | 1343
| M2W | HONI | Ontario | 1 | ac | 85 | 52.4691 | 115 | 35.4571 | 3 | [5 empty] | 98.4491 | 108.4016 | Manitouwadge JCT | ON_MTG_JCT | Pic JCT | ON_PIC_JCT |  |  | 1344
| M2W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Manitouwadge JCT B | ON_MTW_JCT | Manitouwadge DS | ON_MTG_DSS |  |  | 1345
| M2W | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Manitouwadge JCT B | ON_MTW_JCT | Manitouwadge TS | ON_MTW_DSS |  |  | 1346
| M2W | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Marathon TS | ON_MRT_TSS | Black River JCT | ON_BKR_JCT |  |  | 1348
| M2W | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Umbata Falls JCT | ON_UBF_JCT | Williams Mine JCT | ON_WLM_JCT |  |  | 1350
| M2W | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Williams Mine JCT | ON_WLM_JCT | Hemlo Mine JCT | ON_HML_JCT |  |  | 1351
| M2W | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Willroy JCT | ON_WRY_JCT | Willroy Mines TS | ON_WRY_ISS |  |  | 1352
| M2W | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Willroy JCT | ON_WRY_JCT | Manitouwadge JCT | ON_MTG_JCT |  |  | 1353
| M31 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Eddy Tap A JCT | ON_EDA_JCT | Espanola GS | ON_ESP_GSS |  |  | 1359
| M31 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Espanola A JCT | ON_EPA_JCT | Eddy Tap A JCT | ON_EDA_JCT |  |  | 1360
| M31 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Espanola TS | ON_ESP_DSS | Espanola A JCT | ON_EPA_JCT |  |  | 1361
| M31 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | S2B-M31 JCT | ON_S2B_JCT | Espanola A JCT | ON_EPA_JCT |  |  | 1362
| M3E | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Manitou Falls GS | ON_MNF_GSS | Ear Falls TS | ON_EAF_DSS |  |  | 1395
| M6E | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Bracebridge JCT | ON_BRA_JCT | Bracebridge TS | ON_BRA_DSS |  |  | 1412
| M6E | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Bracebridge JCT | ON_BRA_JCT | Muskoka TS | ON_MSK_DSS |  |  | 1413
| M6E | HONI | Ontario | 1 | ac | 28 | 17.284 | 230 | 13.44 | 3 | [5 empty] | 402 | 435 | Cooper's Falls JCT | ON_COF_JCT | Bracebridge JCT | ON_BRA_JCT |  |  | 1414
| M6E | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Cooper's Falls JCT | ON_COF_JCT | Orillia TS | ON_ORI_DSS |  |  | 1415
| M6E | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Midhurst TS | ON_MDH_DSS | Essa TS | ON_ESA_TSS |  |  | 1416
| M6E | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Minden TS | ON_MND_DSS | Cooper's Falls JCT | ON_COF_JCT |  |  | 1417
| M6E | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Orillia TS | ON_ORI_DSS | Midhurst TS | ON_MDH_DSS |  |  | 1418
| M7E | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Bracebridge JCT | ON_BRA_JCT | Muskoka TS | ON_MSK_DSS |  |  | 1419
| M7E | HONI | Ontario | 1 | ac | 28 | 17.284 | 230 | 13.44 | 3 | [5 empty] | 402 | 435 | Cooper's Falls JCT | ON_COF_JCT | Bracebridge JCT | ON_BRA_JCT |  |  | 1420
| M7E | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Cooper's Falls JCT | ON_COF_JCT | Orillia TS | ON_ORI_DSS |  |  | 1421
| M7E | HONI | Ontario | 1 | ac | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Midhurst TS | ON_MDH_DSS | Essa TS | ON_ESA_TSS |  |  | 1422
| M7E | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Minden TS | ON_MND_DSS | Cooper's Falls JCT | ON_COF_JCT |  |  | 1423
| M7E | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Orillia TS | ON_ORI_DSS | Midhurst TS | ON_MDH_DSS |  |  | 1424
| M9K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Moosonee DS | ON_MOO_DSS | Moosonee JCT | ON_MOO_JCT |  |  | 1435
| N1S | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Sarnia Scott TS | ON_SNS_TSS | Vidal JCT | ON_VDL_JCT |  |  | 1438
| N1S | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Vidal JCT | ON_VDL_JCT | Suncor TS | ON_SCR_ISS |  |  | 1439
| N20K | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Nanticoke TS | ON_NTK_TSS | Imperial Oil Nanticoke JCT | ON_ION_JCT |  |  | 1440
| N20K | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Imperial Oil Nanticoke JCT | ON_ION_JCT | Sandusk JCT | ON_SND_JCT |  |  | 1441
| N20K | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Sandusk JCT | ON_SND_JCT | Sandusk SWS | ON_SND_SWS |  |  | 1442
| N21W | HONI | Ontario | 1 | ac | 100 | 61.7284 | 230 | 48 | 2.796 | [5 empty] | 374.6673 | 405.4236 | Bostwick Road JCT | ON_BOS_JCT | Lucasville JCT | ON_LUC_JCT |  |  | 1448
| N21W | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Lucasville JCT | ON_LUC_JCT | Plank Road JCT | ON_PLK_JCT |  |  | 1449
| N21W | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Lucasville JCT | ON_LUC_JCT | Sarnia Scott TS | ON_SNS_TSS |  |  | 1450
| N21W | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Plank Road JCT | ON_PLK_JCT | Confederation Rd JCT | ON_CON_JCT |  |  | 1451
| N21W | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Confederation Rd JCT | ON_CON_JCT | Modeland TS | ON_MOD_DSS |  |  | 1452
| N22W | HONI | Ontario | 1 | ac | 100 | 61.7284 | 230 | 48 | 2.796 | [5 empty] | 374.6673 | 405.4236 | Bostwick Road JCT | ON_BOS_JCT | Lucasville JCT | ON_LUC_JCT |  |  | 1458
| N22W | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Lucasville JCT | ON_LUC_JCT | Plank Road JCT | ON_PLK_JCT |  |  | 1459
| N22W | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Lucasville JCT | ON_LUC_JCT | Sarnia Scott TS | ON_SNS_TSS |  |  | 1460
| N22W | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Plank Road JCT | ON_PLK_JCT | Confederation Rd JCT | ON_CON_JCT |  |  | 1461
| N22W | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Confederation Rd JCT | ON_CON_JCT | Modeland TS | ON_MOD_DSS |  |  | 1462
| N4S | HONI | Ontario | 1 | ac | 1.5 | 0.92593 | 115 | 0.62571 | 3 | [5 empty] | 98.4491 | 108.4016 | Vidal JCT | ON_VDL_JCT | Suncor TS | ON_SCR_ISS |  |  | 1465
| N582L | HONI | Ontario | 1 | ac | 150 | 92.5926 | 500 | 59.25 | 2.14 | [5 empty] | 1818.9793 | 2300.4738 | Nanticoke TS | ON_NTK_TSS | Longwood TS | ON_LGW_DSS |  |  | 1468
| N6S | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Sarnia Scott JCT | ON_SNS_JCT | Arlanxeo Can Inc JCT | ON_ARX_JCT |  |  | 1483
| N6S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Arlanxeo Can Inc JCT | ON_ARX_JCT | Arlanxeo Can Inc TS | ON_ARX_ISS |  |  | 1484
| N6S | HONI | Ontario | 1 | ac | 1.9 | 1.1728 | 230 | 0.912 | 3 | [5 empty] | 402 | 435 | Arlanxeo Can Inc JCT | ON_ARX_JCT | TransAlta Energy JCT | ON_TRA_JCT |  |  | 1485
| N6S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | TransAlta Energy JCT | ON_TRA_JCT | TransAlta Energy GS | ON_TRA_GSS |  |  | 1486
| N6S | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | TransAlta Energy JCT | ON_TRA_JCT | Imperial Oil TS | ON_IMP_ISS |  |  | 1487
| N7C | HONI | Ontario | 1 | ac | 3.5 | 2.1605 | 115 | 1.46 | 3 | [5 empty] | 98.4491 | 108.4016 | Sarnia Scott TS | ON_SNS_TSS | St. Andrews TS | ON_STA_DSS |  |  | 1488
| N7S | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Sarnia Scott JCT | ON_SNS_JCT | Arlanxeo Can Inc JCT | ON_ARX_JCT |  |  | 1490
| N7S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Arlanxeo Can Inc JCT | ON_ARX_JCT | Arlanxeo Can Inc TS | ON_ARX_ISS |  |  | 1491
| N7S | HONI | Ontario | 1 | ac | 1.9 | 1.1728 | 230 | 0.912 | 3 | [5 empty] | 402 | 435 | Arlanxeo Can Inc JCT | ON_ARX_JCT | TransAlta Energy JCT | ON_TRA_JCT |  |  | 1492
| N7S | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | TransAlta Energy JCT | ON_TRA_JCT | Imperial Oil TS | ON_IMP_ISS |  |  | 1493
| NA41M42 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Holland Marsh JCT | ON_HLM_JCT | West Gwillimbury JCT | ON_WGW_JCT |  |  | 1499
| NAL23M5 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Crosby JCT | ON_CRO_JCT | Newboro DS | ON_NBO_DSS |  |  | 1501
| NAL23M6 | HONI | Ontario | 1 | ac | 6 | 3.7037 | 115 | 2.5029 | 3 | [5 empty] | 98.4491 | 108.4016 | Crosby JCT | ON_CRO_JCT | Elgin JCT | ON_ELG_JCT |  |  | 1502
| NAL82M28 | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | Smiths Falls TS | ON_SMF_DSS | Jasper DS | ON_JSP_DSS |  |  | 1503
| NAR43M21 | HONI | Ontario | 2 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Warden TS | ON_WDN_DSS | Lumsden JCT | ON_LUM_JCT |  |  | 1505
| NAR43M31 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Warden TS | ON_WDN_DSS | Lumsden JCT | ON_LUM_JCT |  |  | 1506
| NAR43M32 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Warden TS | ON_WDN_DSS | Lumsden JCT | ON_LUM_JCT |  |  | 1507
| P13T | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Porcupine TS | ON_PCP_TSS | Timmins TS | ON_TMM_DSS |  |  | 1510
| P15C | HONI | Ontario | 1 | ac | 75 | 46.2963 | 230 | 36 | 3 | [5 empty] | 402 | 435 | Dobbin TS | ON_DOB_DSS | Cherrywood TS | ON_CHW_DSS |  |  | 1511
| P15T | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Porcupine TS | ON_PCP_TSS | Timmins TS | ON_TMM_DSS |  |  | 1512
| P1P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Port Arthur TS #1 | ON_PTA_DSS | Port Arthur JCT | ON_PTA_JCT |  |  | 1513
| P1T | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Port Arthur TS #1 | ON_PTA_DSS | TBPI Thunder Bay JCT | ON_TBP_JCT |  |  | 1514
| P1T | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | TBPI Thunder Bay JCT | ON_TBP_JCT | TBPI Thunder Bay TS | ON_TBP_ISS |  |  | 1515
| P27C | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Pickering B SWS | ON_PKB_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 1546
| P30C | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Pickering B SWS | ON_PKB_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 1547
| P31C | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Pickering B SWS | ON_PKB_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 1548
| P32C | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Pickering B SWS | ON_PKB_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 1549
| P3S | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Dale JCT | ON_DAL_JCT | Port Hope TS | ON_PTH_DSS |  |  | 1552
| P3S | HONI | Ontario | 1 | ac | 55 | 33.9506 | 115 | 22.9429 | 3 | [5 empty] | 98.4491 | 108.4016 | Dale JCT | ON_DAL_JCT | Sidney TS | ON_SDY_DSS |  |  | 1553
| P3S | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Dobbin TS | ON_DOB_DSS | Dale JCT | ON_DAL_JCT |  |  | 1554
| P45 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Parkway TS | ON_PKW_TSS | Markham #4 JCT | ON_MJ4_JCT |  |  | 1555
| P45 | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Markham #4 JCT | ON_MJ4_JCT | Buttonville TS | ON_BUT_DSS |  |  | 1556
| P45 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Markham #4 JCT | ON_MJ4_JCT | Markham #4 MTS | ON_MM4_DSS |  |  | 1557
| P46 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 230 | 0.48 | 3 | [5 empty] | 402 | 435 | Parkway TS | ON_PKW_TSS | Markham #4 JCT | ON_MJ4_JCT |  |  | 1558
| P46 | HONI | Ontario | 1 | ac | 4 | 2.4691 | 230 | 1.92 | 3 | [5 empty] | 402 | 435 | Markham #4 JCT | ON_MJ4_JCT | Buttonville TS | ON_BUT_DSS |  |  | 1559
| P46 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Markham #4 JCT | ON_MJ4_JCT | Markham #4 MTS | ON_MM4_DSS |  |  | 1560
| P4S | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Dale JCT | ON_DAL_JCT | Port Hope TS | ON_PTH_DSS |  |  | 1561
| P4S | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Dale JCT | ON_DAL_JCT | Vernonville JCT | ON_VNN_JCT |  |  | 1562
| P4S | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Dobbin DS | ON_DBN_DSS | Dale JCT | ON_DAL_JCT |  |  | 1563
| P4S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Dobbin TS | ON_DOB_DSS | Dobbin DS | ON_DBN_DSS |  |  | 1564
| P4S | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Hilton JCT | ON_HIL_JCT | Enbridge PL Hilt TS | ON_ENH_ISS |  |  | 1565
| P4S | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | Hilton JCT | ON_HIL_JCT | Sidney TS | ON_SDY_DSS |  |  | 1566
| P4S | HONI | Ontario | 1 | ac | 18 | 11.1111 | 115 | 7.5086 | 3 | [5 empty] | 98.4491 | 108.4016 | Vernonville JCT | ON_VNN_JCT | Hilton JCT | ON_HIL_JCT |  |  | 1567
| P4S | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Vernonville JCT | ON_VNN_JCT | TCPL Cobourg TS | ON_TCC_ISS |  |  | 1568
| P502X | HONI | Ontario | 1 | ac | 200 | 123.4568 | 500 | 79 | 1.7702 | [5 empty] | 1504.6332 | 1902.9185 | Porcupine TS | ON_PCP_TSS | Hanmer TS | ON_HNM_TSS |  |  | 1569
| P6C | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Pickering A SWS | ON_PKA_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 1571
| P7C | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Pickering A SWS | ON_PKA_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 1574
| P7G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Bell Creek JCT | ON_BLC_JCT | Bell Creek TS | ON_BLC_ISS |  |  | 1575
| P7G | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Bell Creek JCT | ON_BLC_JCT | Pamour JCT | ON_PAM_JCT |  |  | 1576
| P7G | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Dome Site JCT | ON_DOM_JCT | Gold Centre JCT | ON_GLC_JCT |  |  | 1577
| P7G | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Ecstall JCT | ON_ECS_JCT | Kidd Contractor TS | ON_KDC_ISS |  |  | 1578
| P7G | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Ecstall JCT | ON_ECS_JCT | Kidd Creek Mine JCT | ON_KCM_JCT |  |  | 1579
| P7G | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Gold Centre JCT | ON_GLC_JCT | Bell Creek JCT | ON_BLC_JCT |  |  | 1580
| P7G | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Gold Centre JCT | ON_GLC_JCT | Echo Bay Aquarius JCT | ON_ECH_JCT |  |  | 1581
| P7G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hoyle JCT | ON_HOY_JCT | Hoyle DS | ON_HOY_DSS |  |  | 1582
| P7G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Hoyle JCT | ON_HOY_JCT | Hoyle Pond Site JCT | ON_HPS_JCT |  |  | 1583
| P7G | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Hoyle Pond Site JCT | ON_HPS_JCT | Ecstall JCT | ON_ECS_JCT |  |  | 1584
| P7G | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kidd Creek Mine JCT | ON_KCM_JCT | Kidd Metsite TS | ON_KMT_ISS |  |  | 1585
| P7G | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kidd Creek Mine JCT | ON_KCM_JCT | Kidd Zinc Refinery TS | ON_KDZ_ISS |  |  | 1586
| P7G | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Pamour JCT | ON_PAM_JCT | Hoyle JCT | ON_HOY_JCT |  |  | 1587
| P7G | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Pamour JCT | ON_PAM_JCT | Royal Oak TS | ON_RYO_ISS |  |  | 1588
| P7G | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Porcupine TS | ON_PCP_TSS | Dome Site JCT | ON_DOM_JCT |  |  | 1589
| P8C | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Pickering A SWS | ON_PKA_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 1590
| P91G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Ansonville JCT | ON_ANS_JCT | Ansonville TS | ON_ANS_TSS |  |  | 1591
| P91G | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | ERG Resources JCT | ON_ERG_JCT | ERG Resources TS | ON_ERG_ISS |  |  | 1592
| P91G | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | ERG Resources JCT | ON_ERG_JCT | Hoyle JCT | ON_HOY_JCT |  |  | 1593
| P91G | HONI | Ontario | 1 | ac | 50 | 30.8642 | 230 | 24 | 3 | [5 empty] | 402 | 435 | Hoyle JCT | ON_HOY_JCT | Ansonville JCT | ON_ANS_JCT |  |  | 1594
| P91G | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Hoyle JCT | ON_HOY_JCT | Kidd Metsite TS | ON_KMT_ISS |  |  | 1595
| P91G | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Porcupine TS | ON_PCP_TSS | ERG Resources JCT | ON_ERG_JCT |  |  | 1596
| P9C | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Pickering A SWS | ON_PKA_SWS | Cherrywood TS | ON_CHW_DSS |  |  | 1597
| Q21P | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Beck Pump Storage GS | ON_BKP_GSS |  |  | 1616
| Q22P | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 230 | 0.24 | 3 | [5 empty] | 402 | 435 | Beck #2 TS | ON_BK2_TSS | Beck Pump Storage GS | ON_BKP_GSS |  |  | 1617
| Q3K | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cataraqui TS | ON_CTQ_TSS | Westbrook JCT | ON_WTB_JCT |  |  | 1694
| Q3K | HONI | Ontario | 1 | ac | 12 | 7.4074 | 115 | 5.0057 | 3 | [5 empty] | 98.4491 | 108.4016 | Westbrook JCT | ON_WTB_JCT | Frontenac TS | ON_FRO_DSS |  |  | 1695
| Q3M6 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Frontenac TS | ON_FRO_DSS | Novelis TS | ON_NLS_ISS |  |  | 1696
| Q6N | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | Selby JCT | ON_SBY_JCT | Napanee TS | ON_NAP_DSS |  |  | 1733
| Q6S | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cataraqui TS | ON_CTQ_TSS | Westbrook JCT | ON_WTB_JCT |  |  | 1734
| Q6S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Invista JCT | ON_INV_JCT | Q6S STR M60 JCT | ON_Q6S_JCT |  |  | 1735
| Q6S | HONI | Ontario | 1 | ac | 27 | 16.6667 | 115 | 11.2629 | 3 | [5 empty] | 98.4491 | 108.4016 | Milltown JCT | ON_MLT_JCT | Sidney TS | ON_SDY_DSS |  |  | 1736
| Q6S | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | Milltown JCT | ON_MLT_JCT | TCPL Belleville TS | ON_TCB_ISS |  |  | 1737
| Q6S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Odessa JCT | ON_ODS_JCT | Invista JCT | ON_INV_JCT |  |  | 1738
| Q6S | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Odessa JCT | ON_ODS_JCT | Selby JCT | ON_SBY_JCT |  |  | 1739
| Q6S | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Selby JCT | ON_SBY_JCT | Milltown JCT | ON_MLT_JCT |  |  | 1740
| Q6S | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Westbrook JCT | ON_WTB_JCT | Odessa JCT | ON_ODS_JCT |  |  | 1741
| R21D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Otter Rapids GS | ON_ORP_GSS | Otter Rapids SWS | ON_ORP_SWS |  |  | 1771
| R21D | HONI | Ontario | 1 | ac | 50 | 30.8642 | 230 | 24 | 3 | [5 empty] | 402 | 435 | Otter Rapids SWS | ON_ORP_SWS | Pinard JCT | ON_PIN_JCT |  |  | 1772
| R21D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Pinard JCT | ON_PIN_JCT | Abitibi Canyon GS | ON_ABC_GSS |  |  | 1773
| R21D | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Pinard JCT | ON_PIN_JCT | Pinard TS | ON_PIN_TSS |  |  | 1774
| S1H | HONI | Ontario | 1 | ac | 48 | 29.6296 | 115 | 20.0229 | 3 | [5 empty] | 98.4491 | 108.4016 | Owen Sound TS | ON_OWS_DSS | Hanover TS | ON_HNV_DSS |  |  | 1797
| S1K | HONI | Ontario | 1 | ac | 24 | 14.8148 | 115 | 10.0114 | 3 | [5 empty] | 98.4491 | 108.4016 | Battersea DS | ON_BTT_DSS | Frontenac TS | ON_FRO_DSS |  |  | 1798
| S21N | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Martindale TS | ON_MTD_DSS | Vale Frood Stobie #2 JCT | ON_VLF_JCT |  |  | 1799
| S21N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Vale Frood Stobie #2 JCT | ON_VLF_JCT | Vale Copper #4 TS | ON_VLC_ISS |  |  | 1800
| S21N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Vale Frood Stobie #2 JCT | ON_VLF_JCT | Vale Frood Stobie #2 TS | ON_VLF_ISS |  |  | 1801
| S22A | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Clarabelle JCT | ON_CLA_JCT | Algoma TS | ON_ALG_TSS |  |  | 1802
| S22A | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Clarabelle JCT | ON_CLA_JCT | Clarabelle TS | ON_CLA_DSS |  |  | 1803
| S22A | HONI | Ontario | 1 | ac | 155 | 95.679 | 230 | 74.4 | 2.0942 | [5 empty] | 280.6222 | 303.6584 | Martindale TS | ON_MTD_DSS | Clarabelle JCT | ON_CLA_JCT |  |  | 1804
| S24V | HONI | Ontario | 1 | ac | 45 | 27.7778 | 115 | 18.7714 | 3 | [5 empty] | 98.4491 | 108.4016 | Orangeville TS | ON_ORA_DSS | Shannon GS | ON_SHN_DSS |  |  | 1805
| S25L | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Saunders JCT | ON_SAU_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1806
| S26L | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Saunders JCT | ON_SAU_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1807
| S2B | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Copper Cliff JCT | ON_CFF_JCT | Creighton JCT | ON_CRE_JCT |  |  | 1813
| S2B | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Creighton JCT | ON_CRE_JCT | Nickel Basin JCT | ON_NIC_JCT |  |  | 1814
| S2B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Eacom Nairn Centre JCT | ON_EAC_JCT | Eacom Nairn Centre TS | ON_EAC_ISS |  |  | 1817
| S2B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Eddy Tap JCT | ON_EDA_JCT | Eddy Tap A JCT | ON_EDA_JCT |  |  | 1819
| S2B | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Espanola TS | ON_ESP_DSS | S2B-M31 JCT | ON_S2B_JCT |  |  | 1825
| S2B | HONI | Ontario | 1 | ac | 7 | 4.321 | 115 | 2.92 | 3 | [5 empty] | 98.4491 | 108.4016 | Ethel Lake JCT | ON_ETH_JCT | Whitefish DS | ON_WHF_DSS |  |  | 1826
| S2B | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Martindale TS | ON_MTD_DSS | Copper Cliff JCT | ON_CFF_JCT |  |  | 1828
| S2B | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | McLeans Mountain JCT | ON_MCL_JCT | Manitoulin TS | ON_MNT_DSS |  |  | 1831
| S2B | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | S2B-M31 JCT | ON_S2B_JCT | Baldwin JCT | ON_BDW_JCT |  |  | 1833
| S2B | HONI | Ontario | 1 | ac | 9 | 5.5556 | 115 | 3.7543 | 3 | [5 empty] | 98.4491 | 108.4016 | Turbine JCT | ON_TUR_JCT | Eacom Nairn Centre JCT | ON_EAC_JCT |  |  | 1837
| S2B | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Vermillion JCT | ON_VEM_JCT | Lockerby Mine TS | ON_LBM_ISS |  |  | 1838
| S2N | HONI | Ontario | 1 | ac | 28 | 17.284 | 115 | 11.68 | 3 | [5 empty] | 98.4491 | 108.4016 | Sarnia Scott TS | ON_SNS_TSS | Wanstead JCT | ON_WAN_JCT |  |  | 1840
| S2N | HONI | Ontario | 3 | ac | 2.3 | 1.4198 | 115 | 0.95943 | 3 | [5 empty] | 98.4491 | 108.4016 | Wanstead JCT | ON_WAN_JCT | Wanstead TS | ON_WAN_DSS |  |  | 1841
| S2N | HONI | Ontario | 1 | ac | 12.5 | 7.716 | 115 | 5.2143 | 3 | [5 empty] | 98.4491 | 108.4016 | Wanstead JCT | ON_WAN_JCT | Ennisbrook JCT | ON_ENN_JCT |  |  | 1842
| S2N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Ennisbrook JCT | ON_ENN_JCT | Forest Jura DS | ON_FRJ_DSS |  |  | 1843
| S2N | HONI | Ontario | 1 | ac | 12.5 | 7.716 | 115 | 5.2143 | 3 | [5 empty] | 98.4491 | 108.4016 | Ennisbrook JCT | ON_ENN_JCT | Kerwood JCT | ON_KER_JCT |  |  | 1844
| S2N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kerwood JCT | ON_KER_JCT | Sun Cdn Pipeline TS | ON_SCP_ISS |  |  | 1845
| S2N | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Kerwood JCT | ON_KER_JCT | Adelaide JCT | ON_ADE_JCT |  |  | 1846
| S2N | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Adelaide JCT | ON_ADE_JCT | Landon JCT | ON_LND_JCT |  |  | 1847
| S2N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Landon JCT | ON_LND_JCT | Landon GS | ON_LND_GSS |  |  | 1848
| S2N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Landon JCT | ON_LND_JCT | Enbridge Keyser TS | ON_ENK_ISS |  |  | 1849
| S2N | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Adelaide JCT | ON_ADE_JCT | Sydenham JCT | ON_SYD_JCT |  |  | 1850
| S2S | HONI | Ontario | 1 | ac | 45 | 27.7778 | 115 | 18.7714 | 3 | [5 empty] | 98.4491 | 108.4016 | Meaford TS | ON_MEA_DSS | Stayner TS | ON_STY_DSS |  |  | 1852
| S2S | HONI | Ontario | 1 | ac | 28 | 17.284 | 115 | 11.68 | 3 | [5 empty] | 98.4491 | 108.4016 | Owen Sound TS | ON_OWS_DSS | Meaford TS | ON_MEA_DSS |  |  | 1853
| S30L | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Saunders JCT | ON_SAU_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1854
| S32L | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Saunders JCT | ON_SAU_JCT | St. Lawrence TS | ON_STL_DSS |  |  | 1855
| S3S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kapuskasing R JCT | ON_KAP_JCT | Tembec Kapuskasking TS | ON_TMB_GSS |  |  | 1859
| S3S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | S3S_S4S STR 8 JCT | ON_S3S_JCT | Kapuskasing R JCT | ON_KAP_JCT |  |  | 1860
| S47C | HONI | Ontario | 1 | ac | 24 | 14.8148 | 230 | 11.52 | 3 | [5 empty] | 402 | 435 | Spence SWS | ON_SPC_SWS | Erieau WF JCT | ON_ERI_JCT |  |  | 1861
| S47C | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Erieau WF JCT | ON_ERI_JCT | Erieau WF GS | ON_ERI_GSS |  |  | 1862
| S47C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Erieau WF JCT | ON_ERI_JCT | Chatham SWS | ON_CHT_SWS |  |  | 1863
| S4S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Kapuskasing R JCT | ON_KAP_JCT | Tembec Kapuskasking TS | ON_TMB_GSS |  |  | 1864
| S4S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | S3S_S4S STR 8 JCT | ON_S3S_JCT | Kapuskasing R JCT | ON_KAP_JCT |  |  | 1865
| S5M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | McCrea JCT | ON_MCC_JCT | Thayer Lindsley TS | ON_TLS_ISS |  |  | 1869
| S5M | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Nickel Basin JCT | ON_NIC_JCT | Larchwood TS | ON_LCH_DSS |  |  | 1870
| S5M | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Onaping JCT | ON_ONP_JCT | Nickel Basin JCT | ON_NIC_JCT |  |  | 1871
| S5M | HONI | Ontario | 1 | ac | 30 | 18.5185 | 115 | 12.5143 | 3 | [5 empty] | 98.4491 | 108.4016 | Onaping JCT | ON_ONP_JCT | Onaping Area M&M TS | ON_OAM_ISS |  |  | 1872
| S6N | HONI | Ontario | 1 | ac | 11 | 6.7901 | 115 | 4.5886 | 3 | [5 empty] | 98.4491 | 108.4016 | Selby JCT | ON_SBY_JCT | Napanee TS | ON_NAP_DSS |  |  | 1875
| S7S | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Dominion Drive DS | ON_DMD_DSS | Gervais JCT | ON_GRV_JCT |  |  | 1891
| SK1 | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Forgie JCT | ON_FRG_JCT | Clearwater Bay DS | ON_CWB_DSS |  |  | 1892
| SK1 | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Keewatin JCT | ON_KEE_JCT | Forgie JCT | ON_FRG_JCT |  |  | 1894
| SK1 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Keewatin JCT | ON_KEE_JCT | Keewatin DS | ON_KEE_DSS |  |  | 1895
| SK1 | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Rabbit Lake SWS | ON_RBL_SWS | Keewatin JCT | ON_KEE_JCT |  |  | 1896
| T1B | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Algoma TS | ON_ALG_TSS | Striker DS | ON_STK_DSS |  |  | 1905
| T1B | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Cobden JCT | ON_CBD_JCT | North Shore DS | ON_NOS_DSS |  |  | 1906
| T1B | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cobden JCT | ON_CBD_JCT | Red Rock GS JCT | ON_RRC_JCT |  |  | 1907
| T1B | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Red Rock GS JCT | ON_RRC_JCT | Red Rock GS | ON_RRC_GSS |  |  | 1908
| T1B | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Red Rock GS JCT | ON_RRC_JCT | Sowerby JCT | ON_SOW_JCT |  |  | 1909
| T1B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Sowerby JCT | ON_SOW_JCT | Sowerby DS | ON_SOW_DSS |  |  | 1910
| T1B | HONI | Ontario | 1 | ac | 18 | 11.1111 | 115 | 7.5086 | 3 | [5 empty] | 98.4491 | 108.4016 | Sowerby JCT | ON_SOW_JCT | Wharncliffe JCT | ON_WHA_JCT |  |  | 1911
| T1B | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Striker DS | ON_STK_DSS | Cobden JCT | ON_CBD_JCT |  |  | 1912
| T1B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Wharncliffe JCT | ON_WHA_JCT | Wharncliffe DS | ON_WHA_DSS |  |  | 1913
| T1B | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Wharncliffe JCT | ON_WHA_JCT | Rayner GS | ON_RNR_GSS |  |  | 1914
| T1M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Marathon DS JCT | ON_MRT_JCT | Marathon DS | ON_MRT_DSS |  |  | 1916
| T1M | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Pic JCT | ON_PIC_JCT | Marathon DS JCT | ON_MRT_JCT |  |  | 1917
| T1M | HONI | Ontario | 1 | ac | 0.5 | 0.30864 | 115 | 0.20857 | 3 | [5 empty] | 98.4491 | 108.4016 | Pic JCT | ON_PIC_JCT | Marathon TS | ON_MRT_TSS |  |  | 1918
| T22C | HONI | Ontario | 1 | ac | 210 | 129.6296 | 230 | 100.8 | 1.7141 | [5 empty] | 229.69 | 248.5452 | Chats Falls SWS | ON_CHF_SWS | Marine JCT | ON_MAR_JCT |  |  | 1920
| T22C | HONI | Ontario | 1 | ac | 55 | 33.9506 | 230 | 26.4 | 3 | [5 empty] | 402 | 435 | Marine JCT | ON_MAR_JCT | Clarington TS | ON_CLG_TSS |  |  | 1921
| T22C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Marine JCT | ON_MAR_JCT | Otonabee TS | ON_OTB_DSS |  |  | 1922
| T27P | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Wells GS | ON_WEL_GSS | Mississagi TS | ON_MSS_DSS |  |  | 1924
| T28P | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Wells GS | ON_WEL_GSS | Mississagi TS | ON_MSS_DSS |  |  | 1926
| T29C | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Clarington TS | ON_CLG_TSS | Wilson JCT | ON_WLS_JCT |  |  | 1927
| T29C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Whitby JCT | ON_WHB_JCT | Whitby TS | ON_WHB_DSS |  |  | 1928
| T29C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Whitby JCT | ON_WHB_JCT | Cherrywood TS | ON_CHW_DSS |  |  | 1929
| T29C | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Wilson JCT | ON_WLS_JCT | Wilson TS | ON_WLS_DSS |  |  | 1930
| T29C | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Wilson JCT | ON_WLS_JCT | Whitby JCT | ON_WHB_JCT |  |  | 1931
| T2R | HONI | Ontario | 2 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Blezard Valley JCT | ON_BLZ_JCT | Copper Cliff JCT | ON_CFF_JCT |  |  | 1933
| T2R | HONI | Ontario | 2 | ac | 105 | 64.8148 | 115 | 43.8 | 2.7075 | [5 empty] | 88.85 | 97.8321 | Shiningtree JCT | ON_SGT_JCT | Blezard Valley JCT | ON_BLZ_JCT |  |  | 1935
| T2R | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Timmins TS | ON_TMM_DSS | Wawaitin JCT | ON_WWT_JCT |  |  | 1936
| T2R | HONI | Ontario | 1 | ac | 90 | 55.5556 | 115 | 37.5429 | 2.9972 | [5 empty] | 98.3578 | 108.3011 | Wawaitin JCT | ON_WWT_JCT | Shiningtree JCT | ON_SGT_JCT |  |  | 1937
| T2R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Wawaitin JCT | ON_WWT_JCT | Wawaitin GS | ON_WWT_GSS |  |  | 1938
| T33E | HONI | Ontario | 1 | ac | 255 | 157.4074 | 230 | 122.4 | 1.5081 | [5 empty] | 202.0843 | 218.6733 | Almonte TS | ON_ALM_DSS | Clarington TS | ON_CLG_TSS |  |  | 1941
| T61S | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Ogden JCT | ON_ODG_JCT | Timmins Westmine JCT | ON_TMW_JCT |  |  | 1978
| T61S | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Ogden JCT | ON_ODG_JCT | Kam Kotia DS | ON_KAM_ISS |  |  | 1979
| T61S | HONI | Ontario | 1 | ac | 1 | 0.61728 | 115 | 0.41714 | 3 | [5 empty] | 98.4491 | 108.4016 | Timmins JCT | ON_TMM_JCT | Ogden JCT | ON_ODG_JCT |  |  | 1980
| T61S | HONI | Ontario | 1 | ac | 100 | 61.7284 | 115 | 41.7143 | 2.796 | [5 empty] | 91.7554 | 101.0312 | Timmins JCT | ON_TMM_JCT | Shiningtree DS | ON_SGT_DSS |  |  | 1981
| T61S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Timmins TS | ON_TMM_DSS | Timmins JCT | ON_TMM_JCT |  |  | 1982
| T61S | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Timmins Westmine JCT | ON_TMW_JCT | Timmins Westmine TS | ON_TMW_ISS |  |  | 1983
| T61S | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Timmins WestMine JCT | ON_TMW_JCT | Weston Lake DS | ON_WSL_DSS |  |  | 1984
| T7M | HONI | Ontario | 1 | ac | 40 | 24.6914 | 115 | 16.6857 | 3 | [5 empty] | 98.4491 | 108.4016 | Moosonee SWS | ON_MOO_SWS | Renison JCT | ON_RNS_JCT |  |  | 1985
| T7M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Onakawana JCT | ON_ONA_JCT | Onakawana TS | ON_ONA_ISS |  |  | 1986
| T7M | HONI | Ontario | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Onakawana JCT | ON_ONA_JCT | Otter Rapids SWS | ON_ORP_SWS |  |  | 1987
| T7M | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Renison JCT | ON_RNS_JCT | Renison TS | ON_RNS_ISS |  |  | 1988
| T7M | HONI | Ontario | 1 | ac | 50 | 30.8642 | 115 | 20.8571 | 3 | [5 empty] | 98.4491 | 108.4016 | Renison JCT | ON_RNS_JCT | Onakawana JCT | ON_ONA_JCT |  |  | 1989
| T8M | HONI | Ontario | 1 | ac | 140 | 86.4198 | 115 | 58.4 | 2.2396 | [5 empty] | 73.4954 | 80.9253 | Moosonee SWS | ON_MOO_SWS | Otter Rapids SWS | ON_ORP_SWS |  |  | 1990
| V12M | HONI | Ontario | 1 | ac | 2 | 1.2346 | 115 | 0.83429 | 3 | [5 empty] | 98.4491 | 108.4016 | Val Tetreau JCT | ON_VLT_JCT | Hinchey TS | ON_HIN_DSS |  |  | 1993
| V41H | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Sithe Goreway JCT | ON_SGW_JCT |  |  | 1994
| V41H | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Sithe Goreway JCT | ON_SGW_JCT | Bramalea TS | ON_BML_DSS |  |  | 1995
| V41H | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Bramalea TS | ON_BML_DSS | Cardiff JCT | ON_CDF_JCT |  |  | 1996
| V41H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Cardiff JCT | ON_CDF_JCT | Cardiff TS | ON_CDF_DSS |  |  | 1997
| V41H | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Cardiff JCT | ON_CDF_JCT | Hurontario SWS | ON_HRN_SWS |  |  | 1998
| V41N | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 230 | 1.2 | 3 | [5 empty] | 402 | 435 | Sarnia Scott TS | ON_SNS_TSS | St. Clair E.C. JCT | ON_STE_JCT |  |  | 1999
| V41N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | St. Clair E.C. JCT | ON_STE_JCT | St. Clair E.C. GS | ON_STE_GSS |  |  | 2000
| V41N | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 230 | 1.2 | 3 | [5 empty] | 402 | 435 | St. Clair E.C. JCT | ON_STE_JCT | Nova SWS | ON_NOV_SWS |  |  | 2001
| V41N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Nova SWS | ON_NOV_SWS | Nova Corunna TS | ON_NVC_ISS |  |  | 2002
| V43N | HONI | Ontario | 1 | ac | 2.5 | 1.5432 | 230 | 1.2 | 3 | [5 empty] | 402 | 435 | Sarnia Scott TS | ON_SNS_TSS | St. Clair E.C. JCT | ON_STE_JCT |  |  | 2017
| V43N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | St. Clair E.C. JCT | ON_STE_JCT | St. Clair E.C. GS | ON_STE_GSS |  |  | 2018
| V72R | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Richview TS | ON_RCV_DSS |  |  | 2040
| V73R | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Richview TS | ON_RCV_DSS |  |  | 2041
| V74R | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Westmore JCT | ON_WTM_JCT |  |  | 2042
| V74R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Westmore JCT | ON_WTM_JCT | Rexdale TS | ON_RXD_DSS |  |  | 2043
| V74R | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Westmore JCT | ON_WTM_JCT | Richview TS | ON_RCV_DSS |  |  | 2044
| V76R | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Westmore JCT | ON_WTM_JCT |  |  | 2054
| V76R | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Westmore JCT | ON_WTM_JCT | Rexdale TS | ON_RXD_DSS |  |  | 2055
| V76R | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Westmore JCT | ON_WTM_JCT | Richview TS | ON_RCV_DSS |  |  | 2056
| V77R | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Richview TS | ON_RCV_DSS |  |  | 2057
| V79R | HONI | Ontario | 1 | ac | 9 | 5.5556 | 230 | 4.32 | 3 | [5 empty] | 402 | 435 | Claireville TS | ON_CLV_TSS | Richview TS | ON_RCV_DSS |  |  | 2058
| W2 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Whitedog Falls GS | ON_WDF_GSS | Whitedog Falls SWS | ON_WDF_SWS |  |  | 2060
| W2C | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Chapleau JCT | ON_CHP_JCT | Chapleau DS | ON_CHP_DSS |  |  | 2064
| W2C | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Chapleau JCT | ON_CHP_JCT | Chapleau MTS | ON_CHM_DSS |  |  | 2065
| W2C | HONI | Ontario | 1 | ac | 120 | 74.0741 | 115 | 50.0571 | 2.4793 | [5 empty] | 81.3601 | 89.5851 | Wawa TS | ON_WAW_TSS | Chapleau JCT | ON_CHP_JCT |  |  | 2066
| W3B | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Barrett Chute JCT | ON_BTC_JCT | Barrett Chute SWS | ON_BTC_SWS |  |  | 2075
| W3B | HONI | Ontario | 1 | ac | 4 | 2.4691 | 115 | 1.6686 | 3 | [5 empty] | 98.4491 | 108.4016 | Barrett Chute JCT | ON_BTC_JCT | Barryvale Rd JCT | ON_BRV_JCT |  |  | 2076
| W3B | HONI | Ontario | 1 | ac | 23 | 14.1975 | 115 | 9.5943 | 3 | [5 empty] | 98.4491 | 108.4016 | Barryvale Rd JCT | ON_BRV_JCT | Stewartville TS | ON_STW_DSS |  |  | 2077
| W3B | HONI | Ontario | 1 | ac | 13 | 8.0247 | 115 | 5.4229 | 3 | [5 empty] | 98.4491 | 108.4016 | Mountain Chute DS | ON_MTC_DSS | Barrett Chute JCT | ON_BTC_JCT |  |  | 2078
| W3C | HONI | Ontario | 1 | ac | 20 | 12.3457 | 115 | 8.3429 | 3 | [5 empty] | 98.4491 | 108.4016 | Whitedog Falls SWS | ON_WDF_SWS | Caribou Falls GS | ON_CRF_GSS |  |  | 2079
| W44LC | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Duart JCT | ON_DUA_JCT | Duart TS | ON_DUA_DSS |  |  | 2088
| W44LC | HONI | Ontario | 1 | ac | 40 | 24.6914 | 230 | 19.2 | 3 | [5 empty] | 402 | 435 | Duart JCT | ON_DUA_JCT | Chatham SWS | ON_CHT_SWS |  |  | 2089
| W45LS | HONI | Ontario | 1 | ac | 6 | 3.7037 | 230 | 2.88 | 3 | [5 empty] | 402 | 435 | Duart JCT | ON_DUA_JCT | Duart TS | ON_DUA_DSS |  |  | 2093
| W71D | HONI | Ontario | 1 | ac | 60 | 37.037 | 230 | 28.8 | 3 | [5 empty] | 402 | 435 | Dymond TS | ON_DYM_DSS | Lower Notch JCT | ON_LWN_JCT |  |  | 2111
| W71D | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Lower Notch JCT | ON_LWN_JCT | Lower Notch GS | ON_LWN_GSS |  |  | 2112
| W71D | HONI | Ontario | 1 | ac | 80 | 49.3827 | 230 | 38.4 | 3 | [5 empty] | 402 | 435 | Lower Notch JCT | ON_LWN_JCT | Widdifield SWS | ON_WFD_SWS |  |  | 2113
| W71D | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Widdifield SWS | ON_WFD_SWS | Trout Lake TS | ON_TRL_DSS |  |  | 2114
| W8T | HONI | Ontario | 1 | ac | 8 | 4.9383 | 115 | 3.3371 | 3 | [5 empty] | 98.4491 | 108.4016 | Lyons JCT | ON_LYO_JCT | Cranberry JCT | ON_CRN_JCT |  |  | 2117
| WW1C | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Ingersoll TS | ON_ING_DSS | Lafarge Woodstock TS | ON_LFW_ISS |  |  | 2126
| X1H | HONI | Ontario | 1 | ac | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Hinchinbrooke SWS | ON_HNB_SWS | Cataraqui TS | ON_CTQ_TSS |  |  | 2127
| X1H | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Cataraqui TS | ON_CTQ_TSS | NPIF Kingston JCT | ON_NPK_JCT |  |  | 2128
| X1H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | NPIF Kingston JCT | ON_NPK_JCT | NPIF Kingston GS | ON_NPK_GSS |  |  | 2129
| X1H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | NPIF Kingston JCT | ON_NPK_JCT | Lafarge JCT | ON_LAF_JCT |  |  | 2130
| X1H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Lafarge JCT | ON_LAF_JCT | Lafarge Bath TS | ON_LFB_ISS |  |  | 2131
| X1H | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Lafarge JCT | ON_LAF_JCT | Lennox TS | ON_LEN_TSS |  |  | 2132
| X1P | HONI | Ontario | 1 | ac | 45 | 27.7778 | 230 | 21.6 | 3 | [5 empty] | 402 | 435 | Chenaux TS | ON_CHX_TSS | Mountain Chute JCT | ON_MTC_JCT |  |  | 2133
| X1P | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Massanoga JCT | ON_MOG_JCT | Mazinaw DS | ON_MZW_DSS |  |  | 2134
| X1P | HONI | Ontario | 1 | ac | 110 | 67.9012 | 230 | 52.8 | 2.6257 | [5 empty] | 351.8417 | 380.7242 | Massanoga JCT | ON_MOG_JCT | Dobbin TS | ON_DOB_DSS |  |  | 2135
| X1P | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Mountain Chute JCT | ON_MTC_JCT | Mountain Chute GS | ON_MTC_GSS |  |  | 2136
| X1P | HONI | Ontario | 1 | ac | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Mountain Chute JCT | ON_MTC_JCT | Massanoga JCT | ON_MOG_JCT |  |  | 2137
| X21 | HONI | Ontario | 1 | ac | 17 | 10.4938 | 230 | 8.16 | 3 | [5 empty] | 402 | 435 | Lennox TS | ON_LEN_TSS | Gretna JCT | ON_GNA_JCT |  |  | 2138
| X21 | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Gretna JCT | ON_GNA_JCT | Napanee TS | ON_NAP_DSS |  |  | 2139
| X21 | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Gretna JCT | ON_GNA_JCT | Long Reach East JCT | ON_LRE_JCT |  |  | 2140
| X21 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Long Reach East JCT | ON_LRE_JCT | Long Reach West JCT | ON_LRW_JCT |  |  | 2141
| X21 | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Long Reach West JCT | ON_LRW_JCT | Picton TS | ON_PCT_DSS |  |  | 2142
| X22 | HONI | Ontario | 1 | ac | 17 | 10.4938 | 230 | 8.16 | 3 | [5 empty] | 402 | 435 | Lennox TS | ON_LEN_TSS | Gretna JCT | ON_GNA_JCT |  |  | 2143
| X22 | HONI | Ontario | 1 | ac | 7 | 4.321 | 230 | 3.36 | 3 | [5 empty] | 402 | 435 | Gretna JCT | ON_GNA_JCT | Napanee TS | ON_NAP_DSS |  |  | 2144
| X22 | HONI | Ontario | 1 | ac | 8 | 4.9383 | 230 | 3.84 | 3 | [5 empty] | 402 | 435 | Gretna JCT | ON_GNA_JCT | Long Reach East JCT | ON_LRE_JCT |  |  | 2145
| X22 | HONI | Ontario | 1 | ac | 2 | 1.2346 | 230 | 0.96 | 3 | [5 empty] | 402 | 435 | Long Reach East JCT | ON_LRE_JCT | Long Reach West JCT | ON_LRW_JCT |  |  | 2146
| X22 | HONI | Ontario | 1 | ac | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Long Reach West JCT | ON_LRW_JCT | Picton TS | ON_PCT_DSS |  |  | 2147
| X23N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Clarabelle JCT | ON_CLA_JCT | Clarabelle TS | ON_CLA_DSS |  |  | 2148
| X23N | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Clarabelle JCT | ON_CLA_JCT | Vale Copper #4 TS | ON_VLC_ISS |  |  | 2149
| X23N | HONI | Ontario | 1 | ac | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Hanmer TS | ON_HNM_TSS | Vale Frood Stobie #2 JCT | ON_VLF_JCT |  |  | 2150
| X23N | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Vale Frood Stobie #2 JCT | ON_VLF_JCT | Vale Frood Stobie #2 TS | ON_VLF_ISS |  |  | 2151
| X23N | HONI | Ontario | 1 | ac | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Vale Frood Stobie #2 JCT | ON_VLF_JCT | Clarabelle JCT | ON_CLA_JCT |  |  | 2152
| X25S | HONI | Ontario | 1 | ac | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Hanmer TS | ON_HNM_TSS | Martindale TS | ON_MTD_DSS |  |  | 2153
| X26S | HONI | Ontario | 1 | ac | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Hanmer TS | ON_HNM_TSS | Martindale TS | ON_MTD_DSS |  |  | 2154
| X27A | HONI | Ontario | 1 | ac | 190 | 117.284 | 230 | 91.2 | 1.8311 | [5 empty] | 245.3623 | 265.504 | Hanmer TS | ON_HNM_TSS | Algoma TS | ON_ALG_TSS |  |  | 2155
| X2H | HONI | Ontario | 1 | ac | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Hinchinbrooke SWS | ON_HNB_SWS | Cataraqui TS | ON_CTQ_TSS |  |  | 2156
| X2H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Cataraqui TS | ON_CTQ_TSS | Westbrook JCT | ON_WTB_JCT |  |  | 2157
| X2H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Westbrook JCT | ON_WTB_JCT | Gardiner STR 44 JCT | ON_GAR_JCT |  |  | 2158
| X2H | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Gardiner STR 44 JCT | ON_GAR_JCT | Gardiner TS | ON_GAR_DSS |  |  | 2159
| X2H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Westbrook JCT | ON_WTB_JCT | NPIF Kingston JCT | ON_NPK_JCT |  |  | 2160
| X2H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | NPIF Kingston JCT | ON_NPK_JCT | NPIF Kingston GS | ON_NPK_GSS |  |  | 2161
| X2H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | NPIF Kingston JCT | ON_NPK_JCT | Lafarge JCT | ON_LAF_JCT |  |  | 2162
| X2H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Lafarge JCT | ON_LAF_JCT | Lafarge Bath TS | ON_LFB_ISS |  |  | 2163
| X2H | HONI | Ontario | 1 | ac | 5 | 3.0864 | 230 | 2.4 | 3 | [5 empty] | 402 | 435 | Lafarge JCT | ON_LAF_JCT | Lennox TS | ON_LEN_TSS |  |  | 2164
| X2Y | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Chenaux TS | ON_CHX_TSS | Chenaux JCT | ON_CHX_JCT |  |  | 2166
| X2Y | HONI | Ontario | 1 | ac | 10 | 6.1728 | 115 | 4.1714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cobden TS | ON_CBD_DSS | Haley JCT | ON_HLY_JCT |  |  | 2167
| X2Y | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Haley JCT | ON_HLY_JCT | Magellan Aerospace JCT | ON_MGA_JCT |  |  | 2168
| X2Y | HONI | Ontario | 1 | ac | 5 | 3.0864 | 115 | 2.0857 | 3 | [5 empty] | 98.4491 | 108.4016 | Magellan Aerospace JCT | ON_MGA_JCT | Magellan Aerospace TS | ON_MGA_ISS |  |  | 2169
| X2Y | HONI | Ontario | 1 | ac | 3 | 1.8519 | 115 | 1.2514 | 3 | [5 empty] | 98.4491 | 108.4016 | Magellan Aerospace JCT | ON_MGA_JCT | Chenaux JCT | ON_CHX_JCT |  |  | 2170
| X2Y | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Pembroke TS | ON_PEM_DSS | Cobden TS | ON_CBD_DSS |  |  | 2171
| X3H | HONI | Ontario | 1 | ac | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Hinchinbrooke SWS | ON_HNB_SWS | Cataraqui TS | ON_CTQ_TSS |  |  | 2172
| X3H | HONI | Ontario | 1 | ac | 13 | 8.0247 | 230 | 6.24 | 3 | [5 empty] | 402 | 435 | Cataraqui TS | ON_CTQ_TSS | Kingston Solar JCT | ON_KSS_JCT |  |  | 2173
| X3H | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Kingston Solar JCT | ON_KSS_JCT | Kingston Solar GS | ON_KSS_GSS |  |  | 2174
| X3H | HONI | Ontario | 1 | ac | 18 | 11.1111 | 230 | 8.64 | 3 | [5 empty] | 402 | 435 | Kingston Solar JCT | ON_KSS_JCT | Lennox TS | ON_LEN_TSS |  |  | 2175
| X4H | HONI | Ontario | 1 | ac | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Hinchinbrooke SWS | ON_HNB_SWS | Cataraqui TS | ON_CTQ_TSS |  |  | 2176
| X4H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Cataraqui TS | ON_CTQ_TSS | Westbrook JCT | ON_WTB_JCT |  |  | 2177
| X4H | HONI | Ontario | 1 | ac | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Westbrook JCT | ON_WTB_JCT | Lennox TS | ON_LEN_TSS |  |  | 2178
| X4H | HONI | Ontario | 1 | ac | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Westbrook JCT | ON_WTB_JCT | Gardiner STR 44 JCT | ON_GAR_JCT |  |  | 2179
| X4H | HONI | Ontario | 2 | ac | 0.1 | 0.061728 | 230 | 0.048 | 3 | [5 empty] | 402 | 435 | Gardiner STR 44 JCT | ON_GAR_JCT | Gardiner TS | ON_GAR_DSS |  |  | 2180
| X503E | HONI | Ontario | 1 | ac | 150 | 92.5926 | 500 | 59.25 | 2.14 | [5 empty] | 1818.9793 | 2300.4738 | Hanmer TS | ON_HNM_TSS | Nobel SWS | ON_NOB_SWS |  |  | 2181
| X503E | HONI | Ontario | 1 | ac | 130 | 80.2469 | 500 | 51.35 | 2.3518 | [5 empty] | 1999.0069 | 2528.1558 | Nobel SWS | ON_NOB_SWS | Essa TS | ON_ESA_TSS |  |  | 2182
| X504E | HONI | Ontario | 1 | ac | 150 | 92.5926 | 500 | 59.25 | 2.14 | [5 empty] | 1818.9793 | 2300.4738 | Hanmer TS | ON_HNM_TSS | Nobel SWS | ON_NOB_SWS |  |  | 2183
| X504E | HONI | Ontario | 1 | ac | 130 | 80.2469 | 500 | 51.35 | 2.3518 | [5 empty] | 1999.0069 | 2528.1558 | Nobel SWS | ON_NOB_SWS | Essa TS | ON_ESA_TSS |  |  | 2184
| X520B | HONI | Ontario | 1 | ac | 170 | 104.9383 | 500 | 67.15 | 1.9704 | [5 empty] | 1674.8614 | 2118.2071 | Lennox TS | ON_LEN_TSS | Bowmanville SWS | ON_BOW_SWS |  |  | 2185
| X521B | HONI | Ontario | 1 | ac | 170 | 104.9383 | 500 | 67.15 | 1.9704 | [5 empty] | 1674.8614 | 2118.2071 | Lennox TS | ON_LEN_TSS | Bowmanville SWS | ON_BOW_SWS |  |  | 2186
| X522A | HONI | Ontario | 1 | ac | 190 | 117.284 | 500 | 75.05 | 1.8311 | [5 empty] | 1556.4026 | 1968.3915 | Lennox TS | ON_LEN_TSS | Hawthorne TS | ON_HWT_TSS |  |  | 2187
| X523A | HONI | Ontario | 1 | ac | 190 | 117.284 | 500 | 75.05 | 1.8311 | [5 empty] | 1556.4026 | 1968.3915 | Lennox TS | ON_LEN_TSS | Hawthorne TS | ON_HWT_TSS |  |  | 2188
| X526B | HONI | Ontario | 1 | ac | 170 | 104.9383 | 500 | 67.15 | 1.9704 | [5 empty] | 1674.8614 | 2118.2071 | Lennox TS | ON_LEN_TSS | Bowmanville SWS | ON_BOW_SWS |  |  | 2189
| X527B | HONI | Ontario | 1 | ac | 170 | 104.9383 | 500 | 67.15 | 1.9704 | [5 empty] | 1674.8614 | 2118.2071 | Lennox TS | ON_LEN_TSS | Bowmanville SWS | ON_BOW_SWS |  |  | 2190
| X534N | HONI | Ontario | 1 | ac | 15 | 9.2593 | 500 | 5.925 | 3 | [5 empty] | 2550 | 3225 | Lennox TS | ON_LEN_TSS | Napanee GS | ON_NAP_GSS |  |  | 2191
| X538N | HONI | Ontario | 1 | ac | 15 | 9.2593 | 500 | 5.925 | 3 | [5 empty] | 2550 | 3225 | Lennox TS | ON_LEN_TSS | Napanee GS | ON_NAP_GSS |  |  | 2192
| X6 | HONI | Ontario | 1 | ac | 0.1 | 0.061728 | 115 | 0.041714 | 3 | [5 empty] | 98.4491 | 108.4016 | Cobden X6 JCT | ON_CBX_JCT | Cobden TS | ON_CBD_DSS |  |  | 2193
| X6 | HONI | Ontario | 1 | ac | 15 | 9.2593 | 115 | 6.2571 | 3 | [5 empty] | 98.4491 | 108.4016 | Cobden X6 JCT | ON_CBX_JCT | Chenaux TS | ON_CHX_TSS |  |  | 2194
| X6 | HONI | Ontario | 1 | ac | 25 | 15.4321 | 115 | 10.4286 | 3 | [5 empty] | 98.4491 | 108.4016 | Pembroke TS | ON_PEM_DSS | Cobden X6 JCT | ON_CBD_JCT |  |  | 2195
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## Nodes
ON | EXISTING SUBSTATIONS
| Node Name | Node Code | Owner | Latitude | Longitude | Operating Region | Other References | Notes
| 93K4-89 JCT | ON_93K_JCT | HONI |  |  | Ontario
| A5RK STR O7 JCT | ON_A5R_JCT | HONI |  |  | Ontario
| A8K-19EO JCT | ON_A19_JCT | HONI |  |  | Ontario
| A8K-47EO JCT | ON_A47_JCT | HONI |  |  | Ontario
| Abit Cons NAN91 JCT | ON_ACS_JCT | HONI |  |  | Ontario
| Abitibi Canyon GS | ON_ABC_GSS | HONI |  |  | Ontario
| Abitibi Canyon JCT #2 | ON_AB2_JCT | HONI |  |  | Ontario
| Abitibi JCT | ON_AB1_JCT | HONI |  |  | Ontario
| Adelaide JCT | ON_ADE_JCT | HONI |  |  | Ontario
| Agimak DS | ON_AGM_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Agimak DS JCT | ON_AGM_JCT | HONI |  |  | Ontario
| Agincourt JCT | ON_AGN_JCT | HONI |  |  | Ontario
| Agincourt TS | ON_AGN_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Aguasabon SWS | ON_AGU_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Ainsworth JCT | ON_AIN_JCT | HONI |  |  | Ontario
| Albion JCT | ON_ALB_JCT | HONI |  |  | Ontario
| Albion TS | ON_ALB_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Alexander GS | ON_ALX_GSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Alexander SWS | ON_ALX_SWS | HONI |  |  | Ontario
| Alford JCT | ON_ALF_JCT | HONI |  |  | Ontario
| Algoma TS | ON_ALG_TSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Allanburg Q30M JCT | ON_ALQ_JCT | HONI |  |  | Ontario
| Allanburg TS | ON_ALL_TSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Allanburg West JCT | ON_ALW_JCT | HONI |  |  | Ontario
| Alliston JCT | ON_ALS_JCT | HONI |  |  | Ontario
| Alliston TS | ON_ALS_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Almonte TS | ON_ALM_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Amaranth JCT | ON_AMA_JCT | HONI |  |  | Ontario
| Amaranth TS | ON_AMA_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Ameristeel Cambridge JCT | ON_AMC_JCT | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Ameristeel Cambridge TS | ON_AMC_ISS | HONI |  |  | Ontario
| Andrews TS | ON_AND_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Angler Switch JCT | ON_ANG_JCT | HONI |  |  | Ontario
| Animki JCT | ON_ANM_JCT | HONI |  |  | Ontario
| Anjigami JCT | ON_ANJ_JCT | HONI |  |  | Ontario
| Anjigami JCT #2 | ON_AN2_JCT | HONI |  |  | Ontario
| Anjigami TS | ON_ANJ_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Ansonville JCT | ON_ANS_JCT | HONI |  |  | Ontario
| Ansonville TS | ON_ANS_TSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| AP Calstock GS | ON_APC_GSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| AP Calstock GS JCT | ON_APC_JCT | HONI |  |  | Ontario
| AP Kapuskasing JCT | ON_APK_JCT | HONI |  |  | Ontario
| AP Nipigon GS | ON_APN_GSS | HONI |  |  | Ontario
| AP Nipigon JCT | ON_APN_JCT | HONI |  |  | Ontario
| AP North Bay JCT | ON_APB_JCT | HONI |  |  | Ontario
| AP Tunis JCT | ON_APT_JCT | HONI |  |  | Ontario
| Applewood JCT | ON_APP_JCT | HONI |  |  | Ontario
| Ardoch DS | ON_ARD_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Ardoch JCT | ON_ARD_JCT | HONI |  |  | Ontario
| Arlanxeo Can Inc JCT | ON_ARX_JCT | HONI |  |  | Ontario
| Arlanxeo Can Inc TS | ON_ARX_ISS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Arlen MTS | ON_ARL_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Arlen MTS JCT | ON_ARL_JCT | HONI |  |  | Ontario
| Armitage TS | ON_ATG_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| Armow GS | ON_ARM_GSS | HONI |  |  | Ontario | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan
| Armow JCT | ON_ARM_JCT | HONI |  |  | Ontario
| Arnprior GS | ON_ARN_GSS | HONI |  |  | Ontario
| Arnprior JCT | ON_ARN_JCT | HONI |  |  | Ontario
| Arnprior TS | ON_ARN_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Ashfield SWS | ON_ASH_SWS | HONI |  |  | Ontario | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan
| ASW Steel JCT | ON_ASW_JCT | HONI |  |  | Ontario
| ASW Steel TS | ON_ASW_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Atikokan TGS | ON_ATK_GSS | HONI |  |  | Ontario
| Atlantic Packaging JCT | ON_ATP_JCT | HONI |  |  | Ontario
| Atlantic Packaging TS | ON_ATP_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Aubrey Falls GS | ON_AUB_GSS | HONI |  |  | Ontario
| Aubrey Falls JCT | ON_AUB_JCT | HONI |  |  | Ontario
| AV Terrace Bay JCT | ON_AVT_JCT | HONI |  |  | Ontario
| AV Terrace Bay TS | ON_AVT_ISS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Aylmer TS | ON_AYL_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| B23C H26C Tie JCT | ON_B23_JCT | HONI |  |  | Ontario
| B5D-B31L SWS JCT | ON_B5D_JCT | HONI |  |  | Ontario
| Baldwin JCT | ON_BDW_JCT | HONI |  |  | Ontario
| Balfour JCT | ON_BAL_JCT | HONI |  |  | Ontario
| Balmer JCT | ON_BLM_JCT | HONI |  |  | Ontario
| Bannockburn JCT | ON_BNK_JCT | HONI |  |  | Ontario
| Barrett Chute JCT | ON_BTC_JCT | HONI |  |  | Ontario
| Barrett Chute SWS | ON_BTC_SWS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Barrie TS | ON_BAR_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Barryvale Rd JCT | ON_BRV_JCT | HONI |  |  | Ontario
| Bartlett JCT | ON_BTL_JCT | HONI |  |  | Ontario
| Barwick JCT | ON_BWK_JCT | HONI |  |  | Ontario
| Barwick TS | ON_BWK_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Basin TS | ON_BSN_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Batchawana TS | ON_BWA_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Bathurst JCT | ON_BTH_JCT | HONI |  |  | Ontario
| Bathurst TS | ON_BTH_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Battersea DS | ON_BTT_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Bayview JCT | ON_BYV_JCT | HONI |  |  | Ontario
| Beach JCT | ON_BCH_JCT | HONI |  |  | Ontario
| Beach Road JCT | ON_BCR_JCT | HONI |  |  | Ontario
| Beach TS | ON_BCH_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Beamsville TS | ON_BMS_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Beardmore DS #2 | ON_BRD_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Beardmore JCT | ON_BRD_JCT | HONI |  |  | Ontario
| Beaver JCT | ON_BVR_JCT | HONI |  |  | Ontario
| Beaverton JCT | ON_BVT_JCT | HONI |  |  | Ontario
| Beaverton TS | ON_BVT_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Beck #1 Q2AH JCT | ON_BKQ_JCT | HONI |  |  | Ontario
| Beck #1 SWS | ON_BK1_SWS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Beck #2 TS | ON_BK2_TSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Beck Pump Storage GS | ON_BKP_GSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Bell Creek JCT | ON_BLC_JCT | HONI |  |  | Ontario
| Bell Creek TS | ON_BLC_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Belle River GS | ON_BLR_GSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Belle River JCT | ON_BLR_JCT | HONI |  |  | Ontario
| Belle River JCT #2 | ON_BL2_JCT | HONI |  |  | Ontario
| Belle River TS | ON_BLR_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Belleville TS | ON_BLV_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Bellman JCT | ON_BLL_JCT | HONI |  |  | Ontario
| Bermondsey JCT | ON_BMD_JCT | HONI |  |  | Ontario
| Bermondsey TS | ON_BMD_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| BF Goodrich JCT | ON_BFG_JCT | HONI |  |  | Ontario
| Biddulph JCT | ON_BID_JCT | HONI |  |  | Ontario
| Bilberry Creek JCT | ON_BBC_JCT | HONI |  |  | Ontario
| Bilberry Creek TS | ON_BBC_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Billings JCT | ON_BIL_JCT | HONI |  |  | Ontario
| Birch JCT | ON_BIR_JCT | HONI |  |  | Ontario
| Birch TS | ON_BIR_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Birmingham TS | ON_BRM_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Black River JCT | ON_BKR_JCT | HONI |  |  | Ontario
| Blackburn JCT | ON_BLB_JCT | HONI |  |  | Ontario
| Blezard Valley JCT | ON_BLZ_JCT | HONI |  |  | Ontario
| Blind River TS | ON_BLD_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Blind River TS JCT | ON_BLD_JCT | HONI |  |  | Ontario
| Bloomsburg DS | ON_BLO_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Bloomsburg JCT | ON_BLO_JCT | HONI |  |  | Ontario
| Bloor Street JCT | ON_BLS_JCT | HONI |  |  | Ontario
| Borromee JCT | ON_BOR_JCT | HONI |  |  | Ontario
| Bostwick Road JCT | ON_BOS_JCT | HONI |  |  | Ontario
| Bowmanville SWS | ON_BOW_SWS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Bracebridge JCT | ON_BRA_JCT | HONI |  |  | Ontario
| Bracebridge TS | ON_BRA_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Bramalea TS | ON_BML_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Brant JCT | ON_BRT_JCT | HONI |  |  | Ontario
| Brant TS | ON_BRT_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Brantford TS | ON_BRF_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Bridgman JCT | ON_BRG_JCT | HONI |  |  | Ontario
| Bridgman TS | ON_BRG_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Bridlewood JCT | ON_BRI_JCT | HONI |  |  | Ontario
| Bridlewood MTS | ON_BRI_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Brighton Interface JCT | ON_BTN_JCT | HONI |  |  | Ontario
| Brockville Chem. JCT | ON_BRC_JCT | HONI |  |  | Ontario
| Brockville TS | ON_BRO_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Bronte TS | ON_BRN_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Brookside OPF | ON_BRK_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082) | OPF = Oil pressurization feeder
| Brown Hill TS | ON_BRW_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Bruce A TS | ON_BCA_TSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Bruce B SWS | ON_BCB_SWS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Bruce HWP B TS | ON_BCW_ISS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Bruce JCT | ON_BCC_JCT | HONI |  |  | Ontario
| Buchanan JCT | ON_BUC_JCT | HONI |  |  | Ontario
| Buchanan TS | ON_BUC_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Bunting TS | ON_BUN_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Burleigh DS | ON_BUL_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Burleigh JCT | ON_BUL_JCT | HONI |  |  | Ontario
| Burlington TS | ON_BUR_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Buttonville TS | ON_BUT_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Caistor JCT | ON_CST_JCT | HONI |  |  | Ontario
| Caland Ore JCT | ON_CLO_JCT | HONI |  |  | Ontario
| Calder JCT | ON_CLD_JCT | HONI |  |  | Ontario
| Calder TS | ON_CLD_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Caledonia JCT | ON_CAL_JCT | HONI |  |  | Ontario
| Caledonia Q35M JCT | ON_CAQ_JCT | HONI |  |  | Ontario
| Caledonia TS | ON_CAL_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Calstock DS | ON_CSK_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Cambridge #1 JCT | ON_CMB_JCT | HONI |  |  | Ontario
| Cameron Falls GS | ON_CAM_GSS | HONI |  |  | Ontario
| Cameron Falls JCT | ON_CAM_JCT | HONI |  |  | Ontario
| Camp Lake JCT | ON_CPL_JCT | HONI |  |  | Ontario
| Campbell TS | ON_CBL_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG)
| Canal JCT | ON_CNL_JCT | HONI |  |  | Ontario
| Cardiff JCT | ON_CDF_JCT | HONI |  |  | Ontario
| Cardiff TS | ON_CDF_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Cardinal JCT | ON_CDL_JCT | HONI |  |  | Ontario
| Cardinal Power GS | ON_CDP_GSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Caribou Falls GS | ON_CRF_GSS | HONI |  |  | Ontario
| Carlaw TS | ON_CLW_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Carling TS | ON_CAR_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Carlton TS | ON_CLT_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Carluke JCT | ON_CLK_JCT | HONI |  |  | Ontario
| Carmeuse Lime JCT | ON_CML_JCT | HONI |  |  | Ontario
| Carmichael Falls JCT | ON_CMF_JCT | HONI |  |  | Ontario
| Casco JCT | ON_CSC_JCT | HONI |  |  | Ontario
| Cassburn JCT | ON_CSB_JCT | HONI |  |  | Ontario
| Cassels 2 JCT | ON_CS2_JCT | HONI |  |  | Ontario
| Cassels JCT | ON_CSS_JCT | HONI |  |  | Ontario
| Cat Lake MTS | ON_CTL_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Cataraqui TS | ON_CTQ_TSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Cavanagh MTS | ON_CVN_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Cecil TS | ON_CEC_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Cedar TS | ON_CED_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Centralia TS | ON_CEN_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Centre Point JCT | ON_CTP_JCT | HONI |  |  | Ontario
| Centre Point MTS | ON_CTP_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Chalk River TS | ON_CKR_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Chapleau DS | ON_CHP_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Chapleau JCT | ON_CHP_JCT | HONI |  |  | Ontario
| Chapleau MTS | ON_CHM_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Charles TS | ON_CHL_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Chatham SWS | ON_CHT_SWS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Chats Falls SWS | ON_CHF_SWS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Chenaux JCT | ON_CHX_JCT | HONI |  |  | Ontario
| Chenaux TS | ON_CHX_TSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Cherry JCT | ON_CHR_JCT | HONI |  |  | Ontario
| Cherrywood TS | ON_CHW_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| Chesterville N. JCT | ON_CLN_JCT | HONI |  |  | Ontario
| Chesterville S. JCT | ON_CLS_JCT | HONI |  |  | Ontario
| Chesterville TS | ON_CHS_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Chrysler WAP MTS | ON_CHY_ISS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Churchill Meadows JCT | ON_CHU_JCT | HONI |  |  | Ontario
| Churchill Meadows TS | ON_CHU_ISS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| City View JCT | ON_CTV_JCT | HONI |  |  | Ontario
| Claireville TS | ON_CLV_TSS | HONI | 43.7639 | -79.6149 | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Clarabelle JCT | ON_CLA_JCT | HONI |  |  | Ontario
| Clarabelle TS | ON_CLA_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Clarence DS | ON_CLC_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Clarington JCT | ON_CLG_JCT | HONI |  |  | Ontario
| Clarington TS | ON_CLG_TSS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| Clarke TS | ON_CKE_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Clearwater Bay DS | ON_CWB_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Clergue TS | ON_CGU_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Cobden JCT | ON_CBD_JCT | HONI |  |  | Ontario
| Cobden TS | ON_CBD_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Cobden X6 JCT | ON_CBX_JCT | HONI |  |  | Ontario
| Cochrane West DS | ON_CCW_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Cochrane West JCT | ON_CCW_JCT | HONI |  |  | Ontario
| Cochrane West MTS | ON_COC_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Columbus JCT | ON_CLB_JCT | HONI |  |  | Ontario
| Comber WF GS | ON_COM_GSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Comber WF JCT | ON_COM_JCT | HONI |  |  | Ontario
| Commanda JCT | ON_CMM_JCT | HONI |  |  | Ontario
| Commerce Way JCT | ON_CMC_JCT | HONI |  |  | Ontario
| Commerce Way TS | ON_CMC_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Confederation Rd JCT | ON_CON_JCT | HONI |  |  | Ontario
| Coniston TS | ON_CTN_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Conmee JCT | ON_CNM_JCT | HONI |  |  | Ontario
| Constance DS | ON_CNC_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Cooksville TS | ON_CKV_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Cooper's Falls JCT | ON_COF_JCT | HONI |  |  | Ontario
| Copeland MTS | ON_COP_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Copper Cliff JCT | ON_CFF_JCT | HONI |  |  | Ontario
| Cowal JCT | ON_COW_JCT | HONI |  |  | Ontario
| Craig DS | ON_CRG_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Craig JCT | ON_CRG_JCT | HONI |  |  | Ontario
| Cranberry JCT | ON_CRN_JCT | HONI |  |  | Ontario
| Crawford JCT | ON_CRW_JCT | HONI |  |  | Ontario
| Crawford TS | ON_CRW_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Creighton JCT | ON_CRE_JCT | HONI |  |  | Ontario
| Crosby JCT | ON_CRO_JCT | HONI |  |  | Ontario
| Crosby TS | ON_CRO_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Crossline JCT | ON_CSL_JCT | HONI |  |  | Ontario
| Crow River DS | ON_CRR_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Crowland JCT | ON_CRL_JCT | HONI |  |  | Ontario
| Crowland TS | ON_CRL_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Crystal Falls SWS | ON_CRY_SWS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Crystal Falls TS | ON_CRY_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Cumberland DS | ON_CUS_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Cumberland DS JCT | ON_CUS_JCT | HONI |  |  | Ontario
| Cumberland JCT | ON_CUM_JCT | HONI |  |  | Ontario
| Cumberland TS | ON_CUM_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Cutler JCT | ON_CUT_JCT | HONI |  |  | Ontario
| Cyrville JCT | ON_CYV_JCT | HONI |  |  | Ontario
| Cyrville MTS | ON_CYV_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Cyrville Rd JCT | ON_CYR_JCT | HONI |  |  | Ontario
| Cytec Welland TS | ON_CYT_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| D2L STR 409 JCT | ON_D2L_JCT | HONI |  |  | Ontario
| DA Watson TS | ON_DAW_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Dale JCT | ON_DAL_JCT | HONI |  |  | Ontario
| Dane JCT | ON_DAN_JCT | HONI |  |  | Ontario
| DeCew Falls SWS | ON_DEC_SWS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Deep River DS | ON_DPR_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Denison Mines TS | ON_DNM_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Des Joachims DS | ON_DEJ_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Des Joachims JCT | ON_DEJ_JCT | HONI |  |  | Ontario
| Des Joachims TS | ON_DEJ_TSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Detweiler JCT | ON_DET_JCT | HONI |  |  | Ontario
| Detweiler TS | ON_DET_TSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Devizes JCT | ON_DVZ_JCT | HONI |  |  | Ontario
| Didsbury Road JCT | ON_DID_JCT | HONI |  |  | Ontario
| Dillon RWEC GS | ON_DIL_GSS | HONI |  |  | Ontario
| Dillon RWEC GS JCT | ON_DIL_JCT | HONI |  |  | Ontario
| Dobbin DS | ON_DBN_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Dobbin TS | ON_DOB_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Dofasco Bay Front TS | ON_DBF_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Dofasco Kenilworth TS | ON_DKW_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Dome Site JCT | ON_DOM_JCT | HONI |  |  | Ontario
| Dominion Drive DS | ON_DMD_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Domtar Dryden TS | ON_DTD_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Don Fleet JCT | ON_DFL_JCT | HONI |  |  | Ontario
| Donaldson Cres JCT | ON_DNC_JCT | HONI |  |  | Ontario
| Douglas Point TS | ON_DGP_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Dresser JCT | ON_DRS_JCT | HONI |  |  | Ontario
| Drummond Road JCT | ON_DRU_JCT | HONI |  |  | Ontario
| Dryden JCT B | ON_DRY_JCT | HONI |  |  | Ontario
| Dryden TS | ON_DRY_TSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Duart JCT | ON_DUA_JCT | HONI |  |  | Ontario
| Duart TS | ON_DUA_DSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Dufferin JCT | ON_DUF_JCT | HONI |  |  | Ontario
| Dufferin TS | ON_DUF_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Duffin JCT | ON_DFN_JCT | HONI |  |  | Ontario
| Dundas #2 JCT | ON_DD2_JCT | HONI |  |  | Ontario
| Dundas #2 TS | ON_DD2_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Dundas JCT | ON_DDS_JCT | HONI |  |  | Ontario
| Dundas Street JCT | ON_DST_JCT | HONI |  |  | Ontario
| Dundas TS | ON_DDS_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Dunnville TS | ON_DNV_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Duplex TS | ON_DPX_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Dupont JCT | ON_DUP_JCT | HONI |  |  | Ontario
| Dymond TS | ON_DYM_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Dyno Nobel TS | ON_DYN_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Eacom Nairn Centre JCT | ON_EAC_JCT | HONI |  |  | Ontario
| Eacom Nairn Centre TS | ON_EAC_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Ear Falls TS | ON_EAF_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| East Lake St. Clair GS | ON_ESC_GSS | HONI |  |  | Ontario
| East Lake St. Clair JCT | ON_ESC_JCT | HONI |  |  | Ontario
| East Windsor GS | ON_EWI_GSS | HONI |  |  | Ontario
| Easton JCT | ON_EAS_JCT | HONI |  |  | Ontario
| Easton Yule JCT | ON_EAY_JCT | HONI |  |  | Ontario
| Echo Bay Aquarius JCT | ON_ECH_JCT | HONI |  |  | Ontario
| Echo River DS | ON_ERV_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Echo River JCT | ON_ERV_JCT | HONI |  |  | Ontario
| Ecstall JCT | ON_ECS_JCT | HONI |  |  | Ontario
| Eddy Tap A JCT | ON_EDA_JCT | HONI |  |  | Ontario
| Eddy Tap JCT | ON_EDT_JCT | HONI |  |  | Ontario
| Edgeware JCT | ON_EDG_JCT | HONI |  |  | Ontario
| Edgeware TS | ON_EDG_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Egmondville SWS | ON_EGM_SWS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Elgin JCT | ON_ELG_JCT | HONI |  |  | Ontario
| Elgin TS | ON_ELG_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Elk Lake JCT | ON_ELK_JCT | HONI |  |  | Ontario
| Ellesmere JCT | ON_ELM_JCT | HONI |  |  | Ontario
| Ellesmere TS | ON_ELM_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Elliot Lake JCT | ON_ELL_JCT | HONI |  |  | Ontario
| Elliot Lake TS | ON_ELL_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Ellwood JCT | ON_ELD_JCT | HONI |  |  | Ontario
| Ellwood MTS | ON_ELW_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Ellwood MTS JCT | ON_ELW_JCT | HONI |  |  | Ontario
| Elmira TS | ON_EMA_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Enbridge Bryanston TS | ON_ENB_ISS | HONI |  |  | Ontario | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan
| Enbridge Keyser TS | ON_ENK_ISS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Enbridge PL Card TS | ON_ENC_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Enbridge PL Hilt TS | ON_ENH_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Enbridge Westover N TS | ON_EWN_ISS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Enbridge Westover S TS | ON_EWS_ISS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Energy Inc(Cam) MTS#1 | ON_ENI_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Enfield TS | ON_ENF_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan | In-service 2020
| Ennisbrook JCT | ON_ENN_JCT | HONI |  |  | Ontario
| Erco JCT | ON_ERC_JCT | HONI |  |  | Ontario
| ERG Resources JCT | ON_ERG_JCT | HONI |  |  | Ontario
| ERG Resources TS | ON_ERG_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Erieau WF GS | ON_ERI_GSS | HONI |  |  | Ontario
| Erieau WF JCT | ON_ERI_JCT | HONI |  |  | Ontario
| Erindale JCT | ON_ERD_JCT | HONI |  |  | Ontario
| Erindale TS | ON_ERD_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Espanola A JCT | ON_EPA_JCT | HONI |  |  | Ontario
| Espanola GS | ON_ESP_GSS | HONI |  |  | Ontario
| Espanola JCT | ON_ESP_JCT | HONI |  |  | Ontario
| Espanola TS | ON_ESP_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Esplanade TS | ON_EPL_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Essa TS | ON_ESA_TSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Essex TS | ON_ESX_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| ESWF GS | ON_ESW_GSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report London
| ESWF JCT | ON_ESW_JCT | HONI |  |  | Ontario
| Ethel Lake JCT | ON_ETH_JCT | HONI |  |  | Ontario
| Eton DS | ON_ETO_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Eton JCT | ON_ETO_JCT | HONI |  |  | Ontario
| Etruscan Enterprise TS | ON_ETR_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Etruscan JCT | ON_ETR_JCT | HONI |  |  | Ontario
| Everett JCT | ON_EVT_JCT | HONI |  |  | Ontario
| Everett TS | ON_EVT_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Evergreen SWS | ON_EVG_SWS | HONI |  |  | Ontario | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan
| Extender Min. JCT | ON_EXT_JCT | HONI |  |  | Ontario
| Fairbank TS | ON_FBK_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Fairchild TS | ON_FCD_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Falconbridge 61 JCT | ON_FL6_JCT | HONI |  |  | Ontario
| Falconbridge JCT | ON_FLB_JCT | HONI |  |  | Ontario
| Falconbridge T2R TS | ON_FLB_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Sudbury Algoma
| Fallowfield JCT | ON_FLF_JCT | HONI |  |  | Ontario
| Fallowfield MTS | ON_FLF_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Fauquier DS | ON_FAU_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Fauquier JCT | ON_FAU_JCT | HONI |  |  | Ontario
| Fergus JCT | ON_FGS_JCT | HONI |  |  | Ontario
| Fergus TS | ON_FGS_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Festival MTS #1 | ON_FST_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Festival MTS #1 JCT | ON_FST_JCT | HONI |  |  | Ontario
| Fibre JCT | ON_FBR_JCT | HONI |  |  | Ontario
| Finch JCT | ON_FIN_JCT | HONI |  |  | Ontario
| Finch TS | ON_FIN_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Fitzroy JCT | ON_FTZ_JCT | HONI |  |  | Ontario
| Flakeboard TS | ON_FKB_ISS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Ford Annex MTS | ON_FDA_ISS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Ford Essex JCT | ON_FDE_JCT | HONI |  |  | Ontario
| Ford Essex TS | ON_FDE_ISS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Ford JCT | ON_FRD_JCT | HONI |  |  | Ontario
| Ford Oakville TS | ON_FDO_ISS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Ford Windsor MTS | ON_FDW_ISS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Forest Jura DS | ON_FRJ_DSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Forest Lea DS | ON_FRL_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Forest Lea JCT | ON_FRL_JCT | HONI |  |  | Ontario
| Forgie JCT | ON_FRG_JCT | HONI |  |  | Ontario
| Fort Frances JCT | ON_FRF_JCT | HONI |  |  | Ontario
| Fort Frances MTS | ON_FRM_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Fort Frances TS | ON_FRF_TSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Fort William TS | ON_FRW_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Fournier JCT | ON_FOU_JCT | HONI |  |  | Ontario
| Freeport SWS | ON_FPT_SWS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Frontenac TS | ON_FRO_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| G.M. St. Cath TS | ON_GMS_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| G.M. Windsor MTS | ON_GMW_ISS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Gage JCT | ON_GAG_JCT | HONI |  |  | Ontario
| Gage TS | ON_GAG_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Galetta JCT | ON_GAL_JCT | HONI |  |  | Ontario
| Galt JCT | ON_GTT_JCT | HONI |  |  | Ontario
| Galt North JCT | ON_GTN_JCT | HONI |  |  | Ontario
| Galt South JCT | ON_GTS_JCT | HONI |  |  | Ontario
| Galt TS | ON_GTT_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Gamble H9A JCT | ON_GAM_JCT | HONI |  |  | Ontario
| Gardiner STR 44 JCT | ON_GAR_JCT | HONI |  |  | Ontario
| Gardiner TS | ON_GAR_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Gartshore GS | ON_GSO_GSS | HONI |  |  | Ontario
| Gartshore TS | ON_GSO_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Gerdau A. Whitby TS | ON_GAW_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Gerrard JCT | ON_GER_JCT | HONI |  |  | Ontario
| Gerrard TS | ON_GER_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Gervais JCT | ON_GRV_JCT | HONI |  |  | Ontario
| Gibson JCT | ON_GIB_JCT | HONI |  |  | Ontario
| Glanford JCT | ON_GLF_JCT | HONI |  |  | Ontario
| Glendale JCT | ON_GND_JCT | HONI |  |  | Ontario
| Glendale TS | ON_GND_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Glengrove TS | ON_GLG_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Glenorchy JCT | ON_GLO_JCT | HONI |  |  | Ontario
| Glenorchy MTS #1 | ON_GLO_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Goderich TS | ON_GOD_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Gold Centre JCT | ON_GLC_JCT | HONI |  |  | Ontario
| Golden Patricia JCT | ON_GLP_JCT | HONI |  |  | Ontario
| Goreway JCT | ON_GRW_JCT | HONI |  |  | Ontario
| Goreway TS | ON_GRW_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Gormley JCT | ON_GML_JCT | HONI |  |  | Ontario
| Gosfield GS | ON_GOS_GSS | HONI |  |  | Ontario
| Gosfield GS JCT | ON_GOS_JCT | HONI |  |  | Ontario
| Goshen GS | ON_GSH_GSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Goshen JCT | ON_GSH_JCT | HONI |  |  | Ontario
| Goulais Bay TS | ON_GLB_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Goulais JCT | ON_GLA_JCT | HONI |  |  | Ontario
| Goulais SWS | ON_GLA_SWS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report East Lake Superior Region
| Grand Bend East DS | ON_GRB_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Grand Bend East JCT | ON_GRB_JCT | HONI |  |  | Ontario
| Grand GS | ON_GRD_GSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Grand JCT | ON_GRD_JCT | HONI |  |  | Ontario
| Grant JCT | ON_GRT_JCT | HONI |  |  | Ontario
| Greely DS | ON_GRE_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Greely JCT | ON_GRE_JCT | HONI |  |  | Ontario
| Greenfield Energy GS | ON_GRF_GSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Greenfield Interface JCT | ON_GRF_JCT | HONI |  |  | Ontario
| Greenwater Pr Pk JCT | ON_GWP_JCT | HONI |  |  | Ontario
| Greenwich WF GS | ON_GRH_GSS | HONI |  |  | Ontario | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum. Ontario 230 kV East-West Tie
| Greenwich WF GS JCT | ON_GRH_JCT | HONI |  |  | Ontario
| Gretna JCT | ON_GNA_JCT | HONI |  |  | Ontario
| GSPC JCT | ON_GSP_JCT | HONI |  |  | Ontario
| Guelph North JCT | ON_GUE_JCT | HONI |  |  | Ontario
| Gull Lake North JCT | ON_GLN_JCT | HONI |  |  | Ontario
| Gull Lake South JCT | ON_GLS_JCT | HONI |  |  | Ontario
| GV3 WF GS | ON_GV3_GSS | HONI |  |  | Ontario
| GV3 WF JCT | ON_GV3_JCT | HONI |  |  | Ontario
| H2O Power Calm Lake GS | ON_H2C_GSS | HONI |  |  | Ontario
| H2O Power Fort Frances GS | ON_H2F_GSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| H2O Power Sturgeon Falls GS | ON_H2S_GSS | HONI |  |  | Ontario
| H9K STR 127A JCT | ON_H9K_JCT | HONI |  |  | Ontario
| Haig JCT | ON_HAI_JCT | HONI |  |  | Ontario
| Haley JCT | ON_HLY_JCT | HONI |  |  | Ontario
| Halton Hills GS | ON_HHL_GSS | HONI |  |  | Ontario
| Halton Hills MTS | ON_HHL_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Halton TS | ON_HLT_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Hanlan JCT | ON_HLA_JCT | HONI |  |  | Ontario
| Hanlon JCT | ON_HLO_JCT | HONI |  |  | Ontario
| Hanlon TS | ON_HLO_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Hanmer TS | ON_HNM_TSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Hannon JCT | ON_HNN_JCT | HONI |  |  | Ontario
| Hanover TS | ON_HNV_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Harmon GS | ON_HRJ_GSS | HONI |  |  | Ontario
| Harmon JCT | ON_HRJ_JCT | HONI |  |  | Ontario
| Harper's JCT | ON_HRP_JCT | HONI |  |  | Ontario
| Harris GS | ON_HRS_GSS | HONI |  |  | Ontario
| Harrowsmith DS | ON_HRR_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Harrowsmith JCT | ON_HRR_JCT | HONI |  |  | Ontario
| Hartford JCT | ON_HRT_JCT | HONI |  |  | Ontario
| Havelock TS | ON_HVL_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Hawkesbury MTS #1 | ON_HWK_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Hawthorne TS | ON_HWT_TSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Hearn SWS | ON_HEA_SWS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Hearst TS | ON_HST_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Hemlo Mine JCT | ON_HML_JCT | HONI |  |  | Ontario
| Herridge Lake DS | ON_HRL_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Herridge Lake JCT | ON_HRL_JCT | HONI |  |  | Ontario
| Heyden JCT | ON_HYD_JCT | HONI |  |  | Ontario
| Heyden SWS | ON_HYD_SWS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Highbury TS | ON_HIG_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Hilton JCT | ON_HIL_JCT | HONI |  |  | Ontario
| Hinchey TS | ON_HIN_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Hinchinbrooke DS | ON_HNB_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Hinchinbrooke SWS | ON_HNB_SWS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Hogg GS | ON_HOG_GSS | HONI |  |  | Ontario
| Holland JCT | ON_HLD_JCT | HONI |  |  | Ontario
| Holland Marsh JCT | ON_HLM_JCT | HONI |  |  | Ontario
| Holland Road JCT | ON_HLR_JCT | HONI |  |  | Ontario
| Holland TS | ON_HLD_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Hollingsworth TS | ON_HGW_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Holloway Holt JCT | ON_HLH_JCT | HONI |  |  | Ontario
| Hooper's JCT | ON_HOO_JCT | HONI |  |  | Ontario
| Hornby JCT | ON_HBY_JCT | HONI |  |  | Ontario
| Horner TS | ON_HOR_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Horning JCT | ON_HNG_JCT | HONI |  |  | Ontario
| Horning Mountain JCT | ON_HGM_JCT | HONI |  |  | Ontario
| Horning TS | ON_HNG_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Hoyle DS | ON_HOY_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Hoyle JCT | ON_HOY_JCT | HONI |  |  | Ontario
| Hoyle Pond Site JCT | ON_HPS_JCT | HONI |  |  | Ontario
| Hunta H9K JCT | ON_HHK_JCT | HONI |  |  | Ontario
| Hunta JCT | ON_HTA_JCT | HONI |  |  | Ontario
| Hunta SWS | ON_HTA_SWS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Hurontario SWS | ON_HRN_SWS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Hurricane JCT | ON_HRC_JCT | HONI |  |  | Ontario
| Hwy #11 JCT | ON_H11_JCT | HONI |  |  | Ontario
| Hwy 634 JCT | ON_H63_JCT | HONI |  |  | Ontario
| IBM Markham JCT | ON_IBM_JCT | HONI |  |  | Ontario
| IBM Markham TS | ON_IBM_ISS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Ignace DS JCT | ON_IGD_JCT | HONI |  |  | Ontario
| Ignace JCT | ON_IGN_JCT | HONI |  |  | Ontario
| Imperial Oil Nanticoke JCT | ON_ION_JCT | HONI |  |  | Ontario
| Imperial Oil TS | ON_IMP_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Indian Chute JCT | ON_INC_JCT | HONI |  |  | Ontario
| Ingersoll JCT | ON_ING_JCT | HONI |  |  | Ontario
| Ingersoll TS | ON_ING_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| INT Bunce Creek | XX_ONUS2_INT | ON-US Border | 42.9234 | -82.4564 | Ontario
| INT Massena Cornwall | XX_ONUS6_INT | ON-US Border | 45.0047 | -74.7858 | Ontario
| INT Minnesota | XX_ONUS1_INT | ON-US Border | 48.6086 | -93.4032 | Ontario
| INT Niagara | XX_ONUS5_INT | ON-US Border | 43.1372 | -79.0458 | Ontario
| INT Peace Bridge | XX_ONUS7_INT | ON-US Border | 42.9099 | -78.906 | Ontario
| INT St. Clair | XX_ONUS3_INT | ON-US Border | 42.79 | -82.4741 | Ontario
| INT Waterman | XX_ONUS4_INT | ON-US Border | 42.2923 | -83.0946 | Ontario
| Invista JCT | ON_INV_JCT | HONI |  |  | Ontario
| IPPL Smithville TS | ON_SMV_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| IPT Beauharnois | PP_ONQB1_IPT | ON-QB Border | 45.2142 | -74.3558 | Ontario
| IPT Chats Falls | PP_ONQB4_IPT | ON-QB Border | 45.5169 | -76.2104 | Ontario
| IPT Chenaux | PP_ONQB5_IPT | ON-QB Border | 45.6314 | -76.682 | Ontario
| IPT Dymond | PP_ONQB7_IPT | ON-QB Border | 47.6304 | -79.5176 | Ontario
| IPT Kipawa | PP_ONQB6_IPT | ON-QB Border | 46.3824 | -78.7273 | Ontario
| IPT Masson | PP_ONQB3_IPT | ON-QB Border | 45.5206 | -75.4229 | Ontario
| IPT Outaouais | PP_ONQB2_IPT | ON-QB Border | 45.5206 | -75.4229 | Ontario
| IPT Seven Sisters | PP_ONMB1_IPT | ON-MB Border | 49.908 | -95.1529 | Ontario
| IPT Whiteshell | PP_ONMB2_IPT | ON-MB Border | 49.7886 | -95.152 | Ontario
| Iroq Falls 115 JCT | ON_IRF_JCT | HONI |  |  | Ontario
| Iroquois Falls DS | ON_IQF_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Iroquois Fls DS JCT | ON_IQF_JCT | HONI |  |  | Ontario
| Island Falls GS | ON_ISF_GSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Island Falls JCT | ON_ISF_JCT | HONI |  |  | Ontario
| Ivaco TS | ON_IVO_ISS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| James Street JCT | ON_JMS_JCT | HONI |  |  | Ontario
| Jarvis TS | ON_JRV_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Jasper DS | ON_JSP_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| JBL JCT | ON_JBL_JCT | HONI |  |  | Ontario
| JBL SWS | ON_JBL_SWS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Jefferson JCT | ON_JFF_JCT | HONI |  |  | Ontario
| Jellicoe DS #3 | ON_JLL_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Jellicoe DS #3 JCT | ON_JLL_JCT | HONI |  |  | Ontario
| Jim Yarrow MTS | ON_JMY_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| John TS | ON_JON_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| K2 Wind GS | ON_K2W_GSS | HONI |  |  | Ontario
| K3D-10 SW JCT | ON_K3D_JCT | HONI |  |  | Ontario
| K6F-10 SW JCT | ON_K6F_JCT | HONI |  |  | Ontario
| Kalar JCT | ON_KLR_JCT | HONI |  |  | Ontario
| Kalar MTS | ON_KLR_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Kam Kotia DS | ON_KAM_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Kanata MTS #1 | ON_KAN_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Kapuskasing R JCT | ON_KAP_JCT | HONI |  |  | Ontario
| Kapuskasing TS | ON_KAP_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Karn TS | ON_KRN_TSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report London
| Kashabowie JCT | ON_KSH_JCT | HONI |  |  | Ontario
| Keewatin DS | ON_KEE_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Keewatin JCT | ON_KEE_JCT | HONI |  |  | Ontario
| Keith TS | ON_KEI_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Kenilworth TS | ON_KNL_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Kenora DS | ON_KNO_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Kenora MTS | ON_KNM_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Kenora MTS JCT | ON_KNM_JCT | HONI |  |  | Ontario
| Kenora TS | ON_KNO_TSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Kent JCT | ON_KNT_JCT | HONI |  |  | Ontario
| Kent TS | ON_KNT_DSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| KEPA Wind Farm JCT | ON_KEP_JCT | HONI |  |  | Ontario
| Kerwood JCT | ON_KER_JCT | HONI |  |  | Ontario
| Kettle Creek JCT | ON_KET_JCT | HONI |  |  | Ontario
| Kidd Contractor TS | ON_KDC_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Kidd Creek Mine JCT | ON_KCM_JCT | HONI |  |  | Ontario
| Kidd Metsite TS | ON_KMT_ISS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Kidd Minesite TS | ON_KMN_ISS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Kidd Zinc Refinery TS | ON_KDZ_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Kimball JCT | ON_KIM_JCT | HONI |  |  | Ontario
| King Edward TS | ON_KNE_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Kingston Solar GS | ON_KSS_GSS | HONI |  |  | Ontario
| Kingston Solar JCT | ON_KSS_JCT | HONI |  |  | Ontario
| Kingsville TS | ON_KSV_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Kipling 2 GS | ON_KPG2_GSS | HONI |  |  | Ontario
| Kipling GS | ON_KPG_GSS | HONI |  |  | Ontario
| Kipling JCT | ON_KPG_JCT | HONI |  |  | Ontario
| Kirkland Lake TS | ON_KLL_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Kirkton JCT | ON_KRK_JCT | HONI |  |  | Ontario
| Kitchener #1&4 JCT | ON_KJ1_JCT | HONI |  |  | Ontario
| Kitchener #2&3 JCT | ON_KJ2_JCT | HONI |  |  | Ontario
| Kitchener #6 JCT | ON_KJ6_JCT | HONI |  |  | Ontario
| Kitchener #8 JCT | ON_KJ8_JCT | HONI |  |  | Ontario
| Kitchener #9 JCT | ON_KJ9_JCT | HONI |  |  | Ontario
| Kitchener Graber JCT | ON_KGB_JCT | HONI |  |  | Ontario
| Kitchener MTS #1 | ON_KM1_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Kitchener MTS #3 | ON_KM3_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Kitchener MTS #4 | ON_KM4_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Kitchener MTS #5 | ON_KM5_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Kitchener MTS #6 | ON_KM6_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Kitchener MTS #7 | ON_KM7_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Kitchener MTS #8 | ON_KM8_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Kitchener MTS #9 | ON_KM9_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Kleinburg TS | ON_KLE_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Knob JCT | ON_KNB_JCT | HONI |  |  | Ontario
| Lac Des Iles JCT | ON_LDI_JCT | HONI |  |  | Ontario
| Lac Des Iles Min SWS | ON_LDI_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Lafarge Bath TS | ON_LFB_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Lafarge JCT | ON_LAF_JCT | HONI |  |  | Ontario
| Lafarge Woodstock TS | ON_LFW_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report London
| Laforest Road DS | ON_LFR_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Laforest Road JCT | ON_LFR_JCT | HONI |  |  | Ontario
| Lake Huron WTP TS | ON_LAH_ISS | HONI |  |  | Ontario | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan
| Lake TS | ON_LAK_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Lakehead TS | ON_LKH_TSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Lakeview SWS | ON_LKV_SWS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Lambton TS #2 | ON_LMB_DSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Landon GS | ON_LND_GSS | HONI |  |  | Ontario
| Landon JCT | ON_LND_JCT | HONI |  |  | Ontario
| Lantz JCT | ON_LNZ_JCT | HONI |  |  | Ontario
| Larchwood TS | ON_LCH_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Lasco JCT | ON_LAS_JCT | HONI |  |  | Ontario
| Lauzon JCT | ON_LAU_JCT | HONI |  |  | Ontario
| Lauzon TS | ON_LAU_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Leamington JCT | ON_LEM_JCT | HONI |  |  | Ontario
| Leamington TS | ON_LEM_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Leaside JCT | ON_LES_JCT | HONI |  |  | Ontario
| Leaside TS | ON_LES_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Lennox TS | ON_LEN_TSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Leong JCT | ON_LEO_JCT | HONI |  |  | Ontario
| Leslie East JCT | ON_LSE_JCT | HONI |  |  | Ontario
| Leslie JCT | ON_LSL_JCT | HONI |  |  | Ontario
| Leslie TS | ON_LSL_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Leslie West JCT | ON_LSW_JCT | HONI |  |  | Ontario
| Limebank JCT | ON_LBK_JCT | HONI |  |  | Ontario
| Limebank MTS | ON_LBK_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Lincoln Heights TS | ON_LNH_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Lindsay TS | ON_LND_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Lisgar TS | ON_LSG_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Little Long 2 JCT | ON_LLG2_JCT | HONI |  |  | Ontario
| Little Long JCT | ON_LLG_JCT | HONI |  |  | Ontario
| Little Long SWS | ON_LLG_SWS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Lockerby Mine TS | ON_LBM_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Sudbury Algoma
| Lodgeroom DS | ON_LGR_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Long Reach East JCT | ON_LRE_JCT | HONI |  |  | Ontario
| Long Reach West JCT | ON_LRW_JCT | HONI |  |  | Ontario
| Longlac TS | ON_LLC_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Longueuil JCT | ON_LGU_JCT | HONI |  |  | Ontario
| Longueuil TS | ON_LGU_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Longwood TS | ON_LGW_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Lorne Park TS | ON_LNP_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Louth JCT | ON_LOU_JCT | HONI |  |  | Ontario
| Lower Notch GS | ON_LWN_GSS | HONI |  |  | Ontario
| Lower Notch JCT | ON_LWN_JCT | HONI |  |  | Ontario
| Lucasville JCT | ON_LUC_JCT | HONI |  |  | Ontario
| Lumsden JCT | ON_LUM_JCT | HONI |  |  | Ontario
| Lunenburg JCT | ON_LUN_JCT | HONI |  |  | Ontario
| Lynwood JCT | ON_LYN_JCT | HONI |  |  | Ontario
| Lyons JCT | ON_LYO_JCT | HONI |  |  | Ontario
| Macassa #3 JCT | ON_MAC_JCT | HONI |  |  | Ontario
| Macassa Mill JCT | ON_MAM_JCT | HONI |  |  | Ontario
| MacKay JCT | ON_MKY_JCT | HONI |  |  | Ontario
| Mackay TS | ON_MKY_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Mackenzie TS | ON_MKZ_TSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Magellan Aerospace JCT | ON_MGA_JCT | HONI |  |  | Ontario
| Magellan Aerospace TS | ON_MGA_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Magpie SWS | ON_MGP_SWS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report East Lake Superior Region
| Magpie TS | ON_MGP_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Main TS | ON_MAI_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Majestic JCT | ON_MAJ_JCT | HONI |  |  | Ontario
| Majestic TS | ON_MAJ_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Malden JCT | ON_MLD_JCT | HONI |  |  | Ontario
| Malden TS | ON_MLD_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Malvern TS | ON_MLV_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Manby TS | ON_MBY_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Manhole A OPF | ON_MHA_DSS | HONI |  |  | Ontario
| Manitou Falls GS | ON_MNF_GSS | HONI |  |  | Ontario
| Manitoulin TS | ON_MNT_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Manitouwadge DS | ON_MTG_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Manitouwadge JCT | ON_MTG_JCT | HONI |  |  | Ontario
| Manitouwadge JCT B | ON_MTW_JCT | HONI |  |  | Ontario
| Manitouwadge TS | ON_MTW_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Manordale JCT | ON_MDL_JCT | HONI |  |  | Ontario
| Manordale MTS | ON_MDL_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Manotick DS | ON_MTK_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Manotick JCT | ON_MTK_JCT | HONI |  |  | Ontario
| Marathon DS | ON_MRT_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Marathon DS JCT | ON_MRT_JCT | HONI |  |  | Ontario
| Marathon TS | ON_MRT_TSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Marchwood JCT | ON_MCW_JCT | HONI |  |  | Ontario
| Marchwood MTS | ON_MCW_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Margach DS | ON_MGH_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Margach JCT | ON_MGH_JCT | HONI |  |  | Ontario
| Marine JCT | ON_MAR_JCT | HONI |  |  | Ontario
| Marionville DS | ON_MRN_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Marionville JCT | ON_MRN_JCT | HONI |  |  | Ontario
| Markham #1 JCT | ON_MJ1_JCT | HONI |  |  | Ontario
| Markham #1 MTS | ON_MM1_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Markham #2 JCT | ON_MJ2_JCT | HONI |  |  | Ontario
| Markham #2 MTS | ON_MM2_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Markham #3 JCT | ON_MJ3_JCT | HONI |  |  | Ontario
| Markham #3 MTS | ON_MM3_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Markham #4 JCT | ON_MJ4_JCT | HONI |  |  | Ontario
| Markham #4 MTS | ON_MM4_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Marmion Lake JCT | ON_MRM_JCT | HONI |  |  | Ontario
| Marten River JCT | ON_MRV_JCT | HONI |  |  | Ontario
| Martindale TS | ON_MTD_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Massanoga JCT | ON_MOG_JCT | HONI |  |  | Ontario
| Massey DS | ON_MSY_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Massey JCT | ON_MSY_JCT | HONI |  |  | Ontario
| Matachewan JCT | ON_MWN_JCT | HONI |  |  | Ontario
| Mattabi JCT | ON_MTB_JCT | HONI |  |  | Ontario
| Mazinaw DS | ON_MZW_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| McCrea JCT | ON_MCC_JCT | HONI |  |  | Ontario
| McGillivray R&BP TS | ON_MCG_ISS | HONI |  |  | Ontario | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan
| McKinnon's JCT | ON_MCK_JCT | HONI |  |  | Ontario
| McLeans Mountain GS | ON_MCL_GSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| McLeans Mountain JCT | ON_MCL_JCT | HONI |  |  | Ontario
| McMaster JCT | ON_MCM_JCT | HONI |  |  | Ontario
| McMaster TS | ON_MCM_ISS | HONI |  |  | Ontario | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing
| Meadowvale TS | ON_MDV_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Meaford TS | ON_MEA_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Merivale MTS | ON_MER_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Merivale TS | ON_MER_TSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Michigan JCT | ON_MIC_JCT | HONI |  |  | Ontario
| Middleport TS | ON_MPT_TSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Midhurst TS | ON_MDH_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Mill Creek JCT | ON_MLC_JCT | HONI |  |  | Ontario
| Mill Street JCT | ON_MLS_JCT | HONI |  |  | Ontario
| Milltown JCT | ON_MLT_JCT | HONI |  |  | Ontario
| Milman Foundry JCT | ON_MLF_JCT | HONI |  |  | Ontario
| Milman Foundry TS | ON_MLF_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Milton SWS | ON_MIL_SWS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Minaki DS | ON_MIN_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Minaki JCT | ON_MIN_JCT | HONI |  |  | Ontario
| Minden TS | ON_MND_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Minesing JCT | ON_MNS_JCT | HONI |  |  | Ontario
| Minnova JCT | ON_MNV_JCT | HONI |  |  | Ontario
| Mission Falls GS | ON_MSF_GSS | HONI |  |  | Ontario
| Mississagi TS | ON_MSS_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Mississippi JCT | ON_MSP_JCT | HONI |  |  | Ontario
| Modeland TS | ON_MOD_DSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Mohawk Str 31 EP JCT | ON_MHS_JCT | HONI |  |  | Ontario
| Mohawk TS | ON_MOH_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Monteith DS | ON_MON_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Monteith DS JCT | ON_MON_JCT | HONI |  |  | Ontario
| Monteith SWS | ON_MTT_SWS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Monteith SWS JCT | ON_MTT_JCT | HONI |  |  | Ontario
| Montrose JCT | ON_MTR_JCT | HONI |  |  | Ontario
| Moose Lake TS | ON_MSL_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Moosonee DS | ON_MOO_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Moosonee JCT | ON_MOO_JCT | HONI |  |  | Ontario
| Moosonee SWS | ON_MOO_SWS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Morrisburg JCT | ON_MRB_JCT | HONI |  |  | Ontario
| Morrisburg TS | ON_MRB_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Moulton JCT | ON_MOU_JCT | HONI |  |  | Ontario
| Moulton MTS | ON_MOU_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Mount Hope JCT | ON_MTH_JCT | HONI |  |  | Ontario
| Mountain Chute DS | ON_MTC_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Mountain Chute GS | ON_MTC_GSS | HONI |  |  | Ontario
| Mountain Chute JCT | ON_MTC_JCT | HONI |  |  | Ontario
| Murillo DS | ON_MRL_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Murillo JCT | ON_MRL_JCT | HONI |  |  | Ontario
| Murray TS | ON_MRY_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Muskoka TS | ON_MSK_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Musselwhite SWS | ON_MSW_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Nagagami GS | ON_NAG_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Nagagami GS JCT | ON_NAG_JCT | HONI |  |  | Ontario
| Namewaminikan GS | ON_NAM_GSS | HONI |  |  | Ontario
| Namewaminikan JCT | ON_NAM_JCT | HONI |  |  | Ontario
| Nanticoke Creek JCT | ON_NTC_JCT | HONI |  |  | Ontario
| Nanticoke TS | ON_NTK_TSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Napanee GS | ON_NAP_GSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Napanee TS | ON_NAP_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| National Aeronautical TS | ON_NAE_ISS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| National Research JCT | ON_NRS_JCT | HONI |  |  | Ontario
| Navan DS | ON_NVN_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Neale JCT | ON_NEA_JCT | HONI |  |  | Ontario
| Nebo JCT | ON_NEB_JCT | HONI |  |  | Ontario
| Nebo TS | ON_NEB_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Nelson TS | ON_NEL_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Nepean Epworth JCT | ON_NPE_JCT | HONI |  |  | Ontario
| Nepean Epworth MTS | ON_NPE_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Nepean TS | ON_NEP_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Nestor Falls DS | ON_NES_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Nestor Falls JCT | ON_NES_JCT | HONI |  |  | Ontario
| New Liskeard JCT | ON_NLK_JCT | HONI |  |  | Ontario
| New Liskeard JCT #2 | ON_NLK2_JCT | HONI |  |  | Ontario
| Newboro DS | ON_NBO_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Newington DS | ON_NWG_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Newington JCT | ON_NWG_JCT | HONI |  |  | Ontario
| Newport JCT | ON_NWP_JCT | HONI |  |  | Ontario
| Newton TS | ON_NWT_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Niagara A1T T#49 JCT | ON_NIT_JCT | HONI |  |  | Ontario
| Niagara JCT | ON_NIA_JCT | HONI |  |  | Ontario
| Niagara West JCT | ON_NIW_JCT | HONI |  |  | Ontario
| Niagara West MTS | ON_NIW_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Nickel Basin JCT | ON_NIC_JCT | HONI |  |  | Ontario
| Nine Mile JCT | ON_NIN_JCT | HONI |  |  | Ontario
| Nipigon DS | ON_NIP_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Nipigon JCT | ON_NIP_JCT | HONI |  |  | Ontario
| Nobel SWS | ON_NOB_SWS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Norfolk TS | ON_NOR_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Norman JCT | ON_NOM_JCT | HONI |  |  | Ontario
| North Bay TS | ON_NBY_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| North Kent 1 GS | ON_NOK_GSS | HONI |  |  | Ontario
| North Kent 1 JCT | ON_NOK_JCT | HONI |  |  | Ontario
| North Shore DS | ON_NOS_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Northbrook DS | ON_NBK_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Northbrook JCT | ON_NBK_JCT | HONI |  |  | Ontario
| Northern Ave TS | ON_NAV_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| NOTL MTS #2 | ON_NM2_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| NOTL York MTS #1 | ON_NM1_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| NOTL York MTS #1 JCT | ON_NJ1_JCT | HONI |  |  | Ontario
| Notre Development TS | ON_NOT_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Nova Corunna TS | ON_NVC_ISS | HONI |  |  | Ontario | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area
| Nova Moore JCT | ON_NVM_JCT | HONI |  |  | Ontario
| Nova Moore TS | ON_NVM_ISS | HONI |  |  | Ontario | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area
| Nova St Clair R TS | ON_NSC_ISS | HONI |  |  | Ontario | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area
| Nova SWS | ON_NOV_SWS | HONI |  |  | Ontario | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area
| Novelis TS | ON_NLS_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| NPD #2 STR10 JCT | ON_NPD_JCT | HONI |  |  | Ontario
| NPIF Kingston GS | ON_NPK_GSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| NPIF Kingston JCT | ON_NPK_JCT | HONI |  |  | Ontario
| NQL1 B JCT | ON_NQL_JCT | HONI |  |  | Ontario
| NRC TS | ON_NRC_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| O'Brien JCT | ON_OBR_JCT | HONI |  |  | Ontario
| Oakville TS #2 | ON_OAK_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Odessa JCT | ON_ODS_JCT | HONI |  |  | Ontario
| Ogden JCT | ON_ODG_JCT | HONI |  |  | Ontario
| OHSC GS | ON_OHS_GSS | HONI |  |  | Ontario
| OHSC JCT | ON_OHS_JCT | HONI |  |  | Ontario
| Old Armitage JCT | ON_OLA_JCT | HONI |  |  | Ontario
| Onakawana JCT | ON_ONA_JCT | HONI |  |  | Ontario
| Onakawana TS | ON_ONA_ISS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Onaping Area M&M TS | ON_OAM_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Onaping JCT | ON_ONP_JCT | HONI |  |  | Ontario
| Orangeville TS | ON_ORA_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Orillia TS | ON_ORI_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Orleans JCT | ON_ORL_JCT | HONI |  |  | Ontario
| Orleans JCT #2 | ON_OR2_JCT | HONI |  |  | Ontario
| Orleans TS | ON_ORL_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Osgoode JCT | ON_OSG_JCT | HONI |  |  | Ontario
| Oshawa Area JCT | ON_OSH_JCT | HONI |  |  | Ontario
| Oshawa G.M. JCT | ON_OGM_JCT | HONI |  |  | Ontario
| Oshawa G.M. TS | ON_OGM_ISS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| Otonabee TS | ON_OTB_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Ottawa JCT | ON_OTT_JCT | HONI |  |  | Ontario
| Otter Creek JCT | ON_OTC_JCT | HONI |  |  | Ontario
| Otter Rapids GS | ON_ORP_GSS | HONI |  |  | Ontario
| Otter Rapids SWS | ON_ORP_SWS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Otto Holden TS | ON_OTH_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Overbrook TS | ON_OVB_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Owen Sound JCT | ON_OWS_JCT | HONI |  |  | Ontario
| Owen Sound TS | ON_OWS_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Oxford Street JCT | ON_OXS_JCT | HONI |  |  | Ontario
| Oxy Vinyls TS | ON_OXY_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing
| P Sutherland Sr JCT | ON_PSS_JCT | HONI |  |  | Ontario
| P Sutherland Sr SYD | ON_PSS_GSS | HONI |  |  | Ontario
| P7B STR 320 JCT | ON_P7B_JCT | HONI |  |  | Ontario
| Pakwash JCT | ON_PAK_JCT | HONI |  |  | Ontario
| Palermo TS | ON_PAL_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Palermo TxB JCT | ON_PAL_JCT | HONI |  |  | Ontario
| Palmerston TS | ON_PLM_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Pamour JCT | ON_PAM_JCT | HONI |  |  | Ontario
| Panabrasives TS | ON_PNB_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing
| Pancake JCT | ON_PNC_JCT | HONI |  |  | Ontario
| Parkhill TS | ON_PKH_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Parks TS | ON_PKS_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Parkway JCT | ON_PKW_JCT | HONI |  |  | Ontario
| Parkway TS | ON_PKW_TSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Parry Sound JCT | ON_PRS_JCT | HONI |  |  | Ontario
| Parry Sound TS | ON_PRS_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Patrick St TS | ON_PTS_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Pedley JCT | ON_PED_JCT | HONI |  |  | Ontario
| Pelham JCT | ON_PEL_JCT | HONI |  |  | Ontario
| Pembroke TS | ON_PEM_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Perrault Falls DS | ON_PER_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Petawawa DS | ON_PET_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Renfrew
| Petawawa JCT | ON_PET_JCT | HONI |  |  | Ontario
| Pic DS | ON_PIC_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Pic JCT | ON_PIC_JCT | HONI |  |  | Ontario
| Pickering A SWS | ON_PKA_SWS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| Pickering B SWS | ON_PKB_SWS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| Pickle Lake SWS | ON_PKL_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Picton TS | ON_PCT_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Pinard JCT | ON_PIN_JCT | HONI |  |  | Ontario
| Pinard JCT #2 | ON_PI2_JCT | HONI |  |  | Ontario
| Pinard TS | ON_PIN_TSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Pine Portage SWS | ON_PPT_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Placer JCT | ON_PLC_JCT | HONI |  |  | Ontario
| Plank Road JCT | ON_PLK_JCT | HONI |  |  | Ontario
| Pleasant TS | ON_PLE_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Porcupine TS | ON_PCP_TSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Port Alma WF GS | ON_PMA_GSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Port Arthur JCT | ON_PTA_JCT | HONI |  |  | Ontario
| Port Arthur TS #1 | ON_PTA_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Port Colborne TS | ON_PTC_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Port Hope TS | ON_PTH_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Portal JCT | ON_POR_JCT | HONI |  |  | Ontario
| Portland JCT | ON_PTL_JCT | HONI |  |  | Ontario
| Portlands Energy JCT | ON_PTE_JCT | HONI |  |  | Ontario
| Power JCT | ON_POW_JCT | HONI |  |  | Ontario
| Powerline JCT | ON_PWL_JCT | HONI |  |  | Ontario
| Powerline MTS | ON_PWL_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Preston JCT | ON_PRE_JCT | HONI |  |  | Ontario
| Preston TS | ON_PRE_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Pte-Aux-Roches WF GS | ON_PAR_GSS | HONI |  |  | Ontario
| Pte-Aux-Roches WF JCT | ON_PAR_JCT | HONI |  |  | Ontario
| Puslinch DS | ON_PUS_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Puslinch JCT | ON_PUS_JCT | HONI |  |  | Ontario
| Q5B STR A6 JCT | ON_Q5B_JCT | HONI |  |  | Ontario
| Q6S STR M60 JCT | ON_Q6S_JCT | HONI |  |  | Ontario
| Quirke Lake JCT | ON_QUL_JCT | HONI |  |  | Ontario
| Rabbit Lake SWS | ON_RBL_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Railton JCT | ON_RLT_JCT | HONI |  |  | Ontario
| Railway JCT | ON_RLW_JCT | HONI |  |  | Ontario
| Rainy River Gold JCT | ON_RRG_JCT | HONI |  |  | Ontario
| Rainy River Gold SWS | ON_RRG_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Raisin River JCT | ON_RSR_JCT | HONI |  |  | Ontario
| Ramore TS | ON_RMR_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Rayner GS | ON_RNR_GSS | HONI |  |  | Ontario
| Red Lake TS | ON_RDL_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Red Rock DS | ON_RRK_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Red Rock GS | ON_RRC_GSS | HONI |  |  | Ontario
| Red Rock GS JCT | ON_RRC_JCT | HONI |  |  | Ontario
| Red Rock JCT | ON_RRK_JCT | HONI |  |  | Ontario
| Renison JCT | ON_RNS_JCT | HONI |  |  | Ontario
| Renison TS | ON_RNS_ISS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Reserve JCT | ON_RSV_JCT | HONI |  |  | Ontario
| Rexdale TS | ON_RXD_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| RFP Kraft TS | ON_RFK_ISS | HONI |  |  | Ontario | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum. Ontario 230 kV East-West Tie
| RFP Thorold TS | ON_RFT_GSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc and The Haudenosaunee Confederacy Chiefs Council et al Statement of Claim (CV-19-00000152-0000)
| RFP Thunder Bay TS | ON_RFB_GSS | HONI |  |  | Ontario | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum. Ontario 230 kV East-West Tie
| Richmond Hill #2 JCT | ON_RJ2_JCT | HONI |  |  | Ontario
| Richmond Hill JCT | ON_RJ1_JCT | HONI |  |  | Ontario
| Richmond Hill MTS #1 | ON_RM1_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Richmond Hill MTS #2 | ON_RM2_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Richmond MTS | ON_RMD_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Richview JCT | ON_RCV_JCT | HONI |  |  | Ontario
| Richview TS | ON_RCV_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Riverdale JCT | ON_RVD_JCT | HONI |  |  | Ontario
| Riverdale TS | ON_RVD_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Riverside JCT | ON_RVS_JCT | HONI |  |  | Ontario
| Rockland DS | ON_RKL_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Rockland East DS | ON_RKE_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Rockland East DS JCT | ON_RKE_JCT | HONI |  |  | Ontario
| Rockland JCT | ON_RKL_JCT | HONI |  |  | Ontario
| Rosedene JCT | ON_RSD_JCT | HONI |  |  | Ontario
| Rourke Line JCT | ON_RLN_JCT | HONI |  |  | Ontario
| Roxmark JCT | ON_RXK_JCT | HONI |  |  | Ontario
| Roxmark Mine TS | ON_RXM_ISS | HONI |  |  | Ontario | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum. Ontario 230 kV East-West Tie
| Royal Oak TS | ON_RYO_ISS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Runnymede TS | ON_RNY_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Rush MTS | ON_RSH_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Russell DS | ON_RSL_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Russell TS | ON_RSS_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| S2B-M31 JCT | ON_S2B_JCT | HONI |  |  | Ontario
| S3S_S4S STR 8 JCT | ON_S3S_JCT | HONI |  |  | Ontario
| S7M STR 673N JCT | ON_S7M_JCT | HONI |  |  | Ontario
| S7M STR R14-R15 JCT | ON_S7R_JCT | HONI |  |  | Ontario
| Salford JCT | ON_SFD_JCT | HONI |  |  | Ontario
| Saltfleet JCT | ON_SLT_JCT | HONI |  |  | Ontario
| Sam Lake DS | ON_SML_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Sandusk GS | ON_SND_GSS | HONI |  |  | Ontario
| Sandusk JCT | ON_SND_JCT | HONI |  |  | Ontario
| Sandusk SWS | ON_SND_SWS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Sandwich JCT | ON_SNW_JCT | HONI |  |  | Ontario
| Sapawe DS | ON_SPW_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Sapawe JCT | ON_SPW_JCT | HONI |  |  | Ontario
| Sarnia Scott JCT | ON_SNS_JCT | HONI |  |  | Ontario
| Sarnia Scott TS | ON_SNS_TSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Saunders JCT | ON_SAU_JCT | HONI |  |  | Ontario
| Scarboro JCT | ON_SCB_JCT | HONI |  |  | Ontario
| Scarboro TS | ON_SCB_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Scheifele JCT | ON_SCF_JCT | HONI |  |  | Ontario
| Scheifele MTS | ON_SCF_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Schreiber JCT | ON_SCH_JCT | HONI |  |  | Ontario
| Schreiber Winnipeg DS | ON_SCW_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Scout Lake JCT | ON_SCL_JCT | HONI |  |  | Ontario
| Seaforth L7S JCT | ON_SFL_JCT | HONI |  |  | Ontario
| Seaforth TS | ON_SFT_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Seaton MTS | ON_SEN_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan | In-service 2021
| Selby JCT | ON_SBY_JCT | HONI |  |  | Ontario
| Selco JCT | ON_SLC_JCT | HONI |  |  | Ontario
| Serpent River JCT | ON_SER_JCT | HONI |  |  | Ontario
| Shabaqua DS | ON_SBQ_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Shabaqua JCT | ON_SBQ_JCT | HONI |  |  | Ontario
| Shannon GS | ON_SHN_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Sharbot DS | ON_SHR_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Sharbot JCT | ON_SHR_JCT | HONI |  |  | Ontario
| Shebandowan JCT | ON_SHB_JCT | HONI |  |  | Ontario
| Shell Sarnia TS | ON_SHL_ISS | HONI |  |  | Ontario | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area
| Sheppard TS | ON_SHP_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Shiningtree DS | ON_SGT_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Shiningtree JCT | ON_SGT_JCT | HONI |  |  | Ontario
| Sidney TS | ON_SDY_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| Siebert JCT | ON_SBT_JCT | HONI |  |  | Ontario
| Silver Falls GS | ON_SFS_GSS | HONI |  |  | Ontario
| Silvercreek GS | ON_SVC_GSS | HONI |  |  | Ontario
| Silvercreek JCT | ON_SVC_JCT | HONI |  |  | Ontario
| Sioux Narrows DS | ON_SXN_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Sioux Narrows JCT | ON_SXN_JCT | HONI |  |  | Ontario
| Sithe Goreway JCT | ON_SGW_JCT | HONI |  |  | Ontario
| SKWP CMS | ON_SKW_GSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| SKWP CMS JCT | ON_SKW_JCT | HONI |  |  | Ontario
| Slate Falls DS | ON_SLF_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Slate Falls JCT | ON_SLF_JCT | HONI |  |  | Ontario
| Slater TS | ON_SLT_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Smiths Falls TS | ON_SMF_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| Smoky Falls GS | ON_SKF_GSS | HONI |  |  | Ontario
| Smoky Falls JCT | ON_SKF_JCT | HONI |  |  | Ontario
| Smooth Rock Falls DS | ON_SRF_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Smooth Rock Falls JCT | ON_SRF_JCT | HONI |  |  | Ontario
| South Gloucester DS | ON_SGL_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| South Gloucester JCT | ON_SGL_JCT | HONI |  |  | Ontario
| South March SWS | ON_SOM_SWS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| South March TS | ON_SOM_DSS | HONI |  |  | Ontario | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process. (2nd Draft Report). South Nepean MTS & South Nepean Transmission Reinforcement
| Southcote JCT | ON_SCT_JCT | HONI |  |  | Ontario
| Southgate GS | ON_SOG_GSS | HONI |  |  | Ontario
| Southgate JCT | ON_SOG_JCT | HONI |  |  | Ontario
| Sowerby DS | ON_SOW_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Sowerby JCT | ON_SOW_JCT | HONI |  |  | Ontario
| Spanish DS | ON_SPA_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Spanish JCT | ON_SPA_JCT | HONI |  |  | Ontario
| Specialty Bar JCT | ON_SPB_JCT | HONI |  |  | Ontario
| Specialty Bar TS | ON_SPB_ISS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing
| Speed River JCT | ON_SPR_JCT | HONI |  |  | Ontario
| Speedsville JCT | ON_SPS_JCT | HONI |  |  | Ontario
| Spence SWS | ON_SPC_SWS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Spruce Falls JCT | ON_SPF_JCT | HONI |  |  | Ontario
| Spruce Falls TS | ON_SPF_TSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| St. Andrews TS | ON_STA_DSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| St. Anns JCT | ON_STN_JCT | HONI |  |  | Ontario
| St. Clair Avenue JCT | ON_STC_JCT | HONI |  |  | Ontario
| St. Clair E.C. GS | ON_STE_GSS | HONI |  |  | Ontario
| St. Clair E.C. JCT | ON_STE_JCT | HONI |  |  | Ontario
| St. Isidore TS | ON_STI_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| St. Johns Valley JCT | ON_STJ_JCT | HONI |  |  | Ontario
| St. Lawrence TS | ON_STL_DSS | HONI | 45.0588 | -74.6852 | Ontario | Hydro One. 2016. Needs Assessment Report St Lawrence
| St. Marys Cement TS | ON_SMC_ISS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| St. Marys MTS | ON_STM_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| St. Marys TS | ON_SMY_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| St. Paul JCT | ON_STP_JCT | HONI |  |  | Ontario
| St. Thomas TS | ON_STT_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Stanley JCT | ON_SLY_JCT | HONI |  |  | Ontario
| Stanley TS | ON_SLY_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Station 11 SWS | ON_S11_SWS | CNPI |  |  | Ontario | CNPI. 2014. Transmission Revenue Requirement Application
| Station 17 TS | ON_S17_DSS | CNPI |  |  | Ontario | CNPI. 2014. Transmission Revenue Requirement Application
| Station 18 TS | ON_S18_DSS | CNPI |  |  | Ontario | CNPI. 2014. Transmission Revenue Requirement Application
| Stayner TS | ON_STY_DSS | HONI | 44.416 | -80.1107 | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Steephill Falls GS | ON_SHF_GSS | HONI |  |  | Ontario
| Stelco JCT | ON_STO_JCT | HONI |  |  | Ontario
| Stewartville TS | ON_STW_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Stirton TS | ON_STR_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Strachan TS | ON_STH_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Stratford JCT | ON_STF_JCT | HONI |  |  | Ontario
| Stratford TS | ON_STF_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Strathroy TS | ON_SRY_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Striker DS | ON_STK_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Sudbury JCT | ON_SUD_JCT | HONI |  |  | Ontario
| Summerhaven SWS | ON_SUM_SWS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Sun Cdn Pipeline TS | ON_SCP_ISS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Sun Oil Co JCT | ON_SOC_JCT | HONI |  |  | Ontario
| Suncor TS | ON_SCR_ISS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Sydenham JCT | ON_SYD_JCT | HONI |  |  | Ontario
| Talbot TS | ON_TBT_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Talford JCT | ON_TLF_JCT | HONI |  |  | Ontario
| Tarentorus MTS | ON_TRT_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| TBPI Thunder Bay JCT | ON_TBP_JCT | HONI |  |  | Ontario
| TBPI Thunder Bay TS | ON_TBP_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| TCE Halton Hills JCT | ON_TCE_JCT | HONI |  |  | Ontario
| TCPL Belleville TS | ON_TCB_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| TCPL Cobourg TS | ON_TCC_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Peterborough to Kingston Region
| TCPL Vermillion Bay JCT | ON_TCV_JCT | HONI |  |  | Ontario
| TCPL Vermillion Bay TS | ON_TCV_ISS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Tee Lake JCT | ON_TEE_JCT | HONI |  |  | Ontario
| Temagami DS | ON_TMG_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Tembec Kapuskasking TS | ON_TMB_GSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Terauley TS | ON_TER_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Terrace Bay SWS | ON_TRB_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Terry Fox JCT | ON_TRF_JCT | HONI |  |  | Ontario
| Terry Fox MTS | ON_TRF_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Thayer Lindsley TS | ON_TLS_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Third Line TS | ON_TDL_DSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Thornton JCT | ON_THO_JCT | HONI |  |  | Ontario
| Thornton TS | ON_THO_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| Thorold TS | ON_THL_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Thunder Bay SWS | ON_THU_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Tilbury JCT | ON_TLB_JCT | HONI |  |  | Ontario
| Tilbury TS | ON_TLB_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Tilbury West DS | ON_TLW_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Tilbury West JCT | ON_TLW_JCT | HONI |  |  | Ontario
| Tillsonburg JCT | ON_TLL_JCT | HONI |  |  | Ontario
| Tillsonburg TS | ON_TLL_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Timmins JCT | ON_TMM_JCT | HONI |  |  | Ontario
| Timmins TS | ON_TMM_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Timmins Westmine JCT | ON_TMW_JCT | HONI |  |  | Ontario
| Timmins Westmine TS | ON_TMW_ISS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Tisdale JCT | ON_TSD_JCT | HONI |  |  | Ontario
| Todmorden JCT | ON_TOD_JCT | HONI |  |  | Ontario
| Tomken JCT | ON_TOM_JCT | HONI |  |  | Ontario
| Tomken TS | ON_TOM_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Toronto Power T#56 JCT | ON_TOT_JCT | HONI |  |  | Ontario
| Toronto Power TS | ON_TOP_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Toronto Star JCT | ON_TOS_JCT | HONI |  |  | Ontario
| Toyota Woodstock JCT | ON_TYW_JCT | HONI |  |  | Ontario
| Toyota Woodstock TS | ON_TYW_ISS | HONI |  |  | Ontario | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing
| Trafalgar DESN JCT | ON_TFL_JCT | HONI |  |  | Ontario
| Trafalgar TS | ON_TFL_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| TransAlta Energy GS | ON_TRA_GSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| TransAlta Energy JCT | ON_TRA_JCT | HONI |  |  | Ontario
| Trei-bacher JCT | ON_TRB_JCT | HONI |  |  | Ontario
| Tremaine JCT | ON_TRM_JCT | HONI |  |  | Ontario
| Tremaine TS | ON_TRM_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region
| Trinity JCT | ON_TRN_JCT | HONI |  |  | Ontario
| Trout Lake TS | ON_TRL_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Tunnel JCT | ON_TUN_JCT | HONI |  |  | Ontario
| Turbine JCT | ON_TUR_JCT | HONI |  |  | Ontario
| Umbata Falls JCT | ON_UBF_JCT | HONI |  |  | Ontario
| Underwood GS | ON_UDW_GSS | HONI |  |  | Ontario
| Underwood JCT | ON_UDW_JCT | HONI |  |  | Ontario
| Uplands JCT | ON_UPL_JCT | HONI |  |  | Ontario
| Uplands MTS #2 | ON_UPL_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Upper Notch JCT | ON_UPN_JCT | HONI |  |  | Ontario
| Val Tetreau JCT | ON_VLT_JCT | HONI |  |  | Ontario
| Vale Copper #4 TS | ON_VLC_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Vale Frood Stobie #2 JCT | ON_VLF_JCT | HONI |  |  | Ontario
| Vale Frood Stobie #2 TS | ON_VLF_ISS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Vale Inco JCT | ON_VLI_JCT | HONI |  |  | Ontario
| Vale Port Colborne | ON_VLP_ISS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing
| Valerie Falls JCT | ON_VFS_JCT | HONI |  |  | Ontario
| Valora DS | ON_VLA_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Valora JCT | ON_VLA_JCT | HONI |  |  | Ontario
| Vanessa JCT | ON_VNA_JCT | HONI |  |  | Ontario
| Vansco JCT | ON_VNO_JCT | HONI |  |  | Ontario
| Vansickle TS | ON_VNS_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| Vaughan #1 JCT | ON_VJ1_JCT | HONI |  |  | Ontario
| Vaughan #3 JCT | ON_VJ3_JCT | HONI |  |  | Ontario
| Vaughan #4 JCT | ON_VJ4_JCT | HONI |  |  | Ontario
| Vaughan MTS #1 | ON_VM1_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Vaughan MTS #2 | ON_VM2_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Vaughan MTS #3 | ON_VM3_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Vaughan MTS #4 | ON_VM4_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Vermilion Bay DS | ON_VEB_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Vermilion Bay JCT | ON_VEB_JCT | HONI |  |  | Ontario
| Vermillion JCT | ON_VEM_JCT | HONI |  |  | Ontario
| Verner DS | ON_VER_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Verner JCT | ON_VER_JCT | HONI |  |  | Ontario
| Verner Pole 45 JCT | ON_VPL_JCT | HONI |  |  | Ontario
| Vernonville JCT | ON_VNN_JCT | HONI |  |  | Ontario
| Vidal JCT | ON_VDL_JCT | HONI |  |  | Ontario
| Vineland DS | ON_VNL_DSS | HONI |  |  | Ontario | Hydro One. 2016. Needs Assessment Report Niagara
| W3_4T STR B JCT | ON_W34_JCT | HONI |  |  | Ontario
| Walker JCT | ON_WLK_JCT | HONI |  |  | Ontario
| Walker TS | ON_WLK_DSS | HONI |  |  | Ontario | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan
| Wallace JCT | ON_WLL_JCT | HONI |  |  | Ontario
| Wallace Terrace TS | ON_WTC_ISS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Wallace TS | ON_WLL_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Wallaceburg TS | ON_WLB_DSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Wallenstein JCT | ON_WST_JCT | HONI |  |  | Ontario
| Walsh Street JCT | ON_WAL_JCT | HONI |  |  | Ontario
| Wanstead JCT | ON_WAN_JCT | HONI |  |  | Ontario
| Wanstead TS | ON_WAN_DSS | HONI |  |  | Ontario | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan
| Warden TS | ON_WDN_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Warkus JCT | ON_WKS_JCT | HONI |  |  | Ontario
| Warner Road JCT | ON_WNR_JCT | HONI |  |  | Ontario
| Warren DS | ON_WRR_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Waterloo JCT | ON_WTL_JCT | HONI |  |  | Ontario
| Waterloo North MTS 3 | ON_WTN_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Waterloo North MTS 3 JCT | ON_WTN_JCT | HONI |  |  | Ontario
| Waubaushene JCT | ON_WBS_JCT | HONI |  |  | Ontario
| Waubaushene TS | ON_WBS_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report South Georgian Bay - Muskoka.
| Waverly OPF | ON_WAV_DSS | HONI |  |  | Ontario | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices | OPF = Oil pressurization feeder
| Wawa TS | ON_WAW_TSS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| Wawaitin GS | ON_WWT_GSS | HONI |  |  | Ontario
| Wawaitin JCT | ON_WWT_JCT | HONI |  |  | Ontario
| Wells GS | ON_WEL_GSS | HONI |  |  | Ontario
| Wendover DS | ON_WEN_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Wendover JCT | ON_WEN_JCT | HONI |  |  | Ontario
| Wesdome Gold Mines JCT | ON_WGM_JCT | HONI |  |  | Ontario
| Wesdome Gold Mines TS | ON_WGM_ISS | HONI |  |  | Ontario | Hydro One Sault Ste Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356)
| West Gwillimbury JCT | ON_WGW_JCT | HONI |  |  | Ontario
| West Lincoln GS | ON_WLN_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing
| West Lincoln JCT | ON_WLN_JCT | HONI |  |  | Ontario
| West Windsor Power SWS | ON_WWP_SWS | HONI |  |  | Ontario
| Westbrook JCT | ON_WTB_JCT | HONI |  |  | Ontario
| Westmore JCT | ON_WTM_JCT | HONI |  |  | Ontario
| Weston Lake DS | ON_WSL_DSS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Westover A JCT | ON_WVA_JCT | HONI |  |  | Ontario
| Westover JCT | ON_WSV_JCT | HONI |  |  | Ontario
| Weyerhaeuser Kenora TS | ON_WYK_ISS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Wharncliffe DS | ON_WHA_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Wharncliffe JCT | ON_WHA_JCT | HONI |  |  | Ontario
| Whitby GS | ON_WHI_GSS | HONI |  |  | Ontario
| Whitby GS JCT | ON_WHI_JCT | HONI |  |  | Ontario
| Whitby JCT | ON_WHB_JCT | HONI |  |  | Ontario
| Whitby TS | ON_WHB_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| White River DS | ON_WHT_DSS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Whitedog Falls GS | ON_WDF_GSS | HONI |  |  | Ontario
| Whitedog Falls SWS | ON_WDF_SWS | HONI |  |  | Ontario | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan
| Whitefish DS | ON_WHF_DSS | HONI |  |  | Ontario | Hydro One. 2020. Needs Assessment Report Sudbury/Algoma Region
| Widdifield SWS | ON_WFD_SWS | HONI |  |  | Ontario | Hydro One. 2016. GTA West Regional Infrastructure Plan
| Wilhaven DS | ON_WLH_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Wilhaven JCT | ON_WLH_JCT | HONI |  |  | Ontario
| Williams Mine JCT | ON_WLM_JCT | HONI |  |  | Ontario
| Willow Creek JCT | ON_WLC_JCT | HONI |  |  | Ontario
| Willroy JCT | ON_WRY_JCT | HONI |  |  | Ontario
| Willroy Mines TS | ON_WRY_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Wilson JCT | ON_WLS_JCT | HONI |  |  | Ontario
| Wilson TS | ON_WLS_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA East Regional Infrastructure Plan
| Wiltshire TS | ON_WLT_DSS | HONI |  |  | Ontario | Hydro One. 2020. Toronto Regional Infrastructure Plan
| Windsor Airport GS | ON_WDA_GSS | HONI |  |  | Ontario
| Windsor Airport JCT | ON_WDA_JCT | HONI |  |  | Ontario
| Windsor Transalta GS | ON_WDT_GSS | HONI |  |  | Ontario
| Windsor Transalta JCT | ON_WDT_JCT | HONI |  |  | Ontario
| Wingham JCT | ON_WNG_JCT | HONI |  |  | Ontario
| Wingham TS | ON_WNG_DSS | HONI |  |  | Ontario | Hydro One. 2019. Needs Assessment Report Greater Bruce Huron Region
| Winona JCT | ON_WNA_JCT | HONI |  |  | Ontario
| Winona TS | ON_WNA_DSS | HONI |  |  | Ontario | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan
| Wolverton DS | ON_WLV_DSS | HONI |  |  | Ontario | Hydro One. 2018. Needs Assessment Report Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan
| Wolverton JCT | ON_WLV_JCT | HONI |  |  | Ontario
| Wonderland TS | ON_WND_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| Woodbridge JCT | ON_WDB_JCT | HONI |  |  | Ontario
| Woodbridge TS | ON_WDB_DSS | HONI |  |  | Ontario | Hydro One. 2020. GTA North Regional Infrastructure Plan
| Woodroffe TS | ON_WDR_DSS | HONI |  |  | Ontario | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Woodslee JCT | ON_WDS_JCT | HONI |  |  | Ontario
| Woodstock TS | ON_WDK_DSS | HONI |  |  | Ontario | Hydro One. 2017. London Area Regional Infrastructure Plan
| X523A STR 654 JCT | ON_X52_JCT | HONI |  |  | Ontario
| York Energy Centre GS | ON_YEC_GSS | HONI |  |  | Ontario
| York Energy Centre JCT | ON_YEC_JCT | HONI |  |  | Ontario
| Young-Davidson TS | ON_YOD_ISS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Zurich GS | ON_ZUR_DSS | HONI |  |  | Ontario | Hydro One. 2019. List of Transmission Lines by Functional Category (EB-2019-0082)
| Zurich JCT | ON_ZUR_JCT | HONI |  |  | Ontario
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station
Specific Notes:
Additional lines or nodes may be added upon receipt of better system mapping information
General Notes:
Dual function generation/substation nodes are categorized as "GEN"
See inputs tab for assumptions regarding system parameters

## Distribution
ON | EXISTING SUBSTATIONS
| Node Name | Node Code | Owner | Latitude | Longitude | Operating Region | Hydro One Region | Transformers | Primary Voltage | Secondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity (10 min LTR) | Winter Capacity (10 min LTR) | Voltage Reference | Other References | Notes
[9 empty] | (kV) | (kV) | (MVA) | (MVA) |  | (MW) | (MW)
| 93K4-89 JCT | ON_93K_JCT | HONI |  |  | Ontario
| A5RK STR O7 JCT | ON_A5R_JCT | HONI |  |  | Ontario
| A8K-19EO JCT | ON_A19_JCT | HONI |  |  | Ontario
| A8K-47EO JCT | ON_A47_JCT | HONI |  |  | Ontario
| Abit Cons NAN91 JCT | ON_ACS_JCT | HONI |  |  | Ontario
| Abitibi Canyon GS | ON_ABC_GSS | HONI |  |  | Ontario
| Abitibi Canyon JCT #2 | ON_AB2_JCT | HONI |  |  | Ontario
| Abitibi JCT | ON_AB1_JCT | HONI |  |  | Ontario
| Adelaide JCT | ON_ADE_JCT | HONI |  |  | Ontario
| Agimak DS | ON_AGM_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Agimak DS JCT | ON_AGM_JCT | HONI |  |  | Ontario
| Agincourt JCT | ON_AGN_JCT | HONI |  |  | Ontario
| Agincourt TS | ON_AGN_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 174 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Aguasabon SWS | ON_AGU_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Ainsworth JCT | ON_AIN_JCT | HONI |  |  | Ontario
| Albion JCT | ON_ALB_JCT | HONI |  |  | Ontario
| Albion TS | ON_ALB_DSS | HONI |  |  | Ontario | Ottawa |  | 230 | 12.5 |  |  |  | 88 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Alexander GS | ON_ALX_GSS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Alexander SWS | ON_ALX_SWS | HONI |  |  | Ontario
| Alford JCT | ON_ALF_JCT | HONI |  |  | Ontario
| Algoma TS | ON_ALG_TSS | HONI |  |  | Ontario | Sudbury-Algoma |  | 230 | 115 | [6 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Allanburg Q30M JCT | ON_ALQ_JCT | HONI |  |  | Ontario
| Allanburg TS | ON_ALL_TSS | HONI |  |  | Ontario | Niagara |  | 230 | 115 | [6 empty] | Hydro One. 2016. Needs Assessment Report Niagara.
| Allanburg West JCT | ON_ALW_JCT | HONI |  |  | Ontario
| Alliston JCT | ON_ALS_JCT | HONI |  |  | Ontario
| Alliston TS | ON_ALS_DSS | HONI |  |  | Ontario | Georgian Bay | T2/T3/T4 | 230 | 44 |  |  |  | 175 | 190 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Almonte TS | ON_ALM_DSS | HONI |  |  | Ontario | Ottawa |  | 230 | 44 |  |  |  | 100 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Amaranth JCT | ON_AMA_JCT | HONI |  |  | Ontario
| Amaranth TS | ON_AMA_ISS | HONI |  |  | Ontario | KWCG |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Ameristeel Cambridge JCT | ON_AMC_JCT | HONI |  |  | Ontario | KWCG |  | 230 | [7 empty] | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Ameristeel Cambridge TS | ON_AMC_ISS | HONI |  |  | Ontario
| Andrews TS | ON_AND_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 25 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Angler Switch JCT | ON_ANG_JCT | HONI |  |  | Ontario
| Animki JCT | ON_ANM_JCT | HONI |  |  | Ontario
| Anjigami JCT | ON_ANJ_JCT | HONI |  |  | Ontario
| Anjigami JCT #2 | ON_AN2_JCT | HONI |  |  | Ontario
| Anjigami TS | ON_ANJ_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 44 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Ansonville JCT | ON_ANS_JCT | HONI |  |  | Ontario
| Ansonville TS | ON_ANS_TSS | HONI |  |  | Ontario | Northeast | T2 | 230 | 115 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| AP Calstock GS | ON_APC_GSS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| AP Calstock GS JCT | ON_APC_JCT | HONI |  |  | Ontario
| AP Kapuskasing JCT | ON_APK_JCT | HONI |  |  | Ontario
| AP Nipigon GS | ON_APN_GSS | HONI |  |  | Ontario
| AP Nipigon JCT | ON_APN_JCT | HONI |  |  | Ontario
| AP North Bay JCT | ON_APB_JCT | HONI |  |  | Ontario
| AP Tunis JCT | ON_APT_JCT | HONI |  |  | Ontario
| Applewood JCT | ON_APP_JCT | HONI |  |  | Ontario
| Ardoch DS | ON_ARD_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1 | 115 | 12.5 |  |  |  | 12 | 12 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Ardoch JCT | ON_ARD_JCT | HONI |  |  | Ontario
| Arlanxeo Can Inc JCT | ON_ARX_JCT | HONI |  |  | Ontario
| Arlanxeo Can Inc TS | ON_ARX_ISS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Arlen MTS | ON_ARL_DSS | HONI |  |  | Ontario | KWCG |  | 115 |  |  |  |  | 45 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Arlen MTS JCT | ON_ARL_JCT | HONI |  |  | Ontario
| Armitage TS | ON_ATG_DSS | HONI |  |  | Ontario | GTA North | T1/T2/T3/T4 | 230 | 44 |  |  |  | 317 |  |  | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| Armow GS | ON_ARM_GSS | HONI |  |  | Ontario | Bruce-Huron |  | 230 | [7 empty] | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan.
| Armow JCT | ON_ARM_JCT | HONI |  |  | Ontario
| Arnprior GS | ON_ARN_GSS | HONI |  |  | Ontario
| Arnprior JCT | ON_ARN_JCT | HONI |  |  | Ontario
| Arnprior TS | ON_ARN_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 44 |  |  |  | 51 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Ashfield SWS | ON_ASH_SWS | HONI |  |  | Ontario | Bruce-Huron |  | 500 | [7 empty] | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan.
| ASW Steel JCT | ON_ASW_JCT | HONI |  |  | Ontario
| ASW Steel TS | ON_ASW_ISS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Atikokan TGS | ON_ATK_GSS | HONI |  |  | Ontario
| Atlantic Packaging JCT | ON_ATP_JCT | HONI |  |  | Ontario
| Atlantic Packaging TS | ON_ATP_ISS | HONI |  |  | Ontario | GTA East |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Aubrey Falls GS | ON_AUB_GSS | HONI |  |  | Ontario
| Aubrey Falls JCT | ON_AUB_JCT | HONI |  |  | Ontario
| AV Terrace Bay JCT | ON_AVT_JCT | HONI |  |  | Ontario
| AV Terrace Bay TS | ON_AVT_ISS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Aylmer TS | ON_AYL_DSS | HONI |  |  | Ontario | London | T2/T3 | 115 | 27.6 |  |  |  | 55 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| B23C H26C Tie JCT | ON_B23_JCT | HONI |  |  | Ontario
| B5D-B31L SWS JCT | ON_B5D_JCT | HONI |  |  | Ontario
| Baldwin JCT | ON_BDW_JCT | HONI |  |  | Ontario
| Balfour JCT | ON_BAL_JCT | HONI |  |  | Ontario
| Balmer JCT | ON_BLM_JCT | HONI |  |  | Ontario
| Bannockburn JCT | ON_BNK_JCT | HONI |  |  | Ontario
| Barrett Chute JCT | ON_BTC_JCT | HONI |  |  | Ontario
| Barrett Chute SWS | ON_BTC_SWS | HONI |  |  | Ontario | Ottawa |  | 115 | [7 empty] | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Barrie TS | ON_BAR_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2 | 115 | 44 |  |  |  | 109 | 121 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Barryvale Rd JCT | ON_BRV_JCT | HONI |  |  | Ontario
| Bartlett JCT | ON_BTL_JCT | HONI |  |  | Ontario
| Barwick JCT | ON_BWK_JCT | HONI |  |  | Ontario
| Barwick TS | ON_BWK_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 44 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Basin TS | ON_BSN_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 88 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Batchawana TS | ON_BWA_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 12 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Bathurst JCT | ON_BTH_JCT | HONI |  |  | Ontario
| Bathurst TS | ON_BTH_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 334 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Battersea DS | ON_BTT_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 115 | 12.5 |  |  |  | 12 | 12 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Bayview JCT | ON_BYV_JCT | HONI |  |  | Ontario
| Beach JCT | ON_BCH_JCT | HONI |  |  | Ontario
| Beach Road JCT | ON_BCR_JCT | HONI |  |  | Ontario
| Beach TS | ON_BCH_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T3/T4/T5/T6 | 230 | 115/44 |  |  |  | 231 |  |  | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Beamsville TS | ON_BMS_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 27.6 | [6 empty] | Hydro One. 2016. Needs Assessment Report Niagara.
| Beardmore DS #2 | ON_BRD_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Beardmore JCT | ON_BRD_JCT | HONI |  |  | Ontario
| Beaver JCT | ON_BVR_JCT | HONI |  |  | Ontario
| Beaverton JCT | ON_BVT_JCT | HONI |  |  | Ontario
| Beaverton TS | ON_BVT_DSS | HONI |  |  | Ontario | Georgian Bay | T3/T4 | 230 | 44 |  |  |  | 193 | 213 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Beck #1 Q2AH JCT | ON_BKQ_JCT | HONI |  |  | Ontario
| Beck #1 SWS | ON_BK1_SWS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.
| Beck #2 TS | ON_BK2_TSS | HONI |  |  | Ontario | Niagara |  | 345 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2016. Needs Assessment Report Niagara.
| Beck Pump Storage GS | ON_BKP_GSS | HONI |  |  | Ontario | Niagara |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Bell Creek JCT | ON_BLC_JCT | HONI |  |  | Ontario
| Bell Creek TS | ON_BLC_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Belle River GS | ON_BLR_GSS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Belle River JCT | ON_BLR_JCT | HONI |  |  | Ontario
| Belle River JCT #2 | ON_BL2_JCT | HONI |  |  | Ontario
| Belle River TS | ON_BLR_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 54 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Belleville TS | ON_BLV_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 230 | 44 |  |  |  | 161 | 181 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Bellman JCT | ON_BLL_JCT | HONI |  |  | Ontario
| Bermondsey JCT | ON_BMD_JCT | HONI |  |  | Ontario
| Bermondsey TS | ON_BMD_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 348 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| BF Goodrich JCT | ON_BFG_JCT | HONI |  |  | Ontario
| Biddulph JCT | ON_BID_JCT | HONI |  |  | Ontario
| Bilberry Creek JCT | ON_BBC_JCT | HONI |  |  | Ontario
| Bilberry Creek TS | ON_BBC_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 27.6 |  |  |  | 85 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Billings JCT | ON_BIL_JCT | HONI |  |  | Ontario
| Birch JCT | ON_BIR_JCT | HONI |  |  | Ontario
| Birch TS | ON_BIR_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 28.4 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Birmingham TS | ON_BRM_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2/T3/T4 | 115 | 13.8 |  |  |  | 167 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Black River JCT | ON_BKR_JCT | HONI |  |  | Ontario
| Blackburn JCT | ON_BLB_JCT | HONI |  |  | Ontario
| Blezard Valley JCT | ON_BLZ_JCT | HONI |  |  | Ontario
| Blind River TS | ON_BLD_DSS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Blind River TS JCT | ON_BLD_JCT | HONI |  |  | Ontario
| Bloomsburg DS | ON_BLO_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 | 27.6 |  |  |  | 49 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Bloomsburg JCT | ON_BLO_JCT | HONI |  |  | Ontario
| Bloor Street JCT | ON_BLS_JCT | HONI |  |  | Ontario
| Borromee JCT | ON_BOR_JCT | HONI |  |  | Ontario
| Bostwick Road JCT | ON_BOS_JCT | HONI |  |  | Ontario
| Bowmanville SWS | ON_BOW_SWS | HONI |  |  | Ontario | GTA East |  | 500 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Bracebridge JCT | ON_BRA_JCT | HONI |  |  | Ontario
| Bracebridge TS | ON_BRA_DSS | HONI |  |  | Ontario | Georgian Bay | T1 | 230 | 44 |  |  |  | 75 | 75 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Bramalea TS | ON_BML_DSS | HONI |  |  | Ontario | GTA West | T1/T2/T3/T4/T5/T6 | 230 | 27.6 |  |  |  | 450 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Brant JCT | ON_BRT_JCT | HONI |  |  | Ontario
| Brant TS | ON_BRT_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 | 27.6 |  |  |  | 101 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Brantford TS | ON_BRF_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T3/T4 | 230 | 27.6 |  |  |  | 188 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Bridgman JCT | ON_BRG_JCT | HONI |  |  | Ontario
| Bridgman TS | ON_BRG_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 212 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Bridlewood JCT | ON_BRI_JCT | HONI |  |  | Ontario
| Bridlewood MTS | ON_BRI_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 37 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Brighton Interface JCT | ON_BTN_JCT | HONI |  |  | Ontario
| Brockville Chem. JCT | ON_BRC_JCT | HONI |  |  | Ontario
| Brockville TS | ON_BRO_DSS | HONI |  |  | Ontario | St Lawrence |  | 115 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Bronte TS | ON_BRN_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T2/T5/T6 | 115 | 27.6 |  |  |  | 180 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Brookside OPF | ON_BRK_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 | [6 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Brown Hill TS | ON_BRW_DSS | HONI |  |  | Ontario | GTA North | T1/T2 | 230 | 44 |  |  |  | 184 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Bruce A TS | ON_BCA_TSS | HONI |  |  | Ontario | Bruce-Huron |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Bruce B SWS | ON_BCB_SWS | HONI |  |  | Ontario | Bruce-Huron |  | 500 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Bruce HWP B TS | ON_BCW_ISS | HONI |  |  | Ontario | Bruce-Huron |  | 230 |  |  |  |  | 113.2 | 114.8 |  | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Bruce JCT | ON_BRC_JCT | HONI |  |  | Ontario
| Buchanan JCT | ON_BUC_JCT | HONI |  |  | Ontario
| Buchanan TS | ON_BUC_DSS | HONI |  |  | Ontario | London | T13/T14 | 230 | 115/27.6 |  |  |  | 183 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Bunting TS | ON_BUN_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 13.8 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Burleigh DS | ON_BUL_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Burleigh JCT | ON_BUL_JCT | HONI |  |  | Ontario
| Burlington TS | ON_BUR_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T15/T16 | 230 | 115/27.6 |  |  |  | 185 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Buttonville TS | ON_BUT_DSS | HONI |  |  | Ontario | GTA North | T3/T4 | 230 | 27.6 |  |  |  | 166 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Caistor JCT | ON_CST_JCT | HONI |  |  | Ontario
| Caland Ore JCT | ON_CLO_JCT | HONI |  |  | Ontario
| Calder JCT | ON_CLD_JCT | HONI |  |  | Ontario
| Calder TS | ON_CLD_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Caledonia JCT | ON_CAL_JCT | HONI |  |  | Ontario
| Caledonia Q35M JCT | ON_CAQ_JCT | HONI |  |  | Ontario
| Caledonia TS | ON_CAL_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 230 | 27.6 |  |  |  | 99 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Calstock DS | ON_CSK_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 24.9 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Cambridge #1 JCT | ON_CMB_JCT | HONI |  |  | Ontario
| Cameron Falls GS | ON_CAM_GSS | HONI |  |  | Ontario
| Cameron Falls JCT | ON_CAM_JCT | HONI |  |  | Ontario
| Camp Lake JCT | ON_CPL_JCT | HONI |  |  | Ontario
| Campbell TS | ON_CBL_DSS | HONI |  |  | Ontario | KWCG | T1/T2/T3/T4 | 230 | 13.8 |  |  |  | 150 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).
| Canal JCT | ON_CNL_JCT | HONI |  |  | Ontario
| Cardiff JCT | ON_CDF_JCT | HONI |  |  | Ontario
| Cardiff TS | ON_CDF_DSS | HONI |  |  | Ontario | GTA West | T1/T2 | 230 | 27.6 |  |  |  | 114 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Cardinal JCT | ON_CDL_JCT | HONI |  |  | Ontario
| Cardinal Power GS | ON_CDP_GSS | HONI |  |  | Ontario | St Lawrence |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Caribou Falls GS | ON_CRF_GSS | HONI |  |  | Ontario
| Carlaw TS | ON_CLW_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 73 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Carling TS | ON_CAR_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 93 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Carlton TS | ON_CLT_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 13.8 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Carluke JCT | ON_CLK_JCT | HONI |  |  | Ontario
| Carmeuse Lime JCT | ON_CML_JCT | HONI |  |  | Ontario
| Carmichael Falls JCT | ON_CMF_JCT | HONI |  |  | Ontario
| Casco JCT | ON_CSC_JCT | HONI |  |  | Ontario
| Cassburn JCT | ON_CSB_JCT | HONI |  |  | Ontario
| Cassels 2 JCT | ON_CS2_JCT | HONI |  |  | Ontario
| Cassels JCT | ON_CSS_JCT | HONI |  |  | Ontario
| Cat Lake MTS | ON_CTL_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Cataraqui TS | ON_CTQ_TSS | HONI |  |  | Ontario | Peterborough-Kingston |  | 230 | 115 | [6 empty] | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Cavanagh MTS | ON_CVN_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 |  |  |  |  | 157 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Cecil TS | ON_CEC_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 215 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Cedar TS | ON_CED_DSS | HONI |  |  | Ontario | KWCG | T1/T2/T7/T8 | 115 | 13.8 |  |  |  | 143 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Centralia TS | ON_CEN_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | 27.6 |  |  |  | 61.1 | 65.4 |  | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Centre Point JCT | ON_CTP_JCT | HONI |  |  | Ontario
| Centre Point MTS | ON_CTP_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 35 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Chalk River TS | ON_CKR_ISS | HONI |  |  | Ontario | Renfrew |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Renfrew.
| Chapleau DS | ON_CHP_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 44 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Chapleau JCT | ON_CHP_JCT | HONI |  |  | Ontario
| Chapleau MTS | ON_CHM_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 44 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Charles TS | ON_CHL_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 211 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Chatham SWS | ON_CHT_SWS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Chats Falls SWS | ON_CHF_SWS | HONI |  |  | Ontario | Ottawa |  | 230 | [7 empty] | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Chenaux JCT | ON_CHX_JCT | HONI |  |  | Ontario
| Chenaux TS | ON_CHX_TSS | HONI |  |  | Ontario | Renfrew | T3/T4 | 230 | 115 |  |  |  | 112.5 |  | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Cherry JCT | ON_CHR_JCT | HONI |  |  | Ontario
| Cherrywood TS | ON_CHW_DSS | HONI |  |  | Ontario | GTA East | T7/T8 | 500 | 230/44 |  |  |  | 175 |  | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| Chesterville N. JCT | ON_CHS_JCT | HONI |  |  | Ontario
| Chesterville S. JCT | ON_CHS_JCT | HONI |  |  | Ontario
| Chesterville TS | ON_CHS_DSS | HONI |  |  | Ontario | St Lawrence |  | 115 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Chrysler WAP MTS | ON_CHY_ISS | HONI |  |  | Ontario | Windsor-Essex |  | 115 |  |  |  |  | 59 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Churchill Meadows JCT | ON_CHU_JCT | HONI |  |  | Ontario
| Churchill Meadows TS | ON_CHU_ISS | HONI |  |  | Ontario | GTA West | T1/T2 | 230 | 44 |  |  |  | 173 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| City View JCT | ON_CTV_JCT | HONI |  |  | Ontario
| Claireville TS | ON_CLV_TSS | HONI | 43.7639 | -79.6149 | Ontario | GTA Toronto |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Clarabelle JCT | ON_CLA_JCT | HONI |  |  | Ontario
| Clarabelle TS | ON_CLA_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1/T2 | 230 | 44 |  |  |  |  | 184.32 |  | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Clarence DS | ON_CLC_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 8.32 |  |  |  | 4 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Clarington JCT | ON_CLG_JCT | HONI |  |  | Ontario
| Clarington TS | ON_CLG_TSS | HONI |  |  | Ontario | GTA East |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| Clarke TS | ON_CKE_DSS | HONI |  |  | Ontario | London | T3/T4 | 230 | 27.6 |  |  |  | 110 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Clearwater Bay DS | ON_CWB_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Clergue TS | ON_CGU_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 12 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Cobden JCT | ON_CBD_JCT | HONI |  |  | Ontario
| Cobden TS | ON_CBD_DSS | HONI |  |  | Ontario | Renfrew | T1/T2/T3 | 115 | 44 |  |  |  | 49 |  |  | Hydro One. 2016. Needs Assessment Report Renfrew.
| Cobden X6 JCT | ON_CBX_JCT | HONI |  |  | Ontario
| Cochrane West DS | ON_CCW_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Cochrane West JCT | ON_CCW_JCT | HONI |  |  | Ontario
| Cochrane West MTS | ON_COC_DSS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Columbus JCT | ON_CLB_JCT | HONI |  |  | Ontario
| Comber WF GS | ON_COM_GSS | HONI |  |  | Ontario | Windsor-Essex |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Comber WF JCT | ON_COM_JCT | HONI |  |  | Ontario
| Commanda JCT | ON_CMM_JCT | HONI |  |  | Ontario
| Commerce Way JCT | ON_CMC_JCT | HONI |  |  | Ontario
| Commerce Way TS | ON_CMC_DSS | HONI |  |  | Ontario | London | T1/T2 | 115 | 27.6 |  |  |  | 112 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Confederation Rd JCT | ON_CON_JCT | HONI |  |  | Ontario
| Coniston TS | ON_CTN_DSS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | 22 | [6 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Conmee JCT | ON_CNM_JCT | HONI |  |  | Ontario
| Constance DS | ON_CNC_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | 27.6 |  |  |  | 25 | 35 | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Cooksville TS | ON_CKV_DSS | HONI |  |  | Ontario | GTA West | T1/T2/T3/T4 | 230 | 27.6 |  |  |  | 240 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Cooper's Falls JCT | ON_COF_JCT | HONI |  |  | Ontario
| Copeland MTS | ON_COP_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 130 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Copper Cliff JCT | ON_CFF_JCT | HONI |  |  | Ontario
| Cowal JCT | ON_COW_JCT | HONI |  |  | Ontario
| Craig DS | ON_CRG_DSS | HONI |  |  | Ontario | Renfrew | T1/T2 | 115 | 12.5 |  |  |  | 15.9 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Craig JCT | ON_CRG_JCT | HONI |  |  | Ontario
| Cranberry JCT | ON_CRN_JCT | HONI |  |  | Ontario
| Crawford JCT | ON_CRW_JCT | HONI |  |  | Ontario
| Crawford TS | ON_CRW_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 92 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Creighton JCT | ON_CRE_JCT | HONI |  |  | Ontario
| Crosby JCT | ON_CRO_JCT | HONI |  |  | Ontario
| Crosby TS | ON_CRO_DSS | HONI |  |  | Ontario | St Lawrence |  | 230 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Crossline JCT | ON_CSL_JCT | HONI |  |  | Ontario
| Crow River DS | ON_CRR_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Crowland JCT | ON_CRL_JCT | HONI |  |  | Ontario
| Crowland TS | ON_CRL_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Crystal Falls SWS | ON_CRY_SWS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Crystal Falls TS | ON_CRY_DSS | HONI |  |  | Ontario | Northeast |  | 230 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Cumberland DS | ON_CUS_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 8.32 |  |  |  | 15 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Cumberland DS JCT | ON_CUS_JCT | HONI |  |  | Ontario
| Cumberland JCT | ON_CUM_JCT | HONI |  |  | Ontario
| Cumberland TS | ON_CUM_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T3/T4 | 230 | 27.6 |  |  |  | 174 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Cutler JCT | ON_CUT_JCT | HONI |  |  | Ontario
| Cyrville JCT | ON_CYV_JCT | HONI |  |  | Ontario
| Cyrville MTS | ON_CYV_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 59 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Cyrville Rd JCT | ON_CYR_JCT | HONI |  |  | Ontario
| Cytec Welland TS | ON_CYT_ISS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| D2L STR 409 JCT | ON_D2L_JCT | HONI |  |  | Ontario
| DA Watson TS | ON_DAW_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 34.5 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Dale JCT | ON_DAL_JCT | HONI |  |  | Ontario
| Dane JCT | ON_DAN_JCT | HONI |  |  | Ontario
| DeCew Falls SWS | ON_DEC_SWS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.
| Deep River DS | ON_DPR_DSS | HONI |  |  | Ontario | Renfrew | T1/T2/T3 | 115 | 12.5 |  |  |  | 23.8 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Denison Mines TS | ON_DNM_ISS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Des Joachims DS | ON_DEJ_DSS | HONI |  |  | Ontario | Renfrew | T1 | 230 | 12.48 |  |  |  | 11.3 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Des Joachims JCT | ON_DEJ_JCT | HONI |  |  | Ontario
| Des Joachims TS | ON_DEJ_TSS | HONI |  |  | Ontario | Renfrew | T6/T7 | 230 | 115 |  |  |  | 112.5 |  | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Detweiler JCT | ON_DET_JCT | HONI |  |  | Ontario
| Detweiler TS | ON_DET_TSS | HONI |  |  | Ontario | KWCG |  | 230 | 115 | [6 empty] | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Devizes JCT | ON_DVZ_JCT | HONI |  |  | Ontario
| Didsbury Road JCT | ON_DID_JCT | HONI |  |  | Ontario
| Dillon RWEC GS | ON_DIL_GSS | HONI |  |  | Ontario
| Dillon RWEC GS JCT | ON_DIL_JCT | HONI |  |  | Ontario
| Dobbin DS | ON_DBN_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 115 | 27.6 |  |  |  | 24 | 24 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Dobbin TS | ON_DOB_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T3/T4 | 230 | 115/44 |  |  |  | 160 | 177 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Dofasco Bay Front TS | ON_DBF_ISS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Dofasco Kenilworth TS | ON_DKW_ISS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Dome Site JCT | ON_DOM_JCT | HONI |  |  | Ontario
| Dominion Drive DS | ON_DMD_DSS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | 12.47 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Domtar Dryden TS | ON_DTD_ISS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Don Fleet JCT | ON_DFL_JCT | HONI |  |  | Ontario
| Donaldson Cres JCT | ON_DNC_JCT | HONI |  |  | Ontario
| Douglas Point TS | ON_DGP_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 230 | 44 |  |  |  | 97.2 | 109.8 |  | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Dresser JCT | ON_DRS_JCT | HONI |  |  | Ontario
| Drummond Road JCT | ON_DRU_JCT | HONI |  |  | Ontario
| Dryden JCT B | ON_DRY_JCT | HONI |  |  | Ontario
| Dryden TS | ON_DRY_TSS | HONI |  |  | Ontario | Northwest |  | 230 | 115 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Duart JCT | ON_DUA_JCT | HONI |  |  | Ontario
| Duart TS | ON_DUA_DSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Dufferin JCT | ON_DUF_JCT | HONI |  |  | Ontario
| Dufferin TS | ON_DUF_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 170 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Duffin JCT | ON_DFN_JCT | HONI |  |  | Ontario
| Dundas #2 JCT | ON_DD2_JCT | HONI |  |  | Ontario
| Dundas #2 TS | ON_DD2_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T5/T6 | 115 | 27.6 |  |  |  | 89 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Dundas JCT | ON_DDS_JCT | HONI |  |  | Ontario
| Dundas Street JCT | ON_DST_JCT | HONI |  |  | Ontario
| Dundas TS | ON_DDS_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 | 27.6 |  |  |  | 99 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Dunnville TS | ON_DNV_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Duplex TS | ON_DPX_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 128 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Dupont JCT | ON_DUP_JCT | HONI |  |  | Ontario
| Dymond TS | ON_DYM_DSS | HONI |  |  | Ontario | Northeast |  | 230 | 115/44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Dyno Nobel TS | ON_DYN_ISS | HONI |  |  | Ontario | St Lawrence |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Eacom Nairn Centre JCT | ON_EAC_JCT | HONI |  |  | Ontario
| Eacom Nairn Centre TS | ON_EAC_ISS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Ear Falls TS | ON_EAF_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 44 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| East Lake St. Clair GS | ON_ESC_GSS | HONI |  |  | Ontario
| East Lake St. Clair JCT | ON_ESC_JCT | HONI |  |  | Ontario
| East Windsor GS | ON_EWI_GSS | HONI |  |  | Ontario
| Easton JCT | ON_EAS_JCT | HONI |  |  | Ontario
| Easton Yule JCT | ON_EAY_JCT | HONI |  |  | Ontario
| Echo Bay Aquarius JCT | ON_ECH_JCT | HONI |  |  | Ontario
| Echo River DS | ON_ERV_DSS | HONI |  |  | Ontario | East Lake Superior | T1 | 230 | 115/34.5 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Echo River JCT | ON_ERV_JCT | HONI |  |  | Ontario
| Ecstall JCT | ON_ECS_JCT | HONI |  |  | Ontario
| Eddy Tap A JCT | ON_EDY_JCT | HONI |  |  | Ontario
| Eddy Tap JCT | ON_EDY_JCT | HONI |  |  | Ontario
| Edgeware JCT | ON_EDG_JCT | HONI |  |  | Ontario
| Edgeware TS | ON_EDG_DSS | HONI |  |  | Ontario | London | T1/T2 | 230 | 27.6 |  |  |  | 191 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Egmondville SWS | ON_EGM_SWS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Elgin JCT | ON_ELG_JCT | HONI |  |  | Ontario
| Elgin TS | ON_ELG_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 | 13.8 |  |  |  | 135 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Elk Lake JCT | ON_ELK_JCT | HONI |  |  | Ontario
| Ellesmere JCT | ON_ELM_JCT | HONI |  |  | Ontario
| Ellesmere TS | ON_ELM_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 189 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Elliot Lake JCT | ON_ELL_JCT | HONI |  |  | Ontario
| Elliot Lake TS | ON_ELL_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1/T2/T3 | 115 | 44 |  |  |  |  | 66.42 |  | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Ellwood JCT | ON_ELW_JCT | HONI |  |  | Ontario
| Ellwood MTS | ON_ELW_DSS | HONI |  |  | Ontario | Ottawa |  | 230 |  |  |  |  | 59 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Ellwood MTS JCT | ON_ELW_JCT | HONI |  |  | Ontario
| Elmira TS | ON_EMA_DSS | HONI |  |  | Ontario | KWCG |  | 115 | 27.6 |  |  |  | 55 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Enbridge Bryanston TS | ON_ENB_ISS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | [7 empty] | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan.
| Enbridge Keyser TS | ON_ENK_ISS | HONI |  |  | Ontario | London |  | 115 | [7 empty] | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Enbridge PL Card TS | ON_ENC_ISS | HONI |  |  | Ontario | St Lawrence |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Enbridge PL Hilt TS | ON_ENH_ISS | HONI |  |  | Ontario | Peterborough-Kingston |  | 115 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Enbridge Westover N TS | ON_EWN_ISS | HONI |  |  | Ontario | KWCG |  | 115 | [7 empty] | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Enbridge Westover S TS | ON_EWS_ISS | HONI |  |  | Ontario | KWCG |  | 115 | [7 empty] | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Energy Inc(Cam) MTS#1 | ON_ENI_DSS | HONI |  |  | Ontario | KWCG |  | 230 |  |  |  |  | 102 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Enfield TS | ON_ENF_DSS | HONI |  |  | Ontario | GTA East | T1/T2 | 230 | 44 |  |  |  | 157 |  |  | Hydro One. 2020. GTA East Regional Infrastructure Plan. | In-service 2020
| Ennisbrook JCT | ON_ENN_JCT | HONI |  |  | Ontario
| Erco JCT | ON_ERC_JCT | HONI |  |  | Ontario
| ERG Resources TS | ON_ERG_ISS | HONI |  |  | Ontario | Northeast |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Erieau WF GS | ON_ERI_GSS | HONI |  |  | Ontario
| Erieau WF JCT | ON_ERI_JCT | HONI |  |  | Ontario
| Erindale JCT | ON_ERD_JCT | HONI |  |  | Ontario
| Erindale TS | ON_ERD_DSS | HONI |  |  | Ontario | GTA West | T1/T2/T3/T4/T5/T6 | 230 | 27.6 |  |  |  | 540 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Espanola A JCT | ON_ESP_JCT | HONI |  |  | Ontario
| Espanola GS | ON_ESP_GSS | HONI |  |  | Ontario
| Espanola JCT | ON_ESP_JCT | HONI |  |  | Ontario
| Espanola TS | ON_ESP_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1/T2/T3 | 115 | 44 |  |  |  |  | 61.18 |  | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Esplanade TS | ON_EPL_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 187 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Essa TS | ON_ESA_TSS | HONI |  |  | Ontario | Georgian Bay |  | 500 | 230/115 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Essex TS | ON_ESX_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 107 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| ESWF GS | ON_ESW_GSS | HONI |  |  | Ontario | London |  | 115 | [7 empty] | Hydro One. 2020. Needs Assessment Report. London.
| ESWF JCT | ON_ESW_JCT | HONI |  |  | Ontario
| Ethel Lake JCT | ON_ETH_JCT | HONI |  |  | Ontario
| Eton DS | ON_ETO_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Eton JCT | ON_ETO_JCT | HONI |  |  | Ontario
| Etruscan Enterprise TS | ON_ETR_ISS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Etruscan JCT | ON_ETR_JCT | HONI |  |  | Ontario
| Everett JCT | ON_EVT_JCT | HONI |  |  | Ontario
| Everett TS | ON_EVT_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2 | 230 | 44 |  |  |  | 86 | 86 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Evergreen SWS | ON_EVG_SWS | HONI |  |  | Ontario | Bruce-Huron |  | 500 | [7 empty] | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan.
| Extender Min. JCT | ON_EXT_JCT | HONI |  |  | Ontario
| Fairbank TS | ON_FBK_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 27.6 |  |  |  | 182 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Fairchild TS | ON_FCD_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 346 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Falconbridge 61 JCT | ON_FL6_JCT | HONI |  |  | Ontario
| Falconbridge JCT | ON_FLB_JCT | HONI |  |  | Ontario
| Falconbridge T2R TS | ON_FLB_ISS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Sudbury Algoma.
| Fallowfield JCT | ON_FLF_JCT | HONI |  |  | Ontario
| Fallowfield MTS | ON_FLF_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 48 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Fauquier DS | ON_FAU_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Fauquier JCT | ON_FAU_JCT | HONI |  |  | Ontario
| Fergus JCT | ON_FGS_JCT | HONI |  |  | Ontario
| Fergus TS | ON_FGS_DSS | HONI |  |  | Ontario | KWCG |  | 230 | 44 |  |  |  | 154 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Festival MTS #1 | ON_FST_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 230 |  |  |  |  | 62 | 66.7 |  | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Festival MTS #1 JCT | ON_FST_JCT | HONI |  |  | Ontario
| Fibre JCT | ON_FBR_JCT | HONI |  |  | Ontario
| Finch JCT | ON_FIN_JCT | HONI |  |  | Ontario
| Finch TS | ON_FIN_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 365 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Fitzroy JCT | ON_FTZ_JCT | HONI |  |  | Ontario
| Flakeboard TS | ON_FKB_ISS | HONI |  |  | Ontario | East Lake Superior |  | 115 | [7 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Ford Annex MTS | ON_FDA_ISS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 13.8 |  |  |  | 39 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Ford Essex JCT | ON_FDE_JCT | HONI |  |  | Ontario
| Ford Essex TS | ON_FDE_ISS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 13.8 |  |  |  | 39 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Ford JCT | ON_FRD_JCT | HONI |  |  | Ontario
| Ford Oakville TS | ON_FDO_ISS | HONI |  |  | Ontario | GTA West |  | 230 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Ford Windsor MTS | ON_FDW_ISS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 59 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Forest Jura DS | ON_FRJ_DSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Forest Lea DS | ON_FRL_DSS | HONI |  |  | Ontario | Renfrew | T1/T2 | 115 | 12.5 |  |  |  | 9.9 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Forest Lea JCT | ON_FRL_JCT | HONI |  |  | Ontario
| Forgie JCT | ON_FRG_JCT | HONI |  |  | Ontario
| Fort Frances JCT | ON_FRF_JCT | HONI |  |  | Ontario
| Fort Frances MTS | ON_FRM_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Fort Frances TS | ON_FRF_TSS | HONI |  |  | Ontario | Northwest |  | 230 | 115 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Fort William TS | ON_FRW_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Fournier JCT | ON_FOU_JCT | HONI |  |  | Ontario
| Freeport SWS | ON_FPT_SWS | HONI |  |  | Ontario | KWCG |  | 115 | [7 empty] | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Frontenac TS | ON_FRO_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T3/T4 | 115 | 44 |  |  |  | 111 | 122 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| G.M. St. Cath TS | ON_GMS_ISS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| G.M. Windsor MTS | ON_GMW_ISS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 39 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Gage JCT | ON_GAG_JCT | HONI |  |  | Ontario
| Gage TS | ON_GAG_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T3/T4/T5/T6/T8/T9 | 115 | 13.8 |  |  |  | 123 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Galetta JCT | ON_GAL_JCT | HONI |  |  | Ontario
| Galt JCT | ON_GTT_JCT | HONI |  |  | Ontario
| Galt North JCT | ON_GTN_JCT | HONI |  |  | Ontario
| Galt South JCT | ON_GTS_JCT | HONI |  |  | Ontario
| Galt TS | ON_GTT_DSS | HONI |  |  | Ontario | KWCG |  | 230 | 27.6 |  |  |  | 169 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Gamble H9A JCT | ON_GAM_JCT | HONI |  |  | Ontario
| Gardiner STR 44 JCT | ON_GAR_JCT | HONI |  |  | Ontario
| Gardiner TS | ON_GAR_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2/T3/T4 | 230 | 44 |  |  |  | 209 | 227 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Gartshore GS | ON_GSO_GSS | HONI |  |  | Ontario
| Gartshore TS | ON_GSO_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 12 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Gerdau A. Whitby TS | ON_GAW_ISS | HONI |  |  | Ontario | GTA East |  | 230 | 44 | [6 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Gerrard JCT | ON_GER_JCT | HONI |  |  | Ontario
| Gerrard TS | ON_GER_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 102 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Gervais JCT | ON_GRV_JCT | HONI |  |  | Ontario
| Gibson JCT | ON_GIB_JCT | HONI |  |  | Ontario
| Glanford JCT | ON_GLF_JCT | HONI |  |  | Ontario
| Glendale JCT | ON_GND_JCT | HONI |  |  | Ontario
| Glendale TS | ON_GND_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 13.8 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Glengrove TS | ON_GLG_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 88 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Glenorchy JCT | ON_GLO_JCT | HONI |  |  | Ontario
| Glenorchy MTS #1 | ON_GLO_DSS | HONI |  |  | Ontario | GTA West |  | 230 | 27.6 |  |  |  | 153 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Goderich TS | ON_GOD_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 115 |  |  |  |  | 126.5 | 132 |  | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Gold Centre JCT | ON_GLC_JCT | HONI |  |  | Ontario
| Golden Patricia JCT | ON_GLP_JCT | HONI |  |  | Ontario
| Goreway JCT | ON_GRW_JCT | HONI |  |  | Ontario
| Goreway TS | ON_GRW_DSS | HONI |  |  | Ontario | GTA West | T1/T2/T4/T5/T6 | 230 | 44 |  |  |  | 435 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Gormley JCT | ON_GML_JCT | HONI |  |  | Ontario
| Gosfield GS | ON_GOS_GSS | HONI |  |  | Ontario
| Gosfield GS JCT | ON_GOS_JCT | HONI |  |  | Ontario
| Goshen GS | ON_GSH_GSS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | [7 empty] | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Goshen JCT | ON_GSH_JCT | HONI |  |  | Ontario
| Goulais Bay TS | ON_GLB_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 25 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Goulais JCT | ON_GLA_JCT | HONI |  |  | Ontario
| Goulais SWS | ON_GLA_SWS | HONI |  |  | Ontario | East Lake Superior |  | 115 | [7 empty] | Hydro One. 2019. Needs Assessment Report East Lake Superior Region.
| Grand Bend East DS | ON_GRB_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | 27.6 |  |  |  | 31.3 | 40 | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Grand Bend East JCT | ON_GRB_JCT | HONI |  |  | Ontario
| Grand GS | ON_GRD_GSS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 230 | [7 empty] | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Grand JCT | ON_GRD_JCT | HONI |  |  | Ontario
| Grant JCT | ON_GRT_JCT | HONI |  |  | Ontario
| Greely DS | ON_GRE_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 27.6 |  |  |  | 40 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Greely JCT | ON_GRE_JCT | HONI |  |  | Ontario
| Greenfield Energy GS | ON_GRF_GSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Greenfield Interface JCT | ON_GRF_JCT | HONI |  |  | Ontario
| Greenwater Pr Pk JCT | ON_GWP_JCT | HONI |  |  | Ontario
| Greenwich WF GS | ON_GRH_GSS | HONI |  |  | Ontario | Northwest |  | 230 | [7 empty] | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum. Ontario 230 kV East-West Tie.
| Greenwich WF GS JCT | ON_GRH_JCT | HONI |  |  | Ontario
| Gretna JCT | ON_GNA_JCT | HONI |  |  | Ontario
| GSPC JCT | ON_GSP_JCT | HONI |  |  | Ontario
| Guelph North JCT | ON_GUE_JCT | HONI |  |  | Ontario
| Gull Lake North JCT | ON_GLN_JCT | HONI |  |  | Ontario
| Gull Lake South JCT | ON_GLS_JCT | HONI |  |  | Ontario
| GV3 WF GS | ON_GV3_GSS | HONI |  |  | Ontario
| GV3 WF JCT | ON_GV3_JCT | HONI |  |  | Ontario
| H2O Power Calm Lake GS | ON_H2C_GSS | HONI |  |  | Ontario
| H2O Power Fort Frances GS | ON_H2F_GSS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| H2O Power Sturgeon Falls GS | ON_H2S_GSS | HONI |  |  | Ontario
| H9K STR 127A JCT | ON_H9K_JCT | HONI |  |  | Ontario
| Haig JCT | ON_HAI_JCT | HONI |  |  | Ontario
| Haley JCT | ON_HLY_JCT | HONI |  |  | Ontario
| Halton Hills GS | ON_HHL_GSS | HONI |  |  | Ontario
| Halton Hills MTS | ON_HHL_DSS | HONI |  |  | Ontario | GTA West |  | 230 | 27.6 |  |  |  | 102 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Halton TS | ON_HLT_DSS | HONI |  |  | Ontario | GTA West | T3/T4 | 230 | 27.6 |  |  |  | 186 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Hanlan JCT | ON_HLA_JCT | HONI |  |  | Ontario
| Hanlon JCT | ON_HLO_JCT | HONI |  |  | Ontario
| Hanlon TS | ON_HLO_DSS | HONI |  |  | Ontario | KWCG |  | 115 | 13.8 |  |  |  | 43 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Hanmer TS | ON_HNM_TSS | HONI |  |  | Ontario | Sudbury-Algoma |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Hannon JCT | ON_HNN_JCT | HONI |  |  | Ontario
| Hanover TS | ON_HNV_DSS | HONI |  |  | Ontario | Bruce-Huron | T1/T2 DESN | 230 | 115/44 |  |  |  | 109.9 | 124.7 | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Harmon GS | ON_HRJ_GSS | HONI |  |  | Ontario
| Harmon JCT | ON_HRJ_JCT | HONI |  |  | Ontario
| Harper's JCT | ON_HRP_JCT | HONI |  |  | Ontario
| Harris GS | ON_HRS_GSS | HONI |  |  | Ontario
| Harrowsmith DS | ON_HRR_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 115 | 12.5 |  |  |  | 12 | 12 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Harrowsmith JCT | ON_HRR_JCT | HONI |  |  | Ontario
| Hartford JCT | ON_HRT_JCT | HONI |  |  | Ontario
| Havelock TS | ON_HVL_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 230 | 44 |  |  |  | 88 | 97 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Hawkesbury MTS #1 | ON_HWK_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 18 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Hawthorne TS | ON_HWT_TSS | HONI |  |  | Ontario | Ottawa |  | 500 | 230/115 |  |  |  | 153 |  | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Hearn SWS | ON_HEA_SWS | HONI |  |  | Ontario | GTA Toronto |  | 115 | [7 empty] | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Hearst TS | ON_HST_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 24.9 | [6 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Hemlo Mine JCT | ON_HML_JCT | HONI |  |  | Ontario
| Herridge Lake DS | ON_HRL_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Herridge Lake JCT | ON_HRL_JCT | HONI |  |  | Ontario
| Heyden JCT | ON_HYD_JCT | HONI |  |  | Ontario
| Heyden SWS | ON_HYD_SWS | HONI |  |  | Ontario | East Lake Superior |  | 230 | [7 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Highbury TS | ON_HIG_DSS | HONI |  |  | Ontario | London | T3/T4 | 115 | 27.6 |  |  |  | 114 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Hilton JCT | ON_HIL_JCT | HONI |  |  | Ontario
| Hinchey TS | ON_HIN_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 13.8 |  |  |  | 77 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Hinchinbrooke DS | ON_HNB_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1 | 115 | 12.5 |  |  |  | 6 | 6 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Hinchinbrooke SWS | ON_HNB_SWS | HONI |  |  | Ontario | Peterborough-Kingston |  | 230 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Hogg GS | ON_HOG_GSS | HONI |  |  | Ontario
| Holland JCT | ON_HLD_JCT | HONI |  |  | Ontario
| Holland Marsh JCT | ON_HLM_JCT | HONI |  |  | Ontario
| Holland Road JCT | ON_HLR_JCT | HONI |  |  | Ontario
| Holland TS | ON_HLD_DSS | HONI |  |  | Ontario | GTA North | T1/T2 | 230 | 44 |  |  |  | 168 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Hollingsworth TS | ON_HGW_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 12 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Holloway Holt JCT | ON_HLH_JCT | HONI |  |  | Ontario
| Hooper's JCT | ON_HOO_JCT | HONI |  |  | Ontario
| Hornby JCT | ON_HBY_JCT | HONI |  |  | Ontario
| Horner TS | ON_HOR_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 365 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Horning JCT | ON_HNG_JCT | HONI |  |  | Ontario
| Horning Mountain JCT | ON_HGM_JCT | HONI |  |  | Ontario
| Horning TS | ON_HNG_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T3/T4 | 230 | 13.8 |  |  |  | 113 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Hoyle DS | ON_HOY_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Hoyle JCT | ON_HOY_JCT | HONI |  |  | Ontario
| Hoyle Pond Site JCT | ON_HPS_JCT | HONI |  |  | Ontario
| Hunta H9K JCT | ON_HTA_JCT | HONI |  |  | Ontario
| Hunta JCT | ON_HTA_JCT | HONI |  |  | Ontario
| Hunta SWS | ON_HTA_SWS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Hurontario SWS | ON_HRN_SWS | HONI |  |  | Ontario | GTA West |  | 230 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Hurricane JCT | ON_HRC_JCT | HONI |  |  | Ontario
| Hwy #11 JCT | ON_H11_JCT | HONI |  |  | Ontario
| Hwy 634 JCT | ON_H63_JCT | HONI |  |  | Ontario
| IBM Markham JCT | ON_IBM_JCT | HONI |  |  | Ontario
| IBM Markham TS | ON_IBM_ISS | HONI |  |  | Ontario | GTA Toronto |  | 230 | [7 empty] | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Ignace DS JCT | ON_IGN_JCT | HONI |  |  | Ontario
| Ignace JCT | ON_IGN_JCT | HONI |  |  | Ontario
| Imperial Oil Nanticoke JCT | ON_ION_JCT | HONI |  |  | Ontario
| Imperial Oil TS | ON_IMP_ISS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Indian Chute JCT | ON_INC_JCT | HONI |  |  | Ontario
| Ingersoll JCT | ON_ING_JCT | HONI |  |  | Ontario
| Ingersoll TS | ON_ING_DSS | HONI |  |  | Ontario | London | T5/T6 | 230 | 27.6 |  |  |  | 167 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| INT Peace Bridge | XX_ONUS7_INT | ON-US Border | 42.9099 | -78.906 | Ontario
| INT Bunce Creek | XX_ONUS2_INT | ON-US Border | 42.9234 | -82.4564 | Ontario
| INT Massena | XX_ONUS6_INT | ON-US Border | 45.0047 | -74.7858 | Ontario
| INT Minnesota | XX_ONUS1_INT | ON-US Border | 48.6086 | -93.4032 | Ontario
| INT Niagara | XX_ONUS5_INT | ON-US Border | 43.1372 | -79.0458 | Ontario
| INT St. Clair | XX_ONUS3_INT | ON-US Border | 42.79 | -82.4741 | Ontario
| INT Waterman | XX_ONUS4_INT | ON-US Border | 42.2923 | -83.0946 | Ontario
| Invista JCT | ON_INV_JCT | HONI |  |  | Ontario
| IPPL Smithville TS | ON_SMV_ISS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| IPT Beauharnois | PP_ONQU1_IPT | ON-QB Border | 45.2142 | -74.3558 | Ontario
| IPT Chats Falls | PP_ONQU4_IPT | ON-QB Border | 45.5169 | -76.2104 | Ontario
| IPT Chenaux | PP_ONQU5_IPT | ON-QB Border | 45.6314 | -76.682 | Ontario
| IPT Dymond | PP_ONQU7_IPT | ON-QB Border | 47.6304 | -79.5176 | Ontario
| IPT Kipawa | PP_ONQU6_IPT | ON-QB Border | 46.3824 | -78.7273 | Ontario
| IPT Masson | PP_ONQU3_IPT | ON-QB Border | 45.5206 | -75.4229 | Ontario
| IPT Outaouais | PP_ONQU2_IPT | ON-QB Border | 45.5206 | -75.4229 | Ontario
| IPT Seven Sisters | PP_ONMB1_IPT | ON-MB Border | 49.908 | -95.1529 | Ontario
| IPT Whiteshell | PP_ONMB2_IPT | ON-MB Border | 49.7886 | -95.152 | Ontario
| Iroq Falls 115 JCT | ON_IRF_JCT | HONI |  |  | Ontario
| Iroquois Falls DS | ON_IQF_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Iroquois Fls DS JCT | ON_IQF_JCT | HONI |  |  | Ontario
| Island Falls GS | ON_ISF_GSS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Island Falls JCT | ON_ISF_JCT | HONI |  |  | Ontario
| Ivaco TS | ON_IVO_ISS | HONI |  |  | Ontario | Ottawa |  | 230 |  |  |  |  | 100 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| James Street JCT | ON_JMS_JCT | HONI |  |  | Ontario
| Jarvis TS | ON_JRV_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T3/T4 | 230 | 27.6 |  |  |  | 100 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Jasper DS | ON_JSP_DSS | HONI |  |  | Ontario | St Lawrence |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| JBL JCT | ON_JBL_JCT | HONI |  |  | Ontario
| JBL SWS | ON_JBL_SWS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Jefferson JCT | ON_JFF_JCT | HONI |  |  | Ontario
| Jellicoe DS #3 | ON_JLL_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Jellicoe DS #3 JCT | ON_JLL_JCT | HONI |  |  | Ontario
| Jim Yarrow MTS | ON_JMY_DSS | HONI |  |  | Ontario | GTA West |  | 230 | 27.6 |  |  |  | 157 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| John TS | ON_JON_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 314 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| K2 Wind GS | ON_K2W_GSS | HONI |  |  | Ontario
| K3D-10 SW JCT | ON_K3D_JCT | HONI |  |  | Ontario
| K6F-10 SW JCT | ON_K6F_JCT | HONI |  |  | Ontario
| Kalar JCT | ON_KLR_JCT | HONI |  |  | Ontario
| Kalar MTS | ON_KLR_DSS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.
| Kam Kotia DS | ON_KAM_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Kanata MTS #1 | ON_KAN_DSS | HONI |  |  | Ontario | Ottawa |  | 230 |  |  |  |  | 55 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Kapuskasing R JCT | ON_KAP_JCT | HONI |  |  | Ontario
| Kapuskasing TS | ON_KAP_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 24.9 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Karn TS | ON_KRN_TSS | HONI |  |  | Ontario | London |  | 230 | 115 | [6 empty] | Hydro One. 2020. Needs Assessment Report. London.
| Kashabowie JCT | ON_KSH_JCT | HONI |  |  | Ontario
| Keewatin DS | ON_KEE_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Keewatin JCT | ON_KEE_JCT | HONI |  |  | Ontario
| Keith TS | ON_KEI_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 230 | 115/27.6 |  |  |  | 142 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Kenilworth TS | ON_KNL_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T2/T3 | 115 | 14.2 |  |  |  | 127 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Kenora DS | ON_KNO_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Kenora MTS | ON_KNM_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Kenora MTS JCT | ON_KNM_JCT | HONI |  |  | Ontario
| Kenora TS | ON_KNO_TSS | HONI |  |  | Ontario | Northwest |  | 230 | 115 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Kent JCT | ON_KNT_JCT | HONI |  |  | Ontario
| Kent TS | ON_KNT_DSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| KEPA Wind Farm JCT | ON_KEP_JCT | HONI |  |  | Ontario
| Kerwood JCT | ON_KER_JCT | HONI |  |  | Ontario
| Kettle Creek JCT | ON_KET_JCT | HONI |  |  | Ontario
| Kidd Contractor TS | ON_KDC_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Kidd Creek Mine JCT | ON_KCM_JCT | HONI |  |  | Ontario
| Kidd Metsite TS | ON_KMT_ISS | HONI |  |  | Ontario | Northeast |  | 230 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Kidd Minesite TS | ON_KMN_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Kidd Zinc Refinery TS | ON_KDZ_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Kimball JCT | ON_KIM_JCT | HONI |  |  | Ontario
| King Edward TS | ON_KNE_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 71 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Kingston Solar GS | ON_KSS_GSS | HONI |  |  | Ontario
| Kingston Solar JCT | ON_KSS_JCT | HONI |  |  | Ontario
| Kingsville TS | ON_KSV_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 104 | 116 |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Kipling 2 GS | ON_KPG2_GSS | HONI |  |  | Ontario
| Kipling GS | ON_KPG_GSS | HONI |  |  | Ontario
| Kipling JCT | ON_KPG_JCT | HONI |  |  | Ontario
| Kirkland Lake TS | ON_KLL_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Kirkton JCT | ON_KRK_JCT | HONI |  |  | Ontario
| Kitchener #1&4 JCT | ON_KJ1_JCT | HONI |  |  | Ontario
| Kitchener #2&3 JCT | ON_KJ2_JCT | HONI |  |  | Ontario
| Kitchener #6 JCT | ON_KJ6_JCT | HONI |  |  | Ontario
| Kitchener #8 JCT | ON_KJ8_JCT | HONI |  |  | Ontario
| Kitchener #9 JCT | ON_KJ9_JCT | HONI |  |  | Ontario
| Kitchener Graber JCT | ON_KGB_JCT | HONI |  |  | Ontario
| Kitchener MTS #1 | ON_KM1_DSS | HONI |  |  | Ontario | KWCG |  | 115 |  |  |  |  | 54 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Kitchener MTS #3 | ON_KM3_DSS | HONI |  |  | Ontario | KWCG |  | 115 |  |  |  |  | 108 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Kitchener MTS #4 | ON_KM4_DSS | HONI |  |  | Ontario | KWCG |  | 115 |  |  |  |  | 90 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Kitchener MTS #5 | ON_KM5_DSS | HONI |  |  | Ontario | KWCG |  | 115 |  |  |  |  | 80 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Kitchener MTS #6 | ON_KM6_DSS | HONI |  |  | Ontario | KWCG |  | 230 |  |  |  |  | 90 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Kitchener MTS #7 | ON_KM7_DSS | HONI |  |  | Ontario | KWCG |  | 115 |  |  |  |  | 54 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Kitchener MTS #8 | ON_KM8_DSS | HONI |  |  | Ontario | KWCG |  | 230 |  |  |  |  | 54 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Kitchener MTS #9 | ON_KM9_DSS | HONI |  |  | Ontario | KWCG |  | 230 |  |  |  |  | 90 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Kleinburg TS | ON_KLE_DSS | HONI |  |  | Ontario | GTA North | T1/T2 | 230 | 44/27.6 |  |  |  | 196 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Knob JCT | ON_KNB_JCT | HONI |  |  | Ontario
| Lac Des Iles JCT | ON_LDI_JCT | HONI |  |  | Ontario
| Lac Des Iles Min SWS | ON_LDI_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Lafarge Bath TS | ON_LFB_ISS | HONI |  |  | Ontario | Peterborough-Kingston |  | 230 | 13.8 | [6 empty] | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Lafarge JCT | ON_LAF_JCT | HONI |  |  | Ontario
| Lafarge Woodstock TS | ON_LFW_ISS | HONI |  |  | Ontario | London |  | 115 | [7 empty] | Hydro One. 2020. Needs Assessment Report. London.
| Laforest Road DS | ON_LFR_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Laforest Road JCT | ON_LFR_JCT | HONI |  |  | Ontario
| Lake Huron WTP TS | ON_LAH_ISS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | [7 empty] | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan.
| Lake TS | ON_LAK_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2/T3/T4 | 230 | 27.6/13.8 |  |  |  | 207 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Lakehead TS | ON_LKH_TSS | HONI |  |  | Ontario | Northwest |  | 230 | 115 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Lakeview SWS | ON_LKV_SWS | HONI |  |  | Ontario | GTA West |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Lambton TS #2 | ON_LMB_DSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 345 | 230/27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Landon GS | ON_LND_GSS | HONI |  |  | Ontario
| Landon JCT | ON_LND_JCT | HONI |  |  | Ontario
| Lantz JCT | ON_LNZ_JCT | HONI |  |  | Ontario
| Larchwood TS | ON_LCH_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T2 | 115 | 44 |  |  |  |  | 37.53 |  | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Lasco JCT | ON_LAS_JCT | HONI |  |  | Ontario
| Lauzon JCT | ON_LAU_JCT | HONI |  |  | Ontario
| Lauzon TS | ON_LAU_DSS | HONI |  |  | Ontario | Windsor-Essex | T5/T6/T7/T8 | 230 | 115/27.6 |  |  |  | 204 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Leamington JCT | ON_LEM_JCT | HONI |  |  | Ontario
| Leamington TS | ON_LEM_DSS | HONI |  |  | Ontario | Windsor-Essex | T1/T2/T3/T4 | 230 | 27.6 |  |  |  | 366 | 390 |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Leaside JCT | ON_LES_JCT | HONI |  |  | Ontario
| Leaside TS | ON_LES_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 115/13.8 |  |  |  | 202 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Lennox TS | ON_LEN_TSS | HONI |  |  | Ontario | Peterborough-Kingston |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Leong JCT | ON_LEO_JCT | HONI |  |  | Ontario
| Leslie East JCT | ON_LSE_JCT | HONI |  |  | Ontario
| Leslie JCT | ON_LSL_JCT | HONI |  |  | Ontario
| Leslie TS | ON_LSL_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 13.8 |  |  |  | 325 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Leslie West JCT | ON_LSW_JCT | HONI |  |  | Ontario
| Limebank JCT | ON_LBK_JCT | HONI |  |  | Ontario
| Limebank MTS | ON_LBK_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 68 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Lincoln Heights TS | ON_LNH_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 71 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Lindsay TS | ON_LND_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2 | 230 | 44 |  |  |  | 161 | 182 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Lisgar TS | ON_LSG_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 75 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Little Long 2 JCT | ON_LLG2_JCT | HONI |  |  | Ontario
| Little Long JCT | ON_LLG_JCT | HONI |  |  | Ontario
| Little Long SWS | ON_LLG_SWS | HONI |  |  | Ontario | Northeast |  | 230 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Lockerby Mine TS | ON_LBM_ISS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Sudbury Algoma.
| Lodgeroom DS | ON_LGR_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 115 | 12.5 |  |  |  | 11 | 11 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Long Reach East JCT | ON_LRE_JCT | HONI |  |  | Ontario
| Long Reach West JCT | ON_LRW_JCT | HONI |  |  | Ontario
| Longlac TS | ON_LLC_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 44 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Longueuil JCT | ON_LGU_JCT | HONI |  |  | Ontario
| Longueuil TS | ON_LGU_DSS | HONI |  |  | Ontario | Ottawa |  | 230 | 44 |  |  |  | 98 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Longwood TS | ON_LGW_DSS | HONI |  |  | Ontario | London | T13/T14 | 500 | 230/27.6 |  |  |  | 128 |  | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Lorne Park TS | ON_LNP_DSS | HONI |  |  | Ontario | GTA West | T1/T2 | 230 | 27.6 |  |  |  | 197 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Louth JCT | ON_LOU_JCT | HONI |  |  | Ontario
| Lower Notch GS | ON_LWN_GSS | HONI |  |  | Ontario
| Lower Notch JCT | ON_LWN_JCT | HONI |  |  | Ontario
| Lucasville JCT | ON_LUC_JCT | HONI |  |  | Ontario
| Lumsden JCT | ON_LUM_JCT | HONI |  |  | Ontario
| Lunenburg JCT | ON_LUN_JCT | HONI |  |  | Ontario
| Lynwood JCT | ON_LYN_JCT | HONI |  |  | Ontario
| Lyons JCT | ON_LYO_JCT | HONI |  |  | Ontario
| Macassa #3 JCT | ON_MAC_JCT | HONI |  |  | Ontario
| Macassa Mill JCT | ON_MAM_JCT | HONI |  |  | Ontario
| MacKay JCT | ON_MKY_JCT | HONI |  |  | Ontario
| Mackay TS | ON_MKY_DSS | HONI |  |  | Ontario | East Lake Superior |  | 230 | 115/34.5 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Mackenzie TS | ON_MKZ_TSS | HONI |  |  | Ontario | Northwest |  | 230 | 115 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Magellan Aerospace JCT | ON_MGA_JCT | HONI |  |  | Ontario
| Magellan Aerospace TS | ON_MGA_ISS | HONI |  |  | Ontario | Renfrew |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Renfrew.
| Magpie SWS | ON_MGP_SWS | HONI |  |  | Ontario | East Lake Superior |  | 115 | [7 empty] | Hydro One. 2019. Needs Assessment Report East Lake Superior Region.
| Magpie TS | ON_MGP_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 12 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Main TS | ON_MAI_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 77 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Majestic JCT | ON_MAJ_JCT | HONI |  |  | Ontario
| Majestic TS | ON_MAJ_ISS | HONI |  |  | Ontario | Bruce-Huron |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Malden JCT | ON_MLD_JCT | HONI |  |  | Ontario
| Malden TS | ON_MLD_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 230 | 27.6 |  |  |  | 183 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Malvern TS | ON_MLV_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 176 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Manby TS | ON_MBY_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 115/27.6 |  |  |  | 226 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Manitou Falls GS | ON_MNF_GSS | HONI |  |  | Ontario
| Manitoulin TS | ON_MNT_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T3/T4 | 115 | 44 |  |  |  |  | 37.53 |  | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Manitouwadge DS | ON_MTG_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Manitouwadge JCT | ON_MTW_JCT | HONI |  |  | Ontario
| Manitouwadge JCT B | ON_MTW_JCT | HONI |  |  | Ontario
| Manitouwadge TS | ON_MTW_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 44 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Manordale JCT | ON_MDL_JCT | HONI |  |  | Ontario
| Manordale MTS | ON_MDL_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 22 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Manotick DS | ON_MTK_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 8.32 |  |  |  | 17 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Manotick JCT | ON_MTK_JCT | HONI |  |  | Ontario
| Marathon DS | ON_MRT_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Marathon DS JCT | ON_MRT_JCT | HONI |  |  | Ontario
| Marathon TS | ON_MRT_TSS | HONI |  |  | Ontario | Northwest |  | 230 | 115 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Marchwood JCT | ON_MCW_JCT | HONI |  |  | Ontario
| Marchwood MTS | ON_MCW_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 34 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Margach DS | ON_MGH_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Margach JCT | ON_MGH_JCT | HONI |  |  | Ontario
| Marine JCT | ON_MAR_JCT | HONI |  |  | Ontario
| Marionville DS | ON_MRN_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 27.6 |  |  |  | 28 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Marionville JCT | ON_MRN_JCT | HONI |  |  | Ontario
| Markham #1 JCT | ON_MJ1_JCT | HONI |  |  | Ontario
| Markham #1 MTS | ON_MM1_DSS | HONI |  |  | Ontario | GTA North |  | 230 | 27.6 |  |  |  | 81 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Markham #2 JCT | ON_MJ2_JCT | HONI |  |  | Ontario
| Markham #2 MTS | ON_MM2_DSS | HONI |  |  | Ontario | GTA North |  | 230 | 27.6 |  |  |  | 101 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Markham #3 JCT | ON_MJ3_JCT | HONI |  |  | Ontario
| Markham #3 MTS | ON_MM3_DSS | HONI |  |  | Ontario | GTA North | T1/T2/T3/T4 | 230 | 27.6 |  |  |  | 202 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Markham #4 JCT | ON_MJ4_JCT | HONI |  |  | Ontario
| Markham #4 MTS | ON_MM4_DSS | HONI |  |  | Ontario | GTA North |  | 230 | 27.6 |  |  |  | 153 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Marmion Lake JCT | ON_MRM_JCT | HONI |  |  | Ontario
| Marten River JCT | ON_MRV_JCT | HONI |  |  | Ontario
| Martindale TS | ON_MTD_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T25/T26 | 230 | 115/44 |  |  |  |  | 164.34 |  | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Massanoga JCT | ON_MOG_JCT | HONI |  |  | Ontario
| Massey DS | ON_MSY_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1 | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Massey JCT | ON_MSY_JCT | HONI |  |  | Ontario
| Matachewan JCT | ON_MWN_JCT | HONI |  |  | Ontario
| Mattabi JCT | ON_MTB_JCT | HONI |  |  | Ontario
| Mazinaw DS | ON_MZW_DSS | HONI |  |  | Ontario | Renfrew | T1 | 230 | 12.5 |  |  |  | 5.4 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Renfrew.
| McCrea JCT | ON_MCC_JCT | HONI |  |  | Ontario
| McGillivray R&BP TS | ON_MCG_ISS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | [7 empty] | Hydro One. 2017. Bruce - Huron Regional Infrastructure Plan.
| McKinnon's JCT | ON_MCK_JCT | HONI |  |  | Ontario
| McLeans Mountain GS | ON_MCL_GSS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| McLeans Mountain JCT | ON_MCL_JCT | HONI |  |  | Ontario
| McMaster JCT | ON_MCM_JCT | HONI |  |  | Ontario
| McMaster TS | ON_MCM_ISS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 115 | [7 empty] | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing.
| Meadowvale TS | ON_MDV_DSS | HONI |  |  | Ontario | GTA West | T1/T2 | 230 | 44 |  |  |  | 181 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Meaford TS | ON_MEA_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2 | 230 | 44 |  |  |  | 52 | 59 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Merivale MTS | ON_MER_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | [7 empty] | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Merivale TS | ON_MER_TSS | HONI |  |  | Ontario | Ottawa |  | 230 | 115 |  |  |  | 18 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Michigan JCT | ON_MIC_JCT | HONI |  |  | Ontario
| Middleport TS | ON_MPT_TSS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Midhurst TS | ON_MDH_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2/T3/T4 | 230 | 44 |  |  |  | 311 | 355 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Mill Creek JCT | ON_MLC_JCT | HONI |  |  | Ontario
| Mill Street JCT | ON_MLS_JCT | HONI |  |  | Ontario
| Milltown JCT | ON_MLT_JCT | HONI |  |  | Ontario
| Milman Foundry JCT | ON_MLF_JCT | HONI |  |  | Ontario
| Milman Foundry TS | ON_MLF_ISS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Milton SWS | ON_MIL_SWS | HONI |  |  | Ontario | GTA West |  | 500 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Minaki DS | ON_MIN_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Minaki JCT | ON_MIN_JCT | HONI |  |  | Ontario
| Minden TS | ON_MND_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2 | 230 | 44 |  |  |  | 52 | 58 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Minesing JCT | ON_MNS_JCT | HONI |  |  | Ontario
| Minnova JCT | ON_MNV_JCT | HONI |  |  | Ontario
| Mission Falls GS | ON_MSF_GSS | HONI |  |  | Ontario
| Mississagi TS | ON_MSS_DSS | HONI |  |  | Ontario | East Lake Superior |  | 230 | 230 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Mississippi JCT | ON_MSP_JCT | HONI |  |  | Ontario
| Modeland TS | ON_MOD_DSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Mohawk Str 31 EP JCT | ON_MHS_JCT | HONI |  |  | Ontario
| Mohawk TS | ON_MOH_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 | 13.8 |  |  |  | 104 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Monteith DS | ON_MON_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Monteith DS JCT | ON_MON_JCT | HONI |  |  | Ontario
| Monteith SWS | ON_MON_SWS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Monteith SWS JCT | ON_MON_JCT | HONI |  |  | Ontario
| Montrose JCT | ON_MTR_JCT | HONI |  |  | Ontario
| Moose Lake TS | ON_MSL_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 44 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Moosonee DS | ON_MOO_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 24.9 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Moosonee JCT | ON_MOO_JCT | HONI |  |  | Ontario
| Moosonee SWS | ON_MOO_SWS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Morrisburg JCT | ON_MRB_JCT | HONI |  |  | Ontario
| Morrisburg TS | ON_MRB_DSS | HONI |  |  | Ontario | St Lawrence |  | 115 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Moulton JCT | ON_MOU_JCT | HONI |  |  | Ontario
| Moulton MTS | ON_MOU_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 34 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Mount Hope JCT | ON_MTH_JCT | HONI |  |  | Ontario
| Mountain Chute DS | ON_MTC_GSS | HONI |  |  | Ontario | Renfrew | T1 | 115 | 12.5 |  |  |  | 11.3 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Mountain Chute GS | ON_MTC_GSS | HONI |  |  | Ontario
| Mountain Chute JCT | ON_MTC_JCT | HONI |  |  | Ontario
| Murillo DS | ON_MRL_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 26.4 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Murillo JCT | ON_MRL_JCT | HONI |  |  | Ontario
| Murray TS | ON_MRY_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 13.8 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Muskoka TS | ON_MSK_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2 | 230 | 44 |  |  |  | 169 | 199 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Musselwhite SWS | ON_MSW_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Nagagami GS | ON_NAG_DSS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Nagagami GS JCT | ON_NAG_JCT | HONI |  |  | Ontario
| Namewaminikan GS | ON_NAM_GSS | HONI |  |  | Ontario
| Namewaminikan JCT | ON_NAM_JCT | HONI |  |  | Ontario
| Nanticoke Creek JCT | ON_NTC_JCT | HONI |  |  | Ontario
| Nanticoke TS | ON_NTK_TSS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Napanee GS | ON_NAP_GSS | HONI |  |  | Ontario | Peterborough-Kingston |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Napanee TS | ON_NAP_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1 | 230 | 44 |  |  |  | 104 | 117 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| National Aeronautical TS | ON_NAE_ISS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 1 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Nationl Research JCT | ON_NRS_JCT | HONI |  |  | Ontario
| Navan DS | ON_NVN_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 27.6/8.32 |  |  |  | 15 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Neale JCT | ON_NEA_JCT | HONI |  |  | Ontario
| Nebo JCT | ON_NEB_JCT | HONI |  |  | Ontario
| Nebo TS | ON_NEB_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2/T3/T4 | 230 | 27.6 |  |  |  | 229 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Nelson TS | ON_NEL_DSS | HONI |  |  | Ontario | London | T1/T2 | 115 | 27.6 |  |  |  | 105 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Nepean Epworth JCT | ON_NPE_JCT | HONI |  |  | Ontario
| Nepean Epworth MTS | ON_NPE_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 25 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Nepean TS | ON_NEP_DSS | HONI |  |  | Ontario | Ottawa |  | 230 | 44 |  |  |  | 144 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Nestor Falls DS | ON_NES_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 13.2 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Nestor Falls JCT | ON_NES_JCT | HONI |  |  | Ontario
| New Liskeard JCT | ON_NLK_JCT | HONI |  |  | Ontario
| New Liskeard JCT #2 | ON_NLK2_JCT | HONI |  |  | Ontario
| Newboro DS | ON_NBO_DSS | HONI |  |  | Ontario | St Lawrence |  | 115 | 8.32 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Newington DS | ON_NWG_DSS | HONI |  |  | Ontario | St Lawrence |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Newington JCT | ON_NWG_JCT | HONI |  |  | Ontario
| Newport JCT | ON_NWP_JCT | HONI |  |  | Ontario
| Newton TS | ON_NWT_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 | 13.8 |  |  |  | 78 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Niagara A1T T#49 JCT | ON_NIT_JCT | HONI |  |  | Ontario
| Niagara JCT | ON_NIA_JCT | HONI |  |  | Ontario
| Niagara West JCT | ON_NIW_JCT | HONI |  |  | Ontario
| Niagara West MTS | ON_NIW_DSS | HONI |  |  | Ontario | Niagara |  | 230 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.
| Nickel Basin JCT | ON_NIC_JCT | HONI |  |  | Ontario
| Nine Mile JCT | ON_NIN_JCT | HONI |  |  | Ontario
| Nipigon DS | ON_NIP_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 4.16 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Nipigon JCT | ON_NIP_JCT | HONI |  |  | Ontario
| Nobel SWS | ON_NOB_SWS | HONI |  |  | Ontario | Georgian Bay |  | 500 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Norfolk TS | ON_NOR_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 | 27.6 |  |  |  | 97 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Norman JCT | ON_NOM_JCT | HONI |  |  | Ontario
| North Bay TS | ON_NBY_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| North Kent 1 GS | ON_NOK_GSS | HONI |  |  | Ontario
| North Kent 1 JCT | ON_NOK_JCT | HONI |  |  | Ontario
| North Shore DS | ON_NOS_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1 | 115 | 24.9 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Northbrook DS | ON_NBK_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1 | 115 | 12.5 |  |  |  | 12 | 12 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Northbrook JCT | ON_NBK_JCT | HONI |  |  | Ontario
| Northern Ave TS | ON_NAV_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 34.5/12 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| NOTL MTS #2 | ON_NM2_DSS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.
| NOTL York MTS #1 | ON_NM1_DSS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.
| NOTL York MTS #1 JCT | ON_NJ1_JCT | HONI |  |  | Ontario
| Notre Development TS | ON_NOT_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Nova Corunna TS | ON_NVC_ISS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area.
| Nova Moore JCT | ON_NVM_JCT | HONI |  |  | Ontario
| Nova Moore TS | ON_NVM_ISS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area.
| Nova St Clair R TS | ON_NSC_ISS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area.
| Nova SWS | ON_NOV_SWS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area.
| Novelis TS | ON_NLS_ISS | HONI |  |  | Ontario | Peterborough-Kingston |  | 115 | 13.2 | [6 empty] | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| NPD #2 STR10 JCT | ON_NPD_JCT | HONI |  |  | Ontario
| NPIF Kingston GS | ON_NPK_GSS | HONI |  |  | Ontario | Peterborough-Kingston |  | 230 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| NPIF Kingston JCT | ON_NPK_JCT | HONI |  |  | Ontario
| NQL1 B JCT | ON_NQL_JCT | HONI |  |  | Ontario
| NRC TS | ON_NRC_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 25 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| O'Brien JCT | ON_OBR_JCT | HONI |  |  | Ontario
| Oakville TS #2 | ON_OAK_DSS | HONI |  |  | Ontario | GTA West | T1/T2 | 230 | 27.6 |  |  |  | 175 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Odessa JCT | ON_ODS_JCT | HONI |  |  | Ontario
| Ogden JCT | ON_ODG_JCT | HONI |  |  | Ontario
| OHSC GS | ON_OHS_GSS | HONI |  |  | Ontario
| OHSC JCT | ON_OHS_JCT | HONI |  |  | Ontario
| Old Armitage JCT | ON_OLA_JCT | HONI |  |  | Ontario
| Onakawana JCT | ON_ONA_JCT | HONI |  |  | Ontario
| Onakawana TS | ON_ONA_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Onaping Area M&M TS | ON_OAM_ISS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Onaping JCT | ON_ONP_JCT | HONI |  |  | Ontario
| Orangeville TS | ON_ORA_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2/T3/T4 | 230 | 44/27.6 |  |  |  | 194 | 226 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Orillia TS | ON_ORI_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2 | 230 | 44 |  |  |  | 154 | 175 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Orleans JCT | ON_ORL_JCT | HONI |  |  | Ontario
| Orleans JCT #2 | ON_OR2_JCT | HONI |  |  | Ontario
| Orleans TS | ON_ORL_DSS | HONI |  |  | Ontario | Ottawa |  | 230 | 27.6 |  |  |  | 102 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Osgoode JCT | ON_OSG_JCT | HONI |  |  | Ontario
| Oshawa Area JCT | ON_OSH_JCT | HONI |  |  | Ontario
| Oshawa G.M. JCT | ON_OGM_JCT | HONI |  |  | Ontario
| Oshawa G.M. TS | ON_OGM_ISS | HONI |  |  | Ontario | GTA East |  | 230 | [7 empty] | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| Otonabee TS | ON_OTB_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 230 | 44/27.6 |  |  |  | 202 | 224 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Ottawa JCT | ON_OTT_JCT | HONI |  |  | Ontario
| Otter Creek JCT | ON_OTC_JCT | HONI |  |  | Ontario
| Otter Rapids GS | ON_ORP_GSS | HONI |  |  | Ontario
| Otter Rapids SWS | ON_ORP_SWS | HONI |  |  | Ontario | Northeast |  | 230 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Otto Holden TS | ON_OTH_DSS | HONI |  |  | Ontario | Northeast |  | 230 | 115/13.8 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Overbrook TS | ON_OVB_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 130 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Owen Sound JCT | ON_OWS_JCT | HONI |  |  | Ontario
| Owen Sound TS | ON_OWS_DSS | HONI |  |  | Ontario | Bruce-Huron | T3/T4 DESN | 230 | 115/44 |  |  |  | 208.5 | 232.5 | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Oxford Street JCT | ON_OXS_JCT | HONI |  |  | Ontario
| Oxy Vinyls TS | ON_OXY_ISS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing.
| P Sutherland Sr JCT | ON_PSS_JCT | HONI |  |  | Ontario
| P Sutherland Sr SYD | ON_PSS_GSS | HONI |  |  | Ontario
| P7B STR 320 JCT | ON_P7B_JCT | HONI |  |  | Ontario
| Pakwash JCT | ON_PAK_JCT | HONI |  |  | Ontario
| Palermo TS | ON_PAL_DSS | HONI |  |  | Ontario | GTA West | T3/T4 | 230 | 27.6 |  |  |  | 110 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Palermo TxB JCT | ON_PAL_JCT | HONI |  |  | Ontario
| Palmerston TS | ON_PLM_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | 44 |  |  |  | 83.3 | 83.3 | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Pamour JCT | ON_PAM_JCT | HONI |  |  | Ontario
| Panabrasives TS | ON_PNB_ISS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing.
| Pancake JCT | ON_PNC_JCT | HONI |  |  | Ontario
| Parkhill TS | ON_PKH_ISS | HONI |  |  | Ontario | Bruce-Huron |  | 500 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Parks TS | ON_PKS_DSS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Parkway JCT | ON_PKW_JCT | HONI |  |  | Ontario
| Parkway TS | ON_PKW_TSS | HONI |  |  | Ontario | GTA Toronto |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Parry Sound JCT | ON_PRS_JCT | HONI |  |  | Ontario
| Parry Sound TS | ON_PRS_DSS | HONI |  |  | Ontario | Georgian Bay | T1/T2 | 230 | 44 |  |  |  | 47 | 51 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Patrick St TS | ON_PTS_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 34.5 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Pedley JCT | ON_PED_JCT | HONI |  |  | Ontario
| Pelham JCT | ON_PEL_JCT | HONI |  |  | Ontario
| Pembroke TS | ON_PEM_DSS | HONI |  |  | Ontario | Renfrew | T1/T2 | 115 | 44 |  |  |  | 49.6 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Perrault Falls DS | ON_PER_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Petawawa DS | ON_PET_DSS | HONI |  |  | Ontario | Renfrew | T1/T2 | 115 | 12.5 |  |  |  | 14.8 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Renfrew.
| Petawawa JCT | ON_PET_JCT | HONI |  |  | Ontario
| Pic DS | ON_PIC_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Pic JCT | ON_PIC_JCT | HONI |  |  | Ontario
| Pickering A SWS | ON_PKA_SWS | HONI |  |  | Ontario | GTA East |  | 230 | [7 empty] | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| Pickering B SWS | ON_PKB_SWS | HONI |  |  | Ontario | GTA East |  | 230 | [7 empty] | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| Pickle Lake SWS | ON_PKL_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Picton TS | ON_PCT_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 230 | 44 |  |  |  | 78 | 89 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Pinard JCT | ON_PIN_JCT | HONI |  |  | Ontario
| Pinard JCT #2 | ON_PI2_JCT | HONI |  |  | Ontario
| Pinard TS | ON_PIN_TSS | HONI |  |  | Ontario | Northeast |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Pine Portage SWS | ON_PPT_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Placer JCT | ON_PLC_JCT | HONI |  |  | Ontario
| Plank Road JCT | ON_PLK_JCT | HONI |  |  | Ontario
| Pleasant TS | ON_PLE_DSS | HONI |  |  | Ontario | GTA West | T1/T2/T5/T6/T7/T8 | 230 | 44/27.6 |  |  |  | 517 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Porcupine TS | ON_PCP_TSS | HONI |  |  | Ontario | Northeast |  | 500 | 230 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Port Alma WF GS | ON_PMA_GSS | HONI |  |  | Ontario | Windsor-Essex |  | 230 | [7 empty] | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Port Arthur JCT | ON_PTA_JCT | HONI |  |  | Ontario
| Port Arthur TS #1 | ON_PTA_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Port Colborne TS | ON_PTC_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Port Hope TS | ON_PTH_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2/T3/T4 | 115 | 44 |  |  |  | 229 | 256 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Portal JCT | ON_POR_JCT | HONI |  |  | Ontario
| Portland JCT | ON_PTL_JCT | HONI |  |  | Ontario
| Portlands Energy JCT | ON_PTE_JCT | HONI |  |  | Ontario
| Power JCT | ON_POW_JCT | HONI |  |  | Ontario
| Powerline JCT | ON_PWL_JCT | HONI |  |  | Ontario
| Powerline MTS | ON_PWL_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 |  |  |  |  | 114 |  |  | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Preston JCT | ON_PRE_JCT | HONI |  |  | Ontario
| Preston TS | ON_PRE_DSS | HONI |  |  | Ontario | KWCG |  | 230 | 115/27.6 |  |  |  | 113 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Pte-Aux-Roches WF GS | ON_PAR_GSS | HONI |  |  | Ontario
| Pte-Aux-Roches WF JCT | ON_PAR_JCT | HONI |  |  | Ontario
| Puslinch DS | ON_PUS_DSS | HONI |  |  | Ontario | KWCG |  | 115 | 27.6 |  |  |  | 56 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Puslinch JCT | ON_PUS_JCT | HONI |  |  | Ontario
| Q5B STR A6 JCT | ON_Q5B_JCT | HONI |  |  | Ontario
| Q6S STR M60 JCT | ON_Q6S_JCT | HONI |  |  | Ontario
| Quirke Lake JCT | ON_QUL_JCT | HONI |  |  | Ontario
| Rabbit Lake SWS | ON_RBL_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Railton JCT | ON_RLT_JCT | HONI |  |  | Ontario
| Railway JCT | ON_RLW_JCT | HONI |  |  | Ontario
| Rainy River Gold JCT | ON_RRG_JCT | HONI |  |  | Ontario
| Rainy River Gold SWS | ON_RRG_SWS | HONI |  |  | Ontario | Northwest |  | 230 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Raisin River JCT | ON_RSR_JCT | HONI |  |  | Ontario
| Ramore TS | ON_RMR_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Rayner GS | ON_RNR_GSS | HONI |  |  | Ontario
| Red Lake TS | ON_RDL_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 44 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Red Rock DS | ON_RRK_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Red Rock GS | ON_RRC_GSS | HONI |  |  | Ontario
| Red Rock GS JCT | ON_RRC_JCT | HONI |  |  | Ontario
| Red Rock JCT | ON_RRK_JCT | HONI |  |  | Ontario
| Renison JCT | ON_RNS_JCT | HONI |  |  | Ontario
| Renison TS | ON_RNS_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Reserve JCT | ON_RSV_JCT | HONI |  |  | Ontario
| Rexdale TS | ON_RXD_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 187 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| RFP Kraft TS | ON_RFK_ISS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum. Ontario 230 kV East-West Tie.
| RFP Thorold TS | ON_RFT_GSS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.; Ontario Superior Court of Justice. 2019. Hydro One Networks Inc. and The Haudenosaunee Confederacy Chiefs Council et al. Statement of Claim. CV-19-00000152-0000.
| RFP Thunder Bay TS | ON_RFB_GSS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum. Ontario 230 kV East-West Tie.
| Richmond Hill #2 JCT | ON_RJ2_JCT | HONI |  |  | Ontario
| Richmond Hill JCT | ON_RJ1_JCT | HONI |  |  | Ontario
| Richmond Hill MTS #1 | ON_RM1_DSS | HONI |  |  | Ontario | GTA North |  | 230 | 27.6 |  |  |  | 127 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan. | LTR assumed equal between MTS
| Richmond Hill MTS #2 | ON_RM2_DSS | HONI |  |  | Ontario | GTA North |  | 230 | 27.6 |  |  |  | 127 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan. | LTR assumed equal between MTS
| Richmond MTS | ON_RMD_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 5 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Richview JCT | ON_RCV_JCT | HONI |  |  | Ontario
| Richview TS | ON_RCV_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 460 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Riverdale JCT | ON_RVD_JCT | HONI |  |  | Ontario
| Riverdale TS | ON_RVD_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 105 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Riverside JCT | ON_RVS_JCT | HONI |  |  | Ontario
| Rockland DS | ON_RKL_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 8.32 |  |  |  | 9 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Rockland East DS | ON_RKE_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 8.32 |  |  |  | 15 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Rockland East DS JCT | ON_RKE_JCT | HONI |  |  | Ontario
| Rockland JCT | ON_RKL_JCT | HONI |  |  | Ontario
| Rosedene JCT | ON_RSD_JCT | HONI |  |  | Ontario
| Rourke Line JCT | ON_RLN_JCT | HONI |  |  | Ontario
| Roxmark JCT | ON_RXK_JCT | HONI |  |  | Ontario
| Roxmark Mine TS | ON_RXM_ISS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process Addendum. Ontario 230 kV East-West Tie.
| Royal Oak TS | ON_RYO_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Runnymede TS | ON_RNY_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 27.6 |  |  |  | 219 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Rush MTS | ON_RSH_DSS | HONI |  |  | Ontario | KWCG |  | 115 |  |  |  |  | 68 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Russell DS | ON_RSL_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 8.32 |  |  |  | 8 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Russell TS | ON_RSS_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 69 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| S2B-M31 JCT | ON_S2B_JCT | HONI |  |  | Ontario
| S3S_S4S STR 8 JCT | ON_S3S_JCT | HONI |  |  | Ontario
| S7M STR 673N JCT | ON_S7M_JCT | HONI |  |  | Ontario
| S7M STR R14-R15 JCT | ON_S7R_JCT | HONI |  |  | Ontario
| Salford JCT | ON_SFD_JCT | HONI |  |  | Ontario
| Saltfleet JCT | ON_SLT_JCT | HONI |  |  | Ontario
| Sam Lake DS | ON_SML_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 26.4 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Sandusk GS | ON_SND_GSS | HONI |  |  | Ontario
| Sandusk JCT | ON_SND_JCT | HONI |  |  | Ontario
| Sandusk SWS | ON_SND_SWS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 230 | [7 empty] | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Sandwich JCT | ON_SNW_JCT | HONI |  |  | Ontario
| Sapawe DS | ON_SPW_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Sapawe JCT | ON_SPW_JCT | HONI |  |  | Ontario
| Sarnia Scott JCT | ON_SNS_JCT | HONI |  |  | Ontario
| Sarnia Scott TS | ON_SNS_TSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | 115 | [6 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Saunders JCT | ON_SAU_JCT | HONI |  |  | Ontario
| Scarboro JCT | ON_SCB_JCT | HONI |  |  | Ontario
| Scarboro TS | ON_SCB_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 340 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Scheifele JCT | ON_SCF_JCT | HONI |  |  | Ontario
| Scheifele MTS | ON_SCF_DSS | HONI |  |  | Ontario | KWCG |  | 230 |  |  |  |  | 161 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Schreiber JCT | ON_SCH_JCT | HONI |  |  | Ontario
| Schreiber Winnipeg DS | ON_SCW_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Scout Lake JCT | ON_SCL_JCT | HONI |  |  | Ontario
| Seaforth L7S JCT | ON_SFL_JCT | HONI |  |  | Ontario
| Seaforth TS | ON_SFT_DSS | HONI |  |  | Ontario | Bruce-Huron | T1/T2 DESN | 230 | 115/27.6 |  |  |  | 45.1 | 55.4 |  | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Seaton MTS | ON_SEN_DSS | HONI |  |  | Ontario | GTA East | T1/T2 | 230 | 27.6 |  |  |  | 153 |  |  | Hydro One. 2020. GTA East Regional Infrastructure Plan. | In-service 2021
| Selby JCT | ON_SBY_JCT | HONI |  |  | Ontario
| Selco JCT | ON_SLC_JCT | HONI |  |  | Ontario
| Serpent River JCT | ON_SER_JCT | HONI |  |  | Ontario
| Shabaqua DS | ON_SBQ_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Shabaqua JCT | ON_SBQ_JCT | HONI |  |  | Ontario
| Shannon GS | ON_SHN_DSS | HONI |  |  | Ontario | Georgian Bay |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Sharbot DS | ON_SHR_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1 | 230 | 12.5 |  |  |  | 6 | 6 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Sharbot JCT | ON_SHR_JCT | HONI |  |  | Ontario
| Shebandowan JCT | ON_SHB_JCT | HONI |  |  | Ontario
| Shell Sarnia TS | ON_SHL_ISS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Independent Electricity Market Operator. 2004. Connection Assessment & Approval Process. System Impact Assessment Report For the four Generation Developments proposed for the Sarnia-Windsor Area.
| Sheppard TS | ON_SHP_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 205 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Shiningtree DS | ON_SGT_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 24.9 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Shiningtree JCT | ON_SGT_JCT | HONI |  |  | Ontario
| Sidney TS | ON_SDY_DSS | HONI |  |  | Ontario | Peterborough-Kingston | T1/T2 | 115 | 44 |  |  |  | 112 | 112 |  | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| Siebert JCT | ON_SBT_JCT | HONI |  |  | Ontario
| Silver Falls GS | ON_SFS_GSS | HONI |  |  | Ontario
| Silvercreek GS | ON_SVC_GSS | HONI |  |  | Ontario
| Silvercreek JCT | ON_SVC_JCT | HONI |  |  | Ontario
| Sioux Narrows DS | ON_SXN_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Sioux Narrows JCT | ON_SXN_JCT | HONI |  |  | Ontario
| Sithe Goreway JCT | ON_SGW_JCT | HONI |  |  | Ontario
| SKWP CMS | ON_SKW_GSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| SKWP CMS JCT | ON_SKW_JCT | HONI |  |  | Ontario
| Slate Falls DS | ON_SLF_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 24.9 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Slate Falls JCT | ON_SLF_JCT | HONI |  |  | Ontario
| Slater TS | ON_SLT_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 118 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Smiths Falls TS | ON_SMF_DSS | HONI |  |  | Ontario | St Lawrence |  | 115 | 8.32 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report St Lawrence.
| Smoky Falls GS | ON_SKF_GSS | HONI |  |  | Ontario
| Smoky Falls JCT | ON_SKF_JCT | HONI |  |  | Ontario
| Smooth Rock Falls DS | ON_SRF_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Smooth Rock Falls JCT | ON_SRF_JCT | HONI |  |  | Ontario
| South Gloucester DS | ON_SGL_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 8 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| South Gloucester JCT | ON_SGL_JCT | HONI |  |  | Ontario
| South March SWS | ON_SOM_SWS | HONI |  |  | Ontario | Ottawa |  | 230 |  |  |  |  | 109 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| South March TS | ON_SOM_DSS | HONI |  |  | Ontario | Ottawa |  | 230 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | IESO. 2017. System Impact Assessment Report: Connection Assessment & Approval Process. (2nd Draft Report). South Nepean MTS & South Nepean Transmission Reinforcement.
| Southcote JCT | ON_SCT_JCT | HONI |  |  | Ontario
| Southgate GS | ON_SOG_GSS | HONI |  |  | Ontario
| Southgate JCT | ON_SOG_JCT | HONI |  |  | Ontario
| Sowerby DS | ON_SOW_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1 | 115 | 24.9 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Sowerby JCT | ON_SOW_JCT | HONI |  |  | Ontario
| Spanish DS | ON_SPA_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1 | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Spanish JCT | ON_SPA_JCT | HONI |  |  | Ontario
| Specialty Bar JCT | ON_SPB_JCT | HONI |  |  | Ontario
| Specialty Bar TS | ON_SPB_ISS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 115 | [7 empty] | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing.
| Speed River JCT | ON_SPR_JCT | HONI |  |  | Ontario
| Speedsville JCT | ON_SPS_JCT | HONI |  |  | Ontario
| Spence SWS | ON_SPC_SWS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Spruce Falls JCT | ON_SPF_JCT | HONI |  |  | Ontario
| Spruce Falls TS | ON_SPF_TSS | HONI |  |  | Ontario | Northeast |  | 230 | 115 | [5 empty] | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| St. Andrews TS | ON_STA_DSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| St. Anns JCT | ON_STN_JCT | HONI |  |  | Ontario
| St. Clair Avenue JCT | ON_STC_JCT | HONI |  |  | Ontario
| St. Clair E.C. GS | ON_STE_GSS | HONI |  |  | Ontario
| St. Clair E.C. JCT | ON_STE_JCT | HONI |  |  | Ontario
| St. Isidore TS | ON_STI_DSS | HONI |  |  | Ontario | Ottawa |  | 230 | 44 |  |  |  | 52 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| St. Johns Valley JCT | ON_STJ_JCT | HONI |  |  | Ontario
| St. Lawrence TS | ON_STL_DSS | HONI |  |  | Ontario | St Lawrence |  | 230 | 115/44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report St Lawrence.
| St. Marys Cement TS | ON_SMC_ISS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | [7 empty] | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| St. Marys MTS | ON_STM_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 34.5 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| St. Marys TS | ON_SMY_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 115 | 13.8 |  |  |  | 52.8 | 59 | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| St. Paul JCT | ON_STP_JCT | HONI |  |  | Ontario
| St. Thomas TS | ON_STT_DSS | HONI |  |  | Ontario | London | T3/T4 | 115 | 27.6 |  |  |  | 50 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Stanley JCT | ON_SLY_JCT | HONI |  |  | Ontario
| Stanley TS | ON_SLY_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 13.8 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Station 11 SWS | ON_S11_SWS | CNPI |  |  | Ontario | Niagara |  | 115 | [7 empty] | CNPI. 2014. Transmission Revenue Requirement Application
| Station 17 TS | ON_S17_DSS | CNPI |  |  | Ontario | Niagara |  | 115 |  |  |  |  | 56 | 63 |  | CNPI. 2014. Transmission Revenue Requirement Application
| Station 18 TS | ON_S18_DSS | CNPI |  |  | Ontario | Niagara |  | 115 |  |  |  |  | 56 | 63 |  | CNPI. 2014. Transmission Revenue Requirement Application
| Stayner TS | ON_STY_DSS | HONI |  |  | Ontario | Georgian Bay | T3/T4 | 230 | 115/44 |  |  |  | 181 | 202 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Steephill Falls GS | ON_SHF_GSS | HONI |  |  | Ontario
| Stelco JCT | ON_STO_JCT | HONI |  |  | Ontario
| Stewartville TS | ON_STW_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 44 |  |  |  | 55 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Stirton TS | ON_STR_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T3/T4 | 115 | 13.8 |  |  |  | 112 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Strachan TS | ON_STH_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 169 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Stratford JCT | ON_STF_JCT | HONI |  |  | Ontario
| Stratford TS | ON_STF_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 230 | 27.6 |  |  |  | 117.3 | 128.6 | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Strathroy TS | ON_SRY_DSS | HONI |  |  | Ontario | London | T1/T2 | 230 | 27.6 |  |  |  | 50 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Striker DS | ON_STK_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1/T2 | 115 | 24.9 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Sudbury JCT | ON_SUD_JCT | HONI |  |  | Ontario
| Summerhaven SWS | ON_SUM_SWS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 230 | [7 empty] | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Sun Cdn Pipeline TS | ON_SCP_ISS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 115 | [7 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Sun Oil Co JCT | ON_SOC_JCT | HONI |  |  | Ontario
| Suncor TS | ON_SCR_ISS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 115 | [7 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Sydenham JCT | ON_SYD_JCT | HONI |  |  | Ontario
| Talbot TS | ON_TBT_DSS | HONI |  |  | Ontario | London | T1/T2/T3/T4 | 230 | 27.6 |  |  |  | 290 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Talford JCT | ON_TLF_JCT | HONI |  |  | Ontario
| Tarentorus MTS | ON_TRT_DSS | HONI |  |  | Ontario | East Lake Superior |  | 115 | 34.5 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| TBPI Thunder Bay JCT | ON_TBP_JCT | HONI |  |  | Ontario
| TBPI Thunder Bay TS | ON_TBP_ISS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| TCE Halton Hills JCT | ON_TCE_JCT | HONI |  |  | Ontario
| TCPL Belleville TS | ON_TCB_ISS | HONI |  |  | Ontario | Peterborough-Kingston |  | 115 | 4.16 | [6 empty] | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| TCPL Cobourg TS | ON_TCC_ISS | HONI |  |  | Ontario | Peterborough-Kingston |  | 115 | 4.16 | [6 empty] | Hydro One. 2020. Needs Assessment Report. Peterborough to Kingston Region.
| TCPL Vermillion Bay JCT | ON_TCV_JCT | HONI |  |  | Ontario
| TCPL Vermillion Bay TS | ON_TCV_ISS | HONI |  |  | Ontario | Northwest |  | 230 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Tee Lake JCT | ON_TEE_JCT | HONI |  |  | Ontario
| Temagami DS | ON_TMG_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 12.5 | [6 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Tembec Kapuskasking TS | ON_TMB_GSS | HONI |  |  | Ontario | Northeast |  | 230 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Terauley TS | ON_TER_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 249 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Terrace Bay SWS | ON_TRB_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Terry Fox JCT | ON_TRF_JCT | HONI |  |  | Ontario
| Terry Fox MTS | ON_TRF_DSS | HONI |  |  | Ontario | Ottawa |  | 230 |  |  |  |  | 90 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Thayer Lindsley TS | ON_TLS_ISS | HONI |  |  | Ontario | Sudbury-Algoma |  | 115 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Third Line TS | ON_TDL_DSS | HONI |  |  | Ontario | East Lake Superior |  | 230 | 115/34.5 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Thornton JCT | ON_THO_JCT | HONI |  |  | Ontario
| Thornton TS | ON_THO_DSS | HONI |  |  | Ontario | GTA East | T3/T4 | 230 | 44 |  |  |  | 160 |  |  | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| Thorold TS | ON_THL_DSS | HONI |  |  | Ontario | Niagara |  | 230 | 13.8 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Thunder Bay SWS | ON_THU_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Tilbury JCT | ON_TLB_JCT | HONI |  |  | Ontario
| Tilbury TS | ON_TLB_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 7 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Tilbury West DS | ON_TLW_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 31 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Tilbury West JCT | ON_TLW_JCT | HONI |  |  | Ontario
| Tillsonburg JCT | ON_TLL_JCT | HONI |  |  | Ontario
| Tillsonburg TS | ON_TLL_DSS | HONI |  |  | Ontario | London | T1/T3 | 115 | 27.6 |  |  |  | 109 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Timmins JCT | ON_TMM_JCT | HONI |  |  | Ontario
| Timmins TS | ON_TMM_DSS | HONI |  |  | Ontario | Northeast |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Timmins Westmine JCT | ON_TMW_JCT | HONI |  |  | Ontario
| Timmins Westmine TS | ON_TMW_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Tisdale JCT | ON_TSD_JCT | HONI |  |  | Ontario
| Todmorden JCT | ON_TOD_JCT | HONI |  |  | Ontario
| Tomken JCT | ON_TOM_JCT | HONI |  |  | Ontario
| Tomken TS | ON_TOM_DSS | HONI |  |  | Ontario | GTA West | T1/T2/T3/T4 | 230 | 44 |  |  |  | 347 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Toronto Power T#56 JCT | ON_TOT_JCT | HONI |  |  | Ontario
| Toronto Power TS | ON_TOP_DSS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Toronto Star JCT | ON_TOS_JCT | HONI |  |  | Ontario
| Toyota Woodstock JCT | ON_TYW_JCT | HONI |  |  | Ontario
| Toyota Woodstock TS | ON_TYW_ISS | HONI |  |  | Ontario | London |  | 115 | [7 empty] | Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing.
| Trafalgar DESN JCT | ON_TFL_JCT | HONI |  |  | Ontario
| Trafalgar TS | ON_TFL_DSS | HONI |  |  | Ontario | GTA West | T1/T2 | 500 | 230/27.6 |  |  |  | 124 |  | Hydro One. 2016. Transmission System Plan: Introduction. EB-2016-0160, Exhibit B1, Tab 1. | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| TransAlta Energy GS | ON_TRA_GSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | [7 empty] | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| TransAlta Energy JCT | ON_TRA_JCT | HONI |  |  | Ontario
| Trei-bacher JCT | ON_TRB_JCT | HONI |  |  | Ontario
| Tremaine JCT | ON_TRM_JCT | HONI |  |  | Ontario
| Tremaine TS | ON_TRM_DSS | HONI |  |  | Ontario | GTA West | T1/T2 | 230 | 27.6 |  |  |  | 190 |  |  | Hydro One. 2019. Needs Assessment Report Greater Toronto Area (GTA) West Region.
| Trinity JCT | ON_TRN_JCT | HONI |  |  | Ontario
| Trout Lake TS | ON_TRL_DSS | HONI |  |  | Ontario | Northeast |  | 230 | 44 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Tunnel JCT | ON_TUN_JCT | HONI |  |  | Ontario
| Turbine JCT | ON_TUR_JCT | HONI |  |  | Ontario
| Umbata Falls JCT | ON_UBF_JCT | HONI |  |  | Ontario
| Underwood GS | ON_UDW_GSS | HONI |  |  | Ontario
| Underwood JCT | ON_UDW_JCT | HONI |  |  | Ontario
| Uplands JCT | ON_UPL_JCT | HONI |  |  | Ontario
| Uplands MTS #2 | ON_UPL_DSS | HONI |  |  | Ontario | Ottawa |  | 115 |  |  |  |  | 30 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Upper Notch JCT | ON_UPN_JCT | HONI |  |  | Ontario
| Val Tetreau JCT | ON_VLT_JCT | HONI |  |  | Ontario
| Vale Copper #4 TS | ON_VLC_ISS | HONI |  |  | Ontario | Sudbury-Algoma |  | 230 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Vale Frood Stobie #2 JCT | ON_VLF_JCT | HONI |  |  | Ontario
| Vale Frood Stobie #2 TS | ON_VLF_ISS | HONI |  |  | Ontario | Sudbury-Algoma |  | 230 | [7 empty] | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Vale Inco JCT | ON_VLI_JCT | HONI |  |  | Ontario
| Vale Port Colborne | ON_VLP_ISS | HONI |  |  | Ontario | Niagara |  | 115 | [7 empty] | Hydro One. 2016. Needs Assessment Report Niagara.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing.
| Valerie Falls JCT | ON_VFS_JCT | HONI |  |  | Ontario
| Valora DS | ON_VLA_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Valora JCT | ON_VLA_JCT | HONI |  |  | Ontario
| Vanessa JCT | ON_VNA_JCT | HONI |  |  | Ontario
| Vansco JCT | ON_VNO_JCT | HONI |  |  | Ontario
| Vansickle TS | ON_VNS_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 13.8 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| Vaughan #1 JCT | ON_VJ1_JCT | HONI |  |  | Ontario
| Vaughan #3 JCT | ON_VJ3_JCT | HONI |  |  | Ontario
| Vaughan #4 JCT | ON_VJ4_JCT | HONI |  |  | Ontario
| Vaughan MTS #1 | ON_VM1_DSS | HONI |  |  | Ontario | GTA North | T1/T2/T3/T4 | 230 | 27.6 |  |  |  | 306 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Vaughan MTS #2 | ON_VM2_DSS | HONI |  |  | Ontario | GTA North |  | 230 | 27.6 |  |  |  | 153 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Vaughan MTS #3 | ON_VM3_DSS | HONI |  |  | Ontario | GTA North |  | 230 | 27.6 |  |  |  | 153 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Vaughan MTS #4 | ON_VM4_DSS | HONI |  |  | Ontario | GTA North |  | 230 | 27.6 |  |  |  | 153 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Vermilion Bay DS | ON_VEB_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 12.5 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Vermilion Bay JCT | ON_VEB_JCT | HONI |  |  | Ontario
| Vermillion JCT | ON_VEM_JCT | HONI |  |  | Ontario
| Verner DS | ON_VER_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1/T2 | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Verner JCT | ON_VER_JCT | HONI |  |  | Ontario
| Verner Pole 45 JCT | ON_VER_JCT | HONI |  |  | Ontario
| Vernonville JCT | ON_VNN_JCT | HONI |  |  | Ontario
| Vidal JCT | ON_VDL_JCT | HONI |  |  | Ontario
| Vineland DS | ON_VNL_DSS | HONI |  |  | Ontario | Niagara |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2016. Needs Assessment Report Niagara.
| W3_4T STR B JCT | ON_W34_JCT | HONI |  |  | Ontario
| Walker JCT | ON_WLK_JCT | HONI |  |  | Ontario
| Walker TS | ON_WLK_DSS | HONI |  |  | Ontario | Windsor-Essex |  | 115 | 27.6 |  |  |  | 180 |  |  | Hydro One. 2020. Windsor-Essex Regional Infrastructure Plan.
| Wallace JCT | ON_WLL_JCT | HONI |  |  | Ontario
| Wallace Terrace TS | ON_WTC_ISS | HONI |  |  | Ontario | East Lake Superior |  | 115 | [7 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Wallace TS | ON_WLL_DSS | HONI |  |  | Ontario | Georgian Bay | T3/T4 | 230 | 44 |  |  |  | 49 | 54 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Wallaceburg TS | ON_WLB_DSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 115 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Wallenstein JCT | ON_WST_JCT | HONI |  |  | Ontario
| Walsh Street JCT | ON_WAL_JCT | HONI |  |  | Ontario
| Wanstead JCT | ON_WAN_JCT | HONI |  |  | Ontario
| Wanstead TS | ON_WAN_DSS | HONI |  |  | Ontario | Chatham-Lambton-Sarnia |  | 230 | 27.6 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2017. Chatham-Kent/Lambton/Sarnia Regional Infrastructure Plan.
| Warden TS | ON_WDN_DSS | HONI |  |  | Ontario | GTA Toronto |  | 230 | 27.6 |  |  |  | 182 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Warkus JCT | ON_WKS_JCT | HONI |  |  | Ontario
| Warner Road JCT | ON_WNR_JCT | HONI |  |  | Ontario
| Warren DS | ON_WRR_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1/T2 | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Waterloo JCT | ON_WTL_JCT | HONI |  |  | Ontario
| Waterloo North MTS 3 | ON_WTN_DSS | HONI |  |  | Ontario | KWCG |  | 230 |  |  |  |  | 77 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Waterloo North MTS 3 JCT | ON_WTN_JCT | HONI |  |  | Ontario
| Waubaushene JCT | ON_WBS_JCT | HONI |  |  | Ontario
| Waubaushene TS | ON_WBS_DSS | HONI |  |  | Ontario | Georgian Bay | T5/T6 | 230 | 44 |  |  |  | 94 | 104 |  | Hydro One. 2020. Needs Assessment Report. South Georgian Bay - Muskoka.
| Waverly OPF | ON_WAV_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | [7 empty] | IESO. 2015. Central Toronto Integrated Regional Resource Plan - Appendices
| Wawa TS | ON_WAW_TSS | HONI |  |  | Ontario | East Lake Superior |  | 230 | 115 | [6 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| Wawaitin GS | ON_WWT_GSS | HONI |  |  | Ontario
| Wawaitin JCT | ON_WWT_JCT | HONI |  |  | Ontario
| Wells GS | ON_WEL_GSS | HONI |  |  | Ontario
| Wendover DS | ON_WEN_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 27.6 |  |  |  | 34 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Wendover JCT | ON_WEN_JCT | HONI |  |  | Ontario
| Wesdome Gold Mines JCT | ON_WGM_JCT | HONI |  |  | Ontario
| Wesdome Gold Mines TS | ON_WGM_ISS | HONI |  |  | Ontario | East Lake Superior |  | 115 | [7 empty] | Hydro One Sault Ste. Marie LP. 2017. Application for 2017 Transmission Rates - Applicant Responses to Interrogatories from Board Staff, SEC, VECC and AMCO (EB-2016-0356).
| West Gwillimbury JCT | ON_WGW_JCT | HONI |  |  | Ontario
| West Lincoln GS | ON_WLN_DSS | HONI |  |  | Ontario | Burlington-Nanticoke |  | 115 | [7 empty] | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.; Hydro One. 2013. Guelph Area Transmission Refurbishment Project - Application and Evidence Update Filing.
| West Lincoln JCT | ON_WLN_JCT | HONI |  |  | Ontario
| West Windsor Power SWS | ON_WWP_SWS | HONI |  |  | Ontario
| Westbrook JCT | ON_WTB_JCT | HONI |  |  | Ontario
| Westmore JCT | ON_WTM_JCT | HONI |  |  | Ontario
| Weston Lake DS | ON_WSL_DSS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Westover A JCT | ON_WSV_JCT | HONI |  |  | Ontario
| Westover JCT | ON_WSV_JCT | HONI |  |  | Ontario
| Weyerhaeuser Kenora TS | ON_WYK_ISS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Wharncliffe DS | ON_WHA_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1/T2 | 115 | 24.9 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Wharncliffe JCT | ON_WHA_JCT | HONI |  |  | Ontario
| Whitby GS | ON_WHI_GSS | HONI |  |  | Ontario
| Whitby GS JCT | ON_WHI_JCT | HONI |  |  | Ontario
| Whitby JCT | ON_WHI_JCT | HONI |  |  | Ontario
| Whitby TS | ON_WHI_DSS | HONI |  |  | Ontario | GTA East | T1/T2/T3/T4 | 230 | 44/27.6 |  |  |  | 367 |  |  | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| White River DS | ON_WHT_DSS | HONI |  |  | Ontario | Northwest |  | 115 | 25 | [6 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Whitedog Falls GS | ON_WDF_GSS | HONI |  |  | Ontario
| Whitedog Falls SWS | ON_WDF_SWS | HONI |  |  | Ontario | Northwest |  | 115 | [7 empty] | Hydro One. 2017. Northwest Ontario Regional Infrastructure Plan.
| Whitefish DS | ON_WHF_DSS | HONI |  |  | Ontario | Sudbury-Algoma | T1 | 115 | 12.5 | [5 empty] | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2020. Needs Assessment Report. Sudbury/Algoma Region.
| Widdifield SWS | ON_WFD_SWS | HONI |  |  | Ontario | Northeast |  | 230 | [7 empty] | Hydro One. 2016. GTA West Regional Infrastructure Plan.
| Wilhaven DS | ON_WLH_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 27.6 |  |  |  | 58 |  | Hydro One. 2021. Hydro One List of Station Capacity. | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Wilhaven JCT | ON_WLH_JCT | HONI |  |  | Ontario
| Williams Mine JCT | ON_WLM_JCT | HONI |  |  | Ontario
| Willow Creek JCT | ON_WLC_JCT | HONI |  |  | Ontario
| Willroy JCT | ON_WRY_JCT | HONI |  |  | Ontario
| Willroy Mines TS | ON_WRY_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Wilson JCT | ON_WLS_JCT | HONI |  |  | Ontario
| Wilson TS | ON_WLS_DSS | HONI |  |  | Ontario | GTA East | T1/T2/T3/T4 | 230 | 44 |  |  |  | 295 |  |  | Hydro One. 2020. GTA East Regional Infrastructure Plan.
| Wiltshire TS | ON_WLT_DSS | HONI |  |  | Ontario | GTA Toronto |  | 115 | 13.8 |  |  |  | 133 |  |  | Hydro One. 2020. Toronto Regional Infrastructure Plan.
| Windsor Airport GS | ON_WDA_GSS | HONI |  |  | Ontario
| Windsor Airport JCT | ON_WDA_JCT | HONI |  |  | Ontario
| Windsor Transalta GS | ON_WDT_GSS | HONI |  |  | Ontario
| Windsor Transalta JCT | ON_WDT_JCT | HONI |  |  | Ontario
| Wingham JCT | ON_WNG_JCT | HONI |  |  | Ontario
| Wingham TS | ON_WNG_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 230 | 44 |  |  |  | 97 | 107.9 |  | Hydro One. 2019. Needs Assessment Report. Greater Bruce Huron Region.
| Winona JCT | ON_WNA_JCT | HONI |  |  | Ontario
| Winona TS | ON_WNA_DSS | HONI |  |  | Ontario | Burlington-Nanticoke | T1/T2 | 115 | 27.6 |  |  |  | 89 |  |  | Hydro One. 2019. Burlington to Nanticoke Regional Infrastructure Plan.
| Wolverton DS | ON_WLV_DSS | HONI |  |  | Ontario | KWCG |  | 115 | 27.6 |  |  |  | 54 |  |  | Hydro One. 2018. Needs Assessment Report. Kitchener - Waterloo - Cambridge - Guelph (KWCG).; Hydro One. 2015. Kitchener - Waterloo - Cambridge - Guelph Regional Infrastructure Plan.
| Wolverton JCT | ON_WLV_JCT | HONI |  |  | Ontario
| Wonderland TS | ON_WND_DSS | HONI |  |  | Ontario | London | T5/T6 | 230 | 27.6 |  |  |  | 99 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| Woodbridge JCT | ON_WDB_JCT | HONI |  |  | Ontario
| Woodbridge TS | ON_WDB_DSS | HONI |  |  | Ontario | GTA North | T3/T5 | 230 | 27.6 |  |  |  | 160 |  |  | Hydro One. 2020. GTA North Regional Infrastructure Plan.
| Woodroffe TS | ON_WDR_DSS | HONI |  |  | Ontario | Ottawa |  | 115 | 12.5 |  |  |  | 92 |  |  | Hydro One. 2015. Greater Ottawa Regional Infrastructure Plan
| Woodslee JCT | ON_WDS_JCT | HONI |  |  | Ontario
| Woodstock TS | ON_WDK_DSS | HONI |  |  | Ontario | London | T1/T2 | 115 | 27.6 |  |  |  | 87 |  |  | Hydro One. 2017. London Area Regional Infrastructure Plan.
| X523A STR 654 JCT | ON_X52_JCT | HONI |  |  | Ontario
| York Energy Centre GS | ON_YEC_GSS | HONI |  |  | Ontario
| York Energy Centre JCT | ON_YEC_JCT | HONI |  |  | Ontario
| Young-Davidson TS | ON_YOD_ISS | HONI |  |  | Ontario | Northeast |  | 115 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Zurich GS | ON_ZUR_DSS | HONI |  |  | Ontario | Bruce-Huron |  | 230 | [7 empty] | Hydro One. 2019. List of Transmission Lines by Functional Category. EB-2019-0082.
| Zurich JCT | ON_ZUR_JCT | HONI |  |  | Ontario
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station
Specific Notes:
Additional lines or nodes may be added upon receipt of better system mapping information
General Notes:
Dual function generation/substation nodes are categorized as "GEN"
See inputs tab for assumptions regarding system parameters

## System
ON | SYSTEM CHARACTERISTICS
| Generator Type | Installed Capacity (2020) | Effective Capacity (Winter) | Effective Capacity (Summer) | Capacity Adjustment (Winter) | Capacity Adjustment (Summer) | Capacity Adjustment (Average) | Capacity Factor | Notes | Reserve Requirements | Transmission Line Losses | Distribution Line Losses
|  | (GW) | (GW) | (GW) | (%) | (%) | (%) | (%) |  | (% installed MW) | (% across system) | (% across system)
| Nuclear | 11.328 | 10.53 | 10.502 | 92.96% | 92.71% | 92.83% | by facility |  | 19% | 2.5% | 4%
| Natural Gas CC | 10.72 | 9.466 | 8.783 | 88.3% | 81.93% | 85.12% | by facility
| Natural Gas CG | 10.72 | 9.466 | 8.783 | 88.3% | 81.93% | 85.12% | 13% | By facility, or capacity factor reflects average of facilities with known IESO data
| Natural Gas CT | 10.72 | 9.466 | 8.783 | 88.3% | 81.93% | 85.12% | 12% | By facility, or capacity factor reflects average of facilities with known IESO data
| Biomass / Biogas | 0.41 | 0.388 | 0.387 | 94.63% | 94.39% | 94.51% | 20% | By facility, or capacity factor reflects average of facilities with known IESO data
| Hydro_run | 9.419 | 6.77 | 6.121 | 71.88% | 64.99% | 68.43% | 65% | By facility, or capacity factor reflects average of facilities with known IESO data
| Wind | 5.534 | 1.723 | 0.617 | 31.13% | 11.15% | 21.14% | 27% | By facility, or capacity factor reflects average of facilities with known IESO data
| Solar | 2.68 | 0.126 | 0.868 | 4.701% | 32.39% | 18.54% | 18% | By facility, or capacity factor reflects average of facilities with known IESO data
| Demand Response | 0.885 | 0.854 | 0.818 | 96.5% | 92.43% | 94.46%
| TOTAL | 62.416 | 48.789 | 45.662
Notes:
See Figures 10 through 12 in IESO APO-2020

## HGWh
ON | HISTORICAL ANNUAL ENERGY DEMAND | UNIT | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2009-2018
| Gross Annual Energy Demand | (GWh/y) | 0 | 0 | 0 | 0 | 0 | 156210 | 157020 | 158350 | 155230 | 161750
| DSM Savings | (GWh/y) | 0 | 0 | 0 | 0 | 0 | 11270 | 13970 | 15030 | 16730 | 18010
| Net Energy Demand (after DSM) | (GWh/y) | 0 | 0 | 0 | 0 | 0 | 144940 | 143050 | 143320 | 138500 | 143740
| Embedded Generation | (GWh/y) | 0 | 0 | 0 | 0 | 0 | 5140 | 6040 | 6320 | 6390 | 6350
| Annual Energy Demand (After DSM and Embedded) | (GWh/y) | 139000 | 142000 | 141500 | 141300 | 140700 | 139800 | 137010 | 137000 | 132110 | 137390
| Annual Change in Energy Demand | (GWh/y) |  | 3000 | -500 | -200 | -600 | -900 | -2790 | -10 | -4890 | 5280
| Percentage Change in Energy Demand | (%) |  | 2.158% | -0.3521% | -0.1413% | -0.4246% | -0.6397% | -1.996% | -0.007299% | -3.569% | 3.997% | -0.1294%
Specific Notes:

## HMW
ON | HISTORICAL ANNUAL PEAK DEMAND | UNIT | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2009-2018
| Annual Capacity Demand (after DSM) | MW | 24380 | 25075 | 25450 | 24636 | 24927 | 22774 | 22516 | 23213 | 21786 | 23240
| Annual Change in Capacity Demand |  |  | 695 | 375 | -814 | 291 | -2153 | -258 | 697 | -1427 | 1454 | Average
| Percentage Change in Capacity Demand |  |  | 2.851% | 1.496% | -3.198% | 1.181% | -8.637% | -1.133% | 3.096% | -6.147% | 6.674% | -0.5307%
Specific Notes:

## FGWh
ON | FORECAST ANNUAL ENERGY DEMAND | UNIT | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2020-2030 | 2020-2040 | Notes
| Base Case Annual Energy Demand (after DSM) | TWh/y | 144470 | 145810 | 146430 | 147050 | 149060 | 150600 | 151410 | 152600 | 154670 | 155850 | 157580 | 158700 | 160080 | 160960 | 162420 | 163890 | 165500 | 166210 | 167240 | 168260 | 169750 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 0.9275% | 0.4252% | 0.4234% | 1.367% | 1.033% | 0.5378% | 0.7859% | 1.356% | 0.7629% | 1.11% | 0.7108% | 0.8696% | 0.5497% | 0.9071% | 0.9051% | 0.9824% | 0.429% | 0.6197% | 0.6099% | 0.8855% | 0.8724% | 0.8095% | Mid-load forecast for use in COPPER
| Energy Efficiency Case (after DSM) | GWh/y | 144330 | 144740 | 144400 | 144000 | 145010 | 145910 | 146110 | 146700 | 148190 | 148840 | 150130 | 151090 | 152360 | 153270 | 154730 | 156110 | 157680 | 158320 | 159280 | 160230 | 161660 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 0.2841% | -0.2349% | -0.277% | 0.7014% | 0.6206% | 0.1371% | 0.4038% | 1.016% | 0.4386% | 0.8667% | 0.6394% | 0.8406% | 0.5973% | 0.9526% | 0.8919% | 1.006% | 0.4059% | 0.6064% | 0.5964% | 0.8925% | 0.3948% | 0.5686% | Low-load forecast for use in COPPER
Specific Notes:
The above forecasts are NOT inclusive of embedded energy

## FMW
ON | FORECAST ANNUAL PEAK DEMAND | UNIT | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2018 - 2030 | 2018 - 2050 | Notes
| Reference Case Peak Demand Summer (after DSM) | MW | 23970 | 24250 | 24340 | 24420 | 24640 | 24920 | 25030 | 25200 | 25450 | 25720 | 25990 | 26170 | 26300 | 26450 | 26650 | 26860 | 27020 | 27200 | 27350 | 27490 | 27640 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 1.168% | 0.3711% | 0.3287% | 0.9009% | 1.136% | 0.4414% | 0.6792% | 0.9921% | 1.061% | 1.05% | 0.6926% | 0.4968% | 0.5703% | 0.7561% | 0.788% | 0.5957% | 0.6662% | 0.5515% | 0.5119% | 0.5457% | 0.8124% | 0.7148% | Mid-load forecast for use in COPPER
| References Case Peak Demand Winter (after DSM) | MW | 21810 | 21870 | 22120 | 22120 | 22120 | 22330 | 22450 | 22510 | 22720 | 22900 | 23180 | 23340 | 23460 | 23610 | 23780 | 23950 | 24080 | 24220 | 24350 | 24480 | 24610 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 0.2751% | 1.143% | 0% | 0% | 0.9494% | 0.5374% | 0.2673% | 0.9329% | 0.7923% | 1.223% | 0.6903% | 0.5141% | 0.6394% | 0.72% | 0.7149% | 0.5428% | 0.5814% | 0.5367% | 0.5339% | 0.531% | 0.6111% | 0.6004%
| Efficiency Case Peak Demand Summer (after DSM) | MW | 23940 | 24080 | 24030 | 23940 | 24010 | 24180 | 24200 | 24270 | 24430 | 24620 | 24830 | 24980 | 25090 | 25250 | 25460 | 25650 | 25810 | 25980 | 26120 | 26260 | 26400 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 0.5848% | -0.2076% | -0.3745% | 0.2924% | 0.708% | 0.08271% | 0.2893% | 0.6593% | 0.7777% | 0.853% | 0.6041% | 0.4404% | 0.6377% | 0.8317% | 0.7463% | 0.6238% | 0.6587% | 0.5389% | 0.536% | 0.5331% | 0.3657% | 0.4903% | Low-load forecast for use in COPPER
| Efficiency Case Peak Demand Winter (after DSM) | MW | 21810 | 21850 | 21970 | 21820 | 21680 | 21730 | 21760 | 21750 | 21870 | 21950 | 22090 | 22190 | 22290 | 22470 | 22640 | 22810 | 22920 | 23060 | 23200 | 23320 | 23450 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050
| Incremental annual load growth (after DSM) |  |  | 0.1834% | 0.5492% | -0.6827% | -0.6416% | 0.2306% | 0.1381% | -0.04596% | 0.5517% | 0.3658% | 0.6378% | 0.4527% | 0.4507% | 0.8075% | 0.7566% | 0.7509% | 0.4822% | 0.6108% | 0.6071% | 0.5172% | 0.5575% | 0.1276% | 0.5992%
Specific Notes:
The above forecasts are NOT inclusive of embedded energy
Use Summer case in COPPER as it is more consrevative (i.e., higher)

## Hourly
ON | Hourly
See Hourly2018 file in the Hourly-2018 folder
See Hourly2019 file in the Hourly-2019 folder
See 2020-2040 hourly forecasts

## Inputs
ON | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance