## README
PE | LEGEND
| PE-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| Distribution | Characteristics of existing distribution substations
| System | Miscellaneous provincial system characteristics
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review or being gathered
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to sources
See the accompanying calculations file and raw data files for additional supporting information
See the related Gitlab issue for a summary of inventory status

## PE-Sources
PE | SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| Maritime Electric | 2016 | General Rate Application | https://www.maritimeelectric.com/media/1093/general-rate-case-application-and-evidence.pdf |  | Prince Edward Island
| Maritime Electric | 2020 | Integrated System Plan 2020 | http://www.irac.pe.ca/electric/
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" column of the relevant tab
| MECL | 2018 | Environmental Impact Statement (EIS): Proposed Borden-Carleton Transmission Line Project | https://www.princeedwardisland.ca/en/information/environment-water-and-climate-change/projects-under-environmental-review-undertakings |  | Prince Edward Island
| NB Power | 2018 | 2017/18 Annual Report | https://www.nbpower.com/en/about-us/accountability-reports/annual-and-quarterly-reports/ |  | New Brunswick
| AMEC | 2013 | Environmental Impact Statement Hermanville/Clearspring 30 Megawatt Wind Farm Final Report | https://www.princeedwardisland.ca/en/information/environment-water-and-climate-change/projects-under-environmental-review-undertakings |  | Prince Edward Island
| Nova Scotia Power Inc. | 2020 | NS Power 2020 IRP Modeling Results Release | https://irp.nspower.ca/documents/modeling-results/ |  | Nova Scotia
| Energy and Environmental Economics | 2019 | Planning Reserve Margin and Capacity Value Study | https://irp.nspower.ca/documents/pre-irp-deliverables/ |  | Prince Edward Island
| Hatch | 2018 | Nova Scotia Power Inc. Atlantic RECSI | https://canwea.ca/wind-integration-study/full-report/ |  | Atlantic
| IESO | 2020 | Annual Planning Outlook: A view of Ontario's electricity system needs [including data tables] | http://www.ieso.ca/en/Sector-Participants/Planning-and-Forecasting/Annual-Planning-Outlook |  | Ontario
| Maritime Electric | 2019 | Renewable Energy | https://www.maritimeelectric.com/about-us/community-and-environment/renewable-energy/ |  | Prince Edward Island
| Government of PEI | 2019 | Wind Energy in Prince Edward Island | https://www.princeedwardisland.ca/en/information/transportation-infrastructure-and-energy/wind-energy-prince-edward-island |  | Prince Edward Island
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | National
| PEI Energy Corporation | 2019 | Proposed 2019 Windfarm | http://www.peiec.ca/2019-wind-farm.html |  | Prince Edward Island
| Government of PEI | 2016 | Prince Edward Island Provincial Energy Strategy | https://www.princeedwardisland.ca/en/information/transportation-infrastructure-and-energy/energy-strategy |  | Prince Edward Island
| NPCC | 2016 | 2016 Maritimes Area Comprehensive Review of Resource Adequacy | https://www.npcc.org/Library/Resource%20Adequacy/2016%20Maritimes%20Area%20CRRA%20for%20RCCpaf.pdf |  | Prince Edward Island
| Maritime Electric | 2019 | General Rate Application | https://www.maritimeelectric.com/about-us/regulatory/2019-general-rate-application/ |  | Prince Edward Island
| Dunsky Energy Consulting | 2019 | City of Summerside Capacity Resource Plan | https://summerside.ca/residents/electricity/energy_capacity_resource_planning |  | Prince Edward Island
| Maritime Electric | 2019 | Response to Interrogatories from Commission Staff | http://www.irac.pe.ca/electric/ |  | Prince Edward Island
| PEI Energy Commission | 2012 | Charting Our Electric Future Final Report. Appendix D: Maritime Electric Energy Supply System Map | http://www.gov.pe.ca/photos/original/NRGCommish_13.pdf |  | Prince Edward Island
| MECL | 2013 | Environmental Impact Statement (EIS): Proposed West St. Peters Substation and Transmission Line Project | https://www.princeedwardisland.ca/en/information/environment-water-and-climate-change/projects-under-environmental-review-undertakings |  | Prince Edward Island
| MECL | 2013 | Environmental Impact Statement (EIS): Transmission Line Y-104 Church Road Substation to West Royalty Substation | https://www.princeedwardisland.ca/en/information/environment-water-and-climate-change/projects-under-environmental-review-undertakings |  | Prince Edward Island
| MECL | 2016 | Environmental Impact Statement (EIS): Proposed New Glasgow Substation and Transmission Line Project | https://www.princeedwardisland.ca/en/information/environment-water-and-climate-change/projects-under-environmental-review-undertakings |  | Prince Edward Island
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
PE | EXISTING GENERATION | [12 empty] | DESIGN | [7 empty] | OPERATIONS | [13 empty] | OPERATING COSTS
| Project Name | Gen Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy | # of units | Inc Heat Rate @ Max | Minimum Capacity | Maximum Capacity | Minimum Up Time | Minimum Down Time | Spin Up Ramp Rate | Spin Down Ramp Rate | Start Up Ramp Limit | Shut Down Ramp Limit | Must Run | Operating Reserve Fraction | Outage Duration | Forced Outage Rate | Maintenance Outage Rate | Start Up Costs | Fuel Costs | Shut Down Costs | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | (kV) |  |  |  |  | (MW) |  | (MW) | (%) | (GWh/year) | (GWh/year) | (MMBtu/MWh) | (MW) | (MW) | (hours) | (hours) | (%/min) | (%/min) | [MW/hr p MWcap] | [MW/hr p MWcap] | (T/F) | (%) | (hours) | (%) | (days/y) | (S/MWcap) | ($/hour) | (S/MWcap) | ($/year) | ($/MWh)
| PEI Energy Systems | PE_PES00_GEN | Fort Chicago Energy Partners of Calgary | Charlottetown | 46.2517 | -63.1079 | Prince Edward Island.a | Prince Edward Island | Eastern Kings GS | PE_EKS_GSS | 138 | 1983 | 2100 | Biomass | biomass | 1.2 | 95% | 1.14 | 85% | 8.9352 | 1
| Summerside_01 | PE_SSD01_GEN | City of Summerside | Summerside | 46.3936 | -63.7893 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2000 | 2025 | Diesel_CT | diesel | 2 | 78% | 1.56 | 1% | 0.1752 | 8
| Summerside_02 | PE_SSD02_GEN | City of Summerside | Summerside | 46.3936 | -63.7893 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2000 | 2025 | Diesel_CT | diesel | 2 | 78% | 1.56 | 1% | 0.1752 | 8
| Summerside_03 | PE_SSD03_GEN | City of Summerside | Summerside | 46.3936 | -63.7893 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2000 | 2025 | Diesel_CT | diesel | 2 | 78% | 1.56 | 1% | 0.1752 | 8
| Summerside_04 | PE_SSD04_GEN | City of Summerside | Summerside | 46.3936 | -63.7893 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2000 | 2025 | Diesel_CT | diesel | 2 | 78% | 1.56 | 1% | 0.1752 | 8
| Summerside_05 | PE_SSD05_GEN | City of Summerside | Summerside | 46.3936 | -63.7893 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2000 | 2025 | Diesel_CT | diesel | 1 | 78% | 0.78 | 1% | 0.0876 | 8
| Summerside_06 | PE_SSD06_GEN | City of Summerside | Summerside | 46.3936 | -63.7893 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2000 | 2025 | Diesel_CT | diesel | 1 | 78% | 0.78 | 1% | 0.0876 | 8
| Summerside_07 | PE_SSD07_GEN | City of Summerside | Summerside | 46.3936 | -63.7893 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2000 | 2025 | Diesel_CT | diesel | 1 | 78% | 0.78 | 1% | 0.0876 | 8
| Summerside_08 | PE_SSD08_GEN | City of Summerside | Summerside | 46.3936 | -63.7893 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2000 | 2025 | Diesel_CT | diesel | 4 | 78% | 3.12 | 1% | 0.3504 | 8
| Borden_01 | PE_BOR01_GEN | Maritime Electric | Borden | 46.2493 | -63.6881 | Prince Edward Island.a | Prince Edward Island | Borden | PE_BOR_DFS | 138 | 1971 | 2030 | Diesel_CT | diesel | 15 | 78% | 11.7 | 1% | 1.314 | 2 | [20 empty] | Provides non-spinning reserve; 10 minute start capability; 10 MW max. winter capacity
| Borden_02 | PE_BOR02_GEN | Maritime Electric | Borden | 46.2493 | -63.6881 | Prince Edward Island.a | Prince Edward Island | Borden | PE_BOR_DFS | 138 | 1973 | 2030 | Diesel_CT | diesel | 25 | 78% | 19.5 | 1% | 2.19 | 2 | [20 empty] | Provides non-spinning reserve; 10 minute start capability; 20 MW max. winter capacity
| Combustion Turbine #3 | PE_CTB03_GEN | Maritime Electric | Charlottetown | 46.2403 | -63.1162 | Prince Edward Island.a | Prince Edward Island | Charlottetown | PE_CHA_DFS | 69 | 2005 | 2100 | Diesel_CT | diesel | 49 | 78% | 38.22 | 1% | 4.2924 | 1 | [20 empty] | Can provide non-spinning reserve; 10 minute start capability; 35 MW max. winter capacity
| CONTRACTED - NBPower-MECL | PP_NBPE100_GEN | NB Power | NB-PEI Border | 46.2051 | -63.7575 | Prince Edward Island.a | Prince Edward Island | IPB Richmond Cove | PP_NBPE1_IPT | 138 | 2000 | 2039 | Nuclear | nuclear | 30 | 90% | 27 | 90% | 236.52 | 1
| Charlottetown_09 | PE_CHA09_GEN | Maritime Electric | Charlottetown | 46.2403 | -63.1162 | Prince Edward Island.a | Prince Edward Island | Charlottetown | PE_CHA_DFS | 69 | 1963 | 2021 | Oil_ST | diesel | 19 | 73% | 13.87 | 0% | 0 | 2 | [20 empty] | For contingency purposes only
| Charlottetown_10 | PE_CHA10_GEN | Maritime Electric | Charlottetown | 46.2403 | -63.1162 | Prince Edward Island.a | Prince Edward Island | Charlottetown | PE_CHA_DFS | 69 | 1968 | 2021 | Oil_ST | diesel | 19 | 73% | 13.87 | 0% | 0 | 2 | [20 empty] | For contingency purposes only
| Slemon Park | PE_SLP00_GEN | Maritime Electric | Summerside | 46.4352 | -63.8273 | Prince Edward Island.a | Prince Edward Island | St. Eleanors | PE_STE_DFS | 69 | 2021 | 2041 | Solar_PV | solar | 10 | 5% | 0.5 | 15% | 13.14
| Sunbank | PE_SBK00_GEN | City of Summerside | Summerside | 46.4029 | -63.8124 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2021 | 2041 | Solar_PV | solar | 21 | 5% | 1.05 | 15% | 27.594
| Aeolus | PE_AOL00_GEN | PEI Energy Corporation | Tignish | 47.0368 | -64.005 | Prince Edward Island.a | Prince Edward Island | Aeolus GS | PE_AOL_GSS | 69 | 2003 | 2023 | Wind_Onshore | wind | 3 | 20% | 0.6 | 37% | 9.7236
| Eastern Kings | PE_EKS00_GEN | PEI Energy Corporation | Elmira | 46.4525 | -62.0685 | Prince Edward Island.a | Prince Edward Island | Eastern Kings GS | PE_EKS_GSS | 138 | 2006 | 2026 | Wind_Onshore | wind | 30 | 20% | 6 | 37% | 97.236
| Hermanville | PE_HRM00_GEN | PEI Energy Corporation | Hermanville / Clear Springs | 46.4549 | -62.3143 | Prince Edward Island.a | Prince Edward Island | Hermanville GS | PE_HRM_GSS | 138 | 2014 | 2034 | Wind_Onshore | wind | 30 | 20% | 6 | 37% | 97.236
| Kings County_01 | PE_KCO00_GEN | PEI Energy Corporation | Kings County | 46.4483 | -62.066 | Prince Edward Island.a | Prince Edward Island | Church Road | PE_CHR_TSS | 138 | 2019 | 2039 | Wind_Onshore | wind | 30 | 20% | 6 | 37% | 97.236
| Northcape | PE_NCP00_GEN | PEI Energy Corporation | North Cape | 47.0484 | -63.995 | Prince Edward Island.a | Prince Edward Island | Alberton | PE_ALB_DFS | 69 | 2003 | 2023 | Wind_Onshore | wind | 10.6 | 20% | 2.12 | 37% | 34.3567
| Suez Norway | PE_SZN00_GEN | Engie | Norway | 47.0076 | -64.0207 | Prince Edward Island.a | Prince Edward Island | Suez Norway GS | PE_SZN_GSS | 69 | 2007 | 2027 | Wind_Onshore | wind | 9 | 20% | 1.8 | 37% | 29.1708
| Summerside Wind | PE_SSW00_GEN | City of Summerside | Summerside | 46.4343 | -63.8035 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2009 | 2029 | Wind_Onshore | wind | 12 | 20% | 2.4 | 37% | 38.8944
| WEICan | PE_WEI00_GEN | WEICan | North Cape | 47.0329 | -64.0168 | Prince Edward Island.a | Prince Edward Island | WEICan GS | PE_WEI_GSS | 69 | 2013 | 2033 | Wind_Onshore | wind | 10 | 20% | 2 | 37% | 32.412
| West Cape | PE_WCP00_GEN | Engie | West Cape | 46.6827 | -64.3832 | Prince Edward Island.a | Prince Edward Island | West Cape GS | PE_WCP_GSS | 138 | 2009 | 2029 | Wind_Onshore | wind | 99 | 20% | 19.8 | 37% | 320.8788
Specific Notes:
Average Annual Energy of NB Power Purchses estimated as the sum of the hourly energy transported into PE on the NB-PE intertie in 2018 (i.e. excluding exports from PE to NB)
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Unless noted otherwise, the wind generating stations are presumed to be connected to the nearest 69 kV substation
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit Hydro_run facilities treated as single-unit facilities
RH Additions, Comments and TODOs
Remote projects are not included in this list.
See calculations sheets for sources of values.
Sources

## Storage
PE | EXISTING STORAGE | [12 empty] | DESIGN | [7 empty] | OPERATIONS
| Project Name | Storage Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Technology | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Minimum Up Time | Minimum Down Time | Forced Outage Rate | Maintenance Days | Fixed O&M Cost | Variable O&M Cost | Other References | Notes
[11 empty] | kV | [5 empty] | (MW) | (MWh) | (Hours) |  | ($M) | (hours) | (hours) | (%) | (days/y) | ($/year) | ($/MWh)
| Summerside Storage | PE_SMS_STO | Summerside Electric | Summerside | 46.4029 | -63.8124 | Prince Edward Island.a | Prince Edward Island | Summerside | PE_SMS_DFS | 69 | 2020 | 2040 | Storage | storage | Lithium Ion | 10 | 20 | 2 | Sunbank |  | 2 | 2
| Slemon Park Storage | PE_SLP_STO | Maritime Electric | Summerside | 46.4382 | -63.8237 | Prince Edward Island.a | Prince Edward Island | St. Eleanors | PE_STE_DFS | 69 | 2020 | 2040 | Storage | storage | Lithium Ion | 1 | 2 | 2 | Grid |  | 2 | 2
Specific Notes:

## HydroExisting
PE | EXISTING STORAGE HYDROELECTRIC
Project Name
NONE
Specific Notes:

## HydroRenewals
PE | HYDROELECTRIC RENEWAL
Project Name
NONE
Notes:

## HydroGreenfield
PE | HYDROELECTRIC GREENFIELD
Project Name
NONE
Notes:

## HydroPS
PE | HYDROELECTRIC PUIMPED STORAGE | [15 empty] | Existing Design | [8 empty] | Reservoir Design | [13 empty] | Costs | 1.77% | 1.06 |  |  | 7% | 70
| Pumped Storage Project | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Estimated Round Trip Efficiency | Existing Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Salt/Fresh | Reservoir Types | Reservoir Storage | Storage Requirement | Gross Head | Penstock | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping) | Turbine Type | Pump Type | Generation Duration at Peak Output | Efficient Pumping Capacity Duration | Total Footprint | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Cost of Capacity | Unit Cost of Stored Energy | Levelized Cost | Construction Time | Development Time | Notes
[5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) |  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) |  |  |  |  | (m3) | (MWh) | (m) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2018/MW) | ($2018/MWh) | ($2018/kW-year) | (years) | (years)
Specific Notes:
General Notes:

## Transmission
PE | EXISTING TRANSMISSION
| Circuit ID | Owner | Planning Region | Number of Circuits | Current | Length | Length | Voltage | Reactance | Smax | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes | Count
[5 empty] | (ac/dc) | (km) | (miles) | (kV) | (ohm) |  | (A) | (A) | (MVA) | (MVA) |  | (MW) | (MW)
| T-25 | PEI Energy Corporation | Prince Edward Island | 1 | ac | 0.7 | 0.4321 | 69 | 0.269 | 3 | [5 empty] | 36 | 39 | WEICan GS | PE_WEI_GSS | Aeolus GS | PE_AOL_GSS |  |  | 30
| T-15 | Maritime Electric | Prince Edward Island | 1 | ac | 3.5 | 2.1605 | 69 | 1.345 | 3 | [5 empty] | 36 | 39 | West Royalty | PE_WRY_DSS | Airport | PE_APT_ISS |  |  | 23
| T-03 | Maritime Electric | Prince Edward Island | 1 | ac | 4.6 | 2.8395 | 69 | 1.7677 | 3 | [5 empty] | 36 | 39 | Borden | PE_BOR_DFS | Albany | PE_ABY_DSS |  |  | 10
| T-21 | Maritime Electric | Prince Edward Island | 1 | ac | 18 | 11.1111 | 69 | 6.9171 | 3 | [5 empty] | 36 | 39 | O'Leary | PE_OLY_DSS | Alberton | PE_ALB_DFS |  |  | 25
| T-01 | Maritime Electric | Prince Edward Island | 1 | ac | 5 | 3.0864 | 69 | 1.9214 | 3 | [5 empty] | 36 | 39 | Hunter River | PE_HTR_DSS | Bagnall Road | PE_BAG_DSS |  |  | 2
| Y-113 | Maritime Electric | Prince Edward Island | 1 | ac | 8.3 | 5.1235 | 138 | 3.5986 | 3 | [5 empty] | 141 | 156 | Borden | PE_BOR_DFS | Bedeque | PE_BED_SWS |  |  | 45
| Y-105 | Maritime Electric | Prince Edward Island | 1 | ac | 15.4 | 9.5062 | 138 | 6.677 | 3 | [5 empty] | 141 | 156 | Sherbrooke | PE_SHB_DFS | Bedeque | PE_BED_SWS |  |  | 38
| Y-107 | Maritime Electric | Prince Edward Island | 1 | ac | 8.3 | 5.1235 | 138 | 3.5986 | 3 | [5 empty] | 141 | 156 | Bedeque | PE_BED_SWS | Borden | PE_BOR_DFS |  |  | 39
| T-01 | Maritime Electric | Prince Edward Island | 1 | ac | 4.8 | 2.963 | 69 | 1.8446 | 3 | [5 empty] | 36 | 39 | Kensington | PE_KEN_DSS | Cavendish Farms | PE_CAV_ISS |  |  | 5
| T-15 | Maritime Electric | Prince Edward Island | 1 | ac | 9 | 5.5556 | 69 | 3.4586 | 3 | [5 empty] | 36 | 39 | Airport | PE_APT_ISS | Charlottetown | PE_CHA_DFS |  |  | 24
| T-02 | Maritime Electric | Prince Edward Island | 1 | ac | 4 | 2.4691 | 69 | 1.5371 | 3 | [5 empty] | 36 | 39 | Crossroads | PE_CRD_DSS | Charlottetown | PE_CHA_DFS |  |  | 7
| T-13 | Maritime Electric | Prince Edward Island | 1 | ac | 6.2 | 3.8272 | 69 | 2.3826 | 3 | [5 empty] | 36 | 39 | University PEI | PE_UPE_DSS | Charlottetown | PE_CHA_DFS |  |  | 22
| T-08 | Maritime Electric | Prince Edward Island | 1 | ac | 25 | 15.4321 | 69 | 9.6071 | 3 | [5 empty] | 36 | 39 | Georgetown | PE_GRG_DSS | Church Road | PE_CHR_TSS |  |  | 14
| Y-104 | Maritime Electric | Prince Edward Island | 1 | ac | 32.6 | 20.1235 | 138 | 14.1344 | 3 | [5 empty] | 141 | 156 | West St.Peters | PE_WSP_DSS | Church Road | PE_CHR_TSS |  |  | 35
| T-02 | Maritime Electric | Prince Edward Island | 1 | ac | 10 | 6.1728 | 69 | 3.8429 | 3 | [5 empty] | 36 | 39 | Mount Albion | PE_MAB_DSS | Crossroads | PE_CRD_DSS |  |  | 8
| T-08 | Maritime Electric | Prince Edward Island | 1 | ac | 14 | 8.642 | 69 | 5.38 | 3 | [5 empty] | 36 | 39 | Church Road | PE_CHR_TSS | Dingwell Mills | PE_DWM_DSS |  |  | 15
| T-10 | Maritime Electric | Prince Edward Island | 1 | ac | 17.8 | 10.9877 | 69 | 6.8403 | 3 | [5 empty] | 36 | 39 | Victoria Cross | PE_VCX_DSS | Dover | PE_DOV_DSS |  |  | 18
| Y-112 | Maritime Electric | Prince Edward Island | 1 | ac | 18.9 | 11.6667 | 138 | 8.1945 | 3 | [5 empty] | 141 | 156 | Hermanville JCT | PE_HRM_JCT | Eastern Kings GS | PE_EKS_GSS |  |  | 43
| T-08 | Maritime Electric | Prince Edward Island | 1 | ac | 14.9 | 9.1975 | 69 | 5.7259 | 3 | [5 empty] | 36 | 39 | Lorne Valley | PE_LNV_DSS | Georgetown | PE_GRG_DSS |  |  | 16
| Y-112 | Maritime Electric | Prince Edward Island | 1 | ac | 15.8 | 9.7531 | 138 | 6.8504 | 3 | [5 empty] | 141 | 156 | Church Road | PE_CHR_TSS | Hermanville JCT | PE_HRM_JCT |  |  | 44
| Y-108 | Maritime Electric | Prince Edward Island | 1 | ac | 10.3 | 6.358 | 138 | 4.4658 | 3 | [5 empty] | 141 | 156 | Hermanville GS | PE_HRM_GSS | Hermanville JCT | PE_HRM_JCT |  |  | 40
| T-01 | Maritime Electric | Prince Edward Island | 1 | ac | 17.5 | 10.8025 | 69 | 6.725 | 3 | [5 empty] | 36 | 39 | West Royalty | PE_WRY_DSS | Hunter River | PE_HTR_DSS |  |  | 1
| Y-101 | PEI Energy Corporation | Prince Edward Island | 1 | ac | 0.7 | 0.4321 | 138 | 0.3035 | 3 | [5 empty] | 141 | 156 | Richmond Cove | PE_RCV_TSS | IPB Richmond Cove | PP_NBPE1_IPT |  |  | 31
| Y-103 | PEI Energy Corporation | Prince Edward Island | 1 | ac | 0.7 | 0.4321 | 138 | 0.3035 | 3 | [5 empty] | 141 | 156 | Richmond Cove | PE_RCV_TSS | IPB Richmond Cove | PP_NBPE1_IPT |  |  | 33
| T-01 | Maritime Electric | Prince Edward Island | 1 | ac | 16 | 9.8765 | 69 | 6.1486 | 3 | [5 empty] | 36 | 39 | Rattenbury | PE_RTN_DSS | Kensington | PE_KEN_DSS |  |  | 4
| T-02 | Maritime Electric | Prince Edward Island | 1 | ac | 22 | 13.5802 | 69 | 8.4543 | 3 | [5 empty] | 36 | 39 | Lorne Valley | PE_LNV_DSS | Mount Albion | PE_MAB_DSS |  |  | 9
| T-23 | PEI Energy Corporation | Prince Edward Island | 1 | ac | 28.4 | 17.5309 | 69 | 10.9137 | 3 | [5 empty] | 36 | 39 | Alberton | PE_ALB_DFS | Northcape GS | PE_NCP_GSS |  |  | 27
| Y-115 | Maritime Electric | Prince Edward Island | 1 | ac | 67.4 | 41.6049 | 138 | 29.2227 | 3 | [5 empty] | 141 | 156 | Sherbrooke | PE_SHB_DFS | O'Leary | PE_OLY_DSS |  |  | 47
| T-21 | Maritime Electric | Prince Edward Island | 1 | ac | 34.1 | 21.0494 | 69 | 13.1041 | 3 | [5 empty] | 36 | 39 | Wellington | PE_WEL_DSS | O'Leary | PE_OLY_DSS |  |  | 26
| T-01 | Maritime Electric | Prince Edward Island | 1 | ac | 8.5 | 5.2469 | 69 | 3.2664 | 3 | [5 empty] | 36 | 39 | Bagnall Road | PE_BAG_DSS | Rattenbury | PE_RTN_DSS |  |  | 3
| Y-101 | PEI Energy Corporation | Prince Edward Island | 1 | ac | 9 | 5.5556 | 138 | 3.9021 | 3 | [5 empty] | 141 | 156 | Bedeque | PE_BED_SWS | Richmond Cove | PE_RCV_TSS |  |  | 32
| Y-103 | PEI Energy Corporation | Prince Edward Island | 1 | ac | 9.1 | 5.6173 | 138 | 3.9455 | 3 | [5 empty] | 141 | 156 | Bedeque | PE_BED_SWS | Richmond Cove | PE_RCV_TSS |  |  | 34
| T-04 | Maritime Electric | Prince Edward Island | 1 | ac | 20.8 | 12.8395 | 69 | 7.9931 | 3 | [5 empty] | 36 | 39 | Lorne Valley | PE_LNV_DSS | Scotchfort | PE_SCF_DSS |  |  | 11
| Y-104 | Maritime Electric | Prince Edward Island | 1 | ac | 24.3 | 15 | 138 | 10.5358 | 3 | [5 empty] | 141 | 156 | West Royalty | PE_WRY_DSS | Scotchfort | PE_SCF_DSS |  |  | 36
| Y-113 | Maritime Electric | Prince Edward Island | 1 | ac | 15.5 | 9.5679 | 138 | 6.7204 | 3 | [5 empty] | 141 | 156 | Bedeque | PE_BED_SWS | Sherbrooke | PE_SHB_DFS |  |  | 46
| T-01 | Maritime Electric | Prince Edward Island | 1 | ac | 6.5 | 4.0123 | 69 | 2.4979 | 3 | [5 empty] | 36 | 39 | Cavendish Farms | PE_CAV_ISS | Sherbrooke | PE_SHB_DFS |  |  | 6
| T-08 | Maritime Electric | Prince Edward Island | 1 | ac | 15 | 9.2593 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | Dingwell Mills | PE_DWM_DSS | Souris | PE_SOU_DSS |  |  | 17
| T-05 | Maritime Electric | Prince Edward Island | 1 | ac | 4.2 | 2.5926 | 69 | 1.614 | 3 | [5 empty] | 36 | 39 | Sherbrooke | PE_SHB_DFS | St. Eleanors | PE_STE_DFS |  |  | 12
| T-25 | PEI Energy Corporation | Prince Edward Island | 1 | ac | 19 | 11.7284 | 69 | 7.3014 | 3 | [5 empty] | 36 | 39 | Alberton | PE_ALB_DFS | Suez Norway GS | PE_SZN_GSS |  |  | 28
| T-11 | Maritime Electric | Prince Edward Island | 1 | ac | 3.6 | 2.2222 | 69 | 1.3834 | 3 | [5 empty] | 36 | 39 | Sherbrooke | PE_SHB_DFS | Summerside | PE_SMS_DFS |  |  | 20
| T-13 | Maritime Electric | Prince Edward Island | 1 | ac | 6.2 | 3.8272 | 69 | 2.3826 | 3 | [5 empty] | 36 | 39 | West Royalty | PE_WRY_DSS | University PEI | PE_UPE_DSS |  |  | 21
| T-10 | Maritime Electric | Prince Edward Island | 1 | ac | 15.6 | 9.6296 | 69 | 5.9949 | 3 | [5 empty] | 36 | 39 | Lorne Valley | PE_LNV_DSS | Victoria Cross | PE_VCX_DSS |  |  | 19
| T-25 | PEI Energy Corporation | Prince Edward Island | 1 | ac | 2.8 | 1.7284 | 69 | 1.076 | 3 | [5 empty] | 36 | 39 | Suez Norway GS | PE_SZN_GSS | WEICan GS | PE_WEI_GSS |  |  | 29
| T-05 | Maritime Electric | Prince Edward Island | 1 | ac | 15 | 9.2593 | 69 | 5.7643 | 3 | [5 empty] | 36 | 39 | St. Eleanors | PE_STE_DFS | Wellington | PE_WEL_DSS |  |  | 13
| Y-115 | Maritime Electric | Prince Edward Island | 1 | ac | 17.5 | 10.8025 | 138 | 7.5875 | 3 | [5 empty] | 141 | 156 | O'Leary | PE_OLY_DSS | West Cape GS | PE_WCP_GSS |  |  | 48
| Y-111 | Maritime Electric | Prince Edward Island | 1 | ac | 41.1 | 25.3704 | 138 | 17.8198 | 3 | [5 empty] | 141 | 156 | Bedeque | PE_BED_SWS | West Royalty | PE_WRY_DSS |  |  | 42
| Y-109 | Maritime Electric | Prince Edward Island | 1 | ac | 50.9 | 31.4198 | 138 | 22.0688 | 3 | [5 empty] | 141 | 156 | Borden | PE_BOR_DFS | West Royalty | PE_WRY_DSS |  |  | 41
| Y-104 | Maritime Electric | Prince Edward Island | 1 | ac | 26.2 | 16.1728 | 138 | 11.3596 | 3 | [5 empty] | 141 | 156 | Scotchfort | PE_SCF_DSS | West St.Peters | PE_WSP_DSS |  |  | 37
Legend:
CSS = Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
ISS = Industrial Customer Substation
JCT = Junction
SWS = Switching Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## Nodes
PE | EXISTING TRANSMISSION
| Node Name | Node Code | Owner | Latitude | Longitude | Planning Region | Other References | Notes
| Aeolus GS | PE_AOL_GSS | MECL | 47.0368 | -64.005 | Prince Edward Island
| Airport | PE_APT_ISS | MECL | 46.291 | -63.1309 | Prince Edward Island
| Albany | PE_ABY_DSS | MECL | 46.2673 | -63.6399 | Prince Edward Island
| Alberton | PE_ALB_DFS | MECL | 46.8372 | -64.0832 | Prince Edward Island
| Bagnall Road | PE_BAG_DSS | MECL | 46.3844 | -63.3617 | Prince Edward Island
| Bedeque | PE_BED_SWS | MECL | 46.3151 | -63.6696 | Prince Edward Island
| Borden | PE_BOR_DFS | MECL | 46.2493 | -63.6881 | Prince Edward Island
| Cavendish Farms | PE_CAV_ISS | MECL | 46.422 | -63.6789 | Prince Edward Island
| Charlottetown | PE_CHA_DFS | MECL | 46.2403 | -63.1162 | Prince Edward Island
| Church Road | PE_CHR_TSS | MECL | 46.3946 | -62.4185 | Prince Edward Island
| Crossroads | PE_CRD_DSS | MECL | 46.2204 | -63.0792 | Prince Edward Island
| Dingwell Mills | PE_DWM_DSS | MECL | 46.3582 | -62.4467 | Prince Edward Island
| Dover | PE_DOV_DSS | MECL | 46.0225 | -62.6362 | Prince Edward Island
| Eastern Kings GS | PE_EKS_GSS | MECL | 46.4525 | -62.0682 | Prince Edward Island
| Georgetown | PE_GRG_DSS | MECL | 46.1981 | -62.5475 | Prince Edward Island
| Hermanville GS | PE_HRM_GSS | MECL | 46.4549 | -62.3143 | Prince Edward Island
| Hermanville JCT | PE_HRM_JCT | MECL | 46.3975 | -62.25 | Prince Edward Island
| Hunter River | PE_HTR_DSS | MECL | 46.3492 | -63.3572 | Prince Edward Island
| IPB Richmond Cove | PP_NBPE1_IPT | MECL | 46.2051 | -63.7575 | Prince Edward Island |  | Midway across Northumberland Strait
| Kensington | PE_KEN_DSS | MECL | 46.4266 | -63.6184 | Prince Edward Island
| Lorne Valley | PE_LNV_DSS | MECL | 46.2569 | -62.6933 | Prince Edward Island
| Mount Albion | PE_MAB_DSS | MECL | 46.2254 | -62.9634 | Prince Edward Island
| Northcape GS | PE_NCP_GSS | MECL | 47.0485 | -63.995 | Prince Edward Island
| O'Leary | PE_OLY_DSS | MECL | 46.7371 | -64.1788 | Prince Edward Island
| Rattenbury | PE_RTN_DSS | MECL | 46.3955 | -63.506 | Prince Edward Island
| Richmond Cove | PE_RCV_TSS | MECL | 46.324 | -63.7831 | Prince Edward Island
| Scotchfort | PE_SCF_DSS | MECL | 46.3488 | -62.9181 | Prince Edward Island
| Sherbrooke | PE_SHB_DFS | MECL | 46.4217 | -63.7704 | Prince Edward Island
| Souris | PE_SOU_DSS | MECL | 46.3481 | -62.241 | Prince Edward Island
| St. Eleanors | PE_STE_DFS | MECL | 46.4256 | -63.8304 | Prince Edward Island
| Suez Norway GS | PE_SZN_GSS | MECL | 47.0368 | -64.0051 | Prince Edward Island
| Summerside | PE_SMS_DFS | MECL | 46.4352 | -63.8273 | Prince Edward Island
| University PEI | PE_UPE_DSS | MECL | 46.2621 | -63.1403 | Prince Edward Island
| Victoria Cross | PE_VCX_DSS | MECL | 46.1639 | -62.6938 | Prince Edward Island
| WEICan GS | PE_WEI_GSS | MECL | 47.0329 | -64.0168 | Prince Edward Island
| Wellington | PE_WEL_DSS | MECL | 46.4693 | -63.9834 | Prince Edward Island
| West Cape GS | PE_WCP_GSS | MECL | 46.6827 | -64.3832 | Prince Edward Island
| West Royalty | PE_WRY_DSS | MECL | 46.2773 | -63.1611 | Prince Edward Island
| West St.Peters | PE_WSP_DSS | MECL | 46.4112 | -62.7771 | Prince Edward Island
Legend:
CSS = Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
ISS = Industrial Customer Substation
JCT = Junction
SWS = Switching Station
TSS = Terminal Station

## Distribution
PE | EXISTING TRANSMISSION
| Node Name | Node Code | Owner | Latitude | Longitude | Planning Region | Transformers | Primary Voltage | Seondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Other References | Notes
[8 empty] | (kV) |  | (MVA) | (MVA) |  | (MW) | (MW)
| Aeolus GS | PE_AOL_GSS | MECL | 47.0368 | -64.005 | Prince Edward island
| Airport | PE_APT_ISS | MECL | 46.291 | -63.1309 | Prince Edward island
| Albany | PE_ABY_DSS | MECL | 46.2673 | -63.6399 | Prince Edward island
| Alberton | PE_ALB_DFS | MECL | 46.8372 | -64.0832 | Prince Edward island
| Bagnall Road | PE_BAG_DSS | MECL | 46.3844 | -63.3617 | Prince Edward island
| Bedeque | PE_BED_SWS | MECL | 46.3151 | -63.6696 | Prince Edward island
| Borden | PE_BOR_DFS | MECL | 46.2493 | -63.6881 | Prince Edward island | X3 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54
| Cavendish Farms | PE_CAV_ISS | MECL | 46.422 | -63.6789 | Prince Edward island
| Charlottetown | PE_CHA_DFS | MECL | 46.2403 | -63.1162 | Prince Edward island
| Church Road | PE_CHR_TSS | MECL | 46.3946 | -62.4185 | Prince Edward island | X1 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54
| Crossroads | PE_CRD_DSS | MECL | 46.2204 | -63.0792 | Prince Edward island
| Dingwell Mills | PE_DWM_DSS | MECL | 46.3582 | -62.4467 | Prince Edward island
| Dover | PE_DOV_DSS | MECL | 46.0225 | -62.6362 | Prince Edward island
| Eastern Kings GS | PE_EKS_GSS | MECL | 46.4525 | -62.0682 | Prince Edward island
| Georgetown | PE_GRG_DSS | MECL | 46.1981 | -62.5475 | Prince Edward island
| Hermanville GS | PE_HRM_GSS | MECL | 46.4549 | -62.3143 | Prince Edward island
| Hermanville JCT | PE_HRM_JCT | MECL | 46.3975 | -62.25 | Prince Edward island
| Hunter River | PE_HTR_DSS | MECL | 46.3492 | -63.3572 | Prince Edward island
| IPB Richmond Cove | PP_NBPE1_IPT | MECL | 46.2051 | -63.7575 | Prince Edward island
| Kensington | PE_KEN_DSS | MECL | 46.4266 | -63.6184 | Prince Edward island
| Lorne Valley | PE_LNV_DSS | MECL | 46.2569 | -62.6933 | Prince Edward island
| Mount Albion | PE_MAB_DSS | MECL | 46.2254 | -62.9634 | Prince Edward island
| Northcape GS | PE_NCP_GSS | MECL | 47.0485 | -63.995 | Prince Edward island
| O'Leary | PE_OLY_DSS | MECL | 46.7371 | -64.1788 | Prince Edward island
| Rattenbury | PE_RTN_DSS | MECL | 46.3955 | -63.506 | Prince Edward island
| Richmond Cove | PE_RCV_TSS | MECL | 46.324 | -63.7831 | Prince Edward island
| Scotchfort | PE_SCF_DSS | MECL | 46.3488 | -62.9181 | Prince Edward island
| Sherbrooke | PE_SHB_DFS | MECL | 46.4217 | -63.7704 | Prince Edward island | X1 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54
| Sherbrooke | PE_SHB_DFS | MECL | 46.4217 | -63.7704 | Prince Edward island | X2 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54
| Souris | PE_SOU_DSS | MECL | 46.3481 | -62.241 | Prince Edward island
| St. Eleanors | PE_STE_DFS | MECL | 46.4256 | -63.8304 | Prince Edward island
| Suez Norway GS | PE_SZN_GSS | MECL | 47.0368 | -64.0051 | Prince Edward island
| Summerside | PE_SMS_DFS | MECL | 46.4352 | -63.8273 | Prince Edward island
| University PEI | PE_UPE_DSS | MECL | 46.2621 | -63.1403 | Prince Edward island
| Victoria Cross | PE_VCX_DSS | MECL | 46.1639 | -62.6938 | Prince Edward island
| WEICan GS | PE_WEI_GSS | MECL | 47.0329 | -64.0168 | Prince Edward island
| Wellington | PE_WEL_DSS | MECL | 46.4693 | -63.9834 | Prince Edward island
| West Cape GS | PE_WCP_GSS | MECL | 46.6827 | -64.3832 | Prince Edward island
| West Royalty | PE_WRY_DSS | MECL | 46.2773 | -63.1611 | Prince Edward island | X5 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54
| West Royalty | PE_WRY_DSS | MECL | 46.2773 | -63.1611 | Prince Edward island | X6 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54
| West Royalty | PE_WRY_DSS | MECL | 46.2773 | -63.1611 | Prince Edward island | X7 | 138 | 69 | 50 | 60 | 0.9 | 45 | 54
| West St.Peters | PE_WSP_DSS | MECL | 46.4112 | -62.7771 | Prince Edward island
Legend:
CSS = Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
ISS = Industrial Customer Substation
JCT = Junction
SWS = Switching Station
TSS = Terminal Station

## System
PE | SYSTEM CHARACTERISTICS |  |  |  | SYSTEM CHARACTERISTICS
| Generator Type | Capacity Adjustment (ELCC) | Capacity Factor | Notes | Reserve Requirements | Line Losses
|  | (%) | (%) |  | (% installed MW) | (% across system)
| Heavy Fuel Oil | 73% |  |  | 21% | 6.4%
| Light Fuel Oil CT | 78% | 1%
| Natural Gas CC | 73%
| Natural Gas CT | 93% | 1%
| Biomass / Biogas | 95% | 85%
| Nuclear | 90% | 90%
| Wind | 20% | 37% | ELCC for wind drops as more wind is added to the system
| Solar | 5% | 15% | ELCC may be higher for battery connected solar facilities
Notes:
ELCC is a dynamic value that changes as the wind penetration level changes, and is unique to each electricity system depending upon the capabilities of the other system generating units and the load shape.
The minimum monthly capacty factor for purchases from Point Lepreau is 85%, so 90% was used
Capacity adjustments for Nova Scotia (wind and solar) and Ontario (nuclear) have been used

## HGWh
PE | HISTORICAL ANNUAL ENERGY DEMAND | UNIT | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2010-2019
| MECL Annual Energy Demand (After DSM) | GWh/year | 1115 | 1132 | 1165 | 1214 | 1256 | 1279 | 1282 | 1298 | 1349 | 1385
| Summerside Annual Energy Demand (After DSM) | GWh/year | 123 | 127 | 133 | 136 | 139 | 145 | 142 | 145 | 145 | 146
| Island Annual Energy Demand (After DSM) | GWh/year | 1238 | 1259 | 1298 | 1350 | 1395 | 1424 | 1424 | 1443 | 1494 | 1531
| Annual Change in Energy Demand | GWh/year |  | 21 | 39 | 52 | 45 | 29 | 0 | 19 | 51 | 37 | Average
| Percentage Change in Energy Demand | % |  | 1.696% | 3.098% | 4.006% | 3.333% | 2.079% | 0% | 1.334% | 3.534% | 2.477% | 2.388%
Specific notes:
There are two utiities on the Island: : Summerside Electric, which serves Summerside and Maritime Electric, which serves the reaminder of the province

## HMW
PE | HISTORICAL PEAK DEMAND | UNIT | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2010-2019
| MECL Peak Demand (After DSM) | MW
| Summerside Peak Demand (After DSM) | MW
| Island Summer Peak Demand (After DSM) | MW | 190 | 183 | 194 | 196 | 195 | 205 | 200 | 200 | 220 | 227
| Island Winter Peak Demand (After DSM) | MW | 206 | 223 | 228 | 252 | 255 | 264 | 264 | 278 | 280 | 275
| Annual Change in Winter Peak Demand | MW |  | 17 | 5 | 24 | 3 | 9 | 0 | 14 | 2 | -5 | Average
| Percentage Change in Winter Peak Demand | % |  | 8.252% | 2.242% | 10.53% | 1.19% | 3.529% | 0% | 5.303% | 0.7194% | -1.786% | 3.262%
Specific notes:
There are two utiities on the Island: : Summerside Electric, which serves Summerside and Maritime Electric, which serves the reaminder of the province

## FGWh
PE | FORECAST ANNUAL ENERGY DEMAND | UNIT | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2020-2030 | 2020-2050 | Notes
| MECL Annual Energy Demand (After DSM) | GWh/year | 1443 | 1489 | 1525 | 1560 | 1593 | 1625 | 1656 | 1688 | 1720 | 1752 | 1782
| Summerside Annual Energy Demand (After DSM) | GWh/year | 153 | 157 | 162 | 165 | 169 | 173 | 176 | 180 | 183 | 187 | 190
| Island Annual Energy Demand (After DSM) | GWh/year | 1596 | 1646 | 1687 | 1725 | 1762 | 1798 | 1832 | 1868 | 1903 | 1939 | 1972
| Annual Change in Energy Demand | GWh/year |  | 50 | 41 | 38 | 37 | 36 | 34 | 36 | 35 | 36 | 33 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050
| Percentage Change in Energy Demand | % |  | 3.133% | 2.491% | 2.253% | 2.145% | 2.043% | 1.891% | 1.965% | 1.874% | 1.892% | 1.702% | 2.187% | 2.187% | Mid-load forecast for use in COPPER
Specific notes:
There are two utiities on the Island: : Summerside Electric, which serves Summerside and Maritime Electric, which serves the reaminder of the province

## FMW
PE | FORECAST PEAK DEMAND | UNIT | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2020-2030 | 2020-2050 | Notes
| Island Winter Peak Demand (After DSM) | MW | 294 | 304 | 312 | 321 | 329 | 337 | 345 | 353 | 361 | 368 | 374
| Island Summer Peak Demand (After DSM) | MW | 223 | 226 | 230 | 233 | 237 | 240 | 243 | 247 | 250 | 254 | 257
| Annual Change in Energy Demand | MW |  | 10 | 8 | 9 | 8 | 8 | 8 | 8 | 8 | 7 | 6 | 2020-2030 Rate | 2020-2050 Rate | Assume extended to 2050
| Percentage Change in Energy Demand | % |  | 3.401% | 2.632% | 2.885% | 2.492% | 2.432% | 2.374% | 2.319% | 2.266% | 1.939% | 1.63% | 2.526% | 2.526% | Mid-load forecast for use in COPPER
Specific notes:
There are two utiities on the Island: : Summerside Electric, which serves Summerside and Maritime Electric, which serves the reaminder of the province

## Hourly
PE | Hourly
Not yet available

## Inputs
PE | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance