## README
BC | LEGEND
| BC-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| BLANK | Separates included from excluded tabs in CODERS
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Distribution | Characteristics of existing distribution substations
| System | Miscellaneous provincial system characteristics
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to references

## BC-Sources
BC | PRIMARY SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| BC Hydro | 2013 | Integrated Resource Plan 2013 Resource Options Report Update Mica Pumped Storage Report | https://www.bchydro.com/toolbar/about/planning-for-our-future/irp/current-plan/document-centre/reports/november-2013-irp.html |  | British Columbia
| BC Hydro | 2008 | 2008 Long-term Acquisition Plan: Appendix F8 Potential Large Hydro Project Report | https://www.bchydro.com/toolbar/about/planning-for-our-future/irp/past-plans/2008-ltap.html |  | British Columbia
| BC Hydro | 2013 | Integrated Resource Plan Appendix 3A-30. 2013 Resource Options Report Update - Lower Mainland/Vancouver Island Pumped Storage Report and North Coast Pumped Storage Report. Prepared by Knight Piesold Consulting. | https://www.bchydro.com/toolbar/about/planning-for-our-future/irp/current-plan/document-centre/reports/november-2013-irp.html https://www.bchydro.com/toolbar/about/planning-for-our-future/irp/current-plan/document-centre/reports/november-2013-irp.html |  | British Columbia
| BC Hydro | 2021 | BC Hydro and Power Authority Draft 2021 Integrated Resource Plan | https://www.bchydro.com/content/dam/BCHydro/customer-portal/documents/corporate/regulatory-planning-documents/integrated-resource-plans/current-plan/draft-integrated-resource-plan.pdf |  | British Columbia
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" Column of the relevant tab
| BC Hydro | 2020 | T&D System Operations - Operating Order 5T-10. Ratings for all Transmission Circuits 60 kV or Higher | https://www.bchydro.com/content/dam/BCHydro/customer-portal/documents/corporate/suppliers/transmission-system/system_operating_orders/5T-10.pdf |  | British Columbia
| BC Hydro | 2017 | Revelstoke 6 - Environmental Assessment Certificate Application Volume 1 | https://projects.eao.gov.bc.ca/api/document/596657e946ae0a001c1b46b7/fetch/EAC_Application-Revelstoke_Generating_Station_Unit_6-Volume_1.pdf |  | British Columbia
| Water Sustainability Act | 2016 | Water Sustainability Fees, Rentals and Charges Tariff Regulation. B.C. Reg. 37/2016 | http://www.bclaws.ca/civix/document/id/loo99/loo99/37_2016
| FortisBC | 2011 | 2012 Integrated System Plan - Volume 1 | https://fbcdotcomprod.blob.core.windows.net/libraries/docs/default-source/about-us-documents/regulatory-affairs-documents/electric-utility/fortisbc-2012-integrated-system-plan---volume-1---30june2011.pdf |  | British Columbia
| BC Hydro | 2020 | T&D System Operations - Operating Order 5T-14. Ratings for all Transmission and Distribution Transformers | https://www.bchydro.com/content/dam/BCHydro/customer-portal/documents/corporate/suppliers/transmission-system/system_operating_orders/5T-14.pdf |  | British Columbia
| FortisBC | 2013 | Application for Approval of a Multi-Year Performance Based Ratemaking Plan for 2014 through 2018. Response to British Columbia Sustainable Energy Association and Sierra Club of BC (BCSEA) Information Request (IR) No. 1 | https://www.bcuc.com/ApplicationView.aspx?ApplicationId=400 |  | British Columbia
| BC Hydro | 2013 | Integrated Resource Plan 2013 Appendix 3C - Technical Planning Assumptions: Intermittent Resources ELCC & FELCC | https://www.bchydro.com/toolbar/about/planning-for-our-future/irp/current-plan/document-centre/reports/november-2013-irp.html |  | British Columbia
| WECC | 2019 | ADS 2028 Deliverables Datasets | https://www.wecc.org/SystemAdequacyPlanning/Pages/Datasets.aspx |  | Alberta, British Columbia | On the website, under Production Cost Model see 2024 Common Case sheet 150409_2024CC-V1.5_Resources
| BC Hydro | 2019 | Our Facilities | https://www.bchydro.com/energy-in-bc/operations/our-facilities.html |  | British Columbia
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | Canada
| WECC | 2019 | ADS 2028 Deliverables Anchor Data Set | https://www.wecc.org/SystemStabilityPlanning/Pages/AnchorDataSet.aspx |  | Alberta, British Columbia | On the website, see sheet ADS_PCM_V0.3.2_GeneratorList.csv and supporting information
| BC Hydro | 2020 | Independent Power Producers (IPPs) currently supplying power to BC Hydro | https://www.bchydro.com/content/dam/BCHydro/customer-portal/documents/corporate/independent-power-producers-calls-for-power/independent-power-producers/ipp-supply-list-in-operation.pdf |  | British Columbia
| FortisBC | 2019 | Electricity facilities & operations | https://www.fortisbc.com/about-us/facilities-operations-and-energy-information/electricity-facilities-and-operations |  | British Columbia
| BC Hydro | 2019 | Water Use Planning | https://www.bchydro.com/about/sustainability/conservation/water_use_planning.html |  | British Columbia
| BC Hydro | 2013 | Site C Environmental Impact Statement Volume 2, Appendix G | https://www.ceaa-acee.gc.ca/050/evaluations/document/85328?culture=en-CA |  | British Columbia
| BC Hydro | 2020 | Transmission System. BCH Drawing No. G-T06-00010 Station Planning Transmission & Stations Planning | https://www.bchydro.com/content/dam/BCHydro/customer-portal/documents/corporate/suppliers/transmission-system/maps/transplt-Default-000.pdf |  | British Columbia
| Government of BC | 2019 | BC Transmission Lines | https://catalogue.data.gov.bc.ca/dataset/bc-transmission-lines |  | British Columbia | Order csv from website; see spreadsheet TRNS_LNS.csv for original file
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| BCUC | 2017 | British Columbia Hydro and Power Authority - British Columbia Utilities Commission Inquiry Respecting Site C - Project No. 1598922 - Final Report [A-24] | https://www.bcuc.com/Documents/wp-content/11/11-01-2017-BCUC-Site-C-Inquiry-Final-Report.pdf |  | British Columbia
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Columbia Power | 2021 | Columbia Power Facilities | http://columbiapower.org/projects/
| BC Hydro | 2021 | Historical Transmission Data: Gross Telemetered Load: British Columbia | https://www.bchydro.com/energy-in-bc/operations/transmission/transmission-system/balancing-authority-load-data/historical-transmission-data.html |  | British Columbia
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
BC | EXISTING GENERATION | [12 empty] | DESIGN
| Project Name | Gen Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Unit | # of units | Other References | Notes
[11 empty] | (kV) |  |  |  |  | (MW) |  | (MW) | (%) | (GWh/year)
| 150 Mile House | BC_OFM00_GEN | EnPower Green Energy Generation Limited Partnership | 150 Mile House | 52.1287 | -121.9288 | British Columbia.a | British Columbia | Soda Creek | BC_SCK_DSS | 69 | 2008 | 2038 | Biomass | biomass | 6.5 | 97% | 6.305 | 59.71% | 34 | 1 |  | Energy recovery generator
| Aberfeldie_01 | BC_ABN01_GEN | BC Hydro | Cranbrook | 49.4933 | -115.3624 | British Columbia.a | British Columbia | Aberfeldie GS | BC_ABN_GSS | 69 | 2009 | 2049 | Hydro_daily | hydro_daily | 8 | 100% | 8 | 33.12% | 23.208 | 3
| Aberfeldie_02 | BC_ABN02_GEN | BC Hydro | Cranbrook | 49.4933 | -115.3624 | British Columbia.a | British Columbia | Aberfeldie GS | BC_ABN_GSS | 69 | 2009 | 2049 | Hydro_daily | hydro_daily | 8 | 100% | 8 | 33.12% | 23.208 | 3
| Aberfeldie_03 | BC_ABN03_GEN | BC Hydro | Cranbrook | 49.4933 | -115.3624 | British Columbia.a | British Columbia | Aberfeldie GS | BC_ABN_GSS | 69 | 2009 | 2049 | Hydro_daily | hydro_daily | 8 | 100% | 8 | 33.12% | 23.208 | 3
| Akolkolex | BC_ALK00_GEN | Canadian Hydro Developers, Inc. | Revelstoke | 50.8227 | -118.0295 | British Columbia.a | British Columbia | Illecillewaet | BC_ILL_DSS | 69 | 1995 | 2035 | Hydro_run | hydro_run | 10 | 32.22% | 3.222 | 46.23% | 40.5 | 1
| Alouette | BC_ALU00_GEN | BC Hydro | Lower Mainland | 49.371 | -122.3124 | British Columbia.a | British Columbia | Alouette GS | BC_ALU_GSS | 69 | 1928 | 2038 | Hydro_daily | hydro_daily | 9 | 100% | 9 | 33.12% | 26.1086 | 1
| Arrow Lakes_01 | BC_ALH01_GEN | Columbia Power / Columbia Basin Trust | Slocan | 49.343 | -117.7688 | British Columbia.a | British Columbia | Arrow Lakes GS | BC_ALH_GSS | 230 | 2002 | 2042 | Hydro_daily | hydro_daily | 92.5 | 100% | 92.5 | 47.33% | 383.5 | 2
| Arrow Lakes_02 | BC_ALH02_GEN | Columbia Power / Columbia Basin Trust | Slocan | 49.343 | -117.7688 | British Columbia.a | British Columbia | Arrow Lakes GS | BC_ALH_GSS | 230 | 2002 | 2042 | Hydro_daily | hydro_daily | 92.5 | 100% | 92.5 | 47.33% | 383.5 | 2
| Ash | BC_ASH00_GEN | BC Hydro | Vancouver Island | 49.3734 | -125.1506 | British Columbia.a | British Columbia | Ash River GS | BC_ASH_GSS | 138 | 1958 | 2028 | Hydro_daily | hydro_daily | 28 | 100% | 28 | 33.12% | 81.2266 | 1
| Ashlu Creek | BC_ASL00_GEN | Ashlu Creek Investments LP | Squamish | 49.9143 | -123.325 | British Columbia.a | British Columbia | Ashlu GS | BC_ASL_GSS | 230 | 2009 | 2049 | Hydro_run | hydro_run | 49.9 | 32.22% | 16.0778 | 61.47% | 268.7 | 1
| Barr Creek | BC_BRC00_GEN | Barr Creek Limited Partnership | Tahsis | 49.9278 | -126.7602 | British Columbia.a | British Columbia | Tahsis Village | BC_TSV_DSS | 138 | 2012 | 2052 | Hydro_run | hydro_run | 4 | 32.22% | 1.2888 | 45.66% | 16 | 1
| Bear Mountain | BC_BMW00_GEN | Bear Mountain Wind Limited Partnership | Dawson Creek | 55.7041 | -120.4264 | British Columbia.a | British Columbia | Bear Mountain GS | BC_BMW_GSS | 138 | 2009 | 2029 | Wind_Onshore | wind | 102.5 | 26% | 26.65 | 21.94% | 197 | 1
| Big Silver | BC_BSV00_GEN | Big Silver Creek Power Limited Partnership | Harrison Hot Springs | 49.693 | -121.8591 | British Columbia.a | British Columbia | Big Silver GS | BC_BSV_GSS | 138 | 2016 | 2056 | Hydro_run | hydro_run | 40.6 | 32.22% | 13.0813 | 44.6% | 158.62 | 1
| Bone Creek | BC_BNC00_GEN | Western Sustainable Power Inc. | Kamloops | 52.2553 | -119.1808 | British Columbia.a | British Columbia | Bone Creek GS | BC_BNC_GSS | 138 | 2011 | 2051 | Hydro_run | hydro_run | 20 | 32.22% | 6.444 | 46.23% | 81 | 1
| Bonnington Falls | BC_BNF00_GEN | Nelson Hydro | Kootenay River | 49.4582 | -117.4854 | British Columbia.a | British Columbia | Nelson | BC_NLS_DSS | 63 | 1908 | 2058 | Hydro_run | hydro_run | 16.2 | 32.22% | 5.2196 | 54.13% | 76.81 | 1 | http://www.virtualmuseum.ca/sgc-cms/expositions-exhibitions/hydro/en/dams/?action=bonningtonfalls
| Boston Bar | BC_BBR00_GEN | Boston Bar Limited Partnership | Boston Bar | 49.8113 | -121.4585 | British Columbia.a | British Columbia | Boston Bar | BC_BBR_DSS | 69 | 1994 | 2034 | Hydro_run | hydro_run | 6 | 32.22% | 1.9332 | 70.4% | 37 | 1
| Boulder Creek | BC_BDH00_GEN | Boulder Creek Power Limited Partnership | Pemberton | 50.6355 | -123.4059 | British Columbia.a | British Columbia | Boulder Creek GS | BC_BDH_GSS | 230 | 2015 | 2055 | Hydro_run | hydro_run | 25 | 32.22% | 8.055 | 42.15% | 92.3 | 1
| Box Canyon | BC_BOX00_GEN | Box Canyon Hydro Corporation | Port Mellon | 49.6006 | -123.4267 | British Columbia.a | British Columbia | Box Canyon GS | BC_BOX_GSS | 138 | 2015 | 2055 | Hydro_run | hydro_run | 14.7 | 32.22% | 4.7363 | 36.81% | 47.4 | 1
| Brandywine Creek | BC_BDW00_GEN | Rockford Energy Corp. | Whistler | 49.9783 | -123.1417 | British Columbia.a | British Columbia | Function Junction | BC_FCN_DSS | 230 | 2003 | 2043 | Hydro_run | hydro_run | 7.6 | 32.22% | 2.4487 | 51.22% | 34.1 | 1
| Bridge1_01 | BC_BR0101_GEN | BC Hydro | Lillooet | 50.7299 | -122.24 | British Columbia.a | British Columbia | Bridge River 1 GS | BC_BR1_DFS | 230 | 1934 | 2044 | Hydro_daily | hydro_daily | 51.5 | 100% | 51.5 | 33.12% | 149.399 | 4
| Bridge1_02 | BC_BR0102_GEN | BC Hydro | Lillooet | 50.7299 | -122.24 | British Columbia.a | British Columbia | Bridge River 1 GS | BC_BR1_DFS | 230 | 1934 | 2044 | Hydro_daily | hydro_daily | 51.5 | 100% | 51.5 | 33.12% | 149.399 | 4
| Bridge1_03 | BC_BR0103_GEN | BC Hydro | Lillooet | 50.7299 | -122.24 | British Columbia.a | British Columbia | Bridge River 1 GS | BC_BR1_DFS | 230 | 1934 | 2044 | Hydro_daily | hydro_daily | 51.5 | 100% | 51.5 | 33.12% | 149.399 | 4
| Bridge1_04 | BC_BR0104_GEN | BC Hydro | Lillooet | 50.7299 | -122.24 | British Columbia.a | British Columbia | Bridge River 1 GS | BC_BR1_DFS | 230 | 1934 | 2044 | Hydro_daily | hydro_daily | 51.5 | 100% | 51.5 | 33.12% | 149.399 | 4
| Bridge2_01 | BC_BR0201_GEN | BC Hydro | Lillooet | 50.7299 | -122.24 | British Columbia.a | British Columbia | Bridge River 2 GS | BC_BR2_GSS | 360 | 1934 | 2044 | Hydro_daily | hydro_daily | 68.5 | 100% | 68.5 | 33.12% | 198.715 | 4
| Bridge2_02 | BC_BR0202_GEN | BC Hydro | Lillooet | 50.7299 | -122.24 | British Columbia.a | British Columbia | Bridge River 2 GS | BC_BR2_GSS | 360 | 1934 | 2044 | Hydro_daily | hydro_daily | 68.5 | 100% | 68.5 | 33.12% | 198.715 | 4
| Bridge2_03 | BC_BR0203_GEN | BC Hydro | Lillooet | 50.7299 | -122.24 | British Columbia.a | British Columbia | Bridge River 2 GS | BC_BR2_GSS | 360 | 1934 | 2044 | Hydro_daily | hydro_daily | 68.5 | 100% | 68.5 | 33.12% | 198.715 | 4
| Bridge2_04 | BC_BR0204_GEN | BC Hydro | Lillooet | 50.7299 | -122.24 | British Columbia.a | British Columbia | Bridge River 2 GS | BC_BR2_GSS | 360 | 1934 | 2044 | Hydro_daily | hydro_daily | 68.5 | 100% | 68.5 | 33.12% | 198.715 | 4
| Brilliant Expansion | BC_BRX00_GEN | Columbia Power | Castlegar | 49.3231 | -117.6198 | British Columbia.a | British Columbia | Brilliant Expansion GS | BC_BRX_GSS | 230 | 2007 | 2077 | Hydro_daily | hydro_daily | 127.5 | 100% | 127.5 | 38.38% | 428.67 | 1
| Brilliant_01 | BC_BRD01_GEN | Columbia Power | Castlegar | 49.3249 | -117.6207 | British Columbia.a | British Columbia | Brilliant GS | BC_BRD_GSS | 230 | 1944 | 2054 | Hydro_daily | hydro_daily | 37.5 | 100% | 37.5 | 33.12% | 108.786 | 4
| Brilliant_02 | BC_BRD02_GEN | Columbia Power | Castlegar | 49.3249 | -117.6207 | British Columbia.a | British Columbia | Brilliant GS | BC_BRD_GSS | 230 | 1944 | 2054 | Hydro_daily | hydro_daily | 37.5 | 100% | 37.5 | 33.12% | 108.786 | 4
| Brilliant_03 | BC_BRD03_GEN | Columbia Power | Castlegar | 49.3249 | -117.6207 | British Columbia.a | British Columbia | Brilliant GS | BC_BRD_GSS | 230 | 1944 | 2054 | Hydro_daily | hydro_daily | 37.5 | 100% | 37.5 | 33.12% | 108.786 | 4
| Brilliant_04 | BC_BRD04_GEN | Columbia Power | Castlegar | 49.3249 | -117.6207 | British Columbia.a | British Columbia | Brilliant GS | BC_BRD_GSS | 230 | 1944 | 2054 | Hydro_daily | hydro_daily | 37.5 | 100% | 37.5 | 33.12% | 108.786 | 4
| Brown Lake | BC_BRL00_GEN | Brown Miller Power LP | Prince Rupert | 54.0273 | -129.8437 | British Columbia.a | British Columbia | Brown Lake GS | BC_BRL_GSS | 69 | 1996 | 2036 | Hydro_daily | hydro_daily | 7.2 | 100% | 7.2 | 90.37% | 57 | 1
| Cache Creek | BC_CHK00_GEN | Wastech Services Ltd. | Cache Creek | 50.7873 | -121.3197 | British Columbia.a | British Columbia | Cache Creek | BC_CCW_DSS | 69 | 2014 | 2029 | Biogas | biomass | 4.8 | 95% | 4.56 | 84.64% | 35.59 | 1
| Canoe Creek | BC_CNK00_GEN | Canoe Creek Hydro Company | Ucluelet | 49.1769 | -125.3956 | British Columbia.a | British Columbia | Canoe Creek GS | BC_CNK_GSS | 69 | 2010 | 2050 | Hydro_run | hydro_run | 5.5 | 32.22% | 1.7721 | 33.62% | 16.2 | 1
| Cape Scott | BC_CSS00_GEN | Cape Scott Wind LP | Port Hardy | 50.789 | -128.0033 | British Columbia.a | British Columbia | Cape Scott GS | BC_CSS_GSS | 138 | 2013 | 2033 | Wind_Onshore | wind | 99.2 | 26% | 25.792 | 36.4% | 316.3 | 1
| Cariboo Pulp and Paper_01 | BC_CBP01_GEN | Cariboo Pulp and Paper Company | Quesnel | 52.997 | -122.4853 | British Columbia.a | British Columbia | Cariboo Pulp GS | BC_CBP_GSS | 69 | 2012 | 2042 | Biomass | biomass | 30.65 | 97% | 29.7305 | 32.08% | 86.14 | 2
| Cariboo Pulp and Paper_02 | BC_CBP02_GEN | Cariboo Pulp and Paper Company | Quesnel | 52.997 | -122.4853 | British Columbia.a | British Columbia | Cariboo Pulp GS | BC_CBP_GSS | 69 | 2012 | 2042 | Biomass | biomass | 30.65 | 97% | 29.7305 | 32.08% | 86.14 | 2
| Castle Creek | BC_CSC00_GEN | Castle Mountain Hydro Ltd. | McBride | 53.1092 | -120.1942 | British Columbia.a | British Columbia | Rearguard Pumping Station | BC_REG_DSS | 138 | 2014 | 2054 | Hydro_run | hydro_run | 6 | 32.22% | 1.9332 | 64.69% | 34 | 1 |  | Formerly called Benjamin Creek
| Catalyst Paper Crofton | BC_CFT00_GEN | Catalyst Paper | Crofton | 48.8757 | -123.65 | British Columbia.a | British Columbia | Catalyst Paper Crofton GS | BC_CFT_GSS | 138 | 1990 | 2050 | Biomass | biomass | 38 | 97% | 36.86 | 21.19% | 70.54 | 1 | https://www.catalystpaper.com/about/our-facilities
| Catalyst Paper Port Alberni | BC_PAL00_GEN | Catalyst Paper | Port Alberni | 49.2474 | -124.8112 | British Columbia.a | British Columbia | Port Alberni | BC_PAL_DSS | 138 | 1990 | 2050 | Biomass | biomass | 17 | 97% | 16.49 | 21.19% | 31.56 | 1 | https://www.catalystpaper.com/about/our-facilities
| Cedar Road | BC_CDR00_GEN | Cedar Road LFG Inc. | Nanaimo | 49.1184 | -123.8964 | British Columbia.a | British Columbia | Jinglepot | BC_JPT_DSS | 138 | 2009 | 2024 | Biogas | biomass | 1.26 | 95% | 1.197 | 95.49% | 10.54 | 1
| Celgar_01 | BC_CLG01_GEN | Zellstoff Celgar Limited Partnership | Castlegar | 49.3361 | -117.7275 | British Columbia.a | British Columbia | Kraft GS | BC_KRA_GSS | 63 | 2010 | 2040 | Biomass | biomass | 40.67 | 97% | 39.4499 | 33.89% | 120.75 | 2
| Celgar_02 | BC_CLG02_GEN | Zellstoff Celgar Limited Partnership | Castlegar | 49.3361 | -117.7275 | British Columbia.a | British Columbia | Kraft GS | BC_KRA_GSS | 63 | 2010 | 2040 | Biomass | biomass | 37.33 | 97% | 36.2101 | 36.93% | 120.75 | 2
| Cheakamus_01 | BC_CMS01_GEN | BC Hydro | Lower Mainland | 49.9337 | -123.291 | British Columbia.a | British Columbia | Cheakamus GS | BC_CMS_DFS | 230 | 1988 | 2058 | Hydro_daily | hydro_daily | 90 | 100% | 90 | 33.12% | 261.086 | 2
| Cheakamus_02 | BC_CMS02_GEN | BC Hydro | Lower Mainland | 49.9337 | -123.291 | British Columbia.a | British Columbia | Cheakamus GS | BC_CMS_DFS | 230 | 1988 | 2058 | Hydro_daily | hydro_daily | 90 | 100% | 90 | 33.12% | 261.086 | 2
| Chetwynd | BC_CWD00_GEN | West Fraser Mills Ltd. | Chetwynd | 55.7235 | -121.565 | British Columbia.a | British Columbia | Chetwynd GS | BC_LAP_GSS | 138 | 2014 | 2044 | Biomass | biomass | 12 | 97% | 11.64 | 91.67% | 96.36 | 1
| China Creek | BC_CCK00_GEN | Upnit Power Limited Partnership | Port Alberni | 49.1856 | -124.7395 | British Columbia.a | British Columbia | Port Alberni | BC_PAL_DSS | 138 | 2005 | 2045 | Hydro_run | hydro_run | 6.3 | 32.22% | 2.0299 | 44.81% | 24.73 | 1
| Clowhom | BC_COM00_GEN | BC Hydro | Lower Mainland | 49.7109 | -123.5321 | British Columbia.a | British Columbia | Clowhom GS | BC_COM_GSS | 138 | 1958 | 2028 | Hydro_daily | hydro_daily | 45 | 100% | 45 | 33.12% | 130.5428 | 1
| Conifex Green Energy | BC_CGE00_GEN | Conifex Power Inc. | Mackenzie | 55.337 | -123.1823 | British Columbia.a | British Columbia | Parsnip | BC_PRS_DSS | 138 | 2014 | 2044 | Biomass | biomass | 36 | 97% | 34.92 | 69.76% | 220 | 1
| Corra Linn_01 | BC_COR01_GEN | FortisBC | Kootenay Lake | 49.4689 | -117.4686 | British Columbia.a | British Columbia | Corra Linn GS | BC_COR_GSS | 63 | 1932 | 2042 | Hydro_daily | hydro_daily | 17 | 100% | 17 | 33.12% | 49.316 | 3
| Corra Linn_02 | BC_COR02_GEN | FortisBC | Kootenay Lake | 49.4689 | -117.4686 | British Columbia.a | British Columbia | Corra Linn GS | BC_COR_GSS | 63 | 1932 | 2042 | Hydro_daily | hydro_daily | 17 | 100% | 17 | 33.12% | 49.316 | 3
| Corra Linn_03 | BC_COR03_GEN | FortisBC | Kootenay Lake | 49.4689 | -117.4686 | British Columbia.a | British Columbia | Corra Linn GS | BC_COR_GSS | 63 | 1932 | 2042 | Hydro_daily | hydro_daily | 17 | 100% | 17 | 33.12% | 49.316 | 3
| Cranberry Creek Power | BC_CRC00_GEN | Advanced Energy Systems II LP | Revelstoke | 50.7716 | -118.1041 | British Columbia.a | British Columbia | Pingston GS | BC_PIN_GSS | 69 | 2008 | 2048 | Hydro_run | hydro_run | 11.5 | 32.22% | 3.7053 | 8.934% | 9 | 1
| Crowsnest Pass | BC_CRW00_GEN | GIF Crowsnest Power LP | Sparwood | 49.6474 | -114.7151 | British Columbia.a | British Columbia | Crowsnest Pass GS | BC_CRW_GSS | 69 | 2012 | 2042 | Biomass | biomass | 10.5 | 97% | 10.185 | 70.58% | 64.92 | 1 |  | Energy recovery generator
| Culliton Creek | BC_CTN00_GEN | Culliton Creek Power Limited Partnership | Squamish | 49.8772 | -123.1599 | British Columbia.a | British Columbia | Culliton Creek GS | BC_CTN_GSS | 69 | 2014 | 2054 | Hydro_run | hydro_run | 15 | 32.22% | 4.833 | 56.25% | 73.91 | 1
| Cypress Creek | BC_CYK00_GEN | Synex Energy Resources Ltd | Gold River | 49.8427 | -126.1277 | British Columbia.a | British Columbia | Gold River | BC_GLD_DSS | 138 | 2009 | 2049 | Hydro_run | hydro_run | 2.83 | 32.22% | 0.91183 | 49.98% | 12.39 | 1
| Dasque-Middle | BC_DSQ00_GEN | BluEarth Renewables | Terrace | 54.3835 | -128.9149 | British Columbia.a | British Columbia | Dasque Creek GS | BC_DSQ_GSS | 69 | 2014 | 2054 | Hydro_run | hydro_run | 20 | 32.22% | 6.444 | 46.16% | 80.87 | 1
| Dokie | BC_DKW00_GEN | Dokie General Partnership | Chetwynd | 55.8118 | -122.2474 | British Columbia.a | British Columbia | Dokie GS | BC_DKW_GSS | 230 | 2011 | 2031 | Wind_Onshore | wind | 144 | 26% | 37.44 | 29.73% | 375 | 1
| Doran Taylor | BC_DTR00_GEN | Doran Taylor Hydro (JV) | Port Alberni | 49.2964 | -125.2755 | British Columbia.a | British Columbia | Doran Taylor GS | BC_DTR_GSS | 69 | 1996 | 2036 | Hydro_run | hydro_run | 5.6 | 32.22% | 1.8043 | 55.04% | 27 | 1
| Douglas Kwalsa | BC_DGL00_GEN | Harrison Hydro Limited Partnership | Mission | 49.7676 | -122.151 | British Columbia.a | British Columbia | Douglas GS | BC_DGL_GSS | 138 | 2009 | 2049 | Hydro_run | hydro_run | 28.76 | 32.22% | 9.2665 | 56.73% | 142.9345 | 1
| East Toba | BC_ETR00_GEN | Toba Montrose General Partnership | Powell River | 50.6751 | -123.9603 | British Columbia.a | British Columbia | East Toba River GS | BC_ETR_GSS | 230 | 2010 | 2050 | Hydro_run | hydro_run | 147.3 | 32.22% | 47.4601 | 56.73% | 732.0671 | 2
| East Twin | BC_ETW00_GEN | Valemount Hydro Limited Partnership | McBride | 53.4581 | -120.3834 | British Columbia.a | British Columbia | Rearguard Pumping Station | BC_REG_DSS | 69 | 1991 | 2031 | Hydro_run | hydro_run | 1.6 | 32.22% | 0.51552 | 42.81% | 6 | 1
| Eldorado Reservoir | BC_EDR00_GEN | District of Lake Country | Kelowna | 50.019 | -119.3589 | British Columbia.a | British Columbia | Duck Lake | BC_DUC_DSS | 138 | 2008 | 2048 | Hydro_daily | hydro_daily | 1.13 | 100% | 1.13 | 40.41% | 4 | 1
| Elko_01 | BC_ELK01_GEN | BC Hydro | Columbia | 49.2901 | -115.1046 | British Columbia.a | British Columbia | Elko GS | BC_ELK_GSS | 69 | 1924 | 2034 | Hydro_daily | hydro_daily | 6 | 100% | 6 | 33.12% | 17.406 | 2
| Elko_02 | BC_ELK02_GEN | BC Hydro | Columbia | 49.2901 | -115.1046 | British Columbia.a | British Columbia | Elko GS | BC_ELK_GSS | 69 | 1924 | 2034 | Hydro_daily | hydro_daily | 6 | 100% | 6 | 33.12% | 17.406 | 2
| Falls River_01 | BC_FLS01_GEN | BC Hydro | North Coast | 53.9835 | -129.7342 | British Columbia.a | British Columbia | Falls River GS | BC_FLS_GSS | 69 | 1930 | 2040 | Hydro_daily | hydro_daily | 3.5 | 100% | 3.5 | 33.11% | 10.153 | 2
| Falls River_02 | BC_FLS02_GEN | BC Hydro | North Coast | 53.9835 | -129.7342 | British Columbia.a | British Columbia | Falls River GS | BC_FLS_GSS | 69 | 1930 | 2040 | Hydro_daily | hydro_daily | 3.5 | 100% | 3.5 | 33.11% | 10.153 | 2
| Fire Kwalsa | BC_FRE00_GEN | Harrison Hydro Limited Partnership | Mission | 49.7834 | -122.2347 | British Columbia.a | British Columbia | Fire GS | BC_FRE_GSS | 138 | 2009 | 2049 | Hydro_run | hydro_run | 25.28 | 32.22% | 8.1452 | 56.73% | 125.6392 | 1
| Fitzsimmons Creek | BC_FZC00_GEN | Innergex | Whistler | 50.1056 | -122.9448 | British Columbia.a | British Columbia | Cheekye | BC_CKY_DSS | 138 | 2010 | 2050 | Hydro_run | hydro_run | 8 | 32.22% | 2.5776 | 51.37% | 36 | 1
| Forrest Kerr Hydroelectric_01 | BC_FKR01_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Forrest Kerr Hydroelectric_02 | BC_FKR02_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Forrest Kerr Hydroelectric_03 | BC_FKR03_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Forrest Kerr Hydroelectric_04 | BC_FKR04_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Forrest Kerr Hydroelectric_05 | BC_FKR05_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Forrest Kerr Hydroelectric_06 | BC_FKR06_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Forrest Kerr Hydroelectric_07 | BC_FKR07_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Forrest Kerr Hydroelectric_08 | BC_FKR08_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Forrest Kerr Hydroelectric_09 | BC_FKR09_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7172 | -130.6866 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2014 | 2054 | Hydro_run | hydro_run | 23.5 | 32.22% | 7.5717 | 56.73% | 116.793 | 9
| Fort Nelson_01 | BC_FNG01_GEN | BC Hydro | Fort Nelson | 58.801 | -122.7562 | British Columbia.a | Alberta | Fort Nelson GS | BC_FNG_GSS | 138 | 1999 | 2029 | NG_CC | gasCC | 52.2 | 94% | 49.068 | 82.35% | 376.559 | 1 |  | Interconnected to the AESO
| Fort Nelson_02 | BC_FNG02_GEN | BC Hydro | Fort Nelson | 58.801 | -122.7562 | British Columbia.a | Alberta | Fort Nelson GS | BC_FNG_GSS | 138 | 1999 | 2029 | NG_CC | gasCC | 28 | 94% | 26.32 | 22.71% | 55.708 | 1 |  | Interconnected to the AESO
| Fort St. James Green Energy | BC_FGE00_GEN | Fort St. James Green Energy Limited Partnership | Fort St. James | 54.4893 | -124.2153 | British Columbia.a | British Columbia | Fort St James Green Energy GS | BC_FGE_GSS | 69 | 2015 | 2045 | Biomass | biomass | 40 | 97% | 38.8 | 86.62% | 303.53 | 1
| Fraser Lake_01 | BC_FSR01_GEN | West Fraser Mills Ltd. | Fraser Lake | 54.0673 | -124.7484 | British Columbia.a | British Columbia | Fraser Lake | BC_FSR_DSS | 69 | 2014 | 2044 | Biomass | biomass | 6 | 97% | 5.82 | 91.67% | 48.18 | 2
| Fraser Lake_02 | BC_FSR02_GEN | West Fraser Mills Ltd. | Fraser Lake | 54.0673 | -124.7484 | British Columbia.a | British Columbia | Fraser Lake | BC_FSR_DSS | 69 | 2014 | 2044 | Biomass | biomass | 6 | 97% | 5.82 | 91.67% | 48.18 | 2
| Fraser Richmond Soil and Fibre | BC_FRS00_GEN | Harvest Fraser Richmond Organics Ltd. | Richmond | 49.1597 | -123.0378 | British Columbia.a | British Columbia | Kidd #2 | BC_KI2_DSS | 69 | 2013 | 2028 | Biogas | biomass | 1.03 | 95% | 0.9785 | 88.66% | 8 | 1
| Furry Creek | BC_FRI00_GEN | Furry Creek Power Ltd | Lions Bay | 49.5793 | -123.202 | British Columbia.a | British Columbia | Furry Creek GS | BC_FRI_GSS | 69 | 2004 | 2044 | Hydro_run | hydro_run | 10.4 | 32.22% | 3.3509 | 43.36% | 39.5 | 1
| G.M. Shrum_01 | BC_GMS01_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_02 | BC_GMS02_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_03 | BC_GMS03_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_04 | BC_GMS04_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_05 | BC_GMS05_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_06 | BC_GMS06_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_07 | BC_GMS07_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_08 | BC_GMS08_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_09 | BC_GMS09_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| G.M. Shrum_10 | BC_GMS10_GEN | BC Hydro | Peace River | 56.0148 | -122.1957 | British Columbia.a | British Columbia | GM Shrum GS | BC_GMS_GSS | 500 | 1968 | 2038 | Hydro_monthly | hydro_monthly | 305 | 100% | 305 | 60.06% | 1604.745 | 10
| Golden | BC_GLD00_GEN | Louisiana-Pacific Canada Ltd. | Golden | 51.3047 | -116.9761 | British Columbia.a | British Columbia | Kicking Horse | BC_KHS_DSS | 69 | 2011 | 2041 | Biomass | biomass | 7.5 | 97% | 7.275 | 5.327% | 3.5 | 1
| Haa-ak-suuk Creek | BC_HAA00_GEN | Haa-ak-suuk Creek Hydro Limited Partnership | Ucluelet | 49.2479 | -125.3837 | British Columbia.a | British Columbia | Haa-Ak-Suuk GS | BC_HAS_GSS | 69 | 2015 | 2055 | Hydro_run | hydro_run | 6 | 32.22% | 1.9332 | 39% | 20.5 | 1
| Harmac | BC_HMC00_GEN | Nanaimo Forest Products Ltd. | Nanaimo | 49.1385 | -123.8571 | British Columbia.a | British Columbia | Harmac Pacific | BC_HMC_ISS | 138 | 2013 | 2043 | Biomass | biomass | 55 | 97% | 53.35 | 43.37% | 208.96 | 1
| Hartland | BC_HTL00_GEN | Capital Regional District | Saanich | 48.5392 | -123.4624 | British Columbia.a | British Columbia | Catalyst Paper Crofton GS | BC_CFT_GSS | 138 | 2004 | 2034 | Biogas | biomass | 1.8 | 95% | 1.71 | 91.96% | 14.5 | 1
| Hauer Creek | BC_HAC00_GEN | Hauer Creek Power Inc. | Valemount | 52.9342 | -119.4562 | British Columbia.a | British Columbia | Rearguard Pumping Station | BC_REG_DSS | 138 | 2007 | 2047 | Hydro_run | hydro_run | 2.4 | 32.22% | 0.77328 | 59.46% | 12.5 | 1
| Houweling Nurseries | BC_HWL00_GEN | Houweling Nurseries Property Ltd. | Delta | 49.0543 | -123.0449 | British Columbia.a | British Columbia | Arnott | BC_ARN_DSS | 138 | 2014 | 2029 | Biogas | biomass | 8.8 | 95% | 8.36 | 83.9% | 64.68 | 1
| Howe Sound Green Energy_01 | BC_HSG01_GEN | Howe Sound Pulp and Paper Corporation | Port Mellon | 49.522 | -123.4862 | British Columbia.a | British Columbia | Howe Sound Pulp | BC_HSP_ISS | 230 | 2011 | 2041 | Biomass | biomass | 62 | 97% | 60.14 | 36.82% | 200 | 2
| Howe Sound Green Energy_02 | BC_HSG02_GEN | Howe Sound Pulp and Paper Corporation | Port Mellon | 49.522 | -123.4862 | British Columbia.a | British Columbia | Howe Sound Pulp | BC_HSP_ISS | 230 | 2011 | 2041 | Biomass | biomass | 50 | 97% | 48.5 | 45.66% | 200 | 2
| Hunter Creek | BC_HNC00_GEN | Hunter Creek Hydro Limited Partnership | Hope | 49.3648 | -121.5714 | British Columbia.a | British Columbia | Hope | BC_HOP_DSS | 69 | 2018 | 2058 | Hydro_run | hydro_run | 11 | 32.22% | 3.5442 | 38.4% | 37 | 1
| Hystad Creek | BC_HYS00_GEN | Valemount Hydro Limited Partnership | Valemount | 52.8413 | -119.3524 | British Columbia.a | British Columbia | Valemount | BC_VLM_DSS | 138 | 2002 | 2042 | Hydro_run | hydro_run | 6 | 32.22% | 1.9332 | 38.05% | 20 | 1
| Intercon Green Power | BC_IGP00_GEN | Canfor Pulp Limited Partnership | Prince George | 53.9235 | -122.6957 | British Columbia.a | British Columbia | Prince George Pulp | BC_HCR_ISS | 69 | 2015 | 2045 | Biomass | biomass | 31.7 | 97% | 30.749 | 26.29% | 73 | 1
| Island Generation | BC_ICG00_GEN | V.I. Power Limited Partnership | Campbell River | 50.0691 | -125.2819 | British Columbia.a | British Columbia | Island GS | BC_ICG_GSS | 138 | 2002 | 2023 | NG_CC | gasCC | 290 | 94% | 272.6 | 90.54% | 2300 | 1
| Jamie Creek | BC_JME00_GEN | Jamie Creek LP | Gold Bridge | 50.8282 | -123.0568 | British Columbia.a | British Columbia | Jamie Creek GS | BC_JME_GSS | 69 | 2014 | 2054 | Hydro_run | hydro_run | 21.34 | 32.22% | 6.8757 | 39.77% | 74.34 | 1
| Jimmie Creek | BC_JMC00_GEN | Jimmie Creek Limited Partnership | Powell River | 50.604 | -124.0249 | British Columbia.a | British Columbia | Jimmie Creek GS | BC_JMC_GSS | 230 | 2016 | 2056 | Hydro_run | hydro_run | 66.2 | 32.22% | 21.3296 | 56.73% | 329.0078 | 1
| John Hart_01 | BC_JHT01_GEN | BC Hydro | Vancouver Island | 50.044 | -125.3109 | British Columbia.a | British Columbia | John Hart GS | BC_JHT_GSS | 138 | 2021 | 2091 | Hydro_daily | hydro_daily | 46 | 100% | 46 | 33.12% | 133.444 | 3
| John Hart_02 | BC_JHT02_GEN | BC Hydro | Vancouver Island | 50.044 | -125.3109 | British Columbia.a | British Columbia | John Hart GS | BC_JHT_GSS | 138 | 2021 | 2091 | Hydro_daily | hydro_daily | 46 | 100% | 46 | 33.12% | 133.444 | 3
| John Hart_03 | BC_JHT03_GEN | BC Hydro | Vancouver Island | 50.044 | -125.3109 | British Columbia.a | British Columbia | John Hart GS | BC_JHT_GSS | 138 | 2021 | 2091 | Hydro_daily | hydro_daily | 46 | 100% | 46 | 33.12% | 133.444 | 3
| Jordan River | BC_JOR00_GEN | BC Hydro | Vancouver Island | 48.4297 | -124.0523 | British Columbia.a | British Columbia | Jordan River GS | BC_JOR_DFS | 138 | 1971 | 2041 | Hydro_daily | hydro_daily | 170 | 100% | 170 | 33.12% | 493.1617 | 1
| Kamloops Green Energy_01 | BC_KGE01_GEN | Domtar Inc. | Kamloops | 50.6894 | -120.4053 | British Columbia.a | British Columbia | Domtar Kamloops | BC_WEY_ISS | 138 | 2012 | 2042 | Biomass | biomass | 28 | 97% | 27.16 | 50.76% | 124.494 | 2
| Kamloops Green Energy_02 | BC_KGE02_GEN | Domtar Inc. | Kamloops | 50.6894 | -120.4053 | British Columbia.a | British Columbia | Domtar Kamloops | BC_WEY_ISS | 138 | 2012 | 2042 | Biomass | biomass | 16 | 97% | 15.52 | 50.74% | 71.116 | 2
| Kamloops Green Energy_03 | BC_KGE03_GEN | Domtar Inc. | Kamloops | 50.6894 | -120.4053 | British Columbia.a | British Columbia | Domtar Kamloops | BC_WEY_ISS | 138 | 2012 | 2042 | Biomass | biomass | 32 | 97% | 31.04 | 102.8% | 288.3 | 2
| Kemano_01 | BC_KMO01_GEN | Rio Tinto Alcan Inc. | Kitimat | 53.5632 | -127.9426 | British Columbia.a | British Columbia | Kemano GS | BC_KMO_GSS | 287 | 1949 | 2059 | Hydro_monthly | hydro_monthly | 112.5 | 100% | 112.5 | 41.95% | 413.375 | 8
| Kemano_02 | BC_KMO02_GEN | Rio Tinto Alcan Inc. | Kitimat | 53.5632 | -127.9426 | British Columbia.a | British Columbia | Kemano GS | BC_KMO_GSS | 287 | 1949 | 2059 | Hydro_monthly | hydro_monthly | 112.5 | 100% | 112.5 | 41.95% | 413.375 | 8
| Kemano_03 | BC_KMO03_GEN | Rio Tinto Alcan Inc. | Kitimat | 53.5632 | -127.9426 | British Columbia.a | British Columbia | Kemano GS | BC_KMO_GSS | 287 | 1949 | 2059 | Hydro_monthly | hydro_monthly | 112.5 | 100% | 112.5 | 41.95% | 413.375 | 8
| Kemano_04 | BC_KMO04_GEN | Rio Tinto Alcan Inc. | Kitimat | 53.5632 | -127.9426 | British Columbia.a | British Columbia | Kemano GS | BC_KMO_GSS | 287 | 1949 | 2059 | Hydro_monthly | hydro_monthly | 112.5 | 100% | 112.5 | 41.95% | 413.375 | 8
| Kemano_05 | BC_KMO05_GEN | Rio Tinto Alcan Inc. | Kitimat | 53.5632 | -127.9426 | British Columbia.a | British Columbia | Kemano GS | BC_KMO_GSS | 287 | 1949 | 2059 | Hydro_monthly | hydro_monthly | 112.5 | 100% | 112.5 | 41.95% | 413.375 | 8
| Kemano_06 | BC_KMO06_GEN | Rio Tinto Alcan Inc. | Kitimat | 53.5632 | -127.9426 | British Columbia.a | British Columbia | Kemano GS | BC_KMO_GSS | 287 | 1949 | 2059 | Hydro_monthly | hydro_monthly | 112.5 | 100% | 112.5 | 41.95% | 413.375 | 8
| Kemano_07 | BC_KMO07_GEN | Rio Tinto Alcan Inc. | Kitimat | 53.5632 | -127.9426 | British Columbia.a | British Columbia | Kemano GS | BC_KMO_GSS | 287 | 1949 | 2059 | Hydro_monthly | hydro_monthly | 112.5 | 100% | 112.5 | 41.95% | 413.375 | 8
| Kemano_08 | BC_KMO08_GEN | Rio Tinto Alcan Inc. | Kitimat | 53.5632 | -127.9426 | British Columbia.a | British Columbia | Kemano GS | BC_KMO_GSS | 287 | 1949 | 2059 | Hydro_monthly | hydro_monthly | 112.5 | 100% | 112.5 | 41.95% | 413.375 | 8
| Kokish River | BC_KKS00_GEN | Kwagis Power Limited Partnership | Port McNeil | 50.5199 | -126.8755 | British Columbia.a | British Columbia | Kokish GS | BC_KKS_GSS | 138 | 2014 | 2054 | Hydro_run | hydro_run | 45 | 32.22% | 14.499 | 44.38% | 174.93 | 1
| Kootenay Canal_01 | BC_KCL01_GEN | BC Hydro | Columbia | 49.4533 | -117.5179 | British Columbia.a | British Columbia | Kootenay Canal GS | BC_KCL_GSS | 230 | 1975 | 2045 | Hydro_daily | hydro_daily | 146.25 | 100% | 146.25 | 33.12% | 424.2641 | 4
| Kootenay Canal_02 | BC_KCL02_GEN | BC Hydro | Columbia | 49.4533 | -117.5179 | British Columbia.a | British Columbia | Kootenay Canal GS | BC_KCL_GSS | 230 | 1975 | 2045 | Hydro_daily | hydro_daily | 147.25 | 100% | 147.25 | 33.12% | 427.1651 | 4
| Kootenay Canal_03 | BC_KCL03_GEN | BC Hydro | Columbia | 49.4533 | -117.5179 | British Columbia.a | British Columbia | Kootenay Canal GS | BC_KCL_GSS | 230 | 1975 | 2045 | Hydro_daily | hydro_daily | 148.25 | 100% | 148.25 | 33.12% | 430.066 | 4
| Kootenay Canal_04 | BC_KCL04_GEN | BC Hydro | Columbia | 49.4533 | -117.5179 | British Columbia.a | British Columbia | Kootenay Canal GS | BC_KCL_GSS | 230 | 1975 | 2045 | Hydro_daily | hydro_daily | 149.25 | 100% | 149.25 | 33.12% | 432.967 | 4
| Kruger Products Paper Mill | BC_SCP00_GEN | Kruger Energy | New Westminster | 49.2013 | -122.9366 | British Columbia.a | British Columbia | Kruger Products | BC_SCP_ISS | 69 | 2009 | 2039 | Biomass | biomass | 14 | 97% | 13.58 | 21.19% | 25.99 | 1 | https://www.krugerproducts.ca/pdfs/Plant-Fact_Sheets/KrugerFactSheetNewWestminster_EN.pdf
| Kwoiek Creek | BC_KCH00_GEN | Kwoiek Creek Resources Limited Partnership | Lytton | 50.1051 | -121.5671 | British Columbia.a | British Columbia | Kwoiek Creek GS | BC_KCH_GSS | 138 | 2013 | 2053 | Hydro_run | hydro_run | 50 | 32.22% | 16.11 | 51% | 223.38 | 1
| Ladore_01 | BC_LDR01_GEN | BC Hydro | Vancouver Island | 50.0173 | -125.393 | British Columbia.a | British Columbia | Ladore Falls GS | BC_LDR_GSS | 138 | 1956 | 2026 | Hydro_daily | hydro_daily | 23.5 | 100% | 23.5 | 33.12% | 68.172 | 2
| Ladore_02 | BC_LDR02_GEN | BC Hydro | Vancouver Island | 50.0173 | -125.393 | British Columbia.a | British Columbia | Ladore Falls GS | BC_LDR_GSS | 138 | 1956 | 2026 | Hydro_daily | hydro_daily | 23.5 | 100% | 23.5 | 33.12% | 68.172 | 2
| Lajoie | BC_LAJ00_GEN | BC Hydro | Lillooet | 50.8397 | -122.8559 | British Columbia.a | British Columbia | Lajoie GS | BC_LAJ_DFS | 69 | 1957 | 2027 | Hydro_daily | hydro_daily | 25 | 100% | 25 | 33.12% | 72.5238 | 1
| Lake Buntzen | BC_LB00_GEN | BC Hydro | Lower Mainland | 49.3752 | -122.8687 | British Columbia.a | British Columbia | Lake Buntzen GS | BC_LB1_DFS | 69 | 1951 | 2031 | Hydro_daily | hydro_daily | 55 | 100% | 55 | 33.12% | 159.5523 | 1
| Lois Lake | BC_LLK00_GEN | Powell River Energy | Stillwater | 49.7699 | -124.317 | British Columbia.a | British Columbia | Saltery Bay | BC_SAY_DSS | 138 | 1931 | 2041 | Hydro_run | hydro_run | 37 | 32.22% | 11.9214 | 54.13% | 175.44 | 1
| Long Lake_01 | BC_LNL01_GEN | Long Lake Joint Venture | Stewart | 56.0623 | -130.0185 | British Columbia.a | British Columbia | Long Lake GS | BC_LNL_GSS | 138 | 2013 | 2053 | Hydro_daily | hydro_daily | 15.5 | 100% | 15.5 | 56.73% | 77.034 | 2
| Long Lake_02 | BC_LNL02_GEN | Long Lake Joint Venture | Stewart | 56.0623 | -130.0185 | British Columbia.a | British Columbia | Long Lake GS | BC_LNL_GSS | 138 | 2013 | 2053 | Hydro_daily | hydro_daily | 15.5 | 100% | 15.5 | 56.73% | 77.034 | 2
| Lorenzetta Creek | BC_LZT00_GEN | Zella Holdings Ltd. | Laidlaw | 49.3277 | -121.6013 | British Columbia.a | British Columbia | Hope | BC_HOP_DSS | 69 | 2016 | 2056 | Hydro_run | hydro_run | 3.2 | 32.22% | 1.031 | 36.78% | 10.31 | 1
| Lower Bear | BC_BHL00_GEN | Bear Hydro Limited Partnership | Sechelt | 49.748 | -123.5159 | British Columbia.a | British Columbia | Lower Bear GS | BC_BHL_GSS | 138 | 2011 | 2051 | Hydro_run | hydro_run | 10 | 32.22% | 3.222 | 52.74% | 46.2 | 1
| Lower Bonnington_01 | BC_LBO01_GEN | FortisBC | Kootenay River | 49.4617 | -117.5004 | British Columbia.a | British Columbia | Lower Bonnington GS | BC_LBO_GSS | 63 | 1897 | 2047 | Hydro_daily | hydro_daily | 16 | 100% | 16 | 33.12% | 46.415 | 3
| Lower Bonnington_02 | BC_LBO02_GEN | FortisBC | Kootenay River | 49.4617 | -117.5004 | British Columbia.a | British Columbia | Lower Bonnington GS | BC_LBO_GSS | 63 | 1897 | 2047 | Hydro_daily | hydro_daily | 16 | 100% | 16 | 33.12% | 46.415 | 3
| Lower Bonnington_03 | BC_LBO03_GEN | FortisBC | Kootenay River | 49.4617 | -117.5004 | British Columbia.a | British Columbia | Lower Bonnington GS | BC_LBO_GSS | 63 | 1897 | 2047 | Hydro_daily | hydro_daily | 14 | 100% | 14 | 33.12% | 40.613 | 3
| Lower Clowhom | BC_LCH00_GEN | Clowhom Limited Partnership | Sechelt | 49.8176 | -123.3973 | British Columbia.a | British Columbia | Lower Clowhom GS | BC_LCH_GSS | 138 | 2010 | 2050 | Hydro_run | hydro_run | 10.99 | 32.22% | 3.541 | 49.86% | 48 | 1
| Mamquam | BC_MAM00_GEN | Atlantic Power Preferred Equity Ltd. | Squamish | 49.7214 | -123.0919 | British Columbia.a | British Columbia | Mamquam GS | BC_MAM_GSS | 69 | 1996 | 2036 | Hydro_run | hydro_run | 58 | 32.22% | 18.6876 | 49.2% | 250 | 1
| Marion 3 Creek | BC_MRK00_GEN | Marion Creek Hydro Inc. | Port Alberni | 49.2342 | -125.3569 | British Columbia.a | British Columbia | Marion 3 Creek GS | BC_M3C_GSS | 69 | 2005 | 2045 | Hydro_run | hydro_run | 4.6 | 32.22% | 1.4821 | 43.43% | 17.5 | 1
| McIntosh Creek | BC_MIK00_GEN | Snowshoe Power Ltd. | McBride | 53.3687 | -120.3754 | British Columbia.a | British Columbia | Rearguard Pumping Station | BC_REG_DSS | 138 | 2010 | 2050 | Hydro_run | hydro_run | 1.2 | 32.22% | 0.38664 | 39.29% | 4.13 | 1
| McLymont Creek | BC_MCY00_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.6872 | -130.7975 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2015 | 2055 | Hydro_run | hydro_run | 66 | 32.22% | 21.2652 | 42.27% | 244.4 | 1
| McMahon_01 | BC_MCM01_GEN | McMahon Cogeneration Plant JV | Taylor | 56.1463 | -120.6711 | British Columbia.a | British Columbia | McMahon GS | BC_MCM_GSS | 138 | 1993 | 2030 | NG_CG | gasCC | 55 | 94% | 51.7 | 87.17% | 420 | 2
| McMahon_02 | BC_MCM02_GEN | McMahon Cogeneration Plant JV | Taylor | 56.1463 | -120.6711 | British Columbia.a | British Columbia | McMahon GS | BC_MCM_GSS | 138 | 1993 | 2030 | NG_CG | gasCC | 55 | 94% | 51.7 | 87.17% | 420 | 2
| McNair Creek | BC_MCN00_GEN | McNair Creek Hydro Limited Partnership | Sechelt | 49.5158 | -123.5015 | British Columbia.a | British Columbia | Gibsons | BC_GIB_DSS | 138 | 2004 | 2044 | Hydro_run | hydro_run | 9.8 | 32.22% | 3.1576 | 44.26% | 38 | 1
| Mears Creek | BC_MCK00_GEN | Synex Energy Resources Ltd | Gold River | 49.872 | -126.2136 | British Columbia.a | British Columbia | Gold River Pulp | BC_GRP_ISS | 230 | 2004 | 2044 | Hydro_run | hydro_run | 3.8 | 32.22% | 1.2244 | 58.58% | 19.5 | 1
| Meikle | BC_MKL00_GEN | Meikle Wind Energy Limited Partnership | Tumbler Ridge | 55.2856 | -121.4691 | British Columbia.a | British Columbia | Meikle GS | BC_MKL_GSS | 230 | 2015 | 2035 | Wind_Onshore | wind | 194.91 | 26% | 50.6766 | 31.69% | 541 | 1
| Merritt Green Energy | BC_MIG00_GEN | Merritt Green Energy Limited Partnership | Merritt | 50.0971 | -120.7957 | British Columbia.a | British Columbia | Merritt Green GS | BC_MIG_GSS | 138 | 2015 | 2045 | Biomass | biomass | 40 | 97% | 38.8 | 86.62% | 303.53 | 1
| Mica_01 | BC_MCA01_GEN | BC Hydro | Columbia | 52.0759 | -118.5705 | British Columbia.a | British Columbia | Mica GS | BC_MCA_GSS | 500 | 1976 | 2046 | Hydro_monthly | hydro_monthly | 492 | 100% | 492 | 44.94% | 1936.7949 | 6
| Mica_02 | BC_MCA02_GEN | BC Hydro | Columbia | 52.0759 | -118.5705 | British Columbia.a | British Columbia | Mica GS | BC_MCA_GSS | 500 | 1976 | 2046 | Hydro_monthly | hydro_monthly | 492 | 100% | 492 | 44.94% | 1936.7949 | 6
| Mica_03 | BC_MCA03_GEN | BC Hydro | Columbia | 52.0759 | -118.5705 | British Columbia.a | British Columbia | Mica GS | BC_MCA_GSS | 500 | 1976 | 2046 | Hydro_monthly | hydro_monthly | 493.5 | 100% | 493.5 | 44.94% | 1942.6979 | 6
| Mica_04 | BC_MCA04_GEN | BC Hydro | Columbia | 52.0759 | -118.5705 | British Columbia.a | British Columbia | Mica GS | BC_MCA_GSS | 500 | 1976 | 2046 | Hydro_monthly | hydro_monthly | 493.5 | 100% | 493.5 | 44.94% | 1942.6979 | 6
| Mica_05 | BC_MCA05_GEN | BC Hydro | Columbia | 52.0759 | -118.5705 | British Columbia.a | British Columbia | Mica GS | BC_MCA_GSS | 500 | 2014 | 2084 | Hydro_monthly | hydro_monthly | 500 | 100% | 500 | 44.94% | 1968.4528 | 6
| Mica_06 | BC_MCA06_GEN | BC Hydro | Columbia | 52.0759 | -118.5705 | British Columbia.a | British Columbia | Mica GS | BC_MCA_GSS | 500 | 2015 | 2085 | Hydro_monthly | hydro_monthly | 500 | 100% | 500 | 44.94% | 1968.45 | 6
| Miller Creek Power | BC_MCP00_GEN | Brown Miller Power LP | Pemberton | 50.3499 | -122.8714 | British Columbia.a | British Columbia | Tisdall | BC_TIS_DSS | 230 | 2003 | 2043 | Hydro_run | hydro_run | 29.5 | 32.22% | 9.5049 | 45.66% | 118 | 1
| Montrose | BC_MTR00_GEN | Toba Montrose General Partnership | Powell River | 50.6231 | -124.1873 | British Columbia.a | British Columbia | Montrose Creek GS | BC_MTC_GSS | 230 | 2010 | 2050 | Hydro_run | hydro_run | 77.9 | 32.22% | 25.0994 | 64.02% | 436.8547 | 2
| Moose Lake | BC_MLW00_GEN | Moose Lake Wind Limited Partnership | Tumbler Ridge | 55.2856 | -121.2986 | British Columbia.a | British Columbia | Moose Lake GS | BC_MLW_GSS | 230 | 2019 | 2039 | Wind_Onshore | wind | 15 | 26% | 3.9 | 42.59% | 55.96 | 1
| Narrows Inlet | BC_NSI00_GEN | tems sayamkwu Limited Partnership | Sechelt | 49.8295 | -123.6642 | British Columbia.a | British Columbia | Malaspina | BC_MSA_DSS | 138 | 2019 | 2059 | Hydro_run | hydro_run | 33 | 32.22% | 10.6326 | 51.1% | 147.72 | 1
| Nechako Lumber | BC_NCK00_GEN | Nechako Lumber Co. Ltd | Vanderhoof | 54.0147 | -124.0513 | British Columbia.a | British Columbia | Tachick | BC_TAC_DSS | 69 | 1999 | 2029 | Biomass | biomass | 1.8 | 97% | 1.746 | 21.18% | 3.34 | 1 | https://www.sinclar.com/our_organizations/index.php
| Northwest Stave River | BC_NWS00_GEN | Northwest Stave River Hydro Limited Partnership | Mission | 49.6281 | -122.4625 | British Columbia.a | British Columbia | Northwest Stave GS | BC_NWS_GSS | 138 | 2013 | 2053 | Hydro_run | hydro_run | 17.5 | 32.22% | 5.6385 | 42.19% | 64.67 | 1
| Northwood Green Power | BC_NWP00_GEN | Canfor Pulp Ltd. | Prince George | 53.9792 | -122.6936 | British Columbia.a | British Columbia | Northwood | BC_NWP_ISS | 69 | 2014 | 2044 | Biomass | biomass | 60.42 | 97% | 58.6074 | 17.19% | 91 | 1
| NWE Williams Lake WW | BC_NWE00_GEN | Atlantic Power Preferred Equity Ltd. | Williams Lake | 52.1613 | -122.1712 | British Columbia.a | British Columbia | North West Energy | BC_NWE_ISS | 69 | 1993 | 2023 | Biomass | biomass | 67.69 | 97% | 65.6593 | 91.91% | 545 | 1
| Peace Canyon_01 | BC_PCN01_GEN | BC Hydro | Peace River | 55.9826 | -121.995 | British Columbia.a | British Columbia | Peace Canyon GS | BC_PCN_GSS | 500 | 1980 | 2050 | Hydro_monthly | hydro_monthly | 175 | 100% | 175 | 62.21% | 953.603 | 4
| Peace Canyon_02 | BC_PCN02_GEN | BC Hydro | Peace River | 55.9826 | -121.995 | British Columbia.a | British Columbia | Peace Canyon GS | BC_PCN_GSS | 500 | 1980 | 2050 | Hydro_monthly | hydro_monthly | 175 | 100% | 175 | 62.21% | 953.603 | 4
| Peace Canyon_03 | BC_PCN03_GEN | BC Hydro | Peace River | 55.9826 | -121.995 | British Columbia.a | British Columbia | Peace Canyon GS | BC_PCN_GSS | 500 | 1980 | 2050 | Hydro_monthly | hydro_monthly | 175 | 100% | 175 | 62.21% | 953.603 | 4
| Peace Canyon_04 | BC_PCN04_GEN | BC Hydro | Peace River | 55.9826 | -121.995 | British Columbia.a | British Columbia | Peace Canyon GS | BC_PCN_GSS | 500 | 1980 | 2050 | Hydro_monthly | hydro_monthly | 175 | 100% | 175 | 62.21% | 953.603 | 4
| Pennask | BC_PSW00_GEN | Zero Emissions Pennask Limited Partnership | Westbank | 49.9256 | -120.1093 | British Columbia.a | British Columbia | Pennask GS | BC_PSW_GSS | 138 | 2010 | 2030 | Wind_Onshore | wind | 15 | 26% | 3.9 | 37.9% | 49.8 | 1
| PGP Bioenergy Project | BC_PGP00_GEN | Canfor Pulp Ltd. | Prince George | 53.9225 | -122.6851 | British Columbia.a | British Columbia | Prince George Pulp | BC_HCR_ISS | 69 | 2019 | 2049 | Biomass | biomass | 59.9 | 97% | 58.103 | 20.11% | 105.5 | 1
| Pingston Creek | BC_PIN00_GEN | Joint Venture | Revelstoke | 50.5501 | -117.9484 | British Columbia.a | British Columbia | Pingston GS | BC_PIN_GSS | 69 | 2003 | 2043 | Hydro_run | hydro_run | 45 | 32.22% | 14.499 | 48.96% | 193 | 1
| Powell Lake | BC_PWL00_GEN | Brookfield Renewable Power | Powell Lake | 49.8723 | -124.5577 | British Columbia.a | British Columbia | Powell | BC_POW_DSS | 138 | 1911 | 2061 | Hydro_run | hydro_run | 46 | 32.22% | 14.8212 | 44.71% | 180.18 | 1 | https://web.archive.org/web/20120311002558/http://www.brookfieldpower.com/_Global/5/documents/relatedlinks/726.pdf
| Powell River Generation_11 | BC_POW01_GEN | Catalyst Paper | Powell River | 49.8731 | -124.5544 | British Columbia.a | British Columbia | Powell | BC_POW_DSS | 138 | 2012 | 2042 | Biomass | biomass | 10 | 97% | 9.7 | 89.9% | 78.755 | 2
| Powell River Generation_12 | BC_POW02_GEN | Catalyst Paper | Powell River | 49.8731 | -124.5544 | British Columbia.a | British Columbia | Powell | BC_POW_DSS | 138 | 2012 | 2042 | Biomass | biomass | 38 | 97% | 36.86 | 23.66% | 78.755 | 2
| Prince Rupert_01 | BC_RPG01_GEN | BC Hydro | Prince Rupert | 54.3143 | -130.2944 | British Columbia.a | British Columbia | Rupert Gas | BC_RPG_GSS | 69 | 1973 | 2033 | NG_CT | gasSC | 23 | 94% | 21.62 | 26.54% | 53.468 | 2
| Prince Rupert_02 | BC_RPG02_GEN | BC Hydro | Prince Rupert | 54.3143 | -130.2944 | British Columbia.a | British Columbia | Rupert Gas | BC_RPG_GSS | 69 | 1973 | 2033 | NG_CT | gasSC | 23 | 94% | 21.62 | 26.67% | 53.744 | 2
| Ptarmigan Creek | BC_PTM00_GEN | Robson Valley Power Corporation | McBride | 53.6785 | -120.911 | British Columbia.a | British Columbia | Rearguard Pumping Station | BC_REG_DSS | 69 | 1993 | 2033 | Hydro_run | hydro_run | 4.8 | 32.22% | 1.5466 | 62.79% | 26.4 | 1 |  | Also called Robson Valley
| Puntledge | BC_PUN00_GEN | BC Hydro | Vancouver Island | 49.665 | -125.0939 | British Columbia.a | British Columbia | Puntledge GS | BC_PUN_DFS | 138 | 1982 | 2052 | Hydro_daily | hydro_daily | 24 | 100% | 24 | 33.12% | 69.6228 | 1
| Quality | BC_QTY00_GEN | Capital Power L.P. | Tumbler Ridge | 55.1846 | -120.8547 | British Columbia.a | British Columbia | Quality GS | BC_QTY_GSS | 230 | 2012 | 2032 | Wind_Onshore | wind | 142.2 | 26% | 36.972 | 38.29% | 476.91 | 1
| Raging River_01 | BC_RGR01_GEN | Raging River Power & Mining Inc. | Port Alice | 50.3884 | -127.2335 | British Columbia.a | British Columbia | Jeune Landing | BC_JUL_DSS | 138 | 2012 | 2052 | Hydro_daily | hydro_daily | 4 | 100% | 4 | 56.74% | 19.88 | 2
| Raging River_02 | BC_RGR02_GEN | Raging River Power & Mining Inc. | Port Alice | 50.3884 | -127.2335 | British Columbia.a | British Columbia | Jeune Landing | BC_JUL_DSS | 138 | 2012 | 2052 | Hydro_daily | hydro_daily | 4 | 100% | 4 | 56.74% | 19.88 | 2
| Revelstoke District | BC_RVD00_GEN | City of Revelstoke | Revelstoke | 50.9866 | -118.1976 | British Columbia.a | British Columbia | Illecillewaet | BC_ILL_DSS | 69 | 2005 | 2035 | Biomass | biomass | 1.5 | 97% | 1.455 | 21.23% | 2.79 | 1 | https://revelstokecommunityenergy.ca/rcechistory.html
| Revelstoke_01 | BC_REV01_GEN | BC Hydro | Columbia | 51.0486 | -118.1939 | British Columbia.a | British Columbia | Revelstoke GS | BC_REV_GSS | 500 | 1984 | 2054 | Hydro_monthly | hydro_monthly | 500 | 100% | 500 | 40.18% | 1759.97 | 5
| Revelstoke_02 | BC_REV02_GEN | BC Hydro | Columbia | 51.0486 | -118.1939 | British Columbia.a | British Columbia | Revelstoke GS | BC_REV_GSS | 500 | 1984 | 2054 | Hydro_monthly | hydro_monthly | 500 | 100% | 500 | 40.18% | 1759.97 | 5
| Revelstoke_03 | BC_REV03_GEN | BC Hydro | Columbia | 51.0486 | -118.1939 | British Columbia.a | British Columbia | Revelstoke GS | BC_REV_GSS | 500 | 1984 | 2054 | Hydro_monthly | hydro_monthly | 500 | 100% | 500 | 40.18% | 1759.97 | 5
| Revelstoke_04 | BC_REV04_GEN | BC Hydro | Columbia | 51.0486 | -118.1939 | British Columbia.a | British Columbia | Revelstoke GS | BC_REV_GSS | 500 | 1984 | 2054 | Hydro_monthly | hydro_monthly | 500 | 100% | 500 | 40.18% | 1759.97 | 5
| Revelstoke_05 | BC_REV05_GEN | BC Hydro | Columbia | 51.0486 | -118.1939 | British Columbia.a | British Columbia | Revelstoke GS | BC_REV_GSS | 500 | 2010 | 2080 | Hydro_monthly | hydro_monthly | 500 | 100% | 500 | 40.18% | 1759.97 | 5
| Ruskin_01 | BC_RUS01_GEN | BC Hydro | Lower Mainland | 49.195 | -122.4083 | British Columbia.a | British Columbia | Ruskin GS | BC_RUS_GSS | 69 | 1930 | 2040 | Hydro_daily | hydro_daily | 38.33 | 100% | 38.33 | 33.12% | 111.193 | 3
| Ruskin_02 | BC_RUS02_GEN | BC Hydro | Lower Mainland | 49.195 | -122.4083 | British Columbia.a | British Columbia | Ruskin GS | BC_RUS_GSS | 69 | 1930 | 2040 | Hydro_daily | hydro_daily | 38.33 | 100% | 38.33 | 33.12% | 111.193 | 3
| Ruskin_03 | BC_RUS03_GEN | BC Hydro | Lower Mainland | 49.195 | -122.4083 | British Columbia.a | British Columbia | Ruskin GS | BC_RUS_GSS | 69 | 1930 | 2040 | Hydro_daily | hydro_daily | 38.33 | 100% | 38.33 | 33.12% | 111.193 | 3
| Rutherford Creek | BC_RUT00_GEN | Rutherford Creek Power Limited Partnership | Pemberton | 50.2727 | -122.867 | British Columbia.a | British Columbia | Rutherford Creek GS | BC_RUT_GSS | 230 | 2004 | 2044 | Hydro_run | hydro_run | 50 | 32.22% | 16.11 | 39.27% | 172 | 1
| Sakwi Creek | BC_SKW00_GEN | Sakwi Creek Hydro Limited Partnership | Agassiz | 49.3326 | -121.8801 | British Columbia.a | British Columbia | Rosedale | BC_ROS_DSS | 360 | 2014 | 2054 | Hydro_run | hydro_run | 6 | 32.22% | 1.9332 | 39.95% | 21 | 1
| Savona | BC_SVA00_GEN | EnPower Green Energy Generation Limited Partnership | Savona | 50.7488 | -120.8551 | British Columbia.a | British Columbia | Savona | BC_SVA_DSS | 138 | 2008 | 2038 | Biomass | biomass | 5.89 | 97% | 5.7133 | 79.46% | 41 | 1 |  | Energy recovery generator.
| Sechelt Creek | BC_SCG00_GEN | MPT Hydro LP | Sechelt | 49.6775 | -123.5481 | British Columbia.a | British Columbia | Sechelt Creek GS | BC_SCG_GSS | 138 | 2018 | 2058 | Hydro_run | hydro_run | 16.6 | 32.22% | 5.3485 | 58.18% | 84.6
| Seegen | BC_SEG00_GEN | Covanta Burnaby Renewable Energy, ULC | Burnaby | 49.1864 | -122.9777 | British Columbia.a | British Columbia | Ingledow | BC_ING_DSS | 230 | 2003 | 2033 | Biomass | biomass | 22 | 97% | 21.34 | 86.14% | 166 | 1
| Seton | BC_SON00_GEN | BC Hydro | Lillooet | 50.6727 | -121.9241 | British Columbia.a | British Columbia | Seton Lake GS | BC_SON_DFS | 69 | 1956 | 2026 | Hydro_daily | hydro_daily | 48 | 100% | 48 | 33.12% | 139.2457 | 1
| Seven Mile_01 | BC_SEV01_GEN | BC Hydro | Columbia | 49.0302 | -117.5041 | British Columbia.a | British Columbia | Seven Mile GS | BC_SEV_GSS | 230 | 1979 | 2049 | Hydro_daily | hydro_daily | 201.25 | 100% | 201.25 | 33.12% | 583.816 | 4
| Seven Mile_02 | BC_SEV02_GEN | BC Hydro | Columbia | 49.0302 | -117.5041 | British Columbia.a | British Columbia | Seven Mile GS | BC_SEV_GSS | 230 | 1979 | 2049 | Hydro_daily | hydro_daily | 201.25 | 100% | 201.25 | 33.12% | 583.816 | 4
| Seven Mile_03 | BC_SEV03_GEN | BC Hydro | Columbia | 49.0302 | -117.5041 | British Columbia.a | British Columbia | Seven Mile GS | BC_SEV_GSS | 230 | 1979 | 2049 | Hydro_daily | hydro_daily | 201.25 | 100% | 201.25 | 33.12% | 583.816 | 4
| Seven Mile_04 | BC_SEV04_GEN | BC Hydro | Columbia | 49.0302 | -117.5041 | British Columbia.a | British Columbia | Seven Mile GS | BC_SEV_GSS | 230 | 1979 | 2049 | Hydro_daily | hydro_daily | 201.25 | 100% | 201.25 | 33.12% | 583.816 | 4
| Shinish Creek | BC_SHC00_GEN | Zero Emissions Shinish Creek Limited Partnership | Summerland | 49.6602 | -120.1222 | British Columbia.a | British Columbia | RG Anderson | BC_RGA_DSS | 230 | 2010 | 2030 | Wind_Onshore | wind | 15 | 26% | 3.9 | 41.48% | 54.5 | 1
| Shuswap | BC_SHW00_GEN | BC Hydro | Shuswap | 50.296 | -118.8133 | British Columbia.a | British Columbia | Ashton Creek | BC_ACK_DSS | 230 | 1929 | 2039 | Hydro_daily | hydro_daily | 6 | 100% | 6 | 33.12% | 17.41 | 1
| Site C_01 | BC_STC01_GEN | BC Hydro | Peace River | 56.1966 | -120.914 | British Columbia.a | British Columbia | Site C GS | BC_STC_GSS | 500 | 2025 | 2095 | Hydro_monthly | hydro_monthly | 188.6667 | 100% | 188.6667 | 54.1% | 894.0704 | 6
| Site C_02 | BC_STC02_GEN | BC Hydro | Peace River | 56.1966 | -120.914 | British Columbia.a | British Columbia | Site C GS | BC_STC_GSS | 500 | 2025 | 2095 | Hydro_monthly | hydro_monthly | 188.6667 | 100% | 188.6667 | 54.1% | 894.0704 | 6
| Site C_03 | BC_STC03_GEN | BC Hydro | Peace River | 56.1966 | -120.914 | British Columbia.a | British Columbia | Site C GS | BC_STC_GSS | 500 | 2025 | 2095 | Hydro_monthly | hydro_monthly | 188.6667 | 100% | 188.6667 | 54.1% | 894.0704 | 6
| Site C_04 | BC_STC04_GEN | BC Hydro | Peace River | 56.1966 | -120.914 | British Columbia.a | British Columbia | Site C GS | BC_STC_GSS | 500 | 2025 | 2095 | Hydro_monthly | hydro_monthly | 188.6667 | 100% | 188.6667 | 54.1% | 894.0705 | 6
| Site C_05 | BC_STC05_GEN | BC Hydro | Peace River | 56.1966 | -120.914 | British Columbia.a | British Columbia | Site C GS | BC_STC_GSS | 500 | 2025 | 2095 | Hydro_monthly | hydro_monthly | 188.6667 | 100% | 188.6667 | 54.1% | 894.0705 | 6
| Site C_06 | BC_STC06_GEN | BC Hydro | Peace River | 56.1966 | -120.914 | British Columbia.a | British Columbia | Site C GS | BC_STC_GSS | 500 | 2025 | 2095 | Hydro_monthly | hydro_monthly | 188.6667 | 100% | 188.6667 | 54.1% | 894.0705 | 6
| Skookum Power | BC_SKO00_GEN | Skookum Creek Power Partnership | Squamish | 49.7205 | -122.9956 | British Columbia.a | British Columbia | Skookum Creek GS | BC_SKO_GSS | 138 | 2014 | 2054 | Hydro_run | hydro_run | 29.2 | 32.22% | 9.4082 | 39.88% | 102 | 1 |  | Also called Mamquam Skookum
| Skookumchuck | BC_CRS00_GEN | Skookumchuck Pulp Inc. | Skookumchuck | 49.5284 | -115.7578 | British Columbia.a | British Columbia | Crestbrook Skookumchuck | BC_CRS_DFS | 69 | 2009 | 2039 | Biomass | biomass | 51.3 | 97% | 49.761 | 59.35% | 266.7 | 1
| Soo River | BC_SOO00_GEN | Joint Venture | Whistler | 50.2842 | -122.9776 | British Columbia.a | British Columbia | Tisdall | BC_TIS_DSS | 230 | 1994 | 2034 | Hydro_run | hydro_run | 13.3 | 32.22% | 4.2853 | 67.03% | 78.1 | 1
| South Cranberry Creek | BC_SCB00_GEN | Advanced Energy Systems 1 Limited Partnership | Revelstoke | 50.7716 | -118.1041 | British Columbia.a | British Columbia | South Cranberry GS | BC_SCB_GSS | 69 | 2008 | 2048 | Hydro_run | hydro_run | 11.5 | 32.22% | 3.7053 | 26.17% | 26.36 | 1
| South Slocan_01 | BC_SLC01_GEN | FortisBC | Kootenay River | 49.4555 | -117.5197 | British Columbia.a | British Columbia | South Slocan GS | BC_SLC_GSS | 69 | 1928 | 2038 | Hydro_daily | hydro_daily | 19 | 100% | 19 | 33.12% | 55.118 | 3
| South Slocan_02 | BC_SLC02_GEN | FortisBC | Kootenay River | 49.4555 | -117.5197 | British Columbia.a | British Columbia | South Slocan GS | BC_SLC_GSS | 69 | 1928 | 2038 | Hydro_daily | hydro_daily | 19 | 100% | 19 | 33.12% | 55.118 | 3
| South Slocan_03 | BC_SLC03_GEN | FortisBC | Kootenay River | 49.4555 | -117.5197 | British Columbia.a | British Columbia | South Slocan GS | BC_SLC_GSS | 69 | 1928 | 2038 | Hydro_daily | hydro_daily | 19 | 100% | 19 | 33.12% | 55.118 | 3
| South Sutton Creek | BC_SSH00_GEN | South Sutton Creek Hydro Inc. | Port Alberni | 49.2876 | -125.3092 | British Columbia.a | British Columbia | South Sutton GS | BC_SSH_GSS | 69 | 2005 | 2045 | Hydro_run | hydro_run | 4.9 | 32.22% | 1.5788 | 60.57% | 26 | 1
| Spillimacheen | BC_SCN00_GEN | BC Hydro | Columbia | 50.9034 | -116.4089 | British Columbia.a | British Columbia | Spillimacheen GS | BC_SPN_DFS | 69 | 1954 | 2024 | Hydro_run | hydro_run | 4.8 | 32.22% | 1.5466 | 20.7% | 8.7029 | 1
| Squamish Power Project | BC_WFR00_GEN | Woodfibre LNG Limited | Squamish | 49.6761 | -123.2614 | British Columbia.a | British Columbia | Woodfibre | BC_WFR_DSS | 138 | 2013 | 2043 | Biomass | biomass | 1.4 | 97% | 1.358 | 91.65% | 11.24 | 1
| Stave Falls_01 | BC_SFL01_GEN | BC Hydro | Lower Mainland | 49.2288 | -122.3561 | British Columbia.a | British Columbia | Stave Falls GS | BC_SFL_GSS | 69 | 2000 | 2040 | Hydro_daily | hydro_daily | 45.5 | 100% | 45.5 | 33.12% | 131.993 | 2
| Stave Falls_02 | BC_SFL02_GEN | BC Hydro | Lower Mainland | 49.2288 | -122.3561 | British Columbia.a | British Columbia | Stave Falls GS | BC_SFL_GSS | 69 | 2000 | 2040 | Hydro_daily | hydro_daily | 45.5 | 100% | 45.5 | 33.12% | 131.993 | 2
| Stokke Kwalsa | BC_SKK00_GEN | Harrison Hydro Limited Partnership | Mission | 49.7111 | -122.0343 | British Columbia.a | British Columbia | Stokke GS | BC_SKK_GSS | 138 | 2009 | 2049 | Hydro_run | hydro_run | 22.04 | 32.22% | 7.1013 | 56.73% | 109.5367 | 1
| Strathcona_01 | BC_SCA01_GEN | BC Hydro | Vancouver Island | 49.9981 | -125.5856 | British Columbia.a | British Columbia | Strathcona GS | BC_SCA_GSS | 138 | 1958 | 2028 | Hydro_daily | hydro_daily | 32.5 | 100% | 32.5 | 33.12% | 94.281 | 2
| Strathcona_02 | BC_SCA02_GEN | BC Hydro | Vancouver Island | 49.9981 | -125.5856 | British Columbia.a | British Columbia | Strathcona GS | BC_SCA_GSS | 138 | 1958 | 2028 | Hydro_daily | hydro_daily | 32.5 | 100% | 32.5 | 33.12% | 94.281 | 2
| SunMine | BC_SNM00_GEN | City of Kimberley | Kimberley | 49.669 | -115.9476 | British Columbia.a | British Columbia | Cranbrook | BC_CBK_DSS | 69 | 2010 | 2030 | Solar_PV | solar | 1.05 | 24% | 0.252 | 22.29% | 2.05 | 1
| Tipella Kwalsa | BC_TPA00_GEN | Harrison Hydro Limited Partnership | Mission | 49.7409 | -122.1622 | British Columbia.a | British Columbia | Tipella GS | BC_TPA_GSS | 138 | 2009 | 2049 | Hydro_run | hydro_run | 19.36 | 32.22% | 6.2378 | 56.73% | 96.2174 | 1
| Tolko Armstrong | BC_TKA00_GEN | Tolko Industries Ltd. | Armstrong | 50.3922 | -119.2259 | British Columbia.a | British Columbia | Tolko Armstrong GS | BC_RVG_GSS | 138 | 2009 | 2039 | Biomass | biomass | 20.4 | 97% | 19.788 | 91.39% | 163.32 | 1
| Tolko Kelowna | BC_TKK00_GEN | Tolko Industries Ltd. | Kelowna | 49.9014 | -119.4994 | British Columbia.a | British Columbia | DG Bell | BC_DGB_DSS | 230 | 2010 | 2040 | Biomass | biomass | 14.9 | 97% | 14.453 | 8.389% | 10.95 | 1
| Tretheway Creek | BC_TWY00_GEN | Tretheway Creek Power LP | Mission | 49.7038 | -122.0796 | British Columbia.a | British Columbia | Tretheway GS | BC_TWY_GSS | 138 | 2015 | 2055 | Hydro_run | hydro_run | 21.18 | 32.22% | 6.8242 | 43.5% | 80.7 | 1
| Trio Kwalsa | BC_TRE00_GEN | Harrison Hydro Limited Partnership | Mission | 49.6284 | -122.0329 | British Columbia.a | British Columbia | Trio GS | BC_TRE_GSS | 138 | 2018 | 2058 | Hydro_run | hydro_run | 13.75 | 32.22% | 4.4303 | 67% | 80.7 | 1
| Tyson Creek | BC_TYS00_GEN | Tyson Creek Hydro Corp. | Sechelt | 49.8371 | -123.6858 | British Columbia.a | British Columbia | Malaspina | BC_MSA_DSS | 138 | 2009 | 2049 | Hydro_daily | hydro_daily | 9.3 | 100% | 9.3 | 56.73% | 46.2201 | 1
| UBC Nexterra | BC_CSN00_GEN | University of British Columbia | Vancouver | 49.2602 | -123.2545 | British Columbia.a | British Columbia | Camosun | BC_CSN_DSS | 230 | 2012 | 2042 | Biomass | biomass | 2 | 97% | 1.94 | 21.18% | 3.71 | 1 | https://infrastructuredevelopment.ubc.ca/projects/bioenergy-research-demonstration-facility/
| UNBC Bioenergy Plant | BC_PCA00_GEN | University of Northern British Columbia | Prince George | 53.8926 | -122.8149 | British Columbia.a | British Columbia | Patricia | BC_PCA_DSS | 230 | 2009 | 2039 | Biomass | biomass | 4.4 | 97% | 4.268 | 21.2% | 8.17 | 1 | https://www2.unbc.ca/about-unbc/tour/bioenergy-facility
| Upper Bear | BC_BHU00_GEN | Bear Hydro Limited Partnership | Sechelt | 49.7954 | -123.5721 | British Columbia.a | British Columbia | Upper Bear GS | BC_BHU_GSS | 138 | 2012 | 2052 | Hydro_run | hydro_run | 10 | 32.22% | 3.222 | 83.68% | 73.3 | 1
| Upper Bonnington_01 | BC_UBO01_GEN | FortisBC | Kootenay River | 49.4601 | -117.4842 | British Columbia.a | British Columbia | Upper Bonnington GS | BC_UBO_GSS | 63 | 1907 | 2057 | Hydro_daily | hydro_daily | 5.5 | 100% | 5.5 | 33.12% | 15.9552 | 6
| Upper Bonnington_02 | BC_UBO02_GEN | FortisBC | Kootenay River | 49.4601 | -117.4842 | British Columbia.a | British Columbia | Upper Bonnington GS | BC_UBO_GSS | 63 | 1907 | 2057 | Hydro_daily | hydro_daily | 5.5 | 100% | 5.5 | 33.12% | 15.9552 | 6
| Upper Bonnington_03 | BC_UBO03_GEN | FortisBC | Kootenay River | 49.4601 | -117.4842 | British Columbia.a | British Columbia | Upper Bonnington GS | BC_UBO_GSS | 63 | 1907 | 2057 | Hydro_daily | hydro_daily | 5.5 | 100% | 5.5 | 33.12% | 15.9552 | 6
| Upper Bonnington_04 | BC_UBO04_GEN | FortisBC | Kootenay River | 49.4601 | -117.4842 | British Columbia.a | British Columbia | Upper Bonnington GS | BC_UBO_GSS | 63 | 1907 | 2057 | Hydro_daily | hydro_daily | 5.5 | 100% | 5.5 | 33.12% | 15.9552 | 6
| Upper Bonnington_05 | BC_UBO05_GEN | FortisBC | Kootenay River | 49.4601 | -117.4842 | British Columbia.a | British Columbia | Upper Bonnington GS | BC_UBO_GSS | 63 | 1907 | 2057 | Hydro_daily | hydro_daily | 22 | 100% | 22 | 33.12% | 63.8209 | 6
| Upper Bonnington_06 | BC_UBO06_GEN | FortisBC | Kootenay River | 49.4601 | -117.4842 | British Columbia.a | British Columbia | Upper Bonnington GS | BC_UBO_GSS | 63 | 1907 | 2057 | Hydro_daily | hydro_daily | 19 | 100% | 19 | 33.12% | 55.1181 | 6
| Upper Clowhom | BC_UCH00_GEN | Clowhom Limited Partnership | Sechelt | 49.8543 | -123.4461 | British Columbia.a | British Columbia | Upper Clowhom GS | BC_UCH_GSS | 138 | 2010 | 2050 | Hydro_run | hydro_run | 10.99 | 32.22% | 3.541 | 49.86% | 48 | 1
| Upper Lillooet River | BC_ULR00_GEN | Upper Lillooet River Power Limited Partnership | Pemberton | 50.657 | -123.4476 | British Columbia.a | British Columbia | Upper Lillooet River GS | BC_ULR_GSS | 230 | 2016 | 2056 | Hydro_run | hydro_run | 74 | 32.22% | 23.8428 | 51.5% | 333.82 | 1
| Upper Mamquam | BC_UMH00_GEN | Canadian Hydro Developers, Inc. | Squamish | 49.7178 | -123.0546 | British Columbia.a | British Columbia | Upper Mamquam GS | BC_UMH_GSS | 69 | 2005 | 2045 | Hydro_run | hydro_run | 25 | 32.22% | 8.055 | 49.32% | 108 | 1
| Upper Stave | BC_USR00_GEN | Harrison Hydro Limited Partnership | Mission | 49.566 | -122.3503 | British Columbia.a | British Columbia | Upper Stave River GS | BC_USR_GSS | 138 | 2009 | 2049 | Hydro_run | hydro_run | 37.9 | 32.22% | 12.2114 | 56.72% | 188.3097 | 1
| Upper Stave Lamont | BC_USR02_GEN | Harrison Hydro Limited Partnership | Mission | 49.569 | -122.3446 | British Columbia.a | British Columbia | Lamont GS | BC_LMN_GSS | 138 | 2009 | 2049 | Hydro_run | hydro_run | 32.52 | 32.22% | 10.4779 | 56.73% | 161.6213 | 1
| Vancouver Landfill | BC_VCL00_GEN | VF Clean Energy, Inc. | Delta | 49.0989 | -123.0224 | British Columbia.a | British Columbia | Arnott | BC_ARN_DSS | 138 | 2003 | 2033 | Biogas | biomass | 5.85 | 95% | 5.5575 | 78.05% | 40 | 1
| Volcano Creek | BC_VCC00_GEN | Coast Mountain Hydro Limited Partnership | Stewart | 56.7289 | -130.5977 | British Columbia.a | British Columbia | Forest Kerr GS | BC_FKR_GSS | 287 | 2015 | 2055 | Hydro_run | hydro_run | 17.8 | 32.22% | 5.7352 | 32.42% | 50.55 | 1
| Wahleach | BC_WAH00_GEN | BC Hydro | Lower Mainland | 49.2366 | -121.6807 | British Columbia.a | British Columbia | Wahleach GS | BC_WAH_GSS | 360 | 1952 | 2022 | Hydro_daily | hydro_daily | 65 | 100% | 65 | 33.12% | 188.5618 | 1
| Walden North | BC_WDN00_GEN | Cayoose Creek Power Limited Partnership | Lillooet | 50.6605 | -121.9833 | British Columbia.a | British Columbia | Walden North GS | BC_WDN_GSS | 69 | 1994 | 2034 | Hydro_run | hydro_run | 18 | 32.22% | 5.7996 | 34.25% | 54 | 1
| Walter Hardman_01 | BC_WHN01_GEN | BC Hydro | Columbia | 50.8139 | -118.06 | British Columbia.a | British Columbia | Walter Hardman GS | BC_WHN_GSS | 69 | 1960 | 2030 | Hydro_daily | hydro_daily | 4 | 100% | 4 | 33.12% | 11.604 | 2
| Walter Hardman_02 | BC_WHN02_GEN | BC Hydro | Columbia | 50.8139 | -118.06 | British Columbia.a | British Columbia | Walter Hardman GS | BC_WHN_GSS | 69 | 1960 | 2030 | Hydro_daily | hydro_daily | 4 | 100% | 4 | 33.12% | 11.604 | 2
| Waneta Expansion_01 | BC_WAX01_GEN | Columbia Power / Columbia Basin Trust | Trail | 49.0047 | -117.616 | British Columbia.a | British Columbia | Waneta Expansion GS | BC_WAX_GSS | 230 | 2015 | 2055 | Hydro_daily | hydro_daily | 167.5 | 100% | 167.5 | 42.76% | 627.35 | 2
| Waneta Expansion_02 | BC_WAX02_GEN | Columbia Power / Columbia Basin Trust | Trail | 49.0047 | -117.616 | British Columbia.a | British Columbia | Waneta Expansion GS | BC_WAX_GSS | 230 | 2015 | 2055 | Hydro_daily | hydro_daily | 167.5 | 100% | 167.5 | 42.76% | 627.35 | 2
| Waneta_01 | BC_WAN01_GEN | BC Hydro | Columbia | 49.0041 | -117.6129 | British Columbia.a | British Columbia | Waneta GS | BC_WAN_GSS | 230 | 1954 | 2024 | Hydro_daily | hydro_daily | 120 | 100% | 120 | 33.12% | 348.114 | 4
| Waneta_02 | BC_WAN02_GEN | BC Hydro | Columbia | 49.0041 | -117.6129 | British Columbia.a | British Columbia | Waneta GS | BC_WAN_GSS | 230 | 1954 | 2024 | Hydro_daily | hydro_daily | 120 | 100% | 120 | 33.12% | 348.114 | 4
| Waneta_03 | BC_WAN03_GEN | BC Hydro | Columbia | 49.0041 | -117.6129 | British Columbia.a | British Columbia | Waneta GS | BC_WAN_GSS | 230 | 1954 | 2024 | Hydro_daily | hydro_daily | 120 | 100% | 120 | 33.12% | 348.114 | 4
| Waneta_04 | BC_WAN04_GEN | BC Hydro | Columbia | 49.0041 | -117.6129 | British Columbia.a | British Columbia | Waneta GS | BC_WAN_GSS | 230 | 1954 | 2024 | Hydro_daily | hydro_daily | 120 | 100% | 120 | 33.12% | 348.114 | 4
| Whatshan | BC_WGS00_GEN | BC Hydro | Columbia | 49.9106 | -118.0718 | British Columbia.a | British Columbia | Whatshan GS | BC_WGS_GSS | 138 | 1951 | 2021 | Hydro_daily | hydro_daily | 54 | 100% | 54 | 33.12% | 156.6514 | 1
| Winchie Creek | BC_WCC00_GEN | Winchie Creek Hydro Limited Partnership | Ucluelet | 49.2177 | -125.5082 | British Columbia.a | British Columbia | Great Central | BC_GCL_DSS | 138 | 2019 | 2059 | Hydro_run | hydro_run | 4 | 32.22% | 1.2888 | 31.62% | 11.08 | 1
| Zeballos Lake_01 | BC_ZBL01_GEN | Zeballos Lake Hydro Limited Partnership | Zeballos | 50.0535 | -126.7797 | British Columbia.a | British Columbia | Zeballos Lake GS | BC_ZBL_GSS | 138 | 2009 | 2049 | Hydro_daily | hydro_daily | 9.38 | 100% | 9.38 | 56.73% | 46.618 | 3
| Zeballos Lake_02 | BC_ZBL02_GEN | Zeballos Lake Hydro Limited Partnership | Zeballos | 50.0535 | -126.7797 | British Columbia.a | British Columbia | Zeballos Lake GS | BC_ZBL_GSS | 138 | 2009 | 2049 | Hydro_daily | hydro_daily | 9.38 | 100% | 9.38 | 56.73% | 46.618 | 3
| Zeballos Lake_03 | BC_ZBL03_GEN | Zeballos Lake Hydro Limited Partnership | Zeballos | 50.0535 | -126.7797 | British Columbia.a | British Columbia | Zeballos Lake GS | BC_ZBL_GSS | 138 | 2009 | 2049 | Hydro_daily | hydro_daily | 3.09 | 100% | 3.09 | 56.73% | 15.357 | 3
Specific Notes:
BC Hydro Integrated System Total Gross Requirements shown in tab FGWh and FGW includes exports to Seattle City Light and Hyder Alaska, which extend beyond 2050 and so are not included as SALES in this list of existing generation
Missing values for "outage duration", "minimum capacity", maximum capacity", "must run", "minimum up time", "minimum down time" filled in using values for similar types of projects where values are known.
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
IPP contract durations presumed to be: all fossil fuel - 30 years; hydroelectric run-of-river - 40 years; wind - 20 years; solar 20 years; storage - 20 years; biomass - 15 years; biogas - 15 years; all renewals same duration as initial contract
Non-IPP project economic lives presumed to be: all fossil fuel - 30 years; nuclear - 50 years + 40 years per renewal; storage (including pumped) hydroelectric - 70 years + 40 years per renewal; hydroelectric run-of-river - 40 years + 40 years per renewal; wind - 20 years + 20 years per renewal; solar 20 years + 20 years per renewal; storage - 20 years + 20 years per renewal; biomass - 15 years; biogas automatically renewed
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit hydro_run facilities treated as single-unit facilities

## Storage
BC | EXISTING STORAGE | [12 empty] | DESIGN
| Project Name | Storage Codes | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Technology | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Other References | Notes
[11 empty] | (kV) | [5 empty] | (MW) | (MWh) | (Hours) |  | ($M)
NONE
Specific Notes:

## Transmission
BC | EXISTING TRANSMISSION
| Circuit ID | Owner | Operating Region | Number of Circuits | Current | Line Segment Length | Line Segment Length | Line Length | Line Length | Voltage | Reactance | Smax | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes | Count
[5 empty] | (ad/dc) | (km) | (miles) | (km) | (miles) | (kV) | (ohm) |  | (A) | (A) | (MVA) | (MVA) |  | (MW) | (MW)
| 1L001 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Lamont GS | BC_LMN_GSS | Upper Stave River GS | BC_USR_GSS |  |  | 1
| 1L001 | BC Hydro | British Columbia | 1 | ac | 9 | 5.5556 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Upper Stave River GS | BC_USR_GSS | Northwest Stave GS | BC_NWS_GSS |  |  | 2
| 1L001 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Northwest Stave GS | BC_NWS_GSS | Tipella GS | BC_TPA_GSS |  |  | 3
| 1L001 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Tipella GS | BC_TPA_GSS | Kwalsa | BC_KWL_TSS |  |  | 4
| 1L001 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Kwalsa | BC_KWL_TSS | Upper Harrison | BC_UHT_DSS |  |  | 5
| 1L001 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Kwalsa | BC_KWL_TSS | Fire GS | BC_FRE_GSS |  |  | 6
| 1L001 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Fire GS | BC_FRE_GSS | Douglas GS | BC_DGL_GSS |  |  | 7
| 1L001 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Douglas GS | BC_DGL_GSS | Stokke GS | BC_SKK_GSS |  |  | 8
| 1L001 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 61 | 37.6543 | 138 | 26.4479 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Stokke GS | BC_SKK_GSS | Big Silver GS | BC_BSV_GSS |  |  | 9
| 1L002 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 20 | 12.3457 | 138 | 8.6714 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Upper Harrison | BC_UHT_DSS | Tretheway GS | BC_TWY_GSS |  | Line name assumed | 10
| 1L002 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 20 | 12.3457 | 138 | 8.6714 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Tretheway GS | BC_TWY_GSS | Bremner GS | BC_BRE_GSS |  | Line name assumed | 11
| 1L002 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 20 | 12.3457 | 138 | 8.6714 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Bremner GS | BC_BRE_GSS | Trio GS | BC_TRE_GSS |  | Line name assumed | 12
| 1L010 | BC Hydro | British Columbia | 1 | ac | 25.39 | 15.6728 | 55.39 | 34.1914 | 138 | 24.0155 |  | 648 | 780 | 154.8869 | 186.4379 | 0.9 | 139.3982 | 167.7942 | Vancouver Island TS | BC_VIT_TSS | Shawnigan JCT | BC_SHA_JCT |  |  | 13
| 1L010SHA | BC Hydro | British Columbia | 1 | ac | 0.082399 | 0.050864 | 0.082399 | 0.050864 | 138 | 0.035726 |  | 725 | 925 | 173.2917 | 221.0963 | 0.9 | 155.9625 | 198.9867 | Shawnigan JCT | BC_SHA_JCT | Shawnigan | BC_SHA_DSS |  |  | 14
| 1L010 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 55.39 | 34.1914 | 138 | 24.0155 |  | 520 | 735 | 124.292 | 175.6819 | 0.9 | 111.8628 | 158.1137 | Shawnigan JCT | BC_SHA_JCT | Goward | BC_GOW_DSS |  |  | 15
| 1L011 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 55.36 | 34.1728 | 138 | 24.0025 |  | 648 | 780 | 154.8869 | 186.4379 | 0.9 | 139.3982 | 167.7942 | Vancouver Island TS | BC_VIT_TSS | Koksilah JCT | BC_KSH_JCT |  |  | 16
| 1L011KSH | BC Hydro | British Columbia | 1 | ac | 3.1888 | 1.9684 | 3.1888 | 1.9684 | 138 | 1.3826 |  | 648 | 780 | 154.8869 | 186.4379 | 0.9 | 139.3982 | 167.7942 | Koksilah JCT | BC_KSH_JCT | Koksilah | BC_KSH_DSS |  |  | 17
| 1L011 | BC Hydro | British Columbia | 1 | ac | 40.36 | 24.9136 | 55.36 | 34.1728 | 138 | 24.0025 |  | 520 | 735 | 124.292 | 175.6819 | 0.9 | 111.8628 | 158.1137 | Koksilah JCT | BC_KSH_JCT | Goward | BC_GOW_DSS |  |  | 18
| 1L012 | BC Hydro | British Columbia | 1 | ac | 6.3182 | 3.9001 | 6.3182 | 3.9001 | 138 | 2.7394 |  | 725 | 925 | 173.2917 | 221.0963 | 0.9 | 155.9625 | 198.9867 | Goward | BC_GOW_DSS | George Tripp | BC_GTP_DSS |  |  | 19
| 1L014 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 62.92 | 38.8395 | 138 | 27.2803 |  | 725 | 925 | 173.2917 | 221.0963 | 0.9 | 155.9625 | 198.9867 | Vancouver Island TS | BC_VIT_TSS | Koksilah JCT | BC_KSH_JCT |  |  | 20
| 1L014KSH | BC Hydro | British Columbia | 1 | ac | 3.2231 | 1.9895 | 3.2231 | 1.9895 | 138 | 1.3974 |  | 725 | 925 | 173.2917 | 221.0963 | 0.9 | 155.9625 | 198.9867 | Koksilah JCT | BC_KSH_JCT | Koksilah | BC_KSH_DSS |  |  | 21
| 1L014 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 62.92 | 38.8395 | 138 | 27.2803 |  | 725 | 925 | 173.2917 | 221.0963 | 0.9 | 155.9625 | 198.9867 | Koksilah JCT | BC_KSH_JCT | Shawnigan JCT | BC_SHA_JCT |  |  | 22
| 1L014SHA | BC Hydro | British Columbia | 1 | ac | 0.087269 | 0.05387 | 0.087269 | 0.05387 | 138 | 0.037838 |  | 725 | 925 | 173.2917 | 221.0963 | 0.9 | 155.9625 | 198.9867 | Shawnigan JCT | BC_SHA_JCT | Shawnigan | BC_SHA_DSS |  |  | 23
| 1L014 | BC Hydro | British Columbia | 1 | ac | 40.92 | 25.2593 | 62.92 | 38.8395 | 138 | 27.2803 |  | 725 | 925 | 173.2917 | 221.0963 | 0.9 | 155.9625 | 198.9867 | Shawnigan JCT | BC_SHA_JCT | George Tripp | BC_GTP_DSS |  |  | 24
| 1L018 | BC Hydro | British Columbia | 1 | ac | 38.17 | 23.5617 | 68.17 | 42.0802 | 138 | 29.5566 |  | 375 | 530 | 89.6336 | 126.6822 | 0.9 | 80.6703 | 114.014 | Arnott | BC_ARN_DSS | Galiano JCT | BC_GLS_JCT |  |  | 25
| 1L018GLS | BC Hydro | British Columbia | 1 | ac | 0.11495 | 0.070957 | 0.11495 | 0.070957 | 138 | 0.049839 |  | 713 | 684 | 170.4234 | 163.4917 | 0.9 | 153.3811 | 147.1426 | Galiano JCT | BC_GLS_JCT | Galiano | BC_GLS_DSS |  |  | 26
| 1L018 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 68.17 | 42.0802 | 138 | 29.5566 |  | 375 | 530 | 89.6336 | 126.6822 | 0.9 | 80.6703 | 114.014 | Galiano JCT | BC_GLS_JCT | Saltspring JCT | BC_SAL_JCT |  |  | 27
| 1L018SAL | BC Hydro | British Columbia | 1 | ac | 0.47984 | 0.2962 | 0.47984 | 0.2962 | 138 | 0.20804 |  | 375 | 642 | 89.6336 | 153.4528 | 0.9 | 80.6703 | 138.1075 | Saltspring JCT | BC_SAL_JCT | Saltspring | BC_SAL_DSS |  |  | 28
| 1L018 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 68.17 | 42.0802 | 138 | 29.5566 |  | 375 | 530 | 89.6336 | 126.6822 | 0.9 | 80.6703 | 114.014 | Saltspring JCT | BC_SAL_JCT | Vancouver Island TS | BC_VIT_TSS |  |  | 29
| 1L031 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 63.04 | 38.9136 | 138 | 27.3323 |  | 515 | 915 | 123.0969 | 218.7061 | 0.9 | 110.7872 | 196.8354 | Cheekye | BC_CKY_DSS | Woodfibre JCT | BC_WFR_JCT |  |  | 30
| 1L031WFR | BC Hydro | British Columbia | 1 | ac | 0.65533 | 0.40453 | 0.65533 | 0.40453 | 138 | 0.28413 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Woodfibre JCT | BC_WFR_JCT | Woodfibre | BC_WFR_DSS |  |  | 31
| 1L031 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 63.04 | 38.9136 | 138 | 27.3323 |  | 260 | 440 | 62.146 | 105.1701 | 0.9 | 55.9314 | 94.6531 | Woodfibre JCT | BC_WFR_JCT | Box Canyon JCT | BC_BOX_JCT |  |  | 32
| 1L031BOX | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 138 | 0.43357 |  | 572 | 689 | 136.7212 | 164.6869 | 0.9 | 123.049 | 148.2182 | Box Canyon JCT | BC_BOX_JCT | Box Canyon GS | BC_BOX_GSS |  |  | 33
| 1L031 | BC Hydro | British Columbia | 1 | ac | 28.04 | 17.3086 | 63.04 | 38.9136 | 138 | 27.3323 |  | 260 | 440 | 62.146 | 105.1701 | 0.9 | 55.9314 | 94.6531 | Box Canyon JCT | BC_BOX_JCT | Gibsons | BC_GIB_DSS |  |  | 34
| 1L032 | BC Hydro | British Columbia | 1 | ac | 20.6792 | 12.7649 | 20.6792 | 12.7649 | 138 | 8.9659 |  | 504 | 601 | 120.4676 | 143.6528 | 0.9 | 108.4208 | 129.2875 | Sechelt | BC_SEC_DSS | Gibsons | BC_GIB_DSS |  |  | 35
| 1L033 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 32.59 | 20.1173 | 138 | 14.1301 |  | 504 | 601 | 120.4676 | 143.6528 | 0.9 | 108.4208 | 129.2875 | Saltery Bay | BC_SAY_DSS | Grief Point JCT | BC_GPT_JCT |  |  | 36
| 1L033GPT | BC Hydro | British Columbia | 1 | ac | 3.9686 | 2.4498 | 3.9686 | 2.4498 | 138 | 1.7207 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Grief Point JCT | BC_GPT_JCT | Grief Point | BC_GPT_DSS |  |  | 37
| 1L033 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 32.59 | 20.1173 | 138 | 14.1301 |  | 504 | 601 | 120.4676 | 143.6528 | 0.9 | 108.4208 | 129.2875 | Grief Point JCT | BC_GPT_JCT | Forest View JCT | BC_FVW_JCT |  |  | 38
| 1L033FVW | BC Hydro | British Columbia | 1 | ac | 0.032467 | 0.020041 | 0.032467 | 0.020041 | 138 | 0.014077 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Forest View JCT | BC_FVW_JCT | Forest View | BC_FVW_DSS |  |  | 39
| 1L033 | BC Hydro | British Columbia | 1 | ac | 3.59 | 2.216 | 32.59 | 20.1173 | 138 | 14.1301 |  | 504 | 601 | 120.4676 | 143.6528 | 0.9 | 108.4208 | 129.2875 | Forest View JCT | BC_FVW_JCT | Powell | BC_POW_DSS |  |  | 40
| 1L035 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 30.6 | 18.8889 | 138 | 13.2673 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Sechelt | BC_SEC_DSS | Pender Harbour | BC_PHR_DSS |  |  | 41
| 1L035 | BC Hydro | British Columbia | 1 | ac | 5.6 | 3.4568 | 30.6 | 18.8889 | 138 | 13.2673 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Pender Harbour | BC_PHR_DSS | Malaspina | BC_MSA_DSS |  |  | 42
| 1L037 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 27.6 | 17.037 | 138 | 11.9666 |  | 504 | 601 | 120.4676 | 143.6528 | 0.9 | 108.4208 | 129.2875 | Malaspina | BC_MSA_DSS | Narrows Inlet JCT | BC_NIT_JCT |  |  | 43
| 1L037NIT | BC Hydro | British Columbia | 1 | ac | 11.9368 | 7.3684 | 11.9368 | 7.3684 | 138 | 5.1755 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Narrows Inlet JCT | BC_NIT_JCT | Narrows Inlet GS | BC_NIT_GSS |  |  | 44
| 1L037 | BC Hydro | British Columbia | 1 | ac | 24.6 | 15.1852 | 27.6 | 17.037 | 138 | 11.9666 |  | 504 | 601 | 120.4676 | 143.6528 | 0.9 | 108.4208 | 129.2875 | Narrows Inlet JCT | BC_NIT_JCT | Saltery Bay | BC_SAY_DSS |  |  | 45
| 1L038 | BC Hydro | British Columbia | 1 | ac | 1.4258 | 0.88012 | 1.4258 | 0.88012 | 138 | 0.61818 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Cheekye | BC_CKY_DSS | Skookum Creek GS | BC_SKO_GSS |  |  | 46
| 1L044 | BC Hydro | British Columbia | 1 | ac | 2.81 | 1.7346 | 50.31 | 31.0556 | 138 | 21.813 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Clowhom GS | BC_COM_GSS | Sechelt Creek GS JCT | BC_SCG_JCT |  |  | 47
| 1L044 | BC Hydro | British Columbia | 1 | ac | 35 | 21.6049 | 50.31 | 31.0556 | 138 | 21.813 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Sechelt Creek GS JCT | BC_SCG_JCT | Sechelt | BC_SEC_DSS |  |  | 48
| 1L044SCG | BC Hydro | British Columbia | 1 | ac | 0.26045 | 0.16077 | 0.26045 | 0.16077 | 138 | 0.11293 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Sechelt Creek GS JCT | BC_SCG_JCT | Sechelt Creek GS | BC_SCG_GSS |  |  | 49
| 1L044 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 50.31 | 31.0556 | 138 | 21.813 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Clowhom GS | BC_COM_GSS | Lower Bear GS | BC_BHL_GSS |  | Line name assumed | 50
| 1L044 | BC Hydro | British Columbia | 1 | ac | 0.5 | 0.30864 | 50.31 | 31.0556 | 138 | 21.813 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Lower Bear GS | BC_BHL_GSS | Bear Creek | BC_BRK_DSS |  | Line name assumed | 51
| 1L044BHU | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 5 | 3.0864 | 138 | 2.1679 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Lower Bear GS | BC_BHL_GSS | Upper Bear GS | BC_BHU_GSS |  | Line name assumed | 52
| 1L044 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 50.31 | 31.0556 | 138 | 21.813 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Bear Creek | BC_BRK_DSS | Lower Clowhom GS | BC_LCH_GSS |  | Line name assumed | 53
| 1L044 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 50.31 | 31.0556 | 138 | 21.813 |  | 490 | 590 | 117.1213 | 141.0236 | 0.9 | 105.4091 | 126.9212 | Lower Clowhom GS | BC_LCH_GSS | Upper Clowhom GS | BC_UCH_GSS |  | Line name assumed | 54
| 1L048 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 31.54 | 19.4691 | 138 | 13.6748 |  | 848 | 1275 | 202.6915 | 304.7543 | 0.9 | 182.4224 | 274.2789 | Saltery Bay | BC_SAY_DSS | Grief Point JCT | BC_GPT_JCT |  |  | 55
| 1L048GPT | BC Hydro | British Columbia | 1 | ac | 4.1854 | 2.5836 | 4.1854 | 2.5836 | 138 | 1.8147 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Grief Point JCT | BC_GPT_JCT | Grief Point | BC_GPT_DSS |  |  | 56
| 1L048 | BC Hydro | British Columbia | 1 | ac | 6.54 | 4.037 | 31.54 | 19.4691 | 138 | 13.6748 |  | 848 | 1275 | 202.6915 | 304.7543 | 0.9 | 182.4224 | 274.2789 | Grief Point JCT | BC_GPT_JCT | Powell | BC_POW_DSS |  |  | 57
| 1L055 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 47.85 | 29.537 | 138 | 20.7464 |  | 851 | 1091 | 203.4086 | 260.7741 | 0.9 | 183.0677 | 234.6967 | Highland | BC_HLD_DSS | Highland Valley Copper JCT | BC_HVC_JCT |  |  | 58
| 1L055HVC | BC Hydro | British Columbia | 1 | ac | 0.58152 | 0.35896 | 0.58152 | 0.35896 | 138 | 0.25213 |  | 851 | 1091 | 203.4086 | 260.7741 | 0.9 | 183.0677 | 234.6967 | Highland Valley Copper JCT | BC_HVC_JCT | Highland Valley Copper | BC_HVC_DSS |  |  | 59
| 1L055 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 47.85 | 29.537 | 138 | 20.7464 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | Highland Valley Copper JCT | BC_HVC_JCT | Lornex Low Level Dam | BC_LLD_ISS |  |  | 60
| 1L055 | BC Hydro | British Columbia | 1 | ac | 12.85 | 7.9321 | 47.85 | 29.537 | 138 | 20.7464 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | Lornex Low Level Dam | BC_LLD_ISS | Spatsum | BC_STL_DSS |  |  | 61
| 1L057 | BC Hydro | British Columbia | 1 | ac | 72.2409 | 44.5931 | 72.2409 | 44.5931 | 138 | 31.3216 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Highland | BC_HLD_DSS | Kwoiek Creek GS | BC_KCH_GSS |  | Line may not be currently energized | 62
| 1L101 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 88.74 | 54.7778 | 138 | 38.4751 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Dunsmuir | BC_DMR_DSS | Buckley Bay JCT | BC_BKB_JCT |  |  | 63
| 1L101BKB | BC Hydro | British Columbia | 1 | ac | 0.089427 | 0.055202 | 0.089427 | 0.055202 | 138 | 0.038773 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Buckley Bay JCT | BC_BKB_JCT | Buckley Bay | BC_BKB_DSS |  |  | 64
| 1L101 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 88.74 | 54.7778 | 138 | 38.4751 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Buckley Bay JCT | BC_BKB_JCT | Comox JCT | BC_CMX_JCT |  |  | 65
| 1L101CMX | BC Hydro | British Columbia | 1 | ac | 7.7474 | 4.7823 | 7.7474 | 4.7823 | 138 | 3.359 |  | 1065 | 1375 | 254.5595 | 328.6566 | 0.9 | 229.1036 | 295.791 | Comox JCT | BC_CMX_JCT | Comox | BC_CMX_DSS |  |  | 66
| 1L101 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 88.74 | 54.7778 | 138 | 38.4751 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Comox JCT | BC_CMX_JCT | Oyster River JCT | BC_OYR_JCT |  |  | 67
| 1L101OYR | BC Hydro | British Columbia | 1 | ac | 0.4782 | 0.29519 | 0.4782 | 0.29519 | 138 | 0.20734 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Oyster River JCT | BC_OYR_JCT | Oyster River | BC_OYR_DSS |  |  | 68
| 1L101 | BC Hydro | British Columbia | 1 | ac | 18.74 | 11.5679 | 88.74 | 54.7778 | 138 | 38.4751 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Oyster River JCT | BC_OYR_JCT | John Hart GS | BC_JHT_GSS |  |  | 69
| 1L102 | BC Hydro | British Columbia | 1 | ac | 2.56 | 1.5802 | 45.56 | 28.1235 | 138 | 19.7535 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Puntledge GS | BC_PUN_DFS | Comox JCT | BC_CMX_JCT |  |  | 70
| 1L102CMX | BC Hydro | British Columbia | 1 | ac | 7.7667 | 4.7943 | 7.7667 | 4.7943 | 138 | 3.3674 |  | 1065 | 1375 | 254.5595 | 328.6566 | 0.9 | 229.1036 | 295.791 | Comox JCT | BC_CMX_JCT | Comox | BC_CMX_DSS |  |  | 71
| 1L102 | BC Hydro | British Columbia | 1 | ac | 40 | 24.6914 | 45.56 | 28.1235 | 138 | 19.7535 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Comox JCT | BC_CMX_JCT | Campbell River JCT | BC_CBL_JCT |  |  | 72
| 1L102 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 45.56 | 28.1235 | 138 | 19.7535 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Campbell River JCT | BC_CBL_JCT | John Hart GS | BC_JHT_GSS |  |  | 73
| 1L102CBL | BC Hydro | British Columbia | 1 | ac | 5.1871 | 3.2019 | 5.1871 | 3.2019 | 138 | 2.249 |  | 320 | 645 | 76.4874 | 154.1698 | 0.9 | 68.8386 | 138.7529 | Campbell River JCT | BC_CBL_JCT | Campbell River | BC_CBL_DSS |  |  | 74
| 1L103 | BC Hydro | British Columbia | 1 | ac | 1.81 | 1.1173 | 3.81 | 2.3519 | 138 | 1.6519 |  | 635 | 805 | 151.7796 | 192.4135 | 0.9 | 136.6017 | 173.1722 | John Hart GS | BC_JHT_GSS | Island GS JCT | BC_ICG_JCT |  |  | 75
| 1L103ICG | BC Hydro | British Columbia | 1 | ac | 0.079499 | 0.049074 | 0.079499 | 0.049074 | 138 | 0.034469 |  | 1308 | 1667 | 312.6421 | 398.4514 | 0.9 | 281.3779 | 358.6062 | Island GS JCT | BC_ICG_JCT | Island GS | BC_ICG_GSS |  |  | 76
| 1L103 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 3.81 | 2.3519 | 138 | 1.6519 |  | 635 | 805 | 151.7796 | 192.4135 | 0.9 | 136.6017 | 173.1722 | Island GS JCT | BC_ICG_JCT | Elk Falls Mill | BC_EFM_ISS |  |  | 77
| 1L104 | BC Hydro | British Columbia | 1 | ac | 1.82 | 1.1235 | 3.82 | 2.358 | 138 | 1.6562 |  | 635 | 805 | 151.7796 | 192.4135 | 0.9 | 136.6017 | 173.1722 | John Hart GS | BC_JHT_GSS | Island GS JCT | BC_ICG_JCT |  |  | 78
| 1L104ICG | BC Hydro | British Columbia | 1 | ac | 0.075074 | 0.046342 | 0.075074 | 0.046342 | 138 | 0.03255 |  | 1308 | 1667 | 312.6421 | 398.4514 | 0.9 | 281.3779 | 358.6062 | Island GS JCT | BC_ICG_JCT | Island GS | BC_ICG_GSS |  |  | 79
| 1L104 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 3.82 | 2.358 | 138 | 1.6562 |  | 635 | 805 | 151.7796 | 192.4135 | 0.9 | 136.6017 | 173.1722 | Island GS JCT | BC_ICG_JCT | Elk Falls Mill | BC_EFM_ISS |  |  | 80
| 1L105 | BC Hydro | British Columbia | 1 | ac | 20.8448 | 12.8672 | 20.8448 | 12.8672 | 138 | 9.0377 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Dunsmuir | BC_DMR_DSS | Port Alberni | BC_PAL_DSS |  |  | 81
| 1L106 | BC Hydro | British Columbia | 1 | ac | 42.8906 | 26.4757 | 42.8906 | 26.4757 | 138 | 18.5961 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Dunsmuir | BC_DMR_DSS | Puntledge GS | BC_PUN_DFS |  |  | 82
| 1L109 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 41.57 | 25.6605 | 138 | 18.0236 |  | 520 | 735 | 124.292 | 175.6819 | 0.9 | 111.8628 | 158.1137 | Harewood West | BC_HWW_DSS | South Wellington JCT | BC_SWN_JCT |  |  | 83
| 1L109SWN | BC Hydro | British Columbia | 1 | ac | 0.9 | 0.55556 | 0.9 | 0.55556 | 138 | 0.39021 |  | 650 | 780 | 155.365 | 186.4379 | 0.9 | 139.8285 | 167.7942 | South Wellington JCT | BC_SWN_JCT | South Wellington | BC_SWN_DSS |  |  | 84
| 1L109 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 41.57 | 25.6605 | 138 | 18.0236 |  | 520 | 735 | 124.292 | 175.6819 | 0.9 | 111.8628 | 158.1137 | South Wellington JCT | BC_SWN_JCT | Prevost | BC_PVO_DSS |  |  | 85
| 1L109 | BC Hydro | British Columbia | 1 | ac | 4.57 | 2.821 | 41.57 | 25.6605 | 138 | 18.0236 |  | 1060 | 1355 | 253.3644 | 323.8762 | 0.9 | 228.028 | 291.4886 | Prevost | BC_PVO_DSS | Vancouver Island TS | BC_VIT_TSS |  |  | 86
| 1L110 | BC Hydro | British Columbia | 1 | ac | 3.0463 | 1.8804 | 3.0463 | 1.8804 | 138 | 1.3208 |  | 1069 | 1529 | 255.5156 | 365.4662 | 0.9 | 229.964 | 328.9196 | Jinglepot | BC_JPT_DSS | Northfield | BC_NFD_DSS |  |  | 87
| 1L112 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 15 | 9.2593 | 138 | 6.5036 |  | 570 | 730 | 136.2431 | 174.4868 | 0.9 | 122.6188 | 157.0381 | Jinglepot | BC_JPT_DSS | Harewood JCT | BC_HWD_JCT |  |  | 88
| 1L112 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 15 | 9.2593 | 138 | 6.5036 |  | 570 | 730 | 136.2431 | 174.4868 | 0.9 | 122.6188 | 157.0381 | Harewood JCT | BC_HWD_JCT | Nexen JCT | BC_NEX_JCT |  |  | 89
| 1L112NEX | BC Hydro | British Columbia | 1 | ac | 0.7068 | 0.43629 | 0.7068 | 0.43629 | 138 | 0.30645 |  | 304 | 571 | 72.663 | 136.4821 | 0.9 | 65.3967 | 122.8339 | Nexen JCT | BC_NEX_JCT | Nexen JCT | BC_NEX_ISS |  |  | 90
| 1L112 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 15 | 9.2593 | 138 | 6.5036 |  | 570 | 730 | 136.2431 | 174.4868 | 0.9 | 122.6188 | 157.0381 | Nexen JCT | BC_NEX_JCT | Harmac Pacific | BC_HMC_ISS |  |  | 91
| 1L114 | BC Hydro | British Columbia | 1 | ac | 20.8064 | 12.8435 | 20.8064 | 12.8435 | 138 | 9.0211 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Dunsmuir | BC_DMR_DSS | Port Alberni | BC_PAL_DSS |  |  | 92
| 1L115 | BC Hydro | British Columbia | 1 | ac | 13 | 8.0247 | 55.19 | 34.0679 | 138 | 23.9288 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Dunsmuir | BC_DMR_DSS | Qualicum JCT | BC_QLC_JCT |  |  | 93
| 1L115QLC | BC Hydro | British Columbia | 1 | ac | 0.056718 | 0.035011 | 0.056718 | 0.035011 | 138 | 0.024591 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Qualicum JCT | BC_QLC_JCT | Qualicum | BC_QLC_DSS |  |  | 94
| 1L115 | BC Hydro | British Columbia | 1 | ac | 13 | 8.0247 | 55.19 | 34.0679 | 138 | 23.9288 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Qualicum JCT | BC_QLC_JCT | Parksville JCT | BC_PVL_JCT |  |  | 95
| 1L115PVL | BC Hydro | British Columbia | 1 | ac | 0.13278 | 0.081965 | 0.13278 | 0.081965 | 138 | 0.057571 |  | 337 | 635 | 80.5508 | 151.7796 | 0.9 | 72.4957 | 136.6017 | Parksville JCT | BC_PVL_JCT | Parksville | BC_PVL_DSS |  |  | 96
| 1L115 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 55.19 | 34.0679 | 138 | 23.9288 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Parksville JCT | BC_PVL_JCT | Lantzville JCT | BC_LTZ_JCT |  |  | 97
| 1L115LTZ | BC Hydro | British Columbia | 1 | ac | 0.056718 | 0.035011 | 0.056718 | 0.035011 | 138 | 0.024591 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Lantzville JCT | BC_LTZ_JCT | Lantzville | BC_LTZ_DSS |  |  | 98
| 1L115 | BC Hydro | British Columbia | 1 | ac | 9.19 | 5.6728 | 55.19 | 34.0679 | 138 | 23.9288 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Lantzville JCT | BC_LTZ_JCT | Jinglepot | BC_JPT_DSS |  |  | 99
| 1L116 | BC Hydro | British Columbia | 1 | ac | 13 | 8.0247 | 55.16 | 34.0494 | 138 | 23.9158 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Dunsmuir | BC_DMR_DSS | Qualicum JCT | BC_QLC_JCT |  |  | 100
| 1L116QLC | BC Hydro | British Columbia | 1 | ac | 0.04891 | 0.030191 | 0.04891 | 0.030191 | 138 | 0.021206 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Qualicum JCT | BC_QLC_JCT | Qualicum | BC_QLC_DSS |  |  | 101
| 1L116 | BC Hydro | British Columbia | 1 | ac | 13 | 8.0247 | 55.16 | 34.0494 | 138 | 23.9158 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Qualicum JCT | BC_QLC_JCT | Parksville JCT | BC_PVL_JCT |  |  | 102
| 1L116PVL | BC Hydro | British Columbia | 1 | ac | 0.13698 | 0.084554 | 0.13698 | 0.084554 | 138 | 0.05939 |  | 337 | 635 | 80.5508 | 151.7796 | 0.9 | 72.4957 | 136.6017 | Parksville JCT | BC_PVL_JCT | Parksville | BC_PVL_DSS |  |  | 103
| 1L116 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 55.16 | 34.0494 | 138 | 23.9158 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Parksville JCT | BC_PVL_JCT | Lantzville JCT | BC_LTZ_JCT |  |  | 104
| 1L116LTZ | BC Hydro | British Columbia | 1 | ac | 0.056718 | 0.035011 | 0.056718 | 0.035011 | 138 | 0.024591 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Lantzville JCT | BC_LTZ_JCT | Lantzville | BC_LTZ_DSS |  |  | 105
| 1L116 | BC Hydro | British Columbia | 1 | ac | 9.16 | 5.6543 | 55.16 | 34.0494 | 138 | 23.9158 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Lantzville JCT | BC_LTZ_JCT | Jinglepot | BC_JPT_DSS |  |  | 106
| 1L117 | BC Hydro | British Columbia | 1 | ac | 6.4938 | 4.0085 | 6.4938 | 4.0085 | 138 | 2.8155 |  | 925 | 1185 | 221.0963 | 283.2423 | 0.9 | 198.9867 | 254.918 | John Hart GS | BC_JHT_GSS | Ladore Falls GS | BC_LDR_GSS |  |  | 107
| 1L118 | BC Hydro | British Columbia | 1 | ac | 6.5069 | 4.0166 | 6.5069 | 4.0166 | 138 | 2.8212 |  | 925 | 1185 | 221.0963 | 283.2423 | 0.9 | 198.9867 | 254.918 | John Hart GS | BC_JHT_GSS | Ladore Falls GS | BC_LDR_GSS |  |  | 108
| 1L119 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 88.47 | 54.6111 | 138 | 38.3581 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Dunsmuir | BC_DMR_DSS | Buckley Bay JCT | BC_BKB_JCT |  |  | 109
| 1L119BKB | BC Hydro | British Columbia | 1 | ac | 0.17719 | 0.10938 | 0.17719 | 0.10938 | 138 | 0.076826 |  | 650 | 830 | 155.365 | 198.3891 | 0.9 | 139.8285 | 178.5502 | Buckley Bay JCT | BC_BKB_JCT | Buckley Bay | BC_BKB_DSS |  |  | 110
| 1L119 | BC Hydro | British Columbia | 1 | ac | 50 | 30.8642 | 88.47 | 54.6111 | 138 | 38.3581 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Buckley Bay JCT | BC_BKB_JCT | Oyster River JCT | BC_OYR_JCT |  |  | 111
| 1L119OYR | BC Hydro | British Columbia | 1 | ac | 0.47644 | 0.2941 | 0.47644 | 0.2941 | 138 | 0.20657 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Oyster River JCT | BC_OYR_JCT | Oyster River | BC_OYR_DSS |  |  | 112
| 1L119 | BC Hydro | British Columbia | 1 | ac | 15.47 | 9.5494 | 88.47 | 54.6111 | 138 | 38.3581 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Oyster River JCT | BC_OYR_JCT | Campbell River JCT | BC_CBL_JCT |  |  | 113
| 1L119CBL | BC Hydro | British Columbia | 1 | ac | 5.2036 | 3.2121 | 5.2036 | 3.2121 | 138 | 2.2561 |  | 320 | 645 | 76.4874 | 154.1698 | 0.9 | 68.8386 | 138.7529 | Campbell River JCT | BC_CBL_JCT | Campbell River | BC_CBL_DSS |  |  | 114
| 1L119 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 88.47 | 54.6111 | 138 | 38.3581 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Campbell River JCT | BC_CBL_JCT | John Hart GS | BC_JHT_GSS |  |  | 115
| 1L120 | BC Hydro | British Columbia | 1 | ac | 47.5883 | 29.3755 | 47.5883 | 29.3755 | 138 | 20.6329 |  | 640 | 815 | 152.9747 | 194.8038 | 0.9 | 137.6773 | 175.3234 | Strathcona GS | BC_SCA_GSS | Gold River | BC_GLD_DSS |  |  | 116
| 1L121 | BC Hydro | British Columbia | 1 | ac | 15.7217 | 9.7048 | 15.7217 | 9.7048 | 138 | 6.8165 |  | 660 | 830 | 157.7552 | 198.3891 | 0.9 | 141.9797 | 178.5502 | Ladore Falls GS | BC_LDR_GSS | Strathcona GS | BC_SCA_GSS |  |  | 117
| 1L122 | BC Hydro | British Columbia | 1 | ac | 19 | 11.7284 | 41.56 | 25.6543 | 138 | 18.0192 |  | 520 | 735 | 124.292 | 175.6819 | 0.9 | 111.8628 | 158.1137 | Harewood West | BC_HWW_DSS | Ladysmith JCT | BC_LDY_JCT |  |  | 118
| 1L122LDY | BC Hydro | British Columbia | 1 | ac | 0.92667 | 0.57202 | 0.92667 | 0.57202 | 138 | 0.40178 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Ladysmith JCT | BC_LDY_JCT | Ladysmith | BC_LDY_DSS |  |  | 119
| 1L122 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 41.56 | 25.6543 | 138 | 18.0192 |  | 520 | 735 | 124.292 | 175.6819 | 0.9 | 111.8628 | 158.1137 | Ladysmith JCT | BC_LDY_JCT | Prevost | BC_PVO_DSS |  |  | 120
| 1L122 | BC Hydro | British Columbia | 1 | ac | 4.56 | 2.8148 | 41.56 | 25.6543 | 138 | 18.0192 |  | 1060 | 1355 | 253.3644 | 323.8762 | 0.9 | 228.028 | 291.4886 | Prevost | BC_PVO_DSS | Vancouver Island TS | BC_VIT_TSS |  |  | 121
| 1L123 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 7.91 | 4.8827 | 138 | 3.4296 |  | 591 | 781 | 141.2626 | 186.677 | 0.9 | 127.1363 | 168.0093 | Harewood West | BC_HWW_DSS | Harewood JCT | BC_HWD_JCT |  |  | 122
| 1L123HWD | BC Hydro | British Columbia | 1 | ac | 2.976 | 1.8371 | 2.976 | 1.8371 | 138 | 1.2903 |  | 1050 | 1350 | 250.9742 | 322.6811 | 0.9 | 225.8767 | 290.413 | Harewood JCT | BC_HWD_JCT | Harewood | BC_HWD_DSS |  |  | 123
| 1L123 | BC Hydro | British Columbia | 1 | ac | 4.91 | 3.0309 | 7.91 | 4.8827 | 138 | 3.4296 |  | 591 | 781 | 141.2626 | 186.677 | 0.9 | 127.1363 | 168.0093 | Harewood JCT | BC_HWD_JCT | Jinglepot | BC_JPT_DSS |  |  | 124
| 1L124 | BC Hydro | British Columbia | 1 | ac | 7.9148 | 4.8857 | 7.9148 | 4.8857 | 138 | 3.4316 |  | 520 | 735 | 124.292 | 175.6819 | 0.9 | 111.8628 | 158.1137 | Harewood West | BC_HWW_DSS | Jinglepot | BC_JPT_DSS |  |  | 125
| 1L125 | BC Hydro | British Columbia | 1 | ac | 18.27 | 11.2778 | 33.27 | 20.537 | 138 | 14.4249 |  | 540 | 1050 | 129.0724 | 250.9742 | 0.9 | 116.1652 | 225.8767 | Kokish GS | BC_KKS_GSS | Port McNeil JCT | BC_PML_JCT |  |  | 126
| 1L125PML | BC Hydro | British Columbia | 1 | ac | 0.15724 | 0.097059 | 0.15724 | 0.097059 | 138 | 0.068173 |  | 1050 | 1350 | 250.9742 | 322.6811 | 0.9 | 225.8767 | 290.413 | Port McNeil JCT | BC_PML_JCT | Port McNeil | BC_PML_DSS |  |  | 127
| 1L125 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 33.27 | 20.537 | 138 | 14.4249 |  | 540 | 1050 | 129.0724 | 250.9742 | 0.9 | 116.1652 | 225.8767 | Port McNeil JCT | BC_PML_JCT | Keogh | BC_KGH_DSS |  |  | 128
| 1L127 | BC Hydro | British Columbia | 1 | ac | 14.675 | 9.0587 | 14.675 | 9.0587 | 138 | 6.3627 |  | 395 | 565 | 94.4141 | 135.048 | 0.9 | 84.9727 | 121.5432 | Port Alberni | BC_PAL_DSS | Great Central | BC_GCL_DSS |  |  | 129
| 1L128 | BC Hydro | British Columbia | 1 | ac | 7.892 | 4.8716 | 7.892 | 4.8716 | 138 | 3.4217 |  | 520 | 735 | 124.292 | 175.6819 | 0.9 | 111.8628 | 158.1137 | Harewood West | BC_HWW_DSS | Jinglepot | BC_JPT_DSS |  |  | 130
| 1L130 | BC Hydro | British Columbia | 1 | ac | 14 | 8.642 | 28.06 | 17.321 | 138 | 12.166 |  | 349 | 580 | 83.419 | 138.6333 | 0.9 | 75.0771 | 124.77 | Keogh | BC_KGH_DSS | Marble River Hatchery JCT | BC_MRH_JCT |  |  | 131
| 1L130MRH | BC Hydro | British Columbia | 1 | ac | 0.012425 | 0.0076698 | 0.012425 | 0.0076698 | 138 | 0.0053871 |  | 150 | 272 | 35.8535 | 65.0143 | 0.9 | 32.2681 | 58.5128 | Marble River Hatchery JCT | BC_MRH_JCT | Marble River Hatchery | BC_MRH_ISS |  |  | 132
| 1L130 | BC Hydro | British Columbia | 1 | ac | 14.06 | 8.679 | 28.06 | 17.321 | 138 | 12.166 |  | 349 | 580 | 83.419 | 138.6333 | 0.9 | 75.0771 | 124.77 | Marble River Hatchery JCT | BC_MRH_JCT | Jeune Landing | BC_JUL_DSS |  |  | 133
| 1L131 | BC Hydro | British Columbia | 1 | ac | 28 | 17.284 | 73.43 | 45.3272 | 138 | 31.8372 |  | 585 | 780 | 139.8285 | 186.4379 | 0.9 | 125.8456 | 167.7942 | Gold River | BC_GLD_DSS | Conuma Hatchery JCT | BC_CMH_JCT |  |  | 134
| 1L131CMH | BC Hydro | British Columbia | 1 | ac | 0.058383 | 0.036039 | 0.058383 | 0.036039 | 138 | 0.025313 |  | 495 | 630 | 118.3164 | 150.5845 | 0.9 | 106.4848 | 135.526 | Conuma Hatchery JCT | BC_CMH_JCT | Conuma Hatchery | BC_CMH_ISS |  |  | 135
| 1L131 | BC Hydro | British Columbia | 1 | ac | 29.43 | 18.1667 | 73.43 | 45.3272 | 138 | 31.8372 |  | 585 | 780 | 139.8285 | 186.4379 | 0.9 | 125.8456 | 167.7942 | Conuma Hatchery JCT | BC_CMH_JCT | Tahsis Village | BC_TSV_DSS |  |  | 136
| 1L131 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 73.43 | 45.3272 | 138 | 31.8372 |  | 585 | 780 | 139.8285 | 186.4379 | 0.9 | 125.8456 | 167.7942 | Tahsis Village | BC_TSV_DSS | Zeballos Lake TS | BC_ZBT_TSS |  |  | 137
| 1L131 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 73.43 | 45.3272 | 138 | 31.8372 |  | 585 | 780 | 139.8285 | 186.4379 | 0.9 | 125.8456 | 167.7942 | Zeballos Lake TS | BC_ZBT_TSS | Zeballos Lake GS | BC_ZBL_GSS |  |  | 138
| 1L134 | BC Hydro | British Columbia | 1 | ac | 13.8359 | 8.5407 | 13.8359 | 8.5407 | 138 | 5.9989 |  | 337 | 635 | 80.5508 | 151.7796 | 0.9 | 72.4957 | 136.6017 | Gold River | BC_GLD_DSS | Gold River Pulp | BC_GRP_ISS |  |  | 139
| 1L137 | BC Hydro | British Columbia | 1 | ac | 22.6347 | 13.972 | 22.6347 | 13.972 | 138 | 9.8138 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Keogh | BC_KGH_DSS | Port Hardy | BC_PHY_DSS |  |  | 140
| 1L138 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 40.67 | 25.1049 | 138 | 17.6334 |  | 591 | 781 | 141.2626 | 186.677 | 0.9 | 127.1363 | 168.0093 | Harewood West | BC_HWW_DSS | South Wellington JCT | BC_SWN_JCT |  |  | 141
| 1L138SWN | BC Hydro | British Columbia | 1 | ac | 0.93 | 0.57407 | 0.93 | 0.57407 | 138 | 0.40322 |  | 650 | 780 | 155.365 | 186.4379 | 0.9 | 139.8285 | 167.7942 | South Wellington JCT | BC_SWN_JCT | South Wellington | BC_SWN_DSS |  |  | 142
| 1L138 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 40.67 | 25.1049 | 138 | 17.6334 |  | 591 | 781 | 141.2626 | 186.677 | 0.9 | 127.1363 | 168.0093 | South Wellington JCT | BC_SWN_JCT | Mount Hayes JCT | BC_MHY_JCT |  |  | 143
| 1L138MHY | BC Hydro | British Columbia | 1 | ac | 0.2 | 0.12346 | 0.2 | 0.12346 | 138 | 0.086714 |  | 880 | 1090 | 210.3403 | 260.5351 | 0.9 | 189.3062 | 234.4816 | Mount Hayes JCT | BC_MHY_JCT | Mount Hayes | BC_MHY_DSS |  |  | 144
| 1L138 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 40.67 | 25.1049 | 138 | 17.6334 |  | 591 | 781 | 141.2626 | 186.677 | 0.9 | 127.1363 | 168.0093 | Mount Hayes JCT | BC_MHY_JCT | Ladysmith JCT | BC_LDY_JCT |  |  | 145
| 1L138LDY | BC Hydro | British Columbia | 1 | ac | 0.92874 | 0.5733 | 0.92874 | 0.5733 | 138 | 0.40268 |  | 625 | 805 | 149.3894 | 192.4135 | 0.9 | 134.4504 | 173.1722 | Ladysmith JCT | BC_LDY_JCT | Ladysmith | BC_LDY_DSS |  |  | 146
| 1L138 | BC Hydro | British Columbia | 1 | ac | 21.67 | 13.3765 | 40.67 | 25.1049 | 138 | 17.6334 |  | 591 | 781 | 141.2626 | 186.677 | 0.9 | 127.1363 | 168.0093 | Ladysmith JCT | BC_LDY_JCT | Vancouver Island TS | BC_VIT_TSS |  |  | 147
| 1L139 | BC Hydro | British Columbia | 1 | ac | 8.9829 | 5.545 | 8.9829 | 5.545 | 138 | 3.8947 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Vancouver Island TS | BC_VIT_TSS | Catalyst Paper Crofton GS | BC_CFT_GSS |  |  | 148
| 1L140 | BC Hydro | British Columbia | 1 | ac | 8.956 | 5.5284 | 8.956 | 5.5284 | 138 | 3.8831 |  | 635 | 810 | 151.7796 | 193.6086 | 0.9 | 136.6017 | 174.2478 | Vancouver Island TS | BC_VIT_TSS | Catalyst Paper Crofton GS | BC_CFT_GSS |  |  | 149
| 1L141 | BC Hydro | British Columbia | 1 | ac | 28 | 17.284 | 28 | 17.284 | 138 | 12.14 |  | 1071 | 1361 | 255.9936 | 325.3103 | 0.9 | 230.3943 | 292.7793 | Cape Scott GS | BC_CSS_GSS | Port Hardy | BC_PHY_DSS |  |  | 150
| 1L142 | BC Hydro | British Columbia | 1 | ac | 16.1793 | 9.9872 | 16.1793 | 9.9872 | 138 | 7.0149 |  | 395 | 565 | 94.4141 | 135.048 | 0.9 | 84.9727 | 121.5432 | Great Central | BC_GCL_DSS | Ash River GS | BC_ASH_GSS |  |  | 151
| 1L143 | BC Hydro | British Columbia | 1 | ac | 22 | 13.5802 | 45.01 | 27.784 | 138 | 19.5151 |  | 850 | 1033 | 203.1696 | 246.9108 | 0.9 | 182.8526 | 222.2197 | Jordan River GS | BC_JOR_DFS | Sooke JCT | BC_SOO_JCT |  |  | 152
| 1L143SOO | BC Hydro | British Columbia | 1 | ac | 2.5013 | 1.544 | 2.5013 | 1.544 | 138 | 1.0845 |  | 850 | 1090 | 203.1696 | 260.5351 | 0.9 | 182.8526 | 234.4816 | Sooke JCT | BC_SOO_JCT | Sooke | BC_SOO_DSS |  |  | 153
| 1L143 | BC Hydro | British Columbia | 1 | ac | 23.01 | 14.2037 | 45.01 | 27.784 | 138 | 19.5151 |  | 850 | 1033 | 203.1696 | 246.9108 | 0.9 | 182.8526 | 222.2197 | Sooke JCT | BC_SOO_JCT | Colwood | BC_CLD_DSS |  |  | 154
| 1L146 | BC Hydro | British Columbia | 1 | ac | 15.2425 | 9.4089 | 15.2425 | 9.4089 | 138 | 6.6087 |  | 850 | 1033 | 203.1696 | 246.9108 | 0.9 | 182.8526 | 222.2197 | Goward | BC_GOW_DSS | Colwood | BC_CLD_DSS |  |  | 155
| 1L152 | BC Hydro | British Columbia | 1 | ac | 3.0916 | 1.9084 | 3.0916 | 1.9084 | 138 | 1.3404 |  | 1069 | 1529 | 255.5156 | 365.4662 | 0.9 | 229.964 | 328.9196 | Jinglepot | BC_JPT_DSS | Northfield | BC_NFD_DSS |  |  | 156
| 1L157 | BC Hydro | British Columbia | 1 | ac | 69.94 | 43.1728 | 109.94 | 67.8642 | 138 | 47.6668 |  | 540 | 1050 | 129.0724 | 250.9742 | 0.9 | 116.1652 | 225.8767 | Gold River | BC_GLD_DSS | Woss JCT | BC_WOS_JCT |  |  | 157
| 1L157WOS | BC Hydro | British Columbia | 1 | ac | 0.078282 | 0.048322 | 0.078282 | 0.048322 | 138 | 0.033941 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Woss JCT | BC_WOS_JCT | Woss | BC_WOS_DSS |  |  | 158
| 1L157 | BC Hydro | British Columbia | 1 | ac | 37 | 22.8395 | 109.94 | 67.8642 | 138 | 47.6668 |  | 540 | 1050 | 129.0724 | 250.9742 | 0.9 | 116.1652 | 225.8767 | Woss JCT | BC_WOS_JCT | Beaver Cove JCT | BC_BVC_JCT |  |  | 159
| 1L157BVC | BC Hydro | British Columbia | 1 | ac | 0.0607 | 0.037469 | 0.0607 | 0.037469 | 138 | 0.026318 |  | 832 | 1007 | 198.8671 | 240.6962 | 0.9 | 178.9804 | 216.6266 | Beaver Cove JCT | BC_BVC_JCT | Beaver Cove | BC_BVC_DSS |  |  | 160
| 1L157 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 109.94 | 67.8642 | 138 | 47.6668 |  | 540 | 1050 | 129.0724 | 250.9742 | 0.9 | 116.1652 | 225.8767 | Beaver Cove JCT | BC_BVC_JCT | Kokish TS | BC_KTS_TSS |  |  | 161
| 1L157KKS | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 138 | 0.43357 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Kokish TS | BC_KTS_TSS | Kokish GS | BC_KKS_GSS |  |  | 162
| 1L201 | BC Hydro | British Columbia | 1 | ac | 85 | 52.4691 | 102.32 | 63.1605 | 138 | 44.363 |  | 411 | 625 | 98.2385 | 149.3894 | 0.9 | 88.4146 | 134.4504 | Monashee | BC_MON_DSS | Lumby #2 JCT | BC_LU2_JCT |  |  | 163
| 1L201LU2 | BC Hydro | British Columbia | 1 | ac | 0.032005 | 0.019756 | 0.032005 | 0.019756 | 138 | 0.013877 |  | 411 | 625 | 98.2385 | 149.3894 | 0.9 | 88.4146 | 134.4504 | Lumby #2 JCT | BC_LU2_JCT | Lumby #2 | BC_LU2_ISS |  |  | 164
| 1L201 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 102.32 | 63.1605 | 138 | 44.363 |  | 411 | 625 | 98.2385 | 149.3894 | 0.9 | 88.4146 | 134.4504 | Lumby #2 JCT | BC_LU2_JCT | Tolko Industries Lavington JCT | BC_TIL_JCT |  |  | 165
| 1L201TIL | BC Hydro | British Columbia | 1 | ac | 0.3182 | 0.19642 | 0.3182 | 0.19642 | 138 | 0.13796 |  | 571 | 728 | 136.4821 | 174.0088 | 0.9 | 122.8339 | 156.6079 | Tolko Industries Lavington JCT | BC_TIL_JCT | Tolko Industries Lavington | BC_TIL_DSS |  |  | 166
| 1L201 | BC Hydro | British Columbia | 1 | ac | 9.32 | 5.7531 | 102.32 | 63.1605 | 138 | 44.363 |  | 411 | 625 | 98.2385 | 149.3894 | 0.9 | 88.4146 | 134.4504 | Tolko Industries Lavington JCT | BC_TIL_JCT | Vernon TS | BC_VNT_TSS |  |  | 167
| 1L202 | BC Hydro | British Columbia | 1 | ac | 85 | 52.4691 | 102.25 | 63.1173 | 138 | 44.3327 |  | 411 | 625 | 98.2385 | 149.3894 | 0.9 | 88.4146 | 134.4504 | Monashee | BC_MON_DSS | Lumby #2 JCT | BC_LU2_JCT |  |  | 168
| 1L202LU2 | BC Hydro | British Columbia | 1 | ac | 0.045248 | 0.027931 | 0.045248 | 0.027931 | 138 | 0.019618 |  | 411 | 625 | 98.2385 | 149.3894 | 0.9 | 88.4146 | 134.4504 | Lumby #2 JCT | BC_LU2_JCT | Lumby #2 | BC_LU2_ISS |  |  | 169
| 1L202 | BC Hydro | British Columbia | 1 | ac | 17.25 | 10.6481 | 102.25 | 63.1173 | 138 | 44.3327 |  | 411 | 625 | 98.2385 | 149.3894 | 0.9 | 88.4146 | 134.4504 | Lumby #2 JCT | BC_LU2_JCT | Vernon TS | BC_VNT_TSS |  |  | 170
| 1L203 | BC Hydro | British Columbia | 1 | ac | 42.0388 | 25.9499 | 42.0388 | 25.9499 | 138 | 18.2268 |  | 723 | 866 | 172.8136 | 206.9939 | 0.9 | 155.5323 | 186.2945 | Savona | BC_SVA_DSS | Highland | BC_HLD_DSS |  |  | 171
| 1L204 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 39.12 | 24.1481 | 138 | 16.9613 |  | 714 | 912 | 170.6624 | 217.989 | 0.9 | 153.5962 | 196.1901 | Savona | BC_SVA_DSS | Afton Mine JCT | BC_AFN_JCT |  |  | 172
| 1L204AFN | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 138 | 0.43357 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Afton Mine JCT | BC_AFN_JCT | Afton Mine | BC_AFN_ISS |  |  | 173
| 1L204 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 39.12 | 24.1481 | 138 | 16.9613 |  | 714 | 912 | 170.6624 | 217.989 | 0.9 | 153.5962 | 196.1901 | Afton Mine JCT | BC_AFN_JCT | TransMountain Kamloops JCT | BC_TMT_JCT |  |  | 174
| 1L204TMT | BC Hydro | British Columbia | 1 | ac | 0.90913 | 0.56119 | 0.90913 | 0.56119 | 138 | 0.39417 |  | 493 | 627 | 117.8383 | 149.8674 | 0.9 | 106.0545 | 134.8807 | TransMountain Kamloops JCT | BC_TMT_JCT | TransMountain Kamloops | BC_TMT_DSS |  |  | 175
| 1L204 | BC Hydro | British Columbia | 1 | ac | 9.12 | 5.6296 | 39.12 | 24.1481 | 138 | 16.9613 |  | 714 | 912 | 170.6624 | 217.989 | 0.9 | 153.5962 | 196.1901 | TransMountain Kamloops JCT | BC_TMT_JCT | Douglas Street | BC_DUG_DSS |  |  | 176
| 1L205 | BC Hydro | British Columbia | 1 | ac | 42.0689 | 25.9684 | 42.0689 | 25.9684 | 138 | 18.2399 |  | 497 | 593 | 118.7944 | 141.7406 | 0.9 | 106.915 | 127.5666 | Savona | BC_SVA_DSS | Highland | BC_HLD_DSS |  |  | 177
| 1L206 | BC Hydro | British Columbia | 1 | ac | 35 | 21.6049 | 35 | 21.6049 | 138 | 15.175 |  | 714 | 886 | 170.6624 | 211.7744 | 0.9 | 153.5962 | 190.5969 | Savona | BC_SVA_DSS | West Kamloops | BC_WKA_DSS |  |  | 178
| 1L209 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 108.89 | 67.216 | 138 | 47.2116 |  | 472 | 658 | 112.8189 | 157.2771 | 0.9 | 101.537 | 141.5494 | Valleyview | BC_VVW_DSS | Lafarge #2 JCT | BC_LF2_JCT |  |  | 179
| 1L209LF2 | BC Hydro | British Columbia | 1 | ac | 0.25462 | 0.15717 | 0.25462 | 0.15717 | 138 | 0.1104 |  | 292 | 566 | 69.7947 | 135.287 | 0.9 | 62.8152 | 121.7583 | Lafarge #2 JCT | BC_LF2_JCT | Lafarge #2 | BC_LF2_ISS |  |  | 180
| 1L209 | BC Hydro | British Columbia | 1 | ac | 42 | 25.9259 | 108.89 | 67.216 | 138 | 47.2116 |  | 472 | 658 | 112.8189 | 157.2771 | 0.9 | 101.537 | 141.5494 | Lafarge #2 JCT | BC_LF2_JCT | Chase JCT | BC_CHS_JCT |  |  | 181
| 1L209CHS | BC Hydro | British Columbia | 1 | ac | 0.25462 | 0.15717 | 0.25462 | 0.15717 | 138 | 0.1104 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Chase JCT | BC_CHS_JCT | Chase | BC_CHS_DSS |  |  | 182
| 1L209 | BC Hydro | British Columbia | 1 | ac | 18.89 | 11.6605 | 108.89 | 67.216 | 138 | 47.2116 |  | 472 | 658 | 112.8189 | 157.2771 | 0.9 | 101.537 | 141.5494 | Chase JCT | BC_CHS_JCT | Sorrento JCT | BC_STO_JCT |  |  | 183
| 1L209STO | BC Hydro | British Columbia | 1 | ac | 0.25462 | 0.15717 | 0.25462 | 0.15717 | 138 | 0.1104 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Sorrento JCT | BC_STO_JCT | Sorrento | BC_STO_DSS |  |  | 184
| 1L209 | BC Hydro | British Columbia | 1 | ac | 40 | 24.6914 | 108.89 | 67.216 | 138 | 47.2116 |  | 472 | 658 | 112.8189 | 157.2771 | 0.9 | 101.537 | 141.5494 | Sorrento JCT | BC_STO_JCT | Salmon Arm | BC_SAM_DSS |  |  | 185
| 1L210 | BC Hydro | British Columbia | 1 | ac | 17 | 10.4938 | 192.5 | 118.8272 | 138 | 83.4625 |  | 493 | 627 | 117.8383 | 149.8674 | 0.9 | 106.0545 | 134.8807 | Brocklehurst | BC_BKL_DSS | Tolko Industries Heffley JCT | BC_TOK_JCT |  |  | 186
| 1L210TOK | BC Hydro | British Columbia | 1 | ac | 0.25023 | 0.15447 | 0.25023 | 0.15447 | 138 | 0.10849 |  | 493 | 627 | 117.8383 | 149.8674 | 0.9 | 106.0545 | 134.8807 | Tolko Industries Heffley JCT | BC_TOK_JCT | Tolko Industries Heffley | BC_TOK_DSS |  |  | 187
| 1L210 | BC Hydro | British Columbia | 1 | ac | 0.5 | 0.30864 | 192.5 | 118.8272 | 138 | 83.4625 |  | 484 | 622 | 115.6871 | 148.6723 | 0.9 | 104.1184 | 133.8051 | Tolko Industries Heffley JCT | BC_TOK_JCT | Heffley JCT | BC_HFY_JCT |  |  | 188
| 1L210HFY | BC Hydro | British Columbia | 1 | ac | 0.081944 | 0.050582 | 0.081944 | 0.050582 | 138 | 0.035528 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | Heffley JCT | BC_HFY_JCT | Heffley | BC_HFY_DSS |  |  | 189
| 1L210 | BC Hydro | British Columbia | 1 | ac | 35 | 21.6049 | 192.5 | 118.8272 | 138 | 83.4625 |  | 484 | 622 | 115.6871 | 148.6723 | 0.9 | 104.1184 | 133.8051 | Heffley JCT | BC_HFY_JCT | Barriere JCT | BC_BAR_JCT |  |  | 190
| 1L210BAR | BC Hydro | British Columbia | 1 | ac | 0.16008 | 0.098817 | 0.16008 | 0.098817 | 138 | 0.069407 |  | 493 | 627 | 117.8383 | 149.8674 | 0.9 | 106.0545 | 134.8807 | Barriere JCT | BC_BAR_JCT | Barriere | BC_BAR_DSS |  |  | 191
| 1L210 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 192.5 | 118.8272 | 138 | 83.4625 |  | 484 | 622 | 115.6871 | 148.6723 | 0.9 | 104.1184 | 133.8051 | Barriere JCT | BC_BAR_JCT | Darfield JCT | BC_DFD_JCT |  |  | 192
| 1L210DFD | BC Hydro | British Columbia | 1 | ac | 1.0985 | 0.67806 | 1.0985 | 0.67806 | 138 | 0.47626 |  | 493 | 627 | 117.8383 | 149.8674 | 0.9 | 106.0545 | 134.8807 | Darfield JCT | BC_DFD_JCT | Darfield | BC_DFD_DSS |  |  | 193
| 1L210 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 192.5 | 118.8272 | 138 | 83.4625 |  | 484 | 622 | 115.6871 | 148.6723 | 0.9 | 104.1184 | 133.8051 | Darfield JCT | BC_DFD_JCT | Blackpool JCT | BC_BLP_JCT |  |  | 194
| 1L210BLP | BC Hydro | British Columbia | 1 | ac | 0.47434 | 0.2928 | 0.47434 | 0.2928 | 138 | 0.20566 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | Blackpool JCT | BC_BLP_JCT | Blackpool | BC_BLP_DSS |  |  | 195
| 1L210 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 192.5 | 118.8272 | 138 | 83.4625 |  | 493 | 627 | 117.8383 | 149.8674 | 0.9 | 106.0545 | 134.8807 | Blackpool JCT | BC_BLP_JCT | Clearwater JCT | BC_CLW_JCT |  |  | 196
| 1L210CLW | BC Hydro | British Columbia | 1 | ac | 1.2866 | 0.79417 | 1.2866 | 0.79417 | 138 | 0.55782 |  | 484 | 622 | 115.6871 | 148.6723 | 0.9 | 104.1184 | 133.8051 | Clearwater JCT | BC_CLW_JCT | Clearwater | BC_CLW_DSS |  |  | 197
| 1L210 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 192.5 | 118.8272 | 138 | 83.4625 |  | 493 | 627 | 117.8383 | 149.8674 | 0.9 | 106.0545 | 134.8807 | Clearwater JCT | BC_CLW_JCT | Vavenby JCT | BC_VBY_JCT |  |  | 198
| 1L210VBY | BC Hydro | British Columbia | 1 | ac | 0.048336 | 0.029837 | 0.048336 | 0.029837 | 138 | 0.020957 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | Vavenby JCT | BC_VBY_JCT | Vavenby | BC_VBY_DSS |  |  | 199
| 1L210 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 192.5 | 118.8272 | 138 | 83.4625 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | Vavenby JCT | BC_VBY_JCT | TransMountain McMurphy JCT | BC_TMM_JCT |  |  | 200
| 1L210 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 192.5 | 118.8272 | 138 | 83.4625 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | TransMountain McMurphy JCT | BC_TMM_JCT | Avola JCT | BC_AVO_JCT |  |  | 201
| 1L210TMM | BC Hydro | British Columbia | 1 | ac | 0.11653 | 0.071932 | 0.11653 | 0.071932 | 138 | 0.050524 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | TransMountain McMurphy JCT | BC_TMM_JCT | TransMountain McMurphy | BC_TMM_DSS |  |  | 202
| 1L210AVO | BC Hydro | British Columbia | 1 | ac | 0.039881 | 0.024618 | 0.039881 | 0.024618 | 138 | 0.017291 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Avola JCT | BC_AVO_JCT | Avola | BC_AVO_DSS |  |  | 203
| 1L211AVO2 | BC Hydro | British Columbia | 1 | ac | 0.069289 | 0.042771 | 0.069289 | 0.042771 | 138 | 0.030042 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Avola JCT | BC_AVO_JCT | Avola | BC_AVO_DSS |  |  | 204
| 1L211 | BC Hydro | British Columbia | 1 | ac | 19 | 11.7284 | 62.44 | 38.5432 | 138 | 27.0722 |  | 484 | 622 | 115.6871 | 148.6723 | 0.9 | 104.1184 | 133.8051 | Avola JCT | BC_AVO_JCT | Finn Pumping Station JCT | BC_FPS_JCT |  |  | 205
| 1L211FPS | BC Hydro | British Columbia | 1 | ac | 2.7017 | 1.6677 | 2.7017 | 1.6677 | 138 | 1.1714 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Finn Pumping Station JCT | BC_FPS_JCT | Finn Pumping Station | BC_FPS_DSS |  |  | 206
| 1L211 | BC Hydro | British Columbia | 1 | ac | 19 | 11.7284 | 62.44 | 38.5432 | 138 | 27.0722 |  | 484 | 622 | 115.6871 | 148.6723 | 0.9 | 104.1184 | 133.8051 | Finn Pumping Station JCT | BC_FPS_JCT | Blue River Pumping Station JCT | BC_BLE_JCT |  |  | 207
| 1L211BLE | BC Hydro | British Columbia | 1 | ac | 2.1544 | 1.3299 | 2.1544 | 1.3299 | 138 | 0.93408 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Blue River Pumping Station JCT | BC_BLE_JCT | Blue River Pumping Station | BC_BLE_DSS |  |  | 208
| 1L211 | BC Hydro | British Columbia | 1 | ac | 2.44 | 1.5062 | 62.44 | 38.5432 | 138 | 27.0722 |  | 484 | 622 | 115.6871 | 148.6723 | 0.9 | 104.1184 | 133.8051 | Blue River Pumping Station JCT | BC_BLE_JCT | Blue River JCT | BC_BLU_JCT |  |  | 209
| 1L211BLU | BC Hydro | British Columbia | 1 | ac | 0.10226 | 0.063122 | 0.10226 | 0.063122 | 138 | 0.044336 |  | 506 | 1351 | 120.9456 | 322.9201 | 0.9 | 108.8511 | 290.6281 | Blue River JCT | BC_BLU_JCT | Blue River | BC_BLU_DSS |  |  | 210
| 1L211 | BC Hydro | British Columbia | 1 | ac | 22 | 13.5802 | 62.44 | 38.5432 | 138 | 27.0722 |  | 1052 | 1347 | 251.4522 | 321.964 | 0.9 | 226.307 | 289.7676 | Blue River JCT | BC_BLU_JCT | Bone Creek | BC_BET_DSS |  |  | 211
| 1L212 | BC Hydro | British Columbia | 1 | ac | 27.7058 | 17.1024 | 27.7058 | 17.1024 | 138 | 12.0125 |  | 254 | 488 | 60.7118 | 116.6432 | 0.9 | 54.6407 | 104.9789 | Valemount | BC_VLM_DSS | Rearguard Pumping Station | BC_REG_DSS |  |  | 212
| 1L214 | BC Hydro | British Columbia | 1 | ac | 111.5692 | 68.8699 | 111.5692 | 68.8699 | 138 | 48.3732 |  | 395 | 617 | 94.4141 | 147.4772 | 0.9 | 84.9727 | 132.7295 | Vernon TS | BC_VNT_TSS | Valleyview | BC_VVW_DSS |  |  | 213
| 1L218 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 57.93 | 35.7593 | 138 | 25.1168 |  | 571 | 728 | 136.4821 | 174.0088 | 0.9 | 122.8339 | 156.6079 | Salmon Arm | BC_SAM_DSS | Enderby JCT | BC_END_JCT |  |  | 214
| 1L218END | BC Hydro | British Columbia | 1 | ac | 0.046052 | 0.028427 | 0.046052 | 0.028427 | 138 | 0.019967 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Enderby JCT | BC_END_JCT | Enderby | BC_END_DSS |  |  | 215
| 1L218 | BC Hydro | British Columbia | 1 | ac | 12 | 7.4074 | 57.93 | 35.7593 | 138 | 25.1168 |  | 571 | 728 | 136.4821 | 174.0088 | 0.9 | 122.8339 | 156.6079 | Enderby JCT | BC_END_JCT | Armstrong JCT | BC_ARM_JCT |  |  | 216
| 1L218ARM | BC Hydro | British Columbia | 1 | ac | 0.046052 | 0.028427 | 0.046052 | 0.028427 | 138 | 0.019967 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Armstrong JCT | BC_ARM_JCT | Armstrong | BC_ARM_DSS |  |  | 217
| 1L218 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 57.93 | 35.7593 | 138 | 25.1168 |  | 571 | 728 | 136.4821 | 174.0088 | 0.9 | 122.8339 | 156.6079 | Armstrong JCT | BC_ARM_JCT | Tolko Armstrong JCT | BC_RVG_JCT |  |  | 218
| 1L218RVG | BC Hydro | British Columbia | 1 | ac | 0.046052 | 0.028427 | 0.046052 | 0.028427 | 138 | 0.019967 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Tolko Armstrong JCT | BC_RVG_JCT | Tolko Armstrong GS | BC_RVG_GSS |  |  | 219
| 1L218 | BC Hydro | British Columbia | 1 | ac | 2.93 | 1.8086 | 57.93 | 35.7593 | 138 | 25.1168 |  | 571 | 728 | 136.4821 | 174.0088 | 0.9 | 122.8339 | 156.6079 | Tolko Armstrong JCT | BC_RVG_JCT | Riverside JCT | BC_RVS_JCT |  |  | 220
| 1L218RVS | BC Hydro | British Columbia | 1 | ac | 0.046052 | 0.028427 | 0.046052 | 0.028427 | 138 | 0.019967 |  | 571 | 728 | 136.4821 | 174.0088 | 0.9 | 122.8339 | 156.6079 | Riverside JCT | BC_RVS_JCT | Riverside | BC_RVS_DSS |  |  | 221
| 1L218 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 57.93 | 35.7593 | 138 | 25.1168 |  | 571 | 728 | 136.4821 | 174.0088 | 0.9 | 122.8339 | 156.6079 | Riverside JCT | BC_RVS_JCT | Vernon TS | BC_VNT_TSS |  |  | 222
| 1L219 | BC Hydro | British Columbia | 1 | ac | 5.1059 | 3.1518 | 13.7159 | 8.4666 | 138 | 5.9468 |  | 710 | 830 | 169.7063 | 198.3891 | 0.9 | 152.7357 | 178.5502 | Valleyview | BC_VVW_DSS | Douglas Street | BC_DUG_DSS |  |  | 223
| 1L219 | BC Hydro | British Columbia | 1 | ac | 7.61 | 4.6975 | 13.7159 | 8.4666 | 138 | 5.9468 |  | 710 | 830 | 169.7063 | 198.3891 | 0.9 | 152.7357 | 178.5502 | Douglas Street | BC_DUG_DSS | Kamwood | BC_KWD_DSS |  |  | 224
| 1L219 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 13.7159 | 8.4666 | 138 | 5.9468 |  | 710 | 830 | 169.7063 | 198.3891 | 0.9 | 152.7357 | 178.5502 | Kamwood | BC_KWD_DSS | Domtar Kamloops | BC_WEY_ISS |  |  | 225
| 1L220 | BC Hydro | British Columbia | 1 | ac | 3.05 | 1.8827 | 3.05 | 1.8827 | 138 | 1.3224 |  | 714 | 886 | 170.6624 | 211.7744 | 0.9 | 153.5962 | 190.5969 | West Kamloops | BC_WKA_DSS | Brocklehurst | BC_BKL_DSS |  |  | 226
| 1L225 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 65.42 | 40.3827 | 138 | 28.3642 |  | 1076 | 1351 | 257.1888 | 322.9201 | 0.9 | 231.4699 | 290.6281 | Bone Creek | BC_BET_DSS | Chappell Pumping Station JCT | BC_CPL_JCT |  |  | 227
| 1L225BNC | BC Hydro | British Columbia | 1 | ac | 0.1 | 0.061728 | 0.1 | 0.061728 | 138 | 0.043357 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Bone Creek | BC_BET_DSS | Bone Creek GS | BC_BNC_GSS |  |  | 228
| 1L225CPL | BC Hydro | British Columbia | 1 | ac | 1.6115 | 0.99477 | 1.6115 | 0.99477 | 138 | 0.69872 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Chappell Pumping Station JCT | BC_CPL_JCT | Chappell Pumping Station | BC_CPL_DSS |  |  | 229
| 1L225 | BC Hydro | British Columbia | 1 | ac | 25.42 | 15.6914 | 65.42 | 40.3827 | 138 | 28.3642 |  | 1076 | 1351 | 257.1888 | 322.9201 | 0.9 | 231.4699 | 290.6281 | Chappell Pumping Station JCT | BC_CPL_JCT | Albreda JCT | BC_ABA_JCT |  |  | 230
| 1L225ABA | BC Hydro | British Columbia | 1 | ac | 0.76673 | 0.47329 | 0.76673 | 0.47329 | 138 | 0.33243 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Albreda JCT | BC_ABA_JCT | Albreda | BC_ABA_DSS |  |  | 231
| 1L225 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 65.42 | 40.3827 | 138 | 28.3642 |  | 1055 | 1351 | 252.1693 | 322.9201 | 0.9 | 226.9523 | 290.6281 | Albreda JCT | BC_ABA_JCT | Valemount | BC_VLM_DSS |  |  | 232
| 1L241 | BC Hydro | British Columbia | 1 | ac | 13.2689 | 8.1907 | 13.2689 | 8.1907 | 138 | 5.753 |  | 725 | 923 | 173.2917 | 220.6182 | 0.9 | 155.9625 | 198.5564 | Valleyview | BC_VVW_DSS | Brocklehurst | BC_BKL_DSS |  |  | 233
| 1L242 | BC Hydro | British Columbia | 1 | ac | 5.1059 | 3.1518 | 5.1059 | 3.1518 | 138 | 2.2138 |  | 714 | 923 | 170.6624 | 220.6182 | 0.9 | 153.5962 | 198.5564 | Douglas Street | BC_DUG_DSS | Valleyview | BC_VVW_DSS |  |  | 234
| 1L243 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 42.88 | 26.4691 | 138 | 18.5915 |  | 714 | 923 | 170.6624 | 220.6182 | 0.9 | 153.5962 | 198.5564 | Highland | BC_HLD_DSS | Stump JCT | BC_STM_JCT |  |  | 235
| 1L243STM | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 138 | 0.86714 |  | 714 | 923 | 170.6624 | 220.6182 | 0.9 | 153.5962 | 198.5564 | Stump JCT | BC_STM_JCT | Stump | BC_STM_ISS |  |  | 236
| 1L243 | BC Hydro | British Columbia | 1 | ac | 12.88 | 7.9506 | 42.88 | 26.4691 | 138 | 18.5915 |  | 714 | 923 | 170.6624 | 220.6182 | 0.9 | 153.5962 | 198.5564 | Stump JCT | BC_STM_JCT | Nicola | BC_NIC_DSS |  |  | 237
| 1L244 | BC Hydro | British Columbia | 1 | ac | 32 | 19.7531 | 77.23 | 47.6728 | 138 | 33.4847 |  | 710 | 920 | 169.7063 | 219.9012 | 0.9 | 152.7357 | 197.9111 | Nicola | BC_NIC_DSS | Pennask JCT | BC_PSW_JCT |  |  | 238
| 1L244PSW | BC Hydro | British Columbia | 1 | ac | 0.1205 | 0.074381 | 0.1205 | 0.074381 | 138 | 0.052244 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Pennask JCT | BC_PSW_JCT | Pennask GS | BC_PSW_GSS |  |  | 239
| 1L244 | BC Hydro | British Columbia | 1 | ac | 13.23 | 8.1667 | 77.23 | 47.6728 | 138 | 33.4847 |  | 710 | 920 | 169.7063 | 219.9012 | 0.9 | 152.7357 | 197.9111 | Pennask JCT | BC_PSW_JCT | Brenda Mines JCT | BC_BDM_JCT |  |  | 240
| 1L244BDM | BC Hydro | British Columbia | 1 | ac | 0.72881 | 0.44988 | 0.72881 | 0.44988 | 138 | 0.31599 |  | 710 | 920 | 169.7063 | 219.9012 | 0.9 | 152.7357 | 197.9111 | Brenda Mines JCT | BC_BDM_JCT | Brenda Mines | BC_BDM_ISS |  |  | 241
| 1L244 | BC Hydro | British Columbia | 1 | ac | 32 | 19.7531 | 77.23 | 47.6728 | 138 | 33.4847 |  | 710 | 920 | 169.7063 | 219.9012 | 0.9 | 152.7357 | 197.9111 | Brenda Mines JCT | BC_BDM_JCT | Westbank | BC_WBK_DSS |  |  | 242
| 1L246 | BC Hydro | British Columbia | 1 | ac | 6.2695 | 3.8701 | 6.2695 | 3.8701 | 138 | 2.7183 |  | 623 | 804 | 148.9113 | 192.1745 | 0.9 | 134.0202 | 172.9571 | Monashee | BC_MON_DSS | Whatshan GS | BC_WGS_GSS |  |  | 243
| 1L249 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 4 | 2.4691 | 138 | 1.7343 |  | 740 | 924 | 176.877 | 220.8573 | 0.9 | 159.1893 | 198.7715 | Merritt Green GS | BC_MIG_GSS | Merritt | BC_MRT_DSS |  |  | 244
| 1L251 | BC Hydro | British Columbia | 1 | ac | 89.4236 | 55.1997 | 99.4236 | 61.3726 | 138 | 43.1072 |  | 490 | 627 | 117.1213 | 149.8674 | 0.9 | 105.4091 | 134.8807 | Nicola | BC_NIC_DSS | Princeton JCT | BC_PRI_JCT |  |  | 245
| 1L251 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 99.4236 | 61.3726 | 138 | 43.1072 |  | 490 | 627 | 117.1213 | 149.8674 | 0.9 | 105.4091 | 134.8807 | Princeton JCT | BC_PRI_JCT | Copper Mountain JCT | BC_CUM_JCT |  |  | 246
| 1L251CUM | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 3 | 1.8519 | 138 | 1.3007 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Copper Mountain JCT | BC_CUM_JCT | Copper Mountain | BC_CUM_DSS |  |  | 247
| 1L251 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 99.4236 | 61.3726 | 138 | 43.1072 |  | 490 | 627 | 117.1213 | 149.8674 | 0.9 | 105.4091 | 134.8807 | Copper Mountain JCT | BC_CUM_JCT | Similco | BC_SCO_DSS |  |  | 248
| 1L254 | BC Hydro | British Columbia | 1 | ac | 35.6477 | 22.0047 | 35.6477 | 22.0047 | 138 | 15.4558 |  | 730 | 924 | 174.4868 | 220.8573 | 0.9 | 157.0381 | 198.7715 | Highland | BC_HLD_DSS | Merritt | BC_MRT_DSS |  |  | 249
| 1L274 | BC Hydro | British Columbia | 1 | ac | 12 | 7.4074 | 103.41 | 63.8333 | 138 | 44.8356 |  | 265 | 442 | 63.3411 | 105.6482 | 0.9 | 57.007 | 95.0834 | Natal | BC_NTL_DSS | Line Creek Coal JCT | BC_LCC_JCT |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 250
| 1L274LCC | BC Hydro | British Columbia | 1 | ac | 3.0614 | 1.8898 | 3.0614 | 1.8898 | 138 | 1.3274 |  | 493 | 590 | 117.8383 | 141.0236 | 0.9 | 106.0545 | 126.9212 | Line Creek Coal JCT | BC_LCC_JCT | Line Creek Coal | BC_LCC_ISS |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 251
| 1L274 | BC Hydro | British Columbia | 1 | ac | 13 | 8.0247 | 103.41 | 63.8333 | 138 | 44.8356 |  | 265 | 442 | 63.3411 | 105.6482 | 0.9 | 57.007 | 95.0834 | Line Creek Coal JCT | BC_LCC_JCT | Elkford JCT | BC_EFD_JCT |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 252
| 1L274EFD | BC Hydro | British Columbia | 1 | ac | 1.0679 | 0.65923 | 1.0679 | 0.65923 | 138 | 0.46303 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Elkford JCT | BC_EFD_JCT | Elkford | BC_EFD_DSS |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 253
| 1L274 | BC Hydro | British Columbia | 1 | ac | 0.01 | 0.0061728 | 103.41 | 63.8333 | 138 | 44.8356 |  | 265 | 442 | 63.3411 | 105.6482 | 0.9 | 57.007 | 95.0834 | Elkford JCT | BC_EFD_JCT | Fording Coal JCT | BC_FRO_JCT |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 254
| 1L274FRO | BC Hydro | British Columbia | 1 | ac | 0.0158 | 0.009753 | 0.0158 | 0.009753 | 138 | 0.0068503 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Fording Coal JCT | BC_FRO_JCT | Fording Coal | BC_FRO_ISS |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 255
| 1L274 | BC Hydro | British Columbia | 1 | ac | 0.9 | 0.55556 | 103.41 | 63.8333 | 138 | 44.8356 |  | 265 | 442 | 63.3411 | 105.6482 | 0.9 | 57.007 | 95.0834 | Fording Coal JCT | BC_FRO_JCT | Greenhills JCT | BC_GRH_JCT |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 256
| 1L274GRH | BC Hydro | British Columbia | 1 | ac | 5.1671 | 3.1896 | 5.1671 | 3.1896 | 138 | 2.2403 |  | 1047 | 1274 | 250.2571 | 304.5153 | 0.9 | 225.2314 | 274.0638 | Greenhills JCT | BC_GRH_JCT | Greenhills | BC_GRH_ISS |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 257
| 1L274 | BC Hydro | British Columbia | 1 | ac | 27.5 | 16.9753 | 103.41 | 63.8333 | 138 | 44.8356 |  | 265 | 442 | 63.3411 | 105.6482 | 0.9 | 57.007 | 95.0834 | Greenhills JCT | BC_GRH_JCT | Britt Creek JCT | BC_BCK_JCT |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 258
| 1L274BCK | BC Hydro | British Columbia | 1 | ac | 0.12 | 0.074074 | 0.12 | 0.074074 | 138 | 0.052029 |  | 265 | 442 | 63.3411 | 105.6482 | 0.9 | 57.007 | 95.0834 | Britt Creek JCT | BC_BCK_JCT | Britt Creek | BC_BCK_ISS |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 259
| 1L274 | BC Hydro | British Columbia | 1 | ac | 50 | 30.8642 | 103.41 | 63.8333 | 138 | 44.8356 |  | 265 | 442 | 63.3411 | 105.6482 | 0.9 | 57.007 | 95.0834 | Britt Creek JCT | BC_BCK_JCT | IPT Natal Pocaterra | PP_BCAB3_IPT |  | DELETIONS and CORRRECTIONS to 1L274 and related lines | 260
| 1L275 | BC Hydro | British Columbia | 1 | ac | 18.5856 | 11.4726 | 18.5856 | 11.4726 | 138 | 8.0582 |  | 414 | 552 | 98.9555 | 131.9407 | 0.9 | 89.06 | 118.7466 | Natal | BC_NTL_DSS | IPT Natal Coleman | PP_BCAB1_IPT |  |  | 261
| 1L348 | BC Hydro | British Columbia | 1 | ac | 13.7869 | 8.5104 | 13.7869 | 8.5104 | 138 | 5.9776 |  | 814 | 1105 | 194.5647 | 264.1204 | 0.9 | 175.1083 | 237.7084 | Bear Mountain | BC_BMT_DSS | Dawson Creek | BC_DAW_DSS |  |  | 262
| 1L349 | BC Hydro | British Columbia | 1 | ac | 20.3885 | 12.5855 | 20.3885 | 12.5855 | 138 | 8.8399 |  | 559 | 674 | 133.6139 | 161.1015 | 0.9 | 120.2525 | 144.9914 | Chetwynd | BC_CWD_DSS | Sundance Lake | BC_SLS_DSS |  |  | 263
| 1L350 | BC Hydro | British Columbia | 1 | ac | 13.8261 | 8.5346 | 13.8261 | 8.5346 | 138 | 5.9946 |  | 814 | 1105 | 194.5647 | 264.1204 | 0.9 | 175.1083 | 237.7084 | Bear Mountain | BC_BMT_DSS | Dawson Creek | BC_DAW_DSS |  |  | 264
| 1L354 | BC Hydro | British Columbia | 1 | ac | 12 | 7.4074 | 12 | 7.4074 | 138 | 5.2029 |  | 468 | 628 | 111.8628 | 150.1065 | 0.9 | 100.6765 | 135.0958 | Bear Mountain | BC_BMT_DSS | Bear Mountain GS | BC_BMW_GSS |  |  | 265
| 1L355 | BC Hydro | British Columbia | 1 | ac | 45 | 27.7778 | 69.28 | 42.7654 | 138 | 30.0378 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Bear Mountain | BC_BMT_DSS | BP Noel 5 JCT | BC_NL5_JCT |  | Line may not be currently energized | 266
| 1L355NL5 | BC Hydro | British Columbia | 1 | ac | 0.37935 | 0.23416 | 0.37935 | 0.23416 | 138 | 0.16447 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | BP Noel 5 JCT | BC_NL5_JCT | BP Noel 5 | BC_NL5_ISS |  |  | 267
| 1L355 | BC Hydro | British Columbia | 1 | ac | 9.28 | 5.7284 | 69.28 | 42.7654 | 138 | 30.0378 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | BP Noel 5 JCT | BC_NL5_JCT | BP Noel 3 JCT | BC_NL3_JCT |  | Line may not be currently energized | 268
| 1L355NL3 | BC Hydro | British Columbia | 1 | ac | 0.33082 | 0.20421 | 0.33082 | 0.20421 | 138 | 0.14343 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | BP Noel 3 JCT | BC_NL3_JCT | BP Noel 3 | BC_NL3_ISS |  |  | 269
| 1L355 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 69.28 | 42.7654 | 138 | 30.0378 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | BP Noel 3 JCT | BC_NL3_JCT | BP Noel 2 | BC_NL2_ISS |  | Line may not be currently energized | 270
| 1L357 | BC Hydro | Alberta | 1 | ac | 11.2424 | 6.9398 | 11.2424 | 6.9398 | 138 | 4.8744 |  | 770 | 910 | 184.0477 | 217.5109 | 0.9 | 165.6429 | 195.7598 | Fort Nelson GS | BC_FNG_GSS | Wescup | BC_WSP_DSS |  |  | 271
| 1L358 | BC Hydro | British Columbia | 1 | ac | 15.1302 | 9.3397 | 24.4902 | 15.1174 | 138 | 10.6183 |  | 559 | 674 | 133.6139 | 161.1015 | 0.9 | 120.2525 | 144.9914 | Bear Mountain | BC_BMT_DSS | Encana 4-26 JCT | BC_E42_JCT |  |  | 272
| 1L358E42 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 138 | 0.43357 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Encana 4-26 JCT | BC_E42_JCT | Encana 4-26 | BC_E42_ISS |  |  | 273
| 1L358 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 24.4902 | 15.1174 | 138 | 10.6183 |  | 559 | 674 | 133.6139 | 161.1015 | 0.9 | 120.2525 | 144.9914 | Encana 4-26 JCT | BC_E42_JCT | Encana 15-27 JCT | BC_E15_JCT |  |  | 274
| 1L358E15 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 138 | 0.43357 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Encana 15-27 JCT | BC_E15_JCT | Encana 15-27 | BC_E15_ISS |  |  | 275
| 1L358 | BC Hydro | British Columbia | 1 | ac | 2.36 | 1.4568 | 24.4902 | 15.1174 | 138 | 10.6183 |  | 559 | 674 | 133.6139 | 161.1015 | 0.9 | 120.2525 | 144.9914 | Encana 15-27 JCT | BC_E15_JCT | Encana 9-27 | BC_KIS_ISS |  |  | 276
| 1L359 | BC Hydro | Alberta | 1 | ac | 25 | 15.4321 | 161.87 | 99.9198 | 138 | 70.1822 |  | 770 | 970 | 184.0477 | 231.8523 | 0.9 | 165.6429 | 208.6671 | Fort Nelson GS | BC_FNG_GSS | PetroCan JCT | BC_KLC_JCT |  |  | 277
| 1L359KLC | BC Hydro | Alberta | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 138 | 0.86714 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | PetroCan JCT | BC_KLC_JCT | PetroCan | BC_KLC_DSS |  |  | 278
| 1L359 | BC Hydro | Alberta | 1 | ac | 115 | 70.9877 | 161.87 | 99.9198 | 138 | 70.1822 |  | 770 | 970 | 184.0477 | 231.8523 | 0.9 | 165.6429 | 208.6671 | PetroCan JCT | BC_KLC_JCT | Harvest Energy JCT | BC_FNC_JCT |  |  | 279
| 1L359FNC | BC Hydro | Alberta | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 138 | 0.86714 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Harvest Energy JCT | BC_FNC_JCT | Harvest Energy | BC_FNC_ISS |  |  | 280
| 1L359 | BC Hydro | Alberta | 1 | ac | 21.87 | 13.5 | 161.87 | 99.9198 | 138 | 70.1822 |  | 770 | 970 | 184.0477 | 231.8523 | 0.9 | 165.6429 | 208.6671 | Harvest Energy JCT | BC_FNC_JCT | IPT Nelson Rainbow | PP_BCAB4_IPT |  |  | 281
| 1L360 | BC Hydro | British Columbia | 1 | ac | 90.22 | 55.6914 | 100.22 | 61.8642 | 138 | 43.4525 |  | 560 | 675 | 133.8529 | 161.3405 | 0.9 | 120.4676 | 145.2065 | GM Shrum GS | BC_GMS_GSS | Site C JCT | BC_STC_JCT |  |  | 282
| 1L360STC | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 138 | 0.86714 |  | 560 | 674 | 133.8529 | 161.1015 | 0.9 | 120.4676 | 144.9914 | Site C JCT | BC_STC_JCT | Site C GS | BC_STC_GSS |  | To be replaced with 5L006 in 2025 | 283
| 1L360 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 100.22 | 61.8642 | 138 | 43.4525 |  | 560 | 675 | 133.8529 | 161.3405 | 0.9 | 120.4676 | 145.2065 | Site C JCT | BC_STC_JCT | Taylor | BC_TAY_DSS |  |  | 284
| 1L361 | BC Hydro | British Columbia | 1 | ac | 65.6265 | 40.5102 | 65.6265 | 40.5102 | 138 | 28.4538 |  | 559 | 674 | 133.6139 | 161.1015 | 0.9 | 120.2525 | 144.9914 | GM Shrum GS | BC_GMS_GSS | Chetwynd | BC_CWD_DSS |  |  | 285
| 1L364 | BC Hydro | British Columbia | 1 | ac | 6.71 | 4.142 | 88.77 | 54.7963 | 138 | 38.4881 |  | 570 | 682 | 136.2431 | 163.0137 | 0.9 | 122.6188 | 146.7123 | GM Shrum GS | BC_GMS_GSS | Portage Pass JCT | BC_PPS_JCT |  |  | 286
| 1L364PPS | BC Hydro | British Columbia | 1 | ac | 0.1 | 0.061728 | 0.1 | 0.061728 | 138 | 0.043357 |  | 290 | 495 | 69.3167 | 118.3164 | 0.9 | 62.385 | 106.4848 | Portage Pass JCT | BC_PPS_JCT | Portage Pass | BC_PPS_DSS |  |  | 287
| 1L364 | BC Hydro | British Columbia | 1 | ac | 64.06 | 39.5432 | 88.77 | 54.7963 | 138 | 38.4881 |  | 570 | 682 | 136.2431 | 163.0137 | 0.9 | 122.6188 | 146.7123 | Portage Pass JCT | BC_PPS_JCT | Fox Creek JCT | BC_FOX_JCT |  |  | 288
| 1L364FOX | BC Hydro | British Columbia | 1 | ac | 56.6631 | 34.9772 | 56.6631 | 34.9772 | 138 | 24.5675 |  | 570 | 725 | 136.2431 | 173.2917 | 0.9 | 122.6188 | 155.9625 | Fox Creek JCT | BC_FOX_JCT | Fox Creek | BC_FOX_DSS |  |  | 289
| 1L364 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 88.77 | 54.7963 | 138 | 38.4881 |  | 570 | 682 | 136.2431 | 163.0137 | 0.9 | 122.6188 | 146.7123 | Fox Creek JCT | BC_FOX_JCT | Fort St. John | BC_FJN_DSS |  |  | 290
| 1L365 | BC Hydro | British Columbia | 1 | ac | 40.91 | 25.2531 | 105.91 | 65.3765 | 138 | 45.9196 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | Salmon Valley | BC_SVY_DSS | McEwan JCT | BC_MWN_JCT |  |  | 291
| 1L365MWN | BC Hydro | British Columbia | 1 | ac | 2.6459 | 1.6333 | 2.6459 | 1.6333 | 138 | 1.1472 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | McEwan JCT | BC_MWN_JCT | McEwan | BC_MWN_DSS |  |  | 292
| 1L365 | BC Hydro | British Columbia | 1 | ac | 65 | 40.1235 | 105.91 | 65.3765 | 138 | 45.9196 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | McEwan JCT | BC_MWN_JCT | Kennedy | BC_KDS_DSS |  |  | 293
| 1L366 | BC Hydro | British Columbia | 1 | ac | 2.31 | 1.4259 | 4.31 | 2.6605 | 138 | 1.8687 |  | 265 | 440 | 63.3411 | 105.1701 | 0.9 | 57.007 | 94.6531 | Morfee | BC_MFE_DSS | Timbernorth JCT | BC_TBN_JCT |  |  | 294
| 1L366TBN | BC Hydro | British Columbia | 1 | ac | 0.4022 | 0.24827 | 0.4022 | 0.24827 | 138 | 0.17438 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Timbernorth JCT | BC_TBN_JCT | Timbernorth | BC_TBN_DSS |  |  | 295
| 1L366 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 4.31 | 2.6605 | 138 | 1.8687 |  | 265 | 440 | 63.3411 | 105.1701 | 0.9 | 57.007 | 94.6531 | Timbernorth JCT | BC_TBN_JCT | Fletcher Challenge | BC_FCC_ISS |  |  | 296
| 1L367 | BC Hydro | British Columbia | 1 | ac | 10.1199 | 6.2468 | 10.1199 | 6.2468 | 138 | 4.3877 |  | 520 | 650 | 124.292 | 155.365 | 0.9 | 111.8628 | 139.8285 | Fort St. John | BC_FJN_DSS | Taylor | BC_TAY_DSS |  |  | 297
| 1L368 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 6 | 3.7037 | 138 | 2.6014 |  | 350 | 495 | 83.6581 | 118.3164 | 0.9 | 75.2922 | 106.4848 | Morfee | BC_MFE_DSS | Parsnip JCT | BC_PRS_JCT |  |  | 298
| 1L368PRS | BC Hydro | British Columbia | 1 | ac | 0.27051 | 0.16698 | 0.27051 | 0.16698 | 138 | 0.11728 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Parsnip JCT | BC_PRS_JCT | Parsnip | BC_PRS_DSS |  |  | 299
| 1L368 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 6 | 3.7037 | 138 | 2.6014 |  | 350 | 495 | 83.6581 | 118.3164 | 0.9 | 75.2922 | 106.4848 | Parsnip JCT | BC_PRS_JCT | Finlay Forest Industries | BC_FFI_ISS |  |  | 300
| 1L371 | BC Hydro | British Columbia | 1 | ac | 47.2115 | 29.1429 | 47.2115 | 29.1429 | 138 | 20.4696 |  | 520 | 650 | 124.292 | 155.365 | 0.9 | 111.8628 | 139.8285 | Fort St. John | BC_FJN_DSS | Texaco | BC_TXB_DSS |  |  | 301
| 1L373 | BC Hydro | British Columbia | 1 | ac | 42.9944 | 26.5398 | 42.9944 | 26.5398 | 138 | 18.6412 |  | 510 | 610 | 121.9017 | 145.804 | 0.9 | 109.7116 | 131.2236 | Kennedy | BC_KDS_DSS | Morfee | BC_MFE_DSS |  |  | 302
| 1L374 | BC Hydro | British Columbia | 1 | ac | 88.97 | 54.9198 | 98.97 | 61.0926 | 138 | 42.9106 |  | 560 | 675 | 133.8529 | 161.3405 | 0.9 | 120.4676 | 145.2065 | GM Shrum GS | BC_GMS_GSS | Site C JCT | BC_STC_JCT |  |  | 303
| 1L374STC | BC Hydro | British Columbia | 1 | ac | 0.087353 | 0.053921 | 0.087353 | 0.053921 | 138 | 0.037874 |  | 560 | 674 | 133.8529 | 161.1015 | 0.9 | 120.4676 | 144.9914 | Site C JCT | BC_STC_JCT | Site C GS | BC_STC_GSS |  |  | 304
| 1L374 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 98.97 | 61.0926 | 138 | 42.9106 |  | 560 | 675 | 133.8529 | 161.3405 | 0.9 | 120.4676 | 145.2065 | Site C JCT | BC_STC_JCT | Fort St. John | BC_FJN_DSS |  |  | 305
| 1L375 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 6.16 | 3.8025 | 138 | 2.6708 |  | 560 | 674 | 133.8529 | 161.1015 | 0.9 | 120.4676 | 144.9914 | Taylor | BC_TAY_DSS | McMahon JCT | BC_MCM_JCT |  |  | 306
| 1L375MCM | BC Hydro | British Columbia | 1 | ac | 2.1088 | 1.3017 | 2.1088 | 1.3017 | 138 | 0.91433 |  | 560 | 674 | 133.8529 | 161.1015 | 0.9 | 120.4676 | 144.9914 | McMahon JCT | BC_MCM_JCT | McMahon GS | BC_MCM_GSS |  |  | 307
| 1L375MGP | BC Hydro | British Columbia | 1 | ac | 0.30359 | 0.1874 | 0.30359 | 0.1874 | 138 | 0.13163 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | McMahon GS | BC_MCM_GSS | McMahon Gas Plant | BC_MGP_ISS |  |  | 308
| 1L375 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 6.16 | 3.8025 | 138 | 2.6708 |  | 560 | 674 | 133.8529 | 161.1015 | 0.9 | 120.4676 | 144.9914 | McMahon JCT | BC_MCM_JCT | Solex Gas | BC_NGL_ISS |  |  | 309
| 1L375 | BC Hydro | British Columbia | 1 | ac | 3.16 | 1.9506 | 6.16 | 3.8025 | 138 | 2.6708 |  | 560 | 674 | 133.8529 | 161.1015 | 0.9 | 120.4676 | 144.9914 | Solex Gas | BC_NGL_ISS | Fiberco JCT | BC_FBC_JCT |  |  | 310
| 1L375FBC | BC Hydro | British Columbia | 1 | ac | 0.69733 | 0.43045 | 0.69733 | 0.43045 | 138 | 0.30234 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Fiberco JCT | BC_FBC_JCT | Fiberco | BC_FBC_DSS |  |  | 311
| 1L377 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 55.56 | 34.2963 | 138 | 24.0892 |  | 567 | 717 | 135.526 | 171.3795 | 0.9 | 121.9734 | 154.2415 | Taylor | BC_TAY_DSS | Septimus JCT | BC_SEP_JCT |  |  | 312
| 1L377SEP | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 15 | 9.2593 | 138 | 6.5036 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Septimus JCT | BC_SEP_JCT | Septimus | BC_SEP_DSS |  |  | 313
| 1L377 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 55.56 | 34.2963 | 138 | 24.0892 |  | 567 | 717 | 135.526 | 171.3795 | 0.9 | 121.9734 | 154.2415 | Septimus JCT | BC_SEP_JCT | Encana Tower JCT | BC_ET3_JCT |  |  | 314
| 1L377ET3 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 8 | 4.9383 | 138 | 3.4686 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Encana Tower JCT | BC_ET3_JCT | Encana Tower | BC_ET3_ISS |  |  | 315
| 1L377 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 55.56 | 34.2963 | 138 | 24.0892 |  | 567 | 717 | 135.526 | 171.3795 | 0.9 | 121.9734 | 154.2415 | Encana Tower JCT | BC_ET3_JCT | Parkland JCT | BC_PLD_JCT |  |  | 316
| 1L377PLD | BC Hydro | British Columbia | 1 | ac | 0.28965 | 0.1788 | 0.28965 | 0.1788 | 138 | 0.12558 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Parkland JCT | BC_PLD_JCT | Parkland | BC_PLD_DSS |  |  | 317
| 1L377 | BC Hydro | British Columbia | 1 | ac | 20.56 | 12.6914 | 55.56 | 34.2963 | 138 | 24.0892 |  | 567 | 717 | 135.526 | 171.3795 | 0.9 | 121.9734 | 154.2415 | Parkland JCT | BC_PLD_JCT | Dawson Creek | BC_DAW_DSS |  |  | 318
| 1L381 | BC Hydro | British Columbia | 1 | ac | 110 | 67.9012 | 167.33 | 103.2901 | 138 | 72.5495 |  | 430 | 545 | 102.7799 | 130.2675 | 0.9 | 92.5019 | 117.2408 | Aiyansh | BC_AYH_DSS | Ellsworth JCT | BC_EWL_JCT |  |  | 319
| 1L381EWL | BC Hydro | British Columbia | 1 | ac | 0.067789 | 0.041845 | 0.067789 | 0.041845 | 138 | 0.029391 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Ellsworth JCT | BC_EWL_JCT | Ellsworth | BC_EWL_DSS |  |  | 320
| 1L381 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 167.33 | 103.2901 | 138 | 72.5495 |  | 430 | 545 | 102.7799 | 130.2675 | 0.9 | 92.5019 | 117.2408 | Ellsworth JCT | BC_EWL_JCT | Meziadin JCT | BC_MEZ_JCT |  |  | 321
| 1L381MEZ | BC Hydro | British Columbia | 1 | ac | 0.104 | 0.064199 | 0.104 | 0.064199 | 138 | 0.045092 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Meziadin JCT | BC_MEZ_JCT | Meziadin | BC_MEZ_DSS |  |  | 322
| 1L381 | BC Hydro | British Columbia | 1 | ac | 37.33 | 23.0432 | 167.33 | 103.2901 | 138 | 72.5495 |  | 430 | 545 | 102.7799 | 130.2675 | 0.9 | 92.5019 | 117.2408 | Meziadin JCT | BC_MEZ_JCT | Long Lake | BC_LNT_DSS |  |  | 323
| 1L384 | BC Hydro | British Columbia | 1 | ac | 40 | 24.6914 | 102.82 | 63.4691 | 138 | 44.5798 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | Glenannan | BC_GLN_DSS | Pinnacle Pellets JCT | BC_PBL_JCT |  |  | 324
| 1L384PBL | BC Hydro | British Columbia | 1 | ac | 0.10721 | 0.066178 | 0.10721 | 0.066178 | 138 | 0.046483 | 3 |  |  | 0 | 0 | 0.9 | 141 | 156 | Pinnacle Pellets JCT | BC_PBL_JCT | Pinnacle Pellets | BC_PBL_ISS |  |  | 325
| 1L384 | BC Hydro | British Columbia | 1 | ac | 12.82 | 7.9136 | 102.82 | 63.4691 | 138 | 44.5798 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | Pinnacle Pellets JCT | BC_PBL_JCT | Burns Lake JCT | BC_BRN_JCT |  |  | 326
| 1L384BRN | BC Hydro | British Columbia | 1 | ac | 2.6512 | 1.6366 | 2.6512 | 1.6366 | 138 | 1.1495 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | Burns Lake JCT | BC_BRN_JCT | Burns Lake | BC_BRN_DSS |  |  | 327
| 1L384 | BC Hydro | British Columbia | 1 | ac | 50 | 30.8642 | 102.82 | 63.4691 | 138 | 44.5798 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | Burns Lake JCT | BC_BRN_JCT | Topley | BC_TPY_DSS |  |  | 328
| 1L385 | BC Hydro | British Columbia | 1 | ac | 40.1158 | 24.7628 | 40.1158 | 24.7628 | 138 | 17.393 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | Telkwa | BC_TKW_DSS | Smithers | BC_SRS_DSS |  |  | 329
| 1L387 | BC Hydro | British Columbia | 1 | ac | 105.7432 | 65.2736 | 105.7432 | 65.2736 | 138 | 45.8472 |  | 265 | 440 | 63.3411 | 105.1701 | 0.9 | 57.007 | 94.6531 | Skeena | BC_SKA_DSS | Aiyansh | BC_AYH_DSS |  |  | 330
| 1L390 | BC Hydro | British Columbia | 1 | ac | 43.2454 | 26.6947 | 43.2454 | 26.6947 | 138 | 18.75 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | Topley | BC_TPY_DSS | Babine Lake | BC_BAB_DSS |  |  | 331
| 1L391 | BC Hydro | British Columbia | 1 | ac | 4.3 | 2.6543 | 94.3 | 58.2099 | 138 | 40.8858 |  | 490 | 595 | 117.1213 | 142.2187 | 0.9 | 105.4091 | 127.9968 | Houston | BC_HUS_DSS | Houston Forest Products | BC_HFP_ISS |  |  | 332
| 1L391 | BC Hydro | British Columbia | 1 | ac | 90 | 55.5556 | 94.3 | 58.2099 | 138 | 40.8858 |  | 490 | 595 | 117.1213 | 142.2187 | 0.9 | 105.4091 | 127.9968 | Houston Forest Products | BC_HFP_ISS | Huckleberry | BC_HML_DSS |  |  | 333
| 1L392 | BC Hydro | British Columbia | 1 | ac | 72.3192 | 44.6415 | 72.3192 | 44.6415 | 138 | 31.3555 |  | 485 | 590 | 115.9262 | 141.0236 | 0.9 | 104.3335 | 126.9212 | Smithers | BC_SRS_DSS | Hazelton | BC_HZN_DSS |  |  | 334
| 1L393 | BC Hydro | British Columbia | 1 | ac | 4.2329 | 2.6129 | 4.2329 | 2.6129 | 138 | 1.8352 |  | 255 | 440 | 60.9509 | 105.1701 | 0.9 | 54.8558 | 94.6531 | Houston | BC_HUS_DSS | Confor Houston Sawmill | BC_NHS_ISS |  |  | 335
| 1L393EQU | BC Hydro | British Columbia | 1 | ac | 2.956 | 1.8247 | 2.956 | 1.8247 | 138 | 1.2816 |  | 255 | 440 | 60.9509 | 105.1701 | 0.9 | 54.8558 | 94.6531 | Houston | BC_HUS_DSS | Equity Silver | BC_EQU_ISS |  |  | 336
| 1L396 | BC Hydro | British Columbia | 1 | ac | 18.1089 | 11.1784 | 18.1089 | 11.1784 | 138 | 7.8515 |  | 503 | 618 | 120.2286 | 147.7162 | 0.9 | 108.2057 | 132.9446 | Houston | BC_HUS_DSS | Telkwa | BC_TKW_DSS |  |  | 337
| 1L398 | BC Hydro | British Columbia | 1 | ac | 33.2558 | 20.5283 | 33.2558 | 20.5283 | 138 | 14.4188 |  | 255 | 440 | 60.9509 | 105.1701 | 0.9 | 54.8558 | 94.6531 | Topley | BC_TPY_DSS | Houston | BC_HUS_DSS |  |  | 338
| 1L402 | BC Hydro | British Columbia | 1 | ac | 6.27 | 3.8704 | 7.27 | 4.4877 | 138 | 3.1521 |  | 430 | 545 | 102.7799 | 130.2675 | 0.9 | 92.5019 | 117.2408 | Long Lake | BC_LNT_DSS | Westmin Resources JCT | BC_WNR_JCT |  |  | 339
| 1L402WRN | BC Hydro | British Columbia | 1 | ac | 0.026838 | 0.016567 | 0.026838 | 0.016567 | 138 | 0.011636 |  | 280 | 450 | 66.9264 | 107.5604 | 0.9 | 60.2338 | 96.8043 | Westmin Resources JCT | BC_WNR_JCT | Westmin Resources | BC_WNR_ISS |  |  | 340
| 1L402 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 7.27 | 4.4877 | 138 | 3.1521 |  | 430 | 545 | 102.7799 | 130.2675 | 0.9 | 92.5019 | 117.2408 | Westmin Resources JCT | BC_WNR_JCT | Stewart | BC_STW_DSS |  |  | 341
| 1L403 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 16 | 9.8765 | 138 | 6.9371 |  | 430 | 545 | 102.7799 | 130.2675 | 0.9 | 92.5019 | 117.2408 | Long Lake | BC_LNT_DSS | Brucejack TS | BC_BJT_TSS |  |  | 342
| 1L403BJK | BC Hydro | British Columbia | 1 | ac | 66 | 40.7407 | 66 | 40.7407 | 138 | 28.6157 |  | 430 | 545 | 102.7799 | 130.2675 | 0.9 | 92.5019 | 117.2408 | Brucejack TS | BC_BJT_TSS | Brucejack Mine | BC_BJK_ISS |  |  | 343
| 1L403 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 16 | 9.8765 | 138 | 6.9371 |  | 430 | 545 | 102.7799 | 130.2675 | 0.9 | 92.5019 | 117.2408 | Brucejack TS | BC_BJT_TSS | Long Lake GS | BC_LNL_GSS |  |  | 344
| 2L001 | BC Hydro | British Columbia | 1 | ac | 7.92 | 4.8889 | 92.92 | 57.358 | 230 | 44.6016 |  | 505 | 884 | 201.1777 | 352.1606 | 0.9 | 181.0599 | 316.9445 | Function Junction | BC_FCN_DSS | Rainbow JCT | BC_RBW_JCT |  |  | 345
| 2L001RBW | BC Hydro | British Columbia | 1 | ac | 0.45306 | 0.27967 | 0.45306 | 0.27967 | 230 | 0.21747 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Rainbow JCT | BC_RBW_JCT | Rainbow | BC_RBW_DSS |  |  | 346
| 2L001 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 92.92 | 57.358 | 230 | 44.6016 |  | 505 | 884 | 201.1777 | 352.1606 | 0.9 | 181.0599 | 316.9445 | Rainbow JCT | BC_RBW_JCT | Tisdall | BC_TIS_DSS |  |  | 347
| 2L001 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 92.92 | 57.358 | 230 | 44.6016 |  | 505 | 884 | 201.1777 | 352.1606 | 0.9 | 181.0599 | 316.9445 | Tisdall | BC_TIS_DSS | Pemberton JCT | BC_PEM_JCT |  |  | 348
| 2L001PEM | BC Hydro | British Columbia | 1 | ac | 0.34892 | 0.21539 | 0.34892 | 0.21539 | 230 | 0.16748 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Pemberton JCT | BC_PEM_JCT | Pemberton | BC_PEM_DSS |  |  | 349
| 2L001 | BC Hydro | British Columbia | 1 | ac | 65 | 40.1235 | 92.92 | 57.358 | 230 | 44.6016 |  | 505 | 884 | 201.1777 | 352.1606 | 0.9 | 181.0599 | 316.9445 | Pemberton JCT | BC_PEM_JCT | Bridge River TS | BC_BRT_TSS |  |  | 350
| 2L002 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 67.43 | 41.6235 | 230 | 32.3664 |  | 952 | 1200 | 379.2498 | 478.046 | 0.9 | 341.3249 | 430.2414 | Tisdall | BC_TIS_DSS | Rutherford Creek JCT | BC_RUT_JCT |  |  | 351
| 2L002RUT | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 230 | 0.48 |  | 952 | 1200 | 379.2498 | 478.046 | 0.9 | 341.3249 | 430.2414 | Rutherford Creek JCT | BC_RUT_JCT | Rutherford Creek GS | BC_RUT_GSS |  |  | 352
| 2L002 | BC Hydro | British Columbia | 1 | ac | 12.43 | 7.6728 | 67.43 | 41.6235 | 230 | 32.3664 |  | 952 | 1200 | 379.2498 | 478.046 | 0.9 | 341.3249 | 430.2414 | Rutherford Creek JCT | BC_RUT_JCT | Rainbow JCT | BC_RBW_JCT |  |  | 353
| 2L002RBW | BC Hydro | British Columbia | 1 | ac | 0.43349 | 0.26759 | 0.43349 | 0.26759 | 230 | 0.20808 |  | 1047 | 1274 | 417.0952 | 507.5255 | 0.9 | 375.3856 | 456.773 | Rainbow JCT | BC_RBW_JCT | Rainbow | BC_RBW_DSS |  |  | 354
| 2L002 | BC Hydro | British Columbia | 1 | ac | 50 | 30.8642 | 67.43 | 41.6235 | 230 | 32.3664 |  | 952 | 1200 | 379.2498 | 478.046 | 0.9 | 341.3249 | 430.2414 | Rainbow JCT | BC_RBW_JCT | Cheekye | BC_CKY_DSS |  |  | 355
| 2L003 | BC Hydro | British Columbia | 1 | ac | 5.2716 | 3.2541 | 5.2716 | 3.2541 | 230 | 2.5304 |  | 995 | 1210 | 396.3798 | 482.0297 | 0.9 | 356.7418 | 433.8268 | Walters | BC_WLT_DSS | Horne Payne | BC_HPN_DSS |  |  | 356
| 2L004 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 22.6759 | 13.9975 | 230 | 10.8844 |  | 990 | 1220 | 394.388 | 486.0135 | 0.9 | 354.9492 | 437.4121 | Ingledow | BC_ING_DSS | Cambie JCT | BC_CAM_JCT |  |  | 357
| 2L004 | BC Hydro | British Columbia | 1 | ac | 0.075922 | 0.046866 | 22.6759 | 13.9975 | 230 | 10.8844 |  | 990 | 1220 | 394.388 | 486.0135 | 0.9 | 354.9492 | 437.4121 | Cambie JCT | BC_CAM_JCT | Cambie | BC_CAM_DSS |  |  | 358
| 2L004 | BC Hydro | British Columbia | 1 | ac | 4.6 | 2.8395 | 22.6759 | 13.9975 | 230 | 10.8844 |  | 990 | 1220 | 394.388 | 486.0135 | 0.9 | 354.9492 | 437.4121 | Cambie JCT | BC_CAM_JCT | Kidd #2 | BC_KI2_DSS |  |  | 359
| 2L005 | BC Hydro | British Columbia | 1 | ac | 38.4717 | 23.7479 | 38.4717 | 23.7479 | 230 | 18.4664 |  | 505 | 884 | 201.1777 | 352.1606 | 0.9 | 181.0599 | 316.9445 | Function Junction | BC_FCN_DSS | Cheekye | BC_CKY_DSS |  |  | 360
| 2L006 | BC Hydro | British Columbia | 1 | ac | 2.85 | 1.7593 | 16.85 | 10.4012 | 230 | 8.088 |  | 2084 | 2540 | 830.2066 | 1011.8641 | 0.9 | 747.1859 | 910.6777 | Ingledow | BC_ING_DSS | Strawberry Hill JCT | BC_SYH_JCT |  |  | 361
| 2L006SYH | BC Hydro | British Columbia | 1 | ac | 0.044051 | 0.027192 | 0.044051 | 0.027192 | 230 | 0.021145 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Strawberry Hill JCT | BC_SYH_JCT | Strawberry Hill | BC_SYH_DSS |  |  | 362
| 2L006 | BC Hydro | British Columbia | 1 | ac | 14 | 8.642 | 16.85 | 10.4012 | 230 | 8.088 |  | 2084 | 2540 | 830.2066 | 1011.8641 | 0.9 | 747.1859 | 910.6777 | Strawberry Hill JCT | BC_SYH_JCT | Arnott | BC_ARN_DSS |  |  | 363
| 2L009 | BC Hydro | British Columbia | 1 | ac | 60.3657 | 37.2628 | 60.3657 | 37.2628 | 230 | 28.9756 |  | 980 | 1193 | 390.4043 | 475.2574 | 0.9 | 351.3638 | 427.7317 | Cheekye | BC_CKY_DSS | Lynn Valley | BC_LYN_DSS |  |  | 364
| 2L010 | BC Hydro | British Columbia | 1 | ac | 16.9413 | 10.4576 | 16.9413 | 10.4576 | 230 | 8.1318 |  | 585 | 933 | 233.0474 | 371.6808 | 0.9 | 209.7427 | 334.5127 | Ingledow | BC_ING_DSS | Arnott | BC_ARN_DSS |  |  | 365
| 2L011 | BC Hydro | British Columbia | 1 | ac | 14.3858 | 8.8801 | 14.3858 | 8.8801 | 230 | 6.9052 |  | 840 | 1160 | 334.6322 | 462.1112 | 0.9 | 301.169 | 415.9 | Burrard | BC_BSY_TSS | Walters | BC_WLT_DSS |  |  | 366
| 2L012 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 19.8 | 12.2222 | 230 | 9.504 |  | 542 | 1021 | 215.9175 | 406.7375 | 0.9 | 194.3257 | 366.0637 | Cheekye | BC_CKY_DSS | Ashlu JCT | BC_ASL_JCT |  |  | 367
| 2L012ASL | BC Hydro | British Columbia | 1 | ac | 2.8191 | 1.7402 | 2.8191 | 1.7402 | 230 | 1.3532 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Ashlu JCT | BC_ASL_JCT | Ashlu GS | BC_ASL_GSS |  |  | 368
| 2L012 | BC Hydro | British Columbia | 1 | ac | 1.8 | 1.1111 | 19.8 | 12.2222 | 230 | 9.504 |  | 542 | 1021 | 215.9175 | 406.7375 | 0.9 | 194.3257 | 366.0637 | Ashlu JCT | BC_ASL_JCT | Cheakamus GS | BC_CMS_DFS |  |  | 369
| 2L013 | BC Hydro | British Columbia | 1 | ac | 60.3035 | 37.2244 | 60.3035 | 37.2244 | 230 | 28.9457 |  | 899 | 1167 | 358.1361 | 464.8998 | 0.9 | 322.3225 | 418.4098 | Cheekye | BC_CKY_DSS | Cypress | BC_CYP_DSS |  |  | 370
| 2L014 | BC Hydro | British Columbia | 1 | ac | 22.8951 | 14.1328 | 22.8951 | 14.1328 | 230 | 10.9896 |  | 850 | 1102 | 338.6159 | 439.0056 | 0.9 | 304.7543 | 395.105 | Cypress | BC_CYP_DSS | Walters | BC_WLT_DSS |  |  | 371
| 2L017 | BC Hydro | British Columbia | 1 | ac | 3.8768 | 2.3931 | 3.8768 | 2.3931 | 230 | 1.8609 |  | 980 | 1193 | 390.4043 | 475.2574 | 0.9 | 351.3638 | 427.7317 | Lynn Valley | BC_LYN_DSS | Walters | BC_WLT_DSS |  |  | 372
| 2L019 | BC Hydro | British Columbia | 1 | ac | 1.671 | 1.0315 | 1.671 | 1.0315 | 230 | 0.80206 |  | 508 | 891 | 202.3728 | 354.9492 | 0.9 | 182.1355 | 319.4543 | Bridge River 1 GS | BC_BR1_DFS | Bridge River TS | BC_BRT_TSS |  |  | 373
| 2L020 | BC Hydro | British Columbia | 1 | ac | 3.364 | 2.0765 | 3.364 | 2.0765 | 230 | 1.6147 |  | 719 | 916 | 286.4292 | 364.9085 | 0.9 | 257.7863 | 328.4176 | Cathedral Square | BC_CSQ_DSS | Mount Pleasant | BC_MPT_DSS |  |  | 374
| 2L022 | BC Hydro | British Columbia | 1 | ac | 22.769 | 14.0549 | 22.769 | 14.0549 | 230 | 10.9291 |  | 989 | 1200 | 393.9896 | 478.046 | 0.9 | 354.5906 | 430.2414 | Meridian | BC_MDN_DSS | Whalley | BC_WHY_DSS |  |  | 375
| 2L027 | BC Hydro | British Columbia | 1 | ac | 5.2747 | 3.256 | 5.2747 | 3.256 | 230 | 2.5318 |  | 989 | 1200 | 393.9896 | 478.046 | 0.9 | 354.5906 | 430.2414 | Ingledow | BC_ING_DSS | Whalley | BC_WHY_DSS |  |  | 376
| 2L029 | BC Hydro | British Columbia | 1 | ac | 0.03 | 0.018519 | 150.03 | 92.6111 | 230 | 72.0144 |  | 1301 | 1591 | 518.2816 | 633.8094 | 0.9 | 466.4534 | 570.4284 | Saltery Bay | BC_SAY_DSS | Plutonic TS | BC_PSY_TSS |  |  | 377
| 2L029 | BC Hydro | British Columbia | 1 | ac | 130 | 80.2469 | 150.03 | 92.6111 | 230 | 72.0144 |  | 1301 | 1591 | 518.2816 | 633.8094 | 0.9 | 466.4534 | 570.4284 | Plutonic TS | BC_PSY_TSS | Jimmie Creek GS | BC_JMC_GSS |  |  | 378
| 2L029 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 150.03 | 92.6111 | 230 | 72.0144 |  | 1301 | 1591 | 518.2816 | 633.8094 | 0.9 | 466.4534 | 570.4284 | Jimmie Creek GS | BC_JMC_GSS | East Toba River GS | BC_ETR_GSS |  |  | 379
| 2L029MTC | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 20 | 12.3457 | 230 | 9.6 |  | 1301 | 1591 | 518.2816 | 633.8094 | 0.9 | 466.4534 | 570.4284 | Jimmie Creek GS | BC_JMC_GSS | Montrose Creek GS | BC_MTC_GSS |  |  | 380
| 2L030 | BC Hydro | British Columbia | 1 | ac | 1.1131 | 0.68707 | 1.1131 | 0.68707 | 230 | 0.53427 |  | 650 | 830 | 258.9416 | 330.6485 | 0.9 | 233.0474 | 297.5836 | Murrin | BC_MUR_DSS | Cathedral Square | BC_CSQ_DSS |  |  | 381
| 2L031 | BC Hydro | British Columbia | 1 | ac | 1.1131 | 0.68707 | 1.1131 | 0.68707 | 230 | 0.53427 |  | 650 | 830 | 258.9416 | 330.6485 | 0.9 | 233.0474 | 297.5836 | Murrin | BC_MUR_DSS | Cathedral Square | BC_CSQ_DSS |  |  | 382
| 2L032 | BC Hydro | British Columbia | 1 | ac | 8.6182 | 5.3198 | 8.6182 | 5.3198 | 230 | 4.1367 |  | 1070 | 1230 | 426.2577 | 489.9972 | 0.9 | 383.6319 | 440.9975 | Cathedral Square | BC_CSQ_DSS | Horne Payne | BC_HPN_DSS |  |  | 383
| 2L033 | BC Hydro | British Columbia | 1 | ac | 8.7231 | 5.3846 | 8.7231 | 5.3846 | 230 | 4.1871 |  | 1250 | 1250 | 497.9646 | 497.9646 | 0.9 | 448.1681 | 448.1681 | Horne Payne | BC_HPN_DSS | Cathedral Square | BC_CSQ_DSS |  |  | 384
| 2L038 | BC Hydro | British Columbia | 1 | ac | 6.3908 | 3.9449 | 6.3908 | 3.9449 | 230 | 3.0676 |  | 2050 | 2560 | 816.662 | 1019.8315 | 0.9 | 734.9958 | 917.8484 | Meridian | BC_MDN_DSS | Como Lake | BC_COK_DSS |  |  | 385
| 2L039 | BC Hydro | British Columbia | 1 | ac | 15.5063 | 9.5718 | 15.5063 | 9.5718 | 230 | 7.443 |  | 950 | 950 | 378.4531 | 378.4531 | 0.9 | 340.6078 | 340.6078 | Como Lake | BC_COK_DSS | Newell | BC_NEL_DSS |  |  | 386
| 2L040 | BC Hydro | British Columbia | 1 | ac | 7.39 | 4.5617 | 12.39 | 7.6481 | 230 | 5.9472 |  | 950 | 950 | 378.4531 | 378.4531 | 0.9 | 340.6078 | 340.6078 | Newell | BC_NEL_DSS | Barnard | BC_BND_DSS |  |  | 387
| 2L040 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 12.39 | 7.6481 | 230 | 5.9472 |  | 1020 | 1260 | 406.3391 | 501.9483 | 0.9 | 365.7052 | 451.7535 | Barnard | BC_BND_DSS | Burrard | BC_BSY_TSS |  |  | 388
| 2L041 | BC Hydro | British Columbia | 1 | ac | 70.0725 | 43.2546 | 70.0725 | 43.2546 | 230 | 33.6348 |  | 1020 | 1780 | 406.3391 | 709.1016 | 0.9 | 365.7052 | 638.1914 | Bridge River TS | BC_BRT_TSS | Tisdall | BC_TIS_DSS |  |  | 389
| 2L042 | BC Hydro | British Columbia | 1 | ac | 40 | 24.6914 | 49.7 | 30.679 | 230 | 23.856 |  | 1047 | 1274 | 417.0952 | 507.5255 | 0.9 | 375.3856 | 456.773 | Tisdall | BC_TIS_DSS | Boulder Creek JCT | BC_BDH_JCT |  |  | 390
| 2L042BDH | BC Hydro | British Columbia | 1 | ac | 0.5 | 0.30864 | 0.5 | 0.30864 | 230 | 0.24 |  | 1047 | 1274 | 417.0952 | 507.5255 | 0.9 | 375.3856 | 456.773 | Boulder Creek JCT | BC_BDH_JCT | Boulder Creek GS | BC_BDH_GSS |  |  | 391
| 2L042 | BC Hydro | British Columbia | 1 | ac | 9.7 | 5.9877 | 49.7 | 30.679 | 230 | 23.856 |  | 1047 | 1274 | 417.0952 | 507.5255 | 0.9 | 375.3856 | 456.773 | Boulder Creek JCT | BC_BDH_JCT | Upper Lillooet River GS | BC_ULR_GSS |  |  | 392
| 2L044 | BC Hydro | British Columbia | 1 | ac | 4.6338 | 2.8604 | 4.6338 | 2.8604 | 230 | 2.2242 |  | 1173 | 1245 | 467.29 | 495.9727 | 0.9 | 420.561 | 446.3755 | Sperling | BC_SPG_DSS | Mount Pleasant | BC_MPT_DSS |  |  | 393
| 2L045 | BC Hydro | British Columbia | 1 | ac | 5.9993 | 3.7033 | 5.9993 | 3.7033 | 230 | 2.8796 |  | 665 | 825 | 264.9172 | 328.6566 | 0.9 | 238.4255 | 295.791 | Camosun | BC_CSN_DSS | Sperling | BC_SPG_DSS |  |  | 394
| 2L047 | BC Hydro | British Columbia | 1 | ac | 61.5566 | 37.9979 | 61.5566 | 37.9979 | 230 | 29.5472 |  | 530 | 940 | 211.137 | 374.4694 | 0.9 | 190.0233 | 337.0224 | Malaspina | BC_MSA_DSS | Howe Sound Pulp | BC_HSP_ISS |  |  | 395
| 2L048 | BC Hydro | British Columbia | 1 | ac | 28.4702 | 17.5742 | 28.4702 | 17.5742 | 230 | 13.6657 |  | 848 | 1036 | 337.8192 | 412.7131 | 0.9 | 304.0373 | 371.4418 | Malaspina | BC_MSA_DSS | Saltery Bay | BC_SAY_DSS |  |  | 396
| 2L049 | BC Hydro | British Columbia | 1 | ac | 19.3089 | 11.9191 | 19.3089 | 11.9191 | 230 | 9.2683 |  | 840 | 1160 | 334.6322 | 462.1112 | 0.9 | 301.169 | 415.9 | Meridian | BC_MDN_DSS | Horne Payne | BC_HPN_DSS |  |  | 397
| 2L050 | BC Hydro | British Columbia | 1 | ac | 16.9688 | 10.4745 | 16.9688 | 10.4745 | 230 | 8.145 |  | 710 | 840 | 282.8439 | 334.6322 | 0.9 | 254.5595 | 301.169 | Burrard | BC_BSY_TSS | Murrin | BC_MUR_DSS |  |  | 398
| 2L051 | BC Hydro | British Columbia | 1 | ac | 8.97 | 5.537 | 16.97 | 10.4753 | 230 | 8.1456 |  | 1075 | 1247 | 428.2496 | 496.7695 | 0.9 | 385.4246 | 447.0925 | Como Lake | BC_COK_DSS | Barnard | BC_BND_DSS |  |  | 399
| 2L051 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 16.97 | 10.4753 | 230 | 8.1456 |  | 1089 | 1259 | 433.8268 | 501.55 | 0.9 | 390.4441 | 451.395 | Barnard | BC_BND_DSS | Horne Payne | BC_HPN_DSS |  |  | 400
| 2L052 | BC Hydro | British Columbia | 1 | ac | 6.3461 | 3.9174 | 6.3461 | 3.9174 | 230 | 3.0461 |  | 2050 | 2560 | 816.662 | 1019.8315 | 0.9 | 734.9958 | 917.8484 | Meridian | BC_MDN_DSS | Como Lake | BC_COK_DSS |  |  | 401
| 2L053 | BC Hydro | British Columbia | 1 | ac | 7.1096 | 4.3886 | 7.1096 | 4.3886 | 230 | 3.4126 |  | 580 | 705 | 231.0556 | 280.852 | 0.9 | 207.95 | 252.7668 | Murrin | BC_MUR_DSS | Mainwaring | BC_MAN_DSS |  |  | 402
| 2L054 | BC Hydro | British Columbia | 1 | ac | 8.0044 | 4.941 | 8.0044 | 4.941 | 230 | 3.8421 |  | 2050 | 2560 | 816.662 | 1019.8315 | 0.9 | 734.9958 | 917.8484 | Burrard | BC_BSY_TSS | Meridian | BC_MDN_DSS |  |  | 403
| 2L055 | BC Hydro | British Columbia | 1 | ac | 11.1861 | 6.905 | 11.1861 | 6.905 | 230 | 5.3693 |  | 665 | 825 | 264.9172 | 328.6566 | 0.9 | 238.4255 | 295.791 | Mainwaring | BC_MAN_DSS | Camosun | BC_CSN_DSS |  |  | 404
| 2L056 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 23.3 | 14.3827 | 230 | 11.184 |  | 1000 | 1220 | 398.3717 | 486.0135 | 0.9 | 358.5345 | 437.4121 | Ingledow | BC_ING_DSS | Cambie JCT | BC_CAM_JCT |  |  | 405
| 2L056CAM | BC Hydro | British Columbia | 1 | ac | 0.059217 | 0.036554 | 0.059217 | 0.036554 | 230 | 0.028424 |  | 1068 | 1293 | 425.461 | 515.0946 | 0.9 | 382.9149 | 463.5851 | Cambie JCT | BC_CAM_JCT | Cambie | BC_CAM_DSS |  |  | 406
| 2L056 | BC Hydro | British Columbia | 1 | ac | 5.3 | 3.2716 | 23.3 | 14.3827 | 230 | 11.184 |  | 665 | 825 | 264.9172 | 328.6566 | 0.9 | 238.4255 | 295.791 | Cambie JCT | BC_CAM_JCT | Mainwaring | BC_MAN_DSS |  |  | 407
| 2L057 | BC Hydro | British Columbia | 1 | ac | 2.88 | 1.7778 | 16.88 | 10.4198 | 230 | 8.1024 |  | 585 | 933 | 233.0474 | 371.6808 | 0.9 | 209.7427 | 334.5127 | Ingledow | BC_ING_DSS | Strawberry Hill JCT | BC_SYH_JCT |  |  | 408
| 2L057SYH | BC Hydro | British Columbia | 1 | ac | 0.077579 | 0.047889 | 0.077579 | 0.047889 | 230 | 0.037238 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Strawberry Hill JCT | BC_SYH_JCT | Strawberry Hill | BC_SYH_DSS |  |  | 409
| 2L057 | BC Hydro | British Columbia | 1 | ac | 14 | 8.642 | 16.88 | 10.4198 | 230 | 8.1024 |  | 585 | 933 | 233.0474 | 371.6808 | 0.9 | 209.7427 | 334.5127 | Strawberry Hill JCT | BC_SYH_JCT | Arnott | BC_ARN_DSS |  |  | 410
| 2L058 | BC Hydro | British Columbia | 1 | ac | 16.7231 | 10.3229 | 16.7231 | 10.3229 | 230 | 8.0271 |  | 830 | 1090 | 330.6485 | 434.2251 | 0.9 | 297.5836 | 390.8026 | Steveston | BC_STV_DSS | Kidd #2 | BC_KI2_DSS |  |  | 411
| 2L061 | BC Hydro | British Columbia | 1 | ac | 8.0104 | 4.9447 | 8.0104 | 4.9447 | 230 | 3.845 |  | 2050 | 2560 | 816.662 | 1019.8315 | 0.9 | 734.9958 | 917.8484 | Burrard | BC_BSY_TSS | Meridian | BC_MDN_DSS |  |  | 412
| 2L062 | BC Hydro | British Columbia | 1 | ac | 12.4325 | 7.6744 | 12.4325 | 7.6744 | 230 | 5.9676 |  | 830 | 1000 | 330.6485 | 398.3717 | 0.9 | 297.5836 | 358.5345 | Arnott | BC_ARN_DSS | Steveston | BC_STV_DSS |  |  | 413
| 2L063 | BC Hydro | British Columbia | 1 | ac | 2.85 | 1.7593 | 16.85 | 10.4012 | 230 | 8.088 |  | 2084 | 2540 | 830.2066 | 1011.8641 | 0.9 | 747.1859 | 910.6777 | Ingledow | BC_ING_DSS | Strawberry Hill JCT | BC_SYH_JCT |  |  | 414
| 2L063SYH | BC Hydro | British Columbia | 1 | ac | 0.050115 | 0.030935 | 0.050115 | 0.030935 | 230 | 0.024055 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Strawberry Hill JCT | BC_SYH_JCT | Strawberry Hill | BC_SYH_DSS |  |  | 415
| 2L063 | BC Hydro | British Columbia | 1 | ac | 14 | 8.642 | 16.85 | 10.4012 | 230 | 8.088 |  | 2084 | 2540 | 830.2066 | 1011.8641 | 0.9 | 747.1859 | 910.6777 | Strawberry Hill JCT | BC_SYH_JCT | Arnott | BC_ARN_DSS |  |  | 416
| 2L064 | BC Hydro | British Columbia | 1 | ac | 7.9071 | 4.8809 | 7.9071 | 4.8809 | 230 | 3.7954 |  | 605 | 765 | 241.0149 | 304.7543 | 0.9 | 216.9134 | 274.2789 | Kidd #2 | BC_KI2_DSS | Sperling | BC_SPG_DSS |  |  | 417
| 2L074 | BC Hydro | British Columbia | 1 | ac | 6.8643 | 4.2372 | 6.8643 | 4.2372 | 230 | 3.2949 |  | 1700 | 2204 | 677.2319 | 878.0112 | 0.9 | 609.5087 | 790.2101 | Ingledow | BC_ING_DSS | Fleetwood | BC_FLW_DSS |  |  | 418
| 2L075 | BC Hydro | British Columbia | 1 | ac | 9.34 | 5.7654 | 9.34 | 5.7654 | 230 | 4.4832 |  | 1700 | 2204 | 677.2319 | 878.0112 | 0.9 | 609.5087 | 790.2101 | Fleetwood | BC_FLW_DSS | McLellan | BC_MLN_DSS |  |  | 419
| 2L076 | BC Hydro | British Columbia | 1 | ac | 27.5617 | 17.0134 | 27.5617 | 17.0134 | 230 | 13.2296 |  | 1700 | 2204 | 677.2319 | 878.0112 | 0.9 | 609.5087 | 790.2101 | McLellan | BC_MLN_DSS | Mount Lehman | BC_MLE_DSS |  |  | 420
| 2L077 | BC Hydro | British Columbia | 1 | ac | 23.9559 | 14.7876 | 23.9559 | 14.7876 | 230 | 11.4988 |  | 1700 | 2204 | 677.2319 | 878.0112 | 0.9 | 609.5087 | 790.2101 | Clayburn | BC_CBN_DSS | Atchelitz | BC_ALZ_DSS |  |  | 421
| 2L078 | BC Hydro | British Columbia | 1 | ac | 19.1324 | 11.8101 | 19.1324 | 11.8101 | 230 | 9.1835 |  | 1700 | 2204 | 677.2319 | 878.0112 | 0.9 | 609.5087 | 790.2101 | Atchelitz | BC_ALZ_DSS | Rosedale | BC_ROS_DSS |  |  | 422
| 2L079 | BC Hydro | British Columbia | 1 | ac | 7.9358 | 4.8987 | 7.9358 | 4.8987 | 230 | 3.8092 |  | 1700 | 2204 | 677.2319 | 878.0112 | 0.9 | 609.5087 | 790.2101 | Mount Lehman | BC_MLE_DSS | Clayburn | BC_CBN_DSS |  |  | 423
| 2L086 | BC Hydro | British Columbia | 1 | ac | 84.4604 | 52.136 | 84.4604 | 52.136 | 230 | 40.541 |  | 899 | 1137 | 358.1361 | 452.9486 | 0.9 | 322.3225 | 407.6537 | Kelly Lake | BC_KLY_DSS | Hundred Mile House | BC_HMH_DSS |  |  | 424
| 2L090 | BC Hydro | British Columbia | 1 | ac | 77.0042 | 47.5335 | 77.0042 | 47.5335 | 230 | 36.962 |  | 510 | 890 | 203.1696 | 354.5508 | 0.9 | 182.8526 | 319.0957 | Bridge River TS | BC_BRT_TSS | Kelly Lake | BC_KLY_DSS |  |  | 425
| 2L091 | BC Hydro | British Columbia | 1 | ac | 75.7164 | 46.7385 | 75.7164 | 46.7385 | 230 | 36.3439 |  | 510 | 890 | 203.1696 | 354.5508 | 0.9 | 182.8526 | 319.0957 | Bridge River TS | BC_BRT_TSS | Kelly Lake | BC_KLY_DSS |  |  | 426
| 2L092 | BC Hydro | British Columbia | 1 | ac | 89.593 | 55.3043 | 89.593 | 55.3043 | 230 | 43.0046 |  | 512 | 1940 | 203.9663 | 772.8411 | 0.9 | 183.5697 | 695.557 | Kelly Lake | BC_KLY_DSS | Savona | BC_SVA_DSS |  |  | 427
| 2L093 | BC Hydro | British Columbia | 1 | ac | 90.8048 | 56.0524 | 90.8048 | 56.0524 | 230 | 43.5863 |  | 512 | 1940 | 203.9663 | 772.8411 | 0.9 | 183.5697 | 695.557 | Kelly Lake | BC_KLY_DSS | Savona | BC_SVA_DSS |  |  | 428
| 2L094 | BC Hydro | British Columbia | 1 | ac | 152.4 | 94.0741 | 152.4 | 94.0741 | 230 | 73.152 |  | 527 | 942 | 209.9419 | 375.2661 | 0.9 | 188.9477 | 337.7395 | Kelly Lake | BC_KLY_DSS | Soda Creek | BC_SCK_DSS |  |  | 429
| 2L095 | BC Hydro | British Columbia | 1 | ac | 85.3368 | 52.677 | 85.3368 | 52.677 | 230 | 40.9617 |  | 510 | 942 | 203.1696 | 375.2661 | 0.9 | 182.8526 | 337.7395 | Soda Creek | BC_SCK_DSS | Red Bluff | BC_RBF_DSS |  |  | 430
| 2L096 | BC Hydro | British Columbia | 1 | ac | 95.3237 | 58.8418 | 95.3237 | 58.8418 | 230 | 45.7554 |  | 770 | 1020 | 306.7462 | 406.3391 | 0.9 | 276.0716 | 365.7052 | Barlow | BC_BLW_DSS | Williston | BC_WSN_DSS |  |  | 431
| 2L097 | BC Hydro | British Columbia | 1 | ac | 33.3089 | 20.561 | 33.3089 | 20.561 | 230 | 15.9883 |  | 950 | 1180 | 378.4531 | 470.0786 | 0.9 | 340.6078 | 423.0707 | Williston | BC_WSN_DSS | Salmon Valley | BC_SVY_DSS |  |  | 432
| 2L099 | BC Hydro | British Columbia | 1 | ac | 59.5888 | 36.7832 | 59.5888 | 36.7832 | 230 | 28.6026 |  | 450 | 1075 | 179.2673 | 428.2496 | 0.9 | 161.3405 | 385.4246 | Minette | BC_MIN_DSS | Skeena | BC_SKA_DSS |  |  | 433
| 2L100 | BC Hydro | British Columbia | 1 | ac | 1.751 | 1.0809 | 76.751 | 47.3772 | 287 | 35.4632 |  | 1325 | 1620 | 658.6556 | 805.2997 | 0.9 | 592.7901 | 724.7697 | Minette | BC_MIN_DSS | Methanex | BC_MHX_ISS |  |  | 434
| 2L100 | BC Hydro | British Columbia | 1 | ac | 75 | 46.2963 | 76.751 | 47.3772 | 287 | 35.4632 |  | 1325 | 1620 | 658.6556 | 805.2997 | 0.9 | 592.7901 | 724.7697 | Methanex | BC_MHX_ISS | Kemano GS | BC_KMO_GSS |  | Line name assumed | 435
| 2L101 | BC Hydro | British Columbia | 1 | ac | 125.4737 | 77.4529 | 125.4737 | 77.4529 | 287 | 57.9758 |  | 640 | 1275 | 318.1431 | 633.8007 | 0.9 | 286.3288 | 570.4206 | Skeena | BC_SKA_DSS | Rupert | BC_RUP_DSS |  |  | 436
| 2L102 | BC Hydro | British Columbia | 1 | ac | 340.6905 | 210.3028 | 340.6905 | 210.3028 | 287 | 157.4179 |  | 1812 | 2352 | 900.7426 | 1169.1759 | 0.9 | 810.6684 | 1052.2583 | Skeena | BC_SKA_DSS | Bob Quinn | BC_BQN_DSS |  |  | 437
| 2L103 | BC Hydro | British Columbia | 1 | ac | 2.5031 | 1.5451 | 2.5031 | 1.5451 | 287 | 1.1566 |  | 632 | 1316 | 314.1663 | 654.1817 | 0.9 | 282.7497 | 588.7636 | Kitimat | BC_KIT_DSS | Minette | BC_MIN_DSS |  |  | 438
| 2L105 | BC Hydro | British Columbia | 1 | ac | 1.5 | 0.92593 | 1.5 | 0.92593 | 287 | 0.69308 |  | 670 | 1190 | 333.056 | 591.5473 | 0.9 | 299.7504 | 532.3926 | Minette | BC_MIN_DSS | Eurocan | BC_EUR_ISS |  |  | 439
| 2L112 | BC Hydro | British Columbia | 1 | ac | 0.86498 | 0.53394 | 0.86498 | 0.53394 | 230 | 0.41519 | [5 empty] | 0.9 | 380 | 380 | Nelway | BC_NLY_DSS | INT Nelway BPA | XX_BCUS2_INT |  |  | 440
| 2L113 | BC Hydro | British Columbia | 1 | ac | 77.2951 | 47.713 | 77.2951 | 47.713 | 230 | 37.1017 |  | 1042 | 1341 | 415.1033 | 534.2164 | 0.9 | 373.593 | 480.7948 | Cranbrook | BC_CBK_DSS | Natal | BC_NTL_DSS |  |  | 441
| 2L123 | BC Hydro | British Columbia | 1 | ac | 45 | 27.7778 | 96.11 | 59.3272 | 230 | 46.1328 |  | 1636 | 2233 | 651.7361 | 889.564 | 0.9 | 586.5625 | 800.6076 | Sahtlam | BC_SAT_DSS | Harewood West JCT | BC_HWW_JCT |  |  | 442
| 2L123HWW | BC Hydro | British Columbia | 1 | ac | 12.1984 | 7.5299 | 12.1984 | 7.5299 | 230 | 5.8552 |  | 2100 | 2568 | 836.5805 | 1023.0185 | 0.9 | 752.9225 | 920.7166 | Harewood West JCT | BC_HWW_JCT | Harewood West | BC_HWW_DSS |  |  | 443
| 2L123 | BC Hydro | British Columbia | 1 | ac | 51.11 | 31.5494 | 96.11 | 59.3272 | 230 | 46.1328 |  | 1636 | 2233 | 651.7361 | 889.564 | 0.9 | 586.5625 | 800.6076 | Harewood West JCT | BC_HWW_JCT | Dunsmuir | BC_DMR_DSS |  |  | 444
| 2L125 | BC Hydro | British Columbia | 1 | ac | 6.9913 | 4.3156 | 6.9913 | 4.3156 | 230 | 3.3558 |  | 2085 | 3289 | 830.605 | 1310.2445 | 0.9 | 747.5445 | 1179.22 | Sahtlam | BC_SAT_DSS | Vancouver Island TS | BC_VIT_TSS |  |  | 445
| 2L126 | BC Hydro | British Columbia | 1 | ac | 54.1089 | 33.4005 | 54.1089 | 33.4005 | 230 | 25.9723 |  | 1637 | 2233 | 652.1344 | 889.564 | 0.9 | 586.921 | 800.6076 | Sahtlam | BC_SAT_DSS | Pike Lake | BC_PIK_DSS |  |  | 446
| 2L128 | BC Hydro | British Columbia | 1 | ac | 45 | 27.7778 | 95.94 | 59.2222 | 230 | 46.0512 |  | 1637 | 2233 | 652.1344 | 889.564 | 0.9 | 586.921 | 800.6076 | Sahtlam | BC_SAT_DSS | Harewood West JCT | BC_HWW_JCT |  |  | 447
| 2L128HWW | BC Hydro | British Columbia | 1 | ac | 12.1692 | 7.5118 | 12.1692 | 7.5118 | 230 | 5.8412 |  | 2100 | 2568 | 836.5805 | 1023.0185 | 0.9 | 752.9225 | 920.7166 | Harewood West JCT | BC_HWW_JCT | Harewood West | BC_HWW_DSS |  |  | 448
| 2L128 | BC Hydro | British Columbia | 1 | ac | 50.94 | 31.4444 | 95.94 | 59.2222 | 230 | 46.0512 |  | 1637 | 2233 | 652.1344 | 889.564 | 0.9 | 586.921 | 800.6076 | Harewood West JCT | BC_HWW_JCT | Dunsmuir | BC_DMR_DSS |  |  | 449
| 2L129 | BC Hydro | British Columbia | 1 | ac | 67.2363 | 41.5039 | 67.2363 | 41.5039 | 230 | 32.2734 |  | 1619 | 1925 | 644.9638 | 766.8655 | 0.9 | 580.4674 | 690.1789 | Arnott | BC_ARN_DSS | Vancouver Island TS | BC_VIT_TSS |  |  | 450
| 2L130 | BC Hydro | British Columbia | 1 | ac | 6.9775 | 4.3071 | 6.9775 | 4.3071 | 230 | 3.3492 |  | 2085 | 2682 | 830.605 | 1068.4329 | 0.9 | 747.5445 | 961.5896 | Sahtlam | BC_SAT_DSS | Vancouver Island TS | BC_VIT_TSS |  |  | 451
| 2L131 | BC Hydro | British Columbia | 1 | ac | 12.3966 | 7.6522 | 12.3966 | 7.6522 | 230 | 5.9504 |  | 972 | 1301 | 387.2173 | 518.2816 | 0.9 | 348.4956 | 466.4534 | Pike Lake | BC_PIK_DSS | Keating | BC_KTG_DSS |  |  | 452
| 2L132 | BC Hydro | British Columbia | 1 | ac | 12.4103 | 7.6607 | 12.4103 | 7.6607 | 230 | 5.9569 |  | 972 | 1301 | 387.2173 | 518.2816 | 0.9 | 348.4956 | 466.4534 | Pike Lake | BC_PIK_DSS | Keating | BC_KTG_DSS |  |  | 453
| 2L142 | BC Hydro | British Columbia | 1 | ac | 4.1609 | 2.5685 | 4.1609 | 2.5685 | 230 | 1.9973 |  | 824 | 913 | 328.2583 | 363.7133 | 0.9 | 295.4324 | 327.342 | George Tripp | BC_GTP_DSS | Horsey | BC_HSY_DSS |  |  | 454
| 2L143 | BC Hydro | British Columbia | 1 | ac | 2.5779 | 1.5913 | 2.5779 | 1.5913 | 230 | 1.2374 |  | 1133 | 1204 | 451.3551 | 479.6395 | 0.9 | 406.2196 | 431.6756 | Horsey | BC_HSY_DSS | Esquimalt | BC_ESQ_DSS |  |  | 455
| 2L144 | BC Hydro | British Columbia | 1 | ac | 2.751 | 1.6981 | 2.751 | 1.6981 | 230 | 1.3205 |  | 1637 | 2233 | 652.1344 | 889.564 | 0.9 | 586.921 | 800.6076 | Pike Lake | BC_PIK_DSS | Goward | BC_GOW_DSS |  |  | 456
| 2L145 | BC Hydro | British Columbia | 1 | ac | 3.8176 | 2.3565 | 9.2167 | 5.6893 | 230 | 4.424 |  | 1637 | 2233 | 652.1344 | 889.564 | 0.9 | 586.921 | 800.6076 | Pike Lake | BC_PIK_DSS | Burnett | BC_BNT_DSS |  |  | 457
| 2L145 | BC Hydro | British Columbia | 1 | ac | 5.3991 | 3.3328 | 9.2167 | 5.6893 | 230 | 4.424 |  | 1032 | 1091 | 411.1196 | 434.6235 | 0.9 | 370.0076 | 391.1612 | Burnett | BC_BNT_DSS | Esquimalt | BC_ESQ_DSS |  |  | 458
| 2L146 | BC Hydro | British Columbia | 1 | ac | 7.0614 | 4.3589 | 7.0614 | 4.3589 | 230 | 3.3895 |  | 735 | 870 | 292.8032 | 346.5834 | 0.9 | 263.5229 | 311.925 | Goward | BC_GOW_DSS | Horsey | BC_HSY_DSS |  |  | 459
| 2L154 | BC Hydro | British Columbia | 1 | ac | 148.8604 | 91.8891 | 148.8604 | 91.8891 | 230 | 71.453 |  | 972 | 1301 | 387.2173 | 518.2816 | 0.9 | 348.4956 | 466.4534 | Dunsmuir | BC_DMR_DSS | Gold River | BC_GLD_DSS |  |  | 460
| 2L170 | BC Hydro | British Columbia | 1 | ac | 54.837 | 33.85 | 54.837 | 33.85 | 230 | 26.3218 |  | 1637 | 2099 | 652.1344 | 836.1822 | 0.9 | 586.921 | 752.564 | Sahtlam | BC_SAT_DSS | Pike Lake | BC_PIK_DSS |  |  | 461
| 2L221 | BC Hydro | British Columbia | 1 | ac | 3.3873 | 2.0909 | 3.3873 | 2.0909 | 230 | 1.6259 |  | 1900 | 2400 | 756.9062 | 956.092 | 0.9 | 681.2156 | 860.4828 | Seven Mile GS | BC_SEV_GSS | Selkirk | BC_SEL_TSS |  |  | 462
| 2L222 | BC Hydro | British Columbia | 1 | ac | 3.4137 | 2.1072 | 3.4137 | 2.1072 | 230 | 1.6386 |  | 1900 | 2400 | 756.9062 | 956.092 | 0.9 | 681.2156 | 860.4828 | Seven Mile GS | BC_SEV_GSS | Selkirk | BC_SEL_TSS |  |  | 463
| 2L240 | BC Hydro | British Columbia | 1 | ac | 37.5859 | 23.2012 | 37.5859 | 23.2012 | 230 | 18.0412 |  | 1045 | 1345 | 416.2984 | 535.8099 | 0.9 | 374.6686 | 482.2289 | Ashton Creek | BC_ACK_DSS | Salmon Arm | BC_SAM_DSS |  |  | 464
| 2L253 | BC Hydro | British Columbia | 1 | ac | 11.9947 | 7.4041 | 11.9947 | 7.4041 | 230 | 5.7574 |  | 1045 | 1345 | 416.2984 | 535.8099 | 0.9 | 374.6686 | 482.2289 | Revelstoke GS | BC_REV_GSS | Illecillewaet | BC_ILL_DSS |  |  | 465
| 2L255 | BC Hydro | British Columbia | 1 | ac | 49.9569 | 30.8376 | 49.9569 | 30.8376 | 230 | 23.9793 |  | 1053 | 1277 | 419.4854 | 508.7206 | 0.9 | 377.5368 | 457.8486 | Ashton Creek | BC_ACK_DSS | Vernon TS | BC_VNT_TSS |  |  | 466
| 2L256 | BC Hydro | British Columbia | 1 | ac | 49.9086 | 30.8078 | 49.9086 | 30.8078 | 230 | 23.9561 |  | 1053 | 1277 | 419.4854 | 508.7206 | 0.9 | 377.5368 | 457.8486 | Ashton Creek | BC_ACK_DSS | Vernon TS | BC_VNT_TSS |  |  | 467
| 2L258 | BC Hydro | British Columbia | 1 | ac | 129.8017 | 80.1245 | 129.8017 | 80.1245 | 230 | 62.3048 |  | 1062 | 1357 | 423.0707 | 540.5904 | 0.9 | 380.7637 | 486.5313 | Cranbrook | BC_CBK_DSS | Invermere | BC_INV_DSS |  |  | 468
| 2L259 | BC Hydro | British Columbia | 1 | ac | 111.6767 | 68.9362 | 111.6767 | 68.9362 | 230 | 53.6048 |  | 1070 | 1280 | 426.2577 | 509.9158 | 0.9 | 383.6319 | 458.9242 | Invermere | BC_INV_DSS | Kicking Horse | BC_KHS_DSS |  |  | 469
| 2L265 | BC Hydro | British Columbia | 1 | ac | 63.3567 | 39.1091 | 63.3567 | 39.1091 | 230 | 30.4112 |  | 1045 | 1345 | 416.2984 | 535.8099 | 0.9 | 374.6686 | 482.2289 | Nicola | BC_NIC_DSS | Valleyview | BC_VVW_DSS |  |  | 470
| 2L293 | BC Hydro | British Columbia | 1 | ac | 16.1568 | 9.9733 | 16.1568 | 9.9733 | 230 | 7.7553 |  | 1053 | 1277 | 419.4854 | 508.7206 | 0.9 | 377.5368 | 457.8486 | Selkirk | BC_SEL_TSS | Nelway | BC_NLY_DSS |  |  | 471
| 2L294 | BC Hydro | British Columbia | 1 | ac | 75 | 46.2963 | 161.71 | 99.821 | 230 | 77.6208 |  | 1053 | 1277 | 419.4854 | 508.7206 | 0.9 | 377.5368 | 457.8486 | Nelway | BC_NLY_DSS | AA Lambert | BC_AAL_DSS |  |  | 472
| 2L294 | BC Hydro | British Columbia | 1 | ac | 86.71 | 53.5247 | 161.71 | 99.821 | 230 | 77.6208 |  | 1053 | 1277 | 419.4854 | 508.7206 | 0.9 | 377.5368 | 457.8486 | AA Lambert | BC_AAL_DSS | Cranbrook | BC_CBK_DSS |  |  | 473
| 2L295 | BC Hydro | British Columbia | 1 | ac | 45.854 | 28.3049 | 45.854 | 28.3049 | 230 | 22.0099 |  | 997 | 1209 | 397.1766 | 481.6314 | 0.9 | 357.4589 | 433.4682 | Kootenay Canal GS | BC_KCL_GSS | Selkirk | BC_SEL_TSS |  |  | 474
| 2L299 | BC Hydro | British Columbia | 1 | ac | 45.854 | 28.3049 | 45.854 | 28.3049 | 230 | 22.0099 |  | 997 | 1209 | 397.1766 | 481.6314 | 0.9 | 357.4589 | 433.4682 | Kootenay Canal GS | BC_KCL_GSS | Selkirk | BC_SEL_TSS |  |  | 475
| 2L307 | BC Hydro | British Columbia | 1 | ac | 5.3479 | 3.3012 | 5.3479 | 3.3012 | 230 | 2.567 |  | 1050 | 1275 | 418.2903 | 507.9239 | 0.9 | 376.4612 | 457.1315 | Barlow | BC_BLW_DSS | Quesnel River Pulp | BC_QRP_ISS |  |  | 476
| 2L308 | BC Hydro | British Columbia | 1 | ac | 23.0209 | 14.2104 | 23.0209 | 14.2104 | 230 | 11.05 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | GM Shrum GS | BC_GMS_GSS | Dokie | BC_DKT_DSS |  |  | 477
| 2L309 | BC Hydro | British Columbia | 1 | ac | 51.3384 | 31.6904 | 51.3384 | 31.6904 | 230 | 24.6424 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Dokie | BC_DKT_DSS | Sukunka | BC_SNK_DSS |  |  | 478
| 2L312 | BC Hydro | British Columbia | 1 | ac | 30.5636 | 18.8664 | 30.5636 | 18.8664 | 230 | 14.6705 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Sukunka | BC_SNK_DSS | Sundance Lake | BC_SLS_DSS |  |  | 479
| 2L313 | BC Hydro | British Columbia | 1 | ac | 29.74 | 18.358 | 32.74 | 20.2099 | 230 | 15.7152 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Sukunka | BC_SNK_DSS | Meikle SWS | BC_MKT_SWS |  | DELETIONS and CORRRECTIONS to 2L313 and related lines | 480
| 2L313KGP | BC Hydro | British Columbia | 1 | ac | 0.014502 | 0.008952 | 16.0145 | 9.8855 | 230 | 7.687 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Sukunka | BC_SNK_DSS | Kwoen JCT | BC_KGP_JCT |  | DELETIONS and CORRRECTIONS to 2L313 and related lines | 481
| 2L313KGP | BC Hydro | British Columbia | 1 | ac | 16 | 9.8765 | 16.0145 | 9.8855 | 230 | 7.687 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Kwoen JCT | BC_KGP_JCT | Kwoen | BC_KGP_ISS |  | DELETIONS and CORRRECTIONS to 2L313 and related lines | 482
| 2L313MNK | BC Hydro | British Columbia | 1 | ac | 0.7 | 0.4321 | 28.7 | 17.716 | 230 | 13.776 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Sukunka | BC_SNK_DSS | Conuma Coal JCT | BC_MNK_JCT |  | DELETIONS and CORRRECTIONS to 2L313 and related lines | 483
| 2L313MNK | BC Hydro | British Columbia | 1 | ac | 28 | 17.284 | 28.7 | 17.716 | 230 | 13.776 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Conuma Coal JCT | BC_MNK_JCT | Conuma Coal | BC_MNK_ISS |  | DELETIONS and CORRRECTIONS to 2L313 and related lines | 484
| 2L313 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 32.74 | 20.2099 | 230 | 15.7152 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Meikle SWS | BC_MKT_SWS | Meikle GS | BC_MKL_GSS |  | DELETIONS and CORRRECTIONS to 2L313 and related lines | 485
| 2L314 | BC Hydro | British Columbia | 1 | ac | 40 | 24.6914 | 40 | 24.6914 | 230 | 19.2 |  | 940 | 160 | 374.4694 | 63.7395 | 0.9 | 337.0224 | 57.3655 | Dokie | BC_DKT_DSS | Dokie GS | BC_DKW_GSS |  |  | 486
| 2L315 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 230 | 0.48 |  | 964 | 1127 | 384.0303 | 448.9649 | 0.9 | 345.6273 | 404.0684 | Tumbler Ridge | BC_TLR_DSS | Quality GS | BC_QTY_GSS |  |  | 487
| 2L319 | BC Hydro | British Columbia | 1 | ac | 90 | 55.5556 | 90 | 55.5556 | 230 | 43.2 | 2.9972 |  |  | 0 | 0 | 0.9 | 401.627 | 434.5964 | Kennedy | BC_KDS_DSS | Mount Milligan | BC_MML_DSS |  |  | 488
| 2L320 | BC Hydro | British Columbia | 1 | ac | 0.64816 | 0.4001 | 0.64816 | 0.4001 | 230 | 0.31112 |  | 729 | 980 | 290.413 | 390.4043 | 0.9 | 261.3717 | 351.3638 | Kennedy | BC_KDS_DSS | Kemess Mine | BC_KMI_DSS |  |  | 489
| 2L321 | BC Hydro | British Columbia | 1 | ac | 0.099169 | 0.061216 | 0.099169 | 0.061216 | 230 | 0.047601 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Tumbler Ridge | BC_TLR_DSS | BC Rail | BC_BCR_ISS |  |  | 490
| 2L322 | BC Hydro | British Columbia | 1 | ac | 28.034 | 17.3049 | 28.034 | 17.3049 | 230 | 13.4563 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Tumbler Ridge | BC_TLR_DSS | Bullmoose | BC_BLM_DSS |  |  | 491
| 2L323 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 20.38 | 12.5802 | 230 | 9.7824 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Tumbler Ridge | BC_TLR_DSS | Murrary River Coal JCT | BC_MRC_JCT |  |  | 492
| 2L323MRC | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 230 | 0.48 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Murrary River Coal JCT | BC_MRC_JCT | Murrary River Coal | BC_MRC_ISS |  |  | 493
| 2L323 | BC Hydro | British Columbia | 1 | ac | 2.38 | 1.4691 | 20.38 | 12.5802 | 230 | 9.7824 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Murrary River Coal JCT | BC_MRC_JCT | Quintette | BC_QNT_DSS |  |  | 494
| 2L329 | BC Hydro | British Columbia | 1 | ac | 44.5552 | 27.5032 | 44.5552 | 27.5032 | 230 | 21.3865 |  | 1664 | 2217 | 662.8905 | 883.19 | 0.9 | 596.6014 | 794.871 | Shell Groundbirch | BC_SGB_ISS | Bear Mountain | BC_BMT_DSS |  |  | 495
| 2L330 | BC Hydro | British Columbia | 1 | ac | 4.6693 | 2.8823 | 4.6693 | 2.8823 | 230 | 2.2413 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Sundance Lake | BC_SLS_DSS | Chetwynd GS | BC_LAP_GSS |  |  | 496
| 2L333 | BC Hydro | British Columbia | 1 | ac | 44.5777 | 27.5171 | 44.5777 | 27.5171 | 230 | 21.3973 |  | 1664 | 2217 | 662.8905 | 883.19 | 0.9 | 596.6014 | 794.871 | Shell Groundbirch | BC_SGB_ISS | Bear Mountain | BC_BMT_DSS |  |  | 497
| 2L337 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 23.17 | 14.3025 | 230 | 11.1216 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Meikle SWS | BC_MKT_SWS | Moose Lake JCT | BC_MLW_JCT |  |  | 498
| 2L337MLW | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 3 | 1.8519 | 230 | 1.44 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Moose Lake JCT | BC_MLW_JCT | Moose Lake GS | BC_MLW_GSS |  |  | 499
| 2L337 | BC Hydro | British Columbia | 1 | ac | 15.17 | 9.3642 | 23.17 | 14.3025 | 230 | 11.1216 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Moose Lake JCT | BC_MLW_JCT | Tumbler Ridge | BC_TLR_DSS |  |  | 500
| 2L339 | BC Hydro | British Columbia | 1 | ac | 4.2547 | 2.6264 | 4.2547 | 2.6264 | 230 | 2.0423 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Meikle GS | BC_MKL_GSS | Meikle SWS | BC_MKT_SWS |  |  | 501
| 2L340 | BC Hydro | British Columbia | 1 | ac | 14.6552 | 9.0464 | 14.6552 | 9.0464 | 230 | 7.0345 |  | 1628 | 2217 | 648.5491 | 883.19 | 0.9 | 583.6942 | 794.871 | Sundance Lake | BC_SLS_DSS | Shell Groundbirch | BC_SGB_ISS |  |  | 502
| 2L342 | BC Hydro | British Columbia | 1 | ac | 14.6431 | 9.039 | 14.6431 | 9.039 | 230 | 7.0287 |  | 1628 | 2217 | 648.5491 | 883.19 | 0.9 | 583.6942 | 794.871 | Sundance Lake | BC_SLS_DSS | Shell Groundbirch | BC_SGB_ISS |  |  | 503
| 2L348 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 40 | 24.6914 | 230 | 19.2 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Shell Groundbirch | BC_SGB_ISS | Shell Saturn Gas Plant JCT | BC_SRN_JCT |  |  | 504
| 2L348SRN | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 10 | 6.1728 | 230 | 4.8 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Shell Saturn Gas Plant JCT | BC_SRN_JCT | Shell Saturn Gas Plant | BC_SRN_ISS |  |  | 505
| 2L348 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 40 | 24.6914 | 230 | 19.2 | 3 |  |  | 0 | 0 | 0.9 | 402 | 435 | Shell Saturn Gas Plant JCT | BC_SRN_JCT | Shell Sunset Prairie | BC_SST_ISS |  |  | 506
| 2L352 | BC Hydro | British Columbia | 1 | ac | 103.1571 | 63.6772 | 103.1571 | 63.6772 | 230 | 49.5154 |  | 1047 | 1270 | 417.0952 | 505.932 | 0.9 | 375.3856 | 455.3388 | Hundred Mile House | BC_HMH_DSS | Soda Creek | BC_SCK_DSS |  |  | 507
| 2L353 | BC Hydro | British Columbia | 1 | ac | 64.3281 | 39.7087 | 64.3281 | 39.7087 | 230 | 30.8775 |  | 1055 | 1280 | 420.2821 | 509.9158 | 0.9 | 378.2539 | 458.9242 | Glenannan | BC_GLN_DSS | Tachick | BC_TAC_DSS |  |  | 508
| 2L354 | BC Hydro | British Columbia | 1 | ac | 9.1458 | 5.6455 | 9.1458 | 5.6455 | 230 | 4.39 |  | 537 | 942 | 213.9256 | 375.2661 | 0.9 | 192.533 | 337.7395 | Red Bluff | BC_RBF_DSS | Barlow | BC_BLW_DSS |  |  | 509
| 2L374 | BC Hydro | British Columbia | 1 | ac | 95.7577 | 59.1097 | 95.7577 | 59.1097 | 287 | 44.2454 |  | 1736 | 2228 | 862.9631 | 1107.5356 | 0.9 | 776.6668 | 996.7821 | Bob Quinn | BC_BQN_DSS | Tatogga | BC_TAT_DSS |  |  | 510
| 2L375 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 25 | 15.4321 | 287 | 11.5514 |  | 1736 | 2228 | 862.9631 | 1107.5356 | 0.9 | 776.6668 | 996.7821 | Tatogga | BC_TAT_DSS | Red Chris Mine | BC_RDC_ISS |  |  | 511
| 2L379 | BC Hydro | British Columbia | 1 | ac | 40 | 24.6914 | 40 | 24.6914 | 287 | 18.4822 | 3 |  |  | 0 | 0 | 0.9 | 641.8364 | 726.7853 | Bob Quinn | BC_BQN_DSS | Forest Kerr GS | BC_FKR_GSS |  |  | 512
| 3L002 | BC Hydro | British Columbia | 1 | ac | 115 | 70.9877 | 145 | 89.5062 | 360 | 63.6657 |  | 960 | 1782 | 598.5968 | 1111.1452 | 0.9 | 538.7371 | 1000.0307 | Bridge River TS | BC_BRT_TSS | Sachteen | BC_SAC_DSS |  |  | 513
| 3L002 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 145 | 89.5062 | 360 | 63.6657 |  | 960 | 1782 | 598.5968 | 1111.1452 | 0.9 | 538.7371 | 1000.0307 | Sachteen | BC_SAC_DSS | Upper Harrison | BC_UHT_DSS |  |  | 514
| 3L003 | BC Hydro | British Columbia | 1 | ac | 10.237 | 6.3191 | 10.237 | 6.3191 | 360 | 4.4948 |  | 1016 | 1782 | 633.5149 | 1111.1452 | 0.9 | 570.1634 | 1000.0307 | Rosedale | BC_ROS_DSS | Wahleach GS | BC_WAH_GSS |  |  | 515
| 3L005 | BC Hydro | British Columbia | 1 | ac | 78.2806 | 48.3213 | 78.2806 | 48.3213 | 360 | 34.371 |  | 960 | 1782 | 598.5968 | 1111.1452 | 0.9 | 538.7371 | 1000.0307 | Rosedale | BC_ROS_DSS | Upper Harrison | BC_UHT_DSS |  |  | 516
| 3L013 | BC Hydro | British Columbia | 1 | ac | 0.52113 | 0.32168 | 0.52113 | 0.32168 | 360 | 0.22881 |  | 1016 | 1782 | 633.5149 | 1111.1452 | 0.9 | 570.1634 | 1000.0307 | Bridge River 2 GS | BC_BR2_GSS | Bridge River TS | BC_BRT_TSS |  |  | 517
| 3L014 | BC Hydro | British Columbia | 1 | ac | 0.46969 | 0.28993 | 0.46969 | 0.28993 | 360 | 0.20623 |  | 1016 | 1782 | 633.5149 | 1111.1452 | 0.9 | 570.1634 | 1000.0307 | Bridge River 1 GS | BC_BR1_DFS | Bridge River TS | BC_BRT_TSS |  |  | 518
| 3L015 | BC Hydro | British Columbia | 1 | ac | 1.2041 | 0.74325 | 1.2041 | 0.74325 | 360 | 0.52868 |  | 1016 | 1782 | 633.5149 | 1111.1452 | 0.9 | 570.1634 | 1000.0307 | Bridge River 1 GS | BC_BR1_DFS | Bridge River TS | BC_BRT_TSS |  |  | 519
| 3L016 | BC Hydro | British Columbia | 1 | ac | 1.2875 | 0.79476 | 1.2875 | 0.79476 | 360 | 0.56531 |  | 1016 | 1782 | 633.5149 | 1111.1452 | 0.9 | 570.1634 | 1000.0307 | Bridge River 1 GS | BC_BR1_DFS | Bridge River TS | BC_BRT_TSS |  |  | 520
| 5L001 | BC Hydro | British Columbia | 1 | ac | 277.7865 | 171.4731 | 277.7865 | 171.4731 | 500 | 109.7257 |  | 2150 | 3130 | 1861.9546 | 2710.6595 | 0.9 | 1675.7592 | 2439.5936 | GM Shrum GS | BC_GMS_GSS | Williston | BC_WSN_DSS |  |  | 521
| 5L002 | BC Hydro | British Columbia | 1 | ac | 277.6418 | 171.3838 | 277.6418 | 171.3838 | 500 | 109.6685 |  | 2150 | 3130 | 1861.9546 | 2710.6595 | 0.9 | 1675.7592 | 2439.5936 | GM Shrum GS | BC_GMS_GSS | Williston | BC_WSN_DSS |  |  | 522
| 5L003 | BC Hydro | British Columbia | 1 | ac | 138.4138 | 85.4406 | 138.4138 | 85.4406 | 500 | 54.6735 |  | 2150 | 3130 | 1861.9546 | 2710.6595 | 0.9 | 1675.7592 | 2439.5936 | Peace Canyon GS | BC_PCN_GSS | Kennedy | BC_KDS_DSS |  |  | 523
| 5L004 | BC Hydro | British Columbia | 1 | ac | 13.9627 | 8.619 | 13.9627 | 8.619 | 500 | 5.5153 |  | 2500 | 3450 | 2165.0635 | 2987.7876 | 0.9 | 1948.5572 | 2689.0089 | GM Shrum GS | BC_GMS_GSS | Peace Canyon GS | BC_PCN_GSS |  |  | 524
| 5L005 | BC Hydro | British Columbia | 1 | ac | 74.9202 | 46.2471 | 74.9202 | 46.2471 | 500 | 29.5935 | 3 |  |  | 0 | 0 | 0.9 | 2550 | 3225 | South Bank | BC_SBK_DSS | Peace Canyon GS | BC_PCN_GSS |  | Not operating until 2025 | 525
| 5L006 | BC Hydro | British Columbia | 1 | ac | 74.8018 | 46.1739 | 74.8018 | 46.1739 | 500 | 29.5467 | 3 |  |  | 0 | 0 | 0.9 | 2550 | 3225 | South Bank | BC_SBK_DSS | Peace Canyon GS | BC_PCN_GSS |  | Not operating until 2025 | 526
| 5L007 | BC Hydro | British Columbia | 1 | ac | 138.7478 | 85.6468 | 138.7478 | 85.6468 | 500 | 54.8054 |  | 2500 | 3450 | 2165.0635 | 2987.7876 | 0.9 | 1948.5572 | 2689.0089 | Kennedy | BC_KDS_DSS | Williston | BC_WSN_DSS |  |  | 527
| 5L011 | BC Hydro | British Columbia | 1 | ac | 330.0781 | 203.7519 | 330.0781 | 203.7519 | 500 | 130.3808 |  | 2500 | 3320 | 2165.0635 | 2875.2043 | 0.9 | 1948.5572 | 2587.6839 | Williston | BC_WSN_DSS | Kelly Lake | BC_KLY_DSS |  |  | 528
| 5L012 | BC Hydro | British Columbia | 1 | ac | 330.075 | 203.75 | 330.075 | 203.75 | 500 | 130.3796 |  | 2500 | 3450 | 2165.0635 | 2987.7876 | 0.9 | 1948.5572 | 2689.0089 | Williston | BC_WSN_DSS | Kelly Lake | BC_KLY_DSS |  |  | 529
| 5L013 | BC Hydro | British Columbia | 1 | ac | 330.1389 | 203.7895 | 330.1389 | 203.7895 | 500 | 130.4049 |  | 3385 | 4568 | 2931.496 | 3956.004 | 0.9 | 2638.3464 | 3560.4036 | Williston | BC_WSN_DSS | Kelly Lake | BC_KLY_DSS |  |  | 530
| 5L029 | BC Hydro | British Columbia | 1 | ac | 68.7281 | 42.4248 | 68.7281 | 42.4248 | 500 | 27.1476 |  | 1260 | 1260 | 1091.192 | 1091.192 | 0.9 | 982.0728 | 982.0728 | Malaspina | BC_MSA_DSS | Dunsmuir | BC_DMR_DSS |  |  | 531
| 5L030 | BC Hydro | British Columbia | 1 | ac | 80.1431 | 49.471 | 80.1431 | 49.471 | 500 | 31.6565 |  | 3238 | 3901 | 2804.1903 | 3378.3651 | 0.9 | 2523.7712 | 3040.5286 | Cheekye | BC_CKY_DSS | Malaspina | BC_MSA_DSS |  |  | 532
| 5L031 | BC Hydro | British Columbia | 1 | ac | 68.5717 | 42.3282 | 68.5717 | 42.3282 | 500 | 27.0858 |  | 1260 | 1260 | 1091.192 | 1091.192 | 0.9 | 982.0728 | 982.0728 | Malaspina | BC_MSA_DSS | Dunsmuir | BC_DMR_DSS |  |  | 533
| 5L032 | BC Hydro | British Columbia | 1 | ac | 80.3637 | 49.6072 | 80.3637 | 49.6072 | 500 | 31.7437 |  | 3238 | 3901 | 2804.1903 | 3378.3651 | 0.9 | 2523.7712 | 3040.5286 | Cheekye | BC_CKY_DSS | Malaspina | BC_MSA_DSS |  |  | 534
| 5L040 | BC Hydro | British Columbia | 1 | ac | 49.7171 | 30.6896 | 49.7171 | 30.6896 | 500 | 19.6383 |  | 2495 | 3448 | 2160.7334 | 2986.0556 | 0.9 | 1944.66 | 2687.45 | Clayburn | BC_CBN_DSS | Ingledow | BC_ING_DSS |  |  | 535
| 5L041 | BC Hydro | British Columbia | 1 | ac | 141.6335 | 87.4281 | 271.6335 | 167.675 | 500 | 107.2952 |  | 2500 | 3320 | 2165.0635 | 2875.2043 | 0.9 | 1948.5572 | 2587.6839 | Kelly Lake | BC_KLY_DSS | Kwoiek Creek GS | BC_KCH_GSS |  |  | 536
| 5L041 | BC Hydro | British Columbia | 1 | ac | 130 | 80.2469 | 271.6335 | 167.675 | 500 | 107.2952 |  | 2500 | 3320 | 2165.0635 | 2875.2043 | 0.9 | 1948.5572 | 2587.6839 | Kwoiek Creek GS | BC_KCH_GSS | Clayburn | BC_CBN_DSS |  |  | 537
| 5L042 | BC Hydro | British Columbia | 1 | ac | 196.8931 | 121.5389 | 196.8931 | 121.5389 | 500 | 77.7728 |  | 2150 | 3130 | 1861.9546 | 2710.6595 | 0.9 | 1675.7592 | 2439.5936 | Kelly Lake | BC_KLY_DSS | Cheekye | BC_CKY_DSS |  |  | 538
| 5L044 | BC Hydro | British Columbia | 1 | ac | 19.5229 | 12.0512 | 19.5229 | 12.0512 | 500 | 7.7115 |  | 2500 | 3470 | 2165.0635 | 3005.1082 | 0.9 | 1948.5572 | 2704.5973 | Meridian | BC_MDN_DSS | Ingledow | BC_ING_DSS |  |  | 539
| 5L045 | BC Hydro | British Columbia | 1 | ac | 66.7232 | 41.1871 | 66.7232 | 41.1871 | 500 | 26.3557 |  | 2150 | 3130 | 1861.9546 | 2710.6595 | 0.9 | 1675.7592 | 2439.5936 | Cheekye | BC_CKY_DSS | Meridian | BC_MDN_DSS |  |  | 540
| 5L051 | BC Hydro | British Columbia | 1 | ac | 21.794 | 13.4531 | 21.794 | 13.4531 | 500 | 8.6086 | [5 empty] | 0.9 | 700 | 700 | Ingledow | BC_ING_DSS | INT Ingledow BPA | XX_BCUS1_INT |  |  | 541
| 5L052 | BC Hydro | British Columbia | 1 | ac | 21.8007 | 13.4572 | 21.8007 | 13.4572 | 500 | 8.6113 | [5 empty] | 0.9 | 700 | 700 | Ingledow | BC_ING_DSS | INT Ingledow BPA | XX_BCUS1_INT |  |  | 542
| 5L061 | BC Hydro | British Columbia | 1 | ac | 174.722 | 107.8531 | 174.722 | 107.8531 | 500 | 69.0152 |  | 2000 | 3140 | 1732.0508 | 2719.3198 | 0.9 | 1558.8457 | 2447.3878 | Williston | BC_WSN_DSS | Glenannan | BC_GLN_DSS |  |  | 543
| 5L062 | BC Hydro | British Columbia | 1 | ac | 130.7262 | 80.6952 | 130.7262 | 80.6952 | 500 | 51.6368 |  | 2000 | 3140 | 1732.0508 | 2719.3198 | 0.9 | 1558.8457 | 2447.3878 | Glenannan | BC_GLN_DSS | Telkwa | BC_TKW_DSS |  |  | 544
| 5L063 | BC Hydro | British Columbia | 1 | ac | 142.7894 | 88.1416 | 142.7894 | 88.1416 | 500 | 56.4018 |  | 2000 | 3035 | 1732.0508 | 2628.3871 | 0.9 | 1558.8457 | 2365.5484 | Telkwa | BC_TKW_DSS | Skeena | BC_SKA_DSS |  |  | 545
| 5L071 | BC Hydro | British Columbia | 1 | ac | 285.3018 | 176.1122 | 285.3018 | 176.1122 | 500 | 112.6942 |  | 2265 | 3302 | 1961.5475 | 2859.6159 | 0.9 | 1765.3928 | 2573.6543 | Mica GS | BC_MCA_GSS | Nicola | BC_NIC_DSS |  |  | 546
| 5L072 | BC Hydro | British Columbia | 1 | ac | 285.2554 | 176.0836 | 285.2554 | 176.0836 | 500 | 112.6759 |  | 2265 | 3302 | 1961.5475 | 2859.6159 | 0.9 | 1765.3928 | 2573.6543 | Mica GS | BC_MCA_GSS | Nicola | BC_NIC_DSS |  |  | 547
| 5L075 | BC Hydro | British Columbia | 1 | ac | 83.6961 | 51.6642 | 83.6961 | 51.6642 | 500 | 33.06 |  | 2870 | 3302 | 2485.4929 | 2859.6159 | 0.9 | 2236.9436 | 2573.6543 | Revelstoke GS | BC_REV_GSS | Ashton Creek | BC_ACK_DSS |  |  | 548
| 5L076 | BC Hydro | British Columbia | 1 | ac | 117.7756 | 72.701 | 117.7756 | 72.701 | 500 | 46.5213 |  | 2265 | 3302 | 1961.5475 | 2859.6159 | 0.9 | 1765.3928 | 2573.6543 | Ashton Creek | BC_ACK_DSS | Nicola | BC_NIC_DSS |  |  | 549
| 5L077 | BC Hydro | British Columbia | 1 | ac | 83.7315 | 51.6861 | 83.7315 | 51.6861 | 500 | 33.074 |  | 2265 | 3302 | 1961.5475 | 2859.6159 | 0.9 | 1765.3928 | 2573.6543 | Revelstoke GS | BC_REV_GSS | Ashton Creek | BC_ACK_DSS |  |  | 550
| 5L079 | BC Hydro | British Columbia | 1 | ac | 117.7391 | 72.6785 | 117.7391 | 72.6785 | 500 | 46.507 |  | 3501 | 4238 | 3031.9549 | 3670.2157 | 0.9 | 2728.7594 | 3303.1941 | Ashton Creek | BC_ACK_DSS | Nicola | BC_NIC_DSS |  |  | 551
| 5L081 | BC Hydro | British Columbia | 1 | ac | 263.9343 | 162.9224 | 263.9343 | 162.9224 | 500 | 104.2541 |  | 2153 | 3130 | 1864.5527 | 2710.6595 | 0.9 | 1678.0974 | 2439.5936 | Nicola | BC_NIC_DSS | Ingledow | BC_ING_DSS |  |  | 552
| 5L082 | BC Hydro | British Columbia | 1 | ac | 248.1894 | 153.2034 | 248.1894 | 153.2034 | 500 | 98.0348 |  | 2265 | 3302 | 1961.5475 | 2859.6159 | 0.9 | 1765.3928 | 2573.6543 | Nicola | BC_NIC_DSS | Meridian | BC_MDN_DSS |  |  | 553
| 5L083 | BC Hydro | British Columbia | 1 | ac | 248.2205 | 153.2225 | 248.2205 | 153.2225 | 500 | 98.0471 |  | 3721 | 4497 | 3222.4805 | 3894.5162 | 0.9 | 2900.2325 | 3505.0646 | Nicola | BC_NIC_DSS | Meridian | BC_MDN_DSS |  |  | 554
| 5L087 | BC Hydro | British Columbia | 1 | ac | 145.9616 | 90.0998 | 145.9616 | 90.0998 | 500 | 57.6548 |  | 3540 | 4284 | 3065.7299 | 3710.0528 | 0.9 | 2759.1569 | 3339.0475 | Kelly Lake | BC_KLY_DSS | Nicola | BC_NIC_DSS |  |  | 555
| 5L091 | BC Hydro | British Columbia | 1 | ac | 223.0616 | 137.6924 | 223.0616 | 137.6924 | 500 | 88.1093 |  | 2369 | 3344 | 2051.6142 | 2895.989 | 0.9 | 1846.4528 | 2606.3901 | Selkirk | BC_SEL_TSS | Ashton Creek | BC_ACK_DSS |  |  | 556
| 5L092 | BC Hydro | British Columbia | 1 | ac | 179.8527 | 111.0202 | 179.8527 | 111.0202 | 500 | 71.0418 |  | 2870 | 3700 | 2485.4929 | 3204.294 | 0.9 | 2236.9436 | 2883.8646 | Selkirk | BC_SEL_TSS | Cranbrook | BC_CBK_DSS |  |  | 557
| 5L094 | BC Hydro | British Columbia | 1 | ac | 108.1598 | 66.7653 | 108.1598 | 66.7653 | 500 | 42.7231 |  | 2052 | 3045 | 1777.0841 | 2637.0474 | 0.9 | 1599.3757 | 2373.3426 | Cranbrook | BC_CBK_DSS | IPT Cranbrook Chapel Rock | PP_BCAB2_IPT |  |  | 558
| 5L096 | BC Hydro | British Columbia | 1 | ac | 162.8725 | 100.5386 | 162.8725 | 100.5386 | 500 | 64.3346 |  | 3506 | 4241 | 3036.2851 | 3672.8137 | 0.9 | 2732.6566 | 3305.5324 | Vaseux Lake | BC_VAS_DSS | Selkirk | BC_SEL_TSS |  |  | 559
| 5L098 | BC Hydro | British Columbia | 1 | ac | 139.1108 | 85.8709 | 139.1108 | 85.8709 | 500 | 54.9488 |  | 3506 | 4241 | 3036.2851 | 3672.8137 | 0.9 | 2732.6566 | 3305.5324 | Nicola | BC_NIC_DSS | Vaseux Lake | BC_VAS_DSS |  |  | 560
| 60L001 | BC Hydro | British Columbia | 1 | ac | 7.596 | 4.6889 | 7.596 | 4.6889 | 69 | 2.919 |  | 580 | 740 | 69.3167 | 88.4385 | 0.9 | 62.385 | 79.5947 | Como Lake | BC_COK_DSS | Barnard | BC_BND_DSS |  |  | 561
| 60L002 | BC Hydro | British Columbia | 1 | ac | 19.8 | 12.2222 | 34.29 | 21.1667 | 69 | 13.1772 |  | 400 | 505 | 47.8046 | 60.3533 | 0.9 | 43.0241 | 54.318 | Stave Falls GS | BC_SFL_GSS | Maple Ridge JCT | BC_MRG_JCT |  |  | 562
| 60L002MRG | BC Hydro | British Columbia | 1 | ac | 0.047723 | 0.029459 | 0.047723 | 0.029459 | 69 | 0.018339 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Maple Ridge JCT | BC_MRG_JCT | Maple Ridge | BC_MRG_DSS |  |  | 563
| 60L002 | BC Hydro | British Columbia | 1 | ac | 12.49 | 7.7099 | 34.29 | 21.1667 | 69 | 13.1772 |  | 400 | 505 | 47.8046 | 60.3533 | 0.9 | 43.0241 | 54.318 | Maple Ridge JCT | BC_MRG_JCT | Coquitlam JCT | BC_CQM_JCT |  |  | 564
| 60L002CQM | BC Hydro | British Columbia | 1 | ac | 0.0098764 | 0.0060965 | 0.0098764 | 0.0060965 | 69 | 0.0037954 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Coquitlam JCT | BC_CQM_JCT | Coquitlam | BC_CQM_DSS |  |  | 565
| 60L002 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 34.29 | 21.1667 | 69 | 13.1772 |  | 732 | 875 | 87.4824 | 104.5726 | 0.9 | 78.7342 | 94.1153 | Coquitlam JCT | BC_CQM_JCT | Como Lake | BC_COK_DSS |  |  | 566
| 60L003 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 19.53 | 12.0556 | 69 | 7.5051 |  | 580 | 740 | 69.3167 | 88.4385 | 0.9 | 62.385 | 79.5947 | Haney | BC_HNY_DSS | Maple Ridge JCT | BC_MRG_JCT |  |  | 567
| 60L003MRG | BC Hydro | British Columbia | 1 | ac | 0.022342 | 0.013791 | 0.022342 | 0.013791 | 69 | 0.0085858 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Maple Ridge JCT | BC_MRG_JCT | Maple Ridge | BC_MRG_DSS |  |  | 568
| 60L003 | BC Hydro | British Columbia | 1 | ac | 15.53 | 9.5864 | 19.53 | 12.0556 | 69 | 7.5051 |  | 580 | 740 | 69.3167 | 88.4385 | 0.9 | 62.385 | 79.5947 | Maple Ridge JCT | BC_MRG_JCT | Como Lake | BC_COK_DSS |  |  | 569
| 60L004 | BC Hydro | British Columbia | 1 | ac | 15.1177 | 9.3319 | 15.1177 | 9.3319 | 69 | 5.8095 |  | 400 | 505 | 47.8046 | 60.3533 | 0.9 | 43.0241 | 54.318 | Lake Buntzen GS | BC_LB1_DFS | Petro Canada Products | BC_PCP_ISS |  |  | 570
| 60L005 | BC Hydro | British Columbia | 1 | ac | 16.3033 | 10.0638 | 16.3033 | 10.0638 | 69 | 6.2651 |  | 400 | 505 | 47.8046 | 60.3533 | 0.9 | 43.0241 | 54.318 | Lake Buntzen GS | BC_LB1_DFS | Shelburn | BC_SHL_DSS |  |  | 571
| 60L006 | BC Hydro | British Columbia | 1 | ac | 8.7899 | 5.4259 | 8.7899 | 5.4259 | 69 | 3.3778 |  | 400 | 505 | 47.8046 | 60.3533 | 0.9 | 43.0241 | 54.318 | Lake Buntzen GS | BC_LB1_DFS | Ioco Esso Petroleum | BC_IOC_ISS |  |  | 572
| 60L007 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 38.9553 | 24.0465 | 69 | 14.97 |  | 735 | 875 | 87.841 | 104.5726 | 0.9 | 79.0569 | 94.1153 | Port Kells | BC_PKL_DSS | Balfour JCT | BC_BAL_JCT |  |  | 573
| 60L007 | BC Hydro | British Columbia | 1 | ac | 8.3453 | 5.1514 | 38.9553 | 24.0465 | 69 | 14.97 |  | 215 | 290 | 25.695 | 34.6583 | 0.9 | 23.1255 | 31.1925 | Balfour JCT | BC_BAL_JCT | Balfour | BC_BAL_DSS |  |  | 574
| 60L007 | BC Hydro | British Columbia | 1 | ac | 10.72 | 6.6173 | 38.9553 | 24.0465 | 69 | 14.97 |  | 1145 | 1388 | 136.8407 | 165.882 | 0.9 | 123.1566 | 149.2938 | Balfour JCT | BC_BAL_JCT | McLellan | BC_MLN_DSS |  |  | 575
| 60L007 | BC Hydro | British Columbia | 1 | ac | 12.89 | 7.9568 | 38.9553 | 24.0465 | 69 | 14.97 |  | 620 | 745 | 74.0971 | 89.0361 | 0.9 | 66.6874 | 80.1325 | Balfour JCT | BC_BAL_JCT | Ruskin GS | BC_RUS_GSS |  | Line connection RUS to MLN assumed | 576
| 60L008 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 47.4453 | 29.2872 | 69 | 18.2325 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Port Kells | BC_PKL_DSS | Balfour JCT | BC_BAL_JCT |  |  | 577
| 60L008 | BC Hydro | British Columbia | 1 | ac | 8.2253 | 5.0773 | 47.4453 | 29.2872 | 69 | 18.2325 |  | 215 | 290 | 25.695 | 34.6583 | 0.9 | 23.1255 | 31.1925 | Balfour JCT | BC_BAL_JCT | Balfour | BC_BAL_DSS |  |  | 578
| 60L008 | BC Hydro | British Columbia | 1 | ac | 10.72 | 6.6173 | 47.4453 | 29.2872 | 69 | 18.2325 |  | 1145 | 1388 | 136.8407 | 165.882 | 0.9 | 123.1566 | 149.2938 | Balfour JCT | BC_BAL_JCT | McLellan | BC_MLN_DSS |  |  | 579
| 60L008 | BC Hydro | British Columbia | 1 | ac | 12.94 | 7.9877 | 47.4453 | 29.2872 | 69 | 18.2325 |  | 620 | 745 | 74.0971 | 89.0361 | 0.9 | 66.6874 | 80.1325 | Balfour JCT | BC_BAL_JCT | Ruskin GS | BC_RUS_GSS |  | Line connection RUS to MLN assumed | 580
| 60L008 | BC Hydro | British Columbia | 1 | ac | 7.56 | 4.6667 | 47.4453 | 29.2872 | 69 | 18.2325 |  | 713 | 864 | 85.2117 | 103.2579 | 0.9 | 76.6905 | 92.9321 | Balfour JCT | BC_BAL_JCT | Gloucester JCT | BC_GLT_JCT |  |  | 581
| 60L008 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 47.4453 | 29.2872 | 69 | 18.2325 |  | 493 | 594 | 58.9192 | 70.9898 | 0.9 | 53.0273 | 63.8909 | Gloucester JCT | BC_GLT_JCT | Gloucester | BC_GLT_DSS |  | DELETION of 60L009 and all connections | 582
| 60L010 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 90.79 | 56.0432 | 69 | 34.8893 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Wahleach GS | BC_WAH_GSS | Wahleach Hope JCT | BC_WHO_JCT |  | DELETIONS and CORRRECTIONS to 60L010 and related lines | 586
| 60L010KEN | BC Hydro | British Columbia | 1 | ac | 13.8895 | 8.5738 | 13.8895 | 8.5738 | 69 | 5.3375 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Wahleach Hope JCT | BC_WHO_JCT | Kent | BC_KEN_DSS |  | DELETIONS and CORRRECTIONS to 60L010 and related lines | 587
| 60L010 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 90.79 | 56.0432 | 69 | 34.8893 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Wahleach Hope JCT | BC_WHO_JCT | Boston Bar JCT | BC_BBR_JCT |  | DELETIONS and CORRRECTIONS to 60L010 and related lines | 588
| 60L010 | BC Hydro | British Columbia | 1 | ac | 35 | 21.6049 | 90.79 | 56.0432 | 69 | 34.8893 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Boston Bar JCT | BC_BBR_JCT | Spuzzum | BC_SZM_DSS |  |  | 589
| 60L010 | BC Hydro | British Columbia | 1 | ac | 25.79 | 15.9198 | 90.79 | 56.0432 | 69 | 34.8893 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Spuzzum | BC_SZM_DSS | Boston Bar | BC_BBR_DSS |  |  | 590
| 60L010HOP | BC Hydro | British Columbia | 1 | ac | 3.1054 | 1.9169 | 3.1054 | 1.9169 | 69 | 1.1934 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Boston Bar JCT | BC_BBR_JCT | Hope | BC_HOP_DSS |  |  | 591
| 60L011 | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 8.35 | 5.1543 | 69 | 3.2088 |  | 400 | 510 | 47.8046 | 60.9509 | 0.9 | 43.0241 | 54.8558 | Ioco Esso Petroleum | BC_IOC_ISS | Simon Fraser University JCT | BC_SFU_JCT |  |  | 592
| 60L011SFU | BC Hydro | British Columbia | 1 | ac | 1.4537 | 0.89735 | 1.4537 | 0.89735 | 69 | 0.55864 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Simon Fraser University JCT | BC_SFU_JCT | Simon Fraser University | BC_SFU_DSS |  |  | 593
| 60L011 | BC Hydro | British Columbia | 1 | ac | 2.35 | 1.4506 | 8.35 | 5.1543 | 69 | 3.2088 |  | 400 | 510 | 47.8046 | 60.9509 | 0.9 | 43.0241 | 54.8558 | Simon Fraser University JCT | BC_SFU_JCT | Barnard | BC_BND_DSS |  |  | 594
| 60L012 | BC Hydro | British Columbia | 1 | ac | 12 | 7.4074 | 22 | 13.5802 | 69 | 8.4543 |  | 731 | 880 | 87.3629 | 105.1701 | 0.9 | 78.6266 | 94.6531 | Stave Falls GS | BC_SFL_GSS | Mission JCT | BC_MIS_JCT |  |  | 595
| 60L012MIS | BC Hydro | British Columbia | 1 | ac | 0.072682 | 0.044865 | 0.072682 | 0.044865 | 69 | 0.027931 |  | 1151 | 1393 | 137.5577 | 166.4795 | 0.9 | 123.802 | 149.8316 | Mission JCT | BC_MIS_JCT | Mission | BC_MIS_DSS |  |  | 596
| 60L012 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 22 | 13.5802 | 69 | 8.4543 |  | 1151 | 1393 | 137.5577 | 166.4795 | 0.9 | 123.802 | 149.8316 | Mission JCT | BC_MIS_JCT | Clayburn | BC_CBN_DSS |  |  | 597
| 60L013 | BC Hydro | British Columbia | 1 | ac | 9 | 5.5556 | 17.52 | 10.8148 | 69 | 6.7327 |  | 245 | 325 | 29.2803 | 38.8412 | 0.9 | 26.3523 | 34.9571 | Alouette GS | BC_ALU_GSS | St Leon Creek JCT | BC_SLK_JCT |  |  | 598
| 60L013SLK | BC Hydro | British Columbia | 1 | ac | 0.037431 | 0.023106 | 0.037431 | 0.023106 | 69 | 0.014384 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | St Leon Creek JCT | BC_SLK_JCT | St Leon Creek | BC_SLK_DSS |  |  | 599
| 60L013 | BC Hydro | British Columbia | 1 | ac | 8.52 | 5.2593 | 17.52 | 10.8148 | 69 | 6.7327 |  | 245 | 325 | 29.2803 | 38.8412 | 0.9 | 26.3523 | 34.9571 | St Leon Creek JCT | BC_SLK_JCT | Stave Falls GS | BC_SFL_GSS |  |  | 600
| 60L014 | BC Hydro | British Columbia | 1 | ac | 3.83 | 2.3642 | 12.83 | 7.9198 | 69 | 4.9304 |  | 1151 | 1393 | 137.5577 | 166.4795 | 0.9 | 123.802 | 149.8316 | Silverdale | BC_SVD_DSS | Mission JCT | BC_MIS_JCT |  |  | 601
| 60L014MIS | BC Hydro | British Columbia | 1 | ac | 0.99264 | 0.61274 | 0.99264 | 0.61274 | 69 | 0.38146 |  | 1151 | 1393 | 137.5577 | 166.4795 | 0.9 | 123.802 | 149.8316 | Mission JCT | BC_MIS_JCT | Mission | BC_MIS_DSS |  |  | 602
| 60L014 | BC Hydro | British Columbia | 1 | ac | 9 | 5.5556 | 12.83 | 7.9198 | 69 | 4.9304 |  | 1151 | 1393 | 137.5577 | 166.4795 | 0.9 | 123.802 | 149.8316 | Mission JCT | BC_MIS_JCT | Clayburn | BC_CBN_DSS |  |  | 603
| 60L015 | BC Hydro | British Columbia | 1 | ac | 6.6356 | 4.0961 | 6.6356 | 4.0961 | 69 | 2.55 |  | 660 | 790 | 78.8776 | 94.4141 | 0.9 | 70.9898 | 84.9727 | Stave Falls GS | BC_SFL_GSS | Ruskin GS | BC_RUS_GSS |  |  | 604
| 60L016 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 |  | 400 | 510 | 47.8046 | 60.9509 | 0.9 | 43.0241 | 54.8558 | Lake Buntzen GS | BC_LB1_DFS | Lake Buntzen #2 | BC_LB2_GSS |  |  | 605
| 60L017 | BC Hydro | British Columbia | 1 | ac | 1.66 | 1.0247 | 7.66 | 4.7284 | 69 | 2.9436 |  | 830 | 1020 | 99.1945 | 121.9017 | 0.9 | 89.2751 | 109.7116 | Como Lake | BC_COK_DSS | New Westminster JCT | BC_NWR_JCT |  |  | 606
| 60L017 | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 7.66 | 4.7284 | 69 | 2.9436 |  | 580 | 740 | 69.3167 | 88.4385 | 0.9 | 62.385 | 79.5947 | New Westminster JCT | BC_NWR_JCT | Barnard | BC_BND_DSS |  |  | 607
| 60L017NWR | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 12.34 | 7.6173 | 69 | 4.7421 |  | 490 | 700 | 58.5606 | 83.6581 | 0.9 | 52.7046 | 75.2922 | New Westminster JCT | BC_NWR_JCT | Newstech Recycling JCT | BC_NRG_JCT |  |  | 608
| 60L017NRG | BC Hydro | British Columbia | 1 | ac | 0.27766 | 0.1714 | 0.27766 | 0.1714 | 69 | 0.1067 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Newstech Recycling JCT | BC_NRG_JCT | Newstech Recycling | BC_NRG_ISS |  |  | 609
| 60L017NWR | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 12.34 | 7.6173 | 69 | 4.7421 |  | 490 | 700 | 58.5606 | 83.6581 | 0.9 | 52.7046 | 75.2922 | Newstech Recycling JCT | BC_NRG_JCT | GVRD Sapperton Pumps JCT | BC_GSP_JCT |  |  | 610
| 60L017GSP | BC Hydro | British Columbia | 1 | ac | 0.014064 | 0.0086812 | 0.014064 | 0.0086812 | 69 | 0.0054044 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | GVRD Sapperton Pumps JCT | BC_GSP_JCT | GVRD Sapperton Pumps | BC_GSP_DSS |  |  | 611
| 60L017NWR | BC Hydro | British Columbia | 1 | ac | 3.34 | 2.0617 | 12.34 | 7.6173 | 69 | 4.7421 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | GVRD Sapperton Pumps JCT | BC_GSP_JCT | New Westminster | BC_NWR_DSS |  |  | 612
| 60L018 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 19.49 | 12.0309 | 69 | 7.4897 |  | 400 | 510 | 47.8046 | 60.9509 | 0.9 | 43.0241 | 54.8558 | Haney | BC_HNY_DSS | Maple Ridge JCT | BC_MRG_JCT |  |  | 613
| 60L018MRG | BC Hydro | British Columbia | 1 | ac | 0.063466 | 0.039176 | 0.063466 | 0.039176 | 69 | 0.024389 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Maple Ridge JCT | BC_MRG_JCT | Maple Ridge | BC_MRG_DSS |  |  | 614
| 60L018 | BC Hydro | British Columbia | 1 | ac | 11.49 | 7.0926 | 19.49 | 12.0309 | 69 | 7.4897 |  | 420 | 515 | 50.1948 | 61.5484 | 0.9 | 45.1753 | 55.3936 | Maple Ridge JCT | BC_MRG_JCT | Esco Foundry JCT | BC_ESC_JCT |  |  | 615
| 60L018ESC | BC Hydro | British Columbia | 1 | ac | 0.14034 | 0.086631 | 0.14034 | 0.086631 | 69 | 0.053931 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Esco Foundry JCT | BC_ESC_JCT | Esco Foundry | BC_ESC_ISS |  |  | 616
| 60L018 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 19.49 | 12.0309 | 69 | 7.4897 |  | 580 | 740 | 69.3167 | 88.4385 | 0.9 | 62.385 | 79.5947 | Esco Foundry JCT | BC_ESC_JCT | Coquitlam JCT | BC_CQM_JCT |  |  | 617
| 60L018CQM | BC Hydro | British Columbia | 1 | ac | 0.0059495 | 0.0036725 | 0.0059495 | 0.0036725 | 69 | 0.0022863 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Coquitlam JCT | BC_CQM_JCT | Coquitlam | BC_CQM_DSS |  |  | 618
| 60L018 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 19.49 | 12.0309 | 69 | 7.4897 |  | 580 | 740 | 69.3167 | 88.4385 | 0.9 | 62.385 | 79.5947 | Coquitlam JCT | BC_CQM_JCT | Como Lake | BC_COK_DSS |  |  | 619
| 60L019 | BC Hydro | British Columbia | 1 | ac | 14.902 | 9.1988 | 14.902 | 9.1988 | 69 | 5.7266 |  | 732 | 875 | 87.4824 | 104.5726 | 0.9 | 78.7342 | 94.1153 | Stave Falls GS | BC_SFL_GSS | Haney | BC_HNY_DSS |  |  | 620
| 60L020 | BC Hydro | British Columbia | 1 | ac | 40.24 | 24.8395 | 74.24 | 45.8272 | 69 | 28.5294 |  | 400 | 525 | 47.8046 | 62.7435 | 0.9 | 43.0241 | 56.4692 | Seton Lake GS | BC_SON_DFS | Pavilion JCT | BC_PAV_JCT |  |  | 621
| 60L020PAV | BC Hydro | British Columbia | 1 | ac | 0.10756 | 0.066392 | 0.10756 | 0.066392 | 69 | 0.041332 |  | 114 | 202 | 13.6243 | 24.1413 | 0.9 | 12.2619 | 21.7272 | Pavilion JCT | BC_PAV_JCT | Pavilion | BC_PAV_DSS |  |  | 622
| 60L020 | BC Hydro | British Columbia | 1 | ac | 11 | 6.7901 | 74.24 | 45.8272 | 69 | 28.5294 |  | 400 | 525 | 47.8046 | 62.7435 | 0.9 | 43.0241 | 56.4692 | Pavilion JCT | BC_PAV_JCT | Continental Lime Limited JCT | BC_CLL_JCT |  |  | 623
| 60L020CLL | BC Hydro | British Columbia | 1 | ac | 0.13999 | 0.086411 | 0.13999 | 0.086411 | 69 | 0.053794 |  | 485 | 588 | 57.9631 | 70.2728 | 0.9 | 52.1668 | 63.2455 | Continental Lime Limited JCT | BC_CLL_JCT | Continental Lime Limited | BC_CLL_ISS |  |  | 624
| 60L020 | BC Hydro | British Columbia | 1 | ac | 23 | 14.1975 | 74.24 | 45.8272 | 69 | 28.5294 |  | 400 | 525 | 47.8046 | 62.7435 | 0.9 | 43.0241 | 56.4692 | Continental Lime Limited JCT | BC_CLL_JCT | Carquille | BC_CRQ_DSS |  |  | 625
| 60L021 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 26.77 | 16.5247 | 69 | 10.2873 |  | 493 | 590 | 58.9192 | 70.5118 | 0.9 | 53.0273 | 63.4606 | Seton Lake GS | BC_SON_DFS | Walden North JCT | BC_WDN_JCT |  |  | 626
| 60L021WDN | BC Hydro | British Columbia | 1 | ac | 1.3143 | 0.8113 | 1.3143 | 0.8113 | 69 | 0.50507 |  | 616 | 691 | 73.6191 | 82.5825 | 0.9 | 66.2572 | 74.3242 | Walden North JCT | BC_WDN_JCT | Walden North GS | BC_WDN_GSS |  |  | 627
| 60L021 | BC Hydro | British Columbia | 1 | ac | 23.77 | 14.6728 | 26.77 | 16.5247 | 69 | 10.2873 |  | 493 | 590 | 58.9192 | 70.5118 | 0.9 | 53.0273 | 63.4606 | Walden North JCT | BC_WDN_JCT | Bridge River 1 GS | BC_BR1_DFS |  |  | 628
| 60L022 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 59.74 | 36.8765 | 69 | 22.9572 |  | 380 | 640 | 45.4144 | 76.4874 | 0.9 | 40.8729 | 68.8386 | Lajoie GS | BC_LAJ_DFS | Tyax Lake JCT | BC_TXL_JCT |  |  | 629
| 60L022TXL | BC Hydro | British Columbia | 1 | ac | 0.065313 | 0.040316 | 0.065313 | 0.040316 | 69 | 0.025099 |  | 380 | 640 | 45.4144 | 76.4874 | 0.9 | 40.8729 | 68.8386 | Tyax Lake JCT | BC_TXL_JCT | Tyax Lake | BC_TXL_DSS |  |  | 630
| 60L022 | BC Hydro | British Columbia | 1 | ac | 49.74 | 30.7037 | 59.74 | 36.8765 | 69 | 22.9572 |  | 380 | 640 | 45.4144 | 76.4874 | 0.9 | 40.8729 | 68.8386 | Tyax Lake JCT | BC_TXL_JCT | Bridge River 1 GS | BC_BR1_DFS |  |  | 631
| 60L023 | BC Hydro | British Columbia | 1 | ac | 14.7773 | 9.1218 | 14.7773 | 9.1218 | 69 | 5.6787 |  | 580 | 740 | 69.3167 | 88.4385 | 0.9 | 62.385 | 79.5947 | Stave Falls GS | BC_SFL_GSS | Haney | BC_HNY_DSS |  |  | 632
| 60L025 | BC Hydro | British Columbia | 1 | ac | 6.9431 | 4.2858 | 6.9431 | 4.2858 | 69 | 2.6681 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Murrin | BC_MUR_DSS | Sperling | BC_SPG_DSS |  |  | 633
| 60L026 | BC Hydro | British Columbia | 1 | ac | 7.6052 | 4.6946 | 7.6052 | 4.6946 | 69 | 2.9226 |  | 580 | 740 | 69.3167 | 88.4385 | 0.9 | 62.385 | 79.5947 | Como Lake | BC_COK_DSS | Barnard | BC_BND_DSS |  |  | 634
| 60L027 | BC Hydro | British Columbia | 1 | ac | 7.9667 | 4.9177 | 7.9667 | 4.9177 | 69 | 3.0615 |  | 710 | 755 | 84.8532 | 90.2312 | 0.9 | 76.3679 | 81.2081 | Kidd #1 | BC_KI1_DSS | Sperling | BC_SPG_DSS |  |  | 635
| 60L028 | BC Hydro | British Columbia | 1 | ac | 2.7402 | 1.6915 | 2.7402 | 1.6915 | 69 | 1.053 |  | 670 | 715 | 80.0727 | 85.4507 | 0.9 | 72.0654 | 76.9057 | George Dickie | BC_GDK_DSS | Sperling | BC_SPG_DSS |  |  | 636
| 60L029 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 59.64 | 36.8148 | 69 | 22.9188 |  | 427 | 604 | 51.0314 | 72.1849 | 0.9 | 45.9283 | 64.9665 | Carquille | BC_CRQ_DSS | Cache Creek JCT | BC_CCW_JCT |  |  | 637
| 60L029CCW | BC Hydro | British Columbia | 1 | ac | 0.5 | 0.30864 | 0.5 | 0.30864 | 69 | 0.19214 |  | 493 | 627 | 58.9192 | 74.9337 | 0.9 | 53.0273 | 67.4403 | Cache Creek JCT | BC_CCW_JCT | Cache Creek | BC_CCW_DSS |  |  | 638
| 60L029 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 59.64 | 36.8148 | 69 | 22.9188 |  | 427 | 604 | 51.0314 | 72.1849 | 0.9 | 45.9283 | 64.9665 | Cache Creek JCT | BC_CCW_JCT | Ashcroft JCT | BC_AFT_JCT |  |  | 639
| 60L029AFT | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 69 | 0.76857 |  | 493 | 627 | 58.9192 | 74.9337 | 0.9 | 53.0273 | 67.4403 | Ashcroft JCT | BC_AFT_JCT | Ashcroft | BC_AFT_DSS |  |  | 640
| 60L029 | BC Hydro | British Columbia | 1 | ac | 39.64 | 24.4691 | 59.64 | 36.8148 | 69 | 22.9188 |  | 427 | 604 | 51.0314 | 72.1849 | 0.9 | 45.9283 | 64.9665 | Ashcroft JCT | BC_AFT_JCT | Spences Bridge | BC_SBR_DSS |  |  | 641
| 60L030 | BC Hydro | British Columbia | 1 | ac | 5.0798 | 3.1357 | 5.0798 | 3.1357 | 69 | 1.9521 |  | 670 | 715 | 80.0727 | 85.4507 | 0.9 | 72.0654 | 76.9057 | Kidd #1 | BC_KI1_DSS | George Dickie | BC_GDK_DSS |  |  | 642
| 60L031 | BC Hydro | British Columbia | 1 | ac | 1.5 | 0.92593 | 7.32 | 4.5185 | 69 | 2.813 |  | 500 | 525 | 59.7558 | 62.7435 | 0.9 | 53.7802 | 56.4692 | Big Bend | BC_BBS_DSS | Tree Island Industries JCT | BC_TII_JCT |  |  | 643
| 60L031TII | BC Hydro | British Columbia | 1 | ac | 1.501 | 0.92656 | 1.501 | 0.92656 | 69 | 0.57682 |  | 500 | 525 | 59.7558 | 62.7435 | 0.9 | 53.7802 | 56.4692 | Tree Island Industries JCT | BC_TII_JCT | Tree Island Industries | BC_TII_DSS |  |  | 644
| 60L031 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 7.32 | 4.5185 | 69 | 2.813 |  | 490 | 515 | 58.5606 | 61.5484 | 0.9 | 52.7046 | 55.3936 | Tree Island Industries JCT | BC_TII_JCT | Annacis Island JCT | BC_ANN_JCT |  |  | 645
| 60L031ANN | BC Hydro | British Columbia | 1 | ac | 0.031403 | 0.019385 | 0.031403 | 0.019385 | 69 | 0.012068 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Annacis Island JCT | BC_ANN_JCT | Annacis Island | BC_ANN_DSS |  |  | 646
| 60L031 | BC Hydro | British Columbia | 1 | ac | 1.5 | 0.92593 | 7.32 | 4.5185 | 69 | 2.813 |  | 810 | 940 | 96.8043 | 112.3408 | 0.9 | 87.1239 | 101.1067 | Annacis Island JCT | BC_ANN_JCT | Annacis Island Wastewater Treatment Plant JCT | BC_AWT_JCT |  |  | 647
| 60L031AWT | BC Hydro | British Columbia | 1 | ac | 1.559 | 0.96237 | 1.559 | 0.96237 | 69 | 0.59911 |  | 505 | 605 | 60.3533 | 72.3045 | 0.9 | 54.318 | 65.074 | Annacis Island Wastewater Treatment Plant JCT | BC_AWT_JCT | Annacis Island Wastewater Treatment Plant | BC_AWT_ISS |  |  | 648
| 60L031IPM | BC Hydro | British Columbia | 1 | ac | 0.88 | 0.54321 | 0.88 | 0.54321 | 69 | 0.33817 |  | 810 | 940 | 96.8043 | 112.3408 | 0.9 | 87.1239 | 101.1067 | Annacis Island Wastewater Treatment Plant JCT | BC_AWT_JCT | Island Paper Mill | BC_IPM_ISS |  |  | 649
| 60L031 | BC Hydro | British Columbia | 1 | ac | 3.32 | 2.0494 | 7.32 | 4.5185 | 69 | 2.813 |  | 810 | 940 | 96.8043 | 112.3408 | 0.9 | 87.1239 | 101.1067 | Annacis Island Wastewater Treatment Plant JCT | BC_AWT_JCT | Ingledow | BC_ING_DSS |  |  | 650
| 60L032 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 9.43 | 5.821 | 69 | 3.6238 |  | 750 | 965 | 89.6336 | 115.3286 | 0.9 | 80.6703 | 103.7957 | Kidd #1 | BC_KI1_DSS | Westcoast Cellufibre JCT | BC_WCF_JCT |  |  | 651
| 60L032WCF | BC Hydro | British Columbia | 1 | ac | 0.026621 | 0.016432 | 0.026621 | 0.016432 | 69 | 0.01023 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Westcoast Cellufibre JCT | BC_WCF_JCT | Westcoast Cellufibre | BC_WCF_ISS |  |  | 652
| 60L032 | BC Hydro | British Columbia | 1 | ac | 8.43 | 5.2037 | 9.43 | 5.821 | 69 | 3.6238 |  | 642 | 692 | 76.7264 | 82.702 | 0.9 | 69.0537 | 74.4318 | Westcoast Cellufibre JCT | BC_WCF_JCT | Big Bend | BC_BBS_DSS |  |  | 653
| 60L033 | BC Hydro | British Columbia | 1 | ac | 0.011787 | 0.0072762 | 0.011787 | 0.0072762 | 69 | 0.0045298 |  | 750 | 960 | 89.6336 | 114.731 | 0.9 | 80.6703 | 103.2579 | Sea Island | BC_SEA_DSS | Vancouver International Airport | BC_YVR_ISS |  |  | 654
| 60L035 | BC Hydro | British Columbia | 1 | ac | 7.615 | 4.7006 | 10.4003 | 6.4199 | 69 | 3.9967 |  | 750 | 960 | 89.6336 | 114.731 | 0.9 | 80.6703 | 103.2579 | Newell | BC_NEL_DSS | Barnard | BC_BND_DSS |  |  | 655
| 60L035 | BC Hydro | British Columbia | 1 | ac | 2.7853 | 1.7193 | 10.4003 | 6.4199 | 69 | 3.9967 |  | 845 | 1020 | 100.9872 | 121.9017 | 0.9 | 90.8885 | 109.7116 | Newell | BC_NEL_DSS | New Westminster | BC_NWR_DSS |  |  | 656
| 60L036 | BC Hydro | British Columbia | 1 | ac | 7.6417 | 4.7171 | 7.6417 | 4.7171 | 69 | 2.9366 |  | 630 | 810 | 75.2922 | 96.8043 | 0.9 | 67.763 | 87.1239 | Newell | BC_NEL_DSS | Barnard | BC_BND_DSS |  |  | 657
| 60L037 | BC Hydro | British Columbia | 1 | ac | 0.72811 | 0.44945 | 0.72811 | 0.44945 | 69 | 0.2798 |  | 870 | 1050 | 103.975 | 125.4871 | 0.9 | 93.5775 | 112.9384 | Kidd #2 | BC_KI2_DSS | Kidd #1 | BC_KI2_DSS |  |  | 658
| 60L038 | BC Hydro | British Columbia | 1 | ac | 0.72303 | 0.44632 | 0.72303 | 0.44632 | 69 | 0.27785 |  | 870 | 1050 | 103.975 | 125.4871 | 0.9 | 93.5775 | 112.9384 | Kidd #2 | BC_KI2_DSS | Kidd #1 | BC_KI1_DSS |  |  | 659
| 60L039 | BC Hydro | British Columbia | 1 | ac | 4.04 | 2.4938 | 9.04 | 5.5802 | 69 | 3.4739 |  | 750 | 965 | 89.6336 | 115.3286 | 0.9 | 80.6703 | 103.7957 | Horne Payne | BC_HPN_DSS | Lougheed JCT | BC_LOH_JCT |  |  | 660
| 60L039LOH | BC Hydro | British Columbia | 1 | ac | 0.040091 | 0.024748 | 0.040091 | 0.024748 | 69 | 0.015407 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Lougheed JCT | BC_LOH_JCT | Lougheed | BC_LOH_DSS |  |  | 661
| 60L039 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 9.04 | 5.5802 | 69 | 3.4739 |  | 750 | 965 | 89.6336 | 115.3286 | 0.9 | 80.6703 | 103.7957 | Lougheed JCT | BC_LOH_JCT | Bingham JCT | BC_BMP_JCT |  |  | 662
| 60L039 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 9.04 | 5.5802 | 69 | 3.4739 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Bingham JCT | BC_BMP_JCT | Barnard | BC_BND_DSS |  |  | 663
| 60L039BMP | BC Hydro | British Columbia | 1 | ac | 1.7398 | 1.074 | 1.7398 | 1.074 | 69 | 0.66859 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Bingham JCT | BC_BMP_JCT | Bingham | BC_BMP_DSS |  |  | 664
| 60L040 | BC Hydro | British Columbia | 1 | ac | 4.01 | 2.4753 | 9.01 | 5.5617 | 69 | 3.4624 |  | 750 | 965 | 89.6336 | 115.3286 | 0.9 | 80.6703 | 103.7957 | Horne Payne | BC_HPN_DSS | Lougheed JCT | BC_LOH_JCT |  |  | 665
| 60L040LOH | BC Hydro | British Columbia | 1 | ac | 0.0099246 | 0.0061263 | 0.0099246 | 0.0061263 | 69 | 0.0038139 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Lougheed JCT | BC_LOH_JCT | Lougheed | BC_LOH_DSS |  |  | 666
| 60L040 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 9.01 | 5.5617 | 69 | 3.4624 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Lougheed JCT | BC_LOH_JCT | Barnard | BC_BND_DSS |  |  | 667
| 60L041 | BC Hydro | British Columbia | 1 | ac | 3.136 | 1.9358 | 3.136 | 1.9358 | 69 | 1.2051 |  | 170 | 170 | 20.317 | 20.317 | 0.9 | 18.2853 | 18.2853 | Kidd #1 | BC_KI1_DSS | Richmond Steel Recycling | BC_RSR_ISS |  |  | 668
| 60L042 | BC Hydro | British Columbia | 1 | ac | 12.8072 | 7.9057 | 12.8072 | 7.9057 | 69 | 4.9216 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Kidd #2 | BC_KI2_DSS | Lafarge #1 | BC_LF1_ISS |  |  | 669
| 60L043 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 4.95 | 3.0556 | 69 | 1.9022 |  | 1165 | 1505 | 139.2309 | 179.8648 | 0.9 | 125.3078 | 161.8783 | Kidd #2 | BC_KI2_DSS | Sea Island JCT | BC_SEA_JCT |  |  | 670
| 60L043SEA | BC Hydro | British Columbia | 1 | ac | 2.7555 | 1.7009 | 2.7555 | 1.7009 | 69 | 1.0589 |  | 605 | 660 | 72.3045 | 78.8776 | 0.9 | 65.074 | 70.9898 | Sea Island JCT | BC_SEA_JCT | Sea Island | BC_SEA_DSS |  |  | 671
| 60L043 | BC Hydro | British Columbia | 1 | ac | 3.95 | 2.4383 | 4.95 | 3.0556 | 69 | 1.9022 |  | 750 | 965 | 89.6336 | 115.3286 | 0.9 | 80.6703 | 103.7957 | Sea Island JCT | BC_SEA_JCT | Richmond | BC_RIM_DSS |  |  | 672
| 60L044 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 4.95 | 3.0556 | 69 | 1.9022 |  | 1160 | 1505 | 138.6333 | 179.8648 | 0.9 | 124.77 | 161.8783 | Kidd #2 | BC_KI2_DSS | Sea Island JCT | BC_SEA_JCT |  |  | 673
| 60L044SEA | BC Hydro | British Columbia | 1 | ac | 2.6095 | 1.6108 | 2.6095 | 1.6108 | 69 | 1.0028 |  | 605 | 660 | 72.3045 | 78.8776 | 0.9 | 65.074 | 70.9898 | Sea Island JCT | BC_SEA_JCT | Sea Island | BC_SEA_DSS |  |  | 674
| 60L044 | BC Hydro | British Columbia | 1 | ac | 3.95 | 2.4383 | 4.95 | 3.0556 | 69 | 1.9022 |  | 750 | 965 | 89.6336 | 115.3286 | 0.9 | 80.6703 | 103.7957 | Sea Island JCT | BC_SEA_JCT | Richmond | BC_RIM_DSS |  |  | 675
| 60L045 | BC Hydro | British Columbia | 1 | ac | 0.72948 | 0.4503 | 0.72948 | 0.4503 | 69 | 0.28033 |  | 870 | 1050 | 103.975 | 125.4871 | 0.9 | 93.5775 | 112.9384 | Kidd #2 | BC_KI2_DSS | Kidd #1 | BC_KI1_DSS |  |  | 676
| 60L046 | BC Hydro | British Columbia | 1 | ac | 0.71862 | 0.44359 | 0.71862 | 0.44359 | 69 | 0.27615 |  | 870 | 1050 | 103.975 | 125.4871 | 0.9 | 93.5775 | 112.9384 | Kidd #2 | BC_KI2_DSS | Kidd #1 | BC_KI1_DSS |  |  | 677
| 60L047 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 32.04 | 19.7778 | 69 | 12.3125 |  | 900 | 1190 | 107.5604 | 142.2187 | 0.9 | 96.8043 | 127.9968 | Atchelitz | BC_ALZ_DSS | Trans Mountain JCT | BC_TMO_JCT |  |  | 678
| 60L047TMO | BC Hydro | British Columbia | 1 | ac | 6.7905 | 4.1917 | 6.7905 | 4.1917 | 69 | 2.6095 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Trans Mountain JCT | BC_TMO_JCT | Trans Mountain | BC_TMO_DSS |  |  | 679
| 60L047 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 32.04 | 19.7778 | 69 | 12.3125 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Trans Mountain JCT | BC_TMO_JCT | Sumas Way JCT | BC_SMW_JCT |  |  | 680
| 60L047SMW | BC Hydro | British Columbia | 1 | ac | 0.035734 | 0.022058 | 0.035734 | 0.022058 | 69 | 0.013732 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Sumas Way JCT | BC_SMW_JCT | Sumas Way | BC_SMW_DSS |  |  | 681
| 60L047 | BC Hydro | British Columbia | 1 | ac | 2.04 | 1.2593 | 32.04 | 19.7778 | 69 | 12.3125 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Sumas Way JCT | BC_SMW_JCT | Abbotsford | BC_ABB_DSS |  |  | 682
| 60L048 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 32.04 | 19.7778 | 69 | 12.3125 |  | 900 | 1190 | 107.5604 | 142.2187 | 0.9 | 96.8043 | 127.9968 | Atchelitz | BC_ALZ_DSS | Trans Mountain JCT | BC_TMO_JCT |  |  | 683
| 60L048TMO | BC Hydro | British Columbia | 1 | ac | 6.7905 | 4.1917 | 6.7905 | 4.1917 | 69 | 2.6095 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Trans Mountain JCT | BC_TMO_JCT | Trans Mountain | BC_TMO_DSS |  |  | 684
| 60L048 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 32.04 | 19.7778 | 69 | 12.3125 |  | 750 | 960 | 89.6336 | 114.731 | 0.9 | 80.6703 | 103.2579 | Trans Mountain JCT | BC_TMO_JCT | Sumas Way JCT | BC_SMW_JCT |  |  | 685
| 60L048SMW | BC Hydro | British Columbia | 1 | ac | 0.067502 | 0.041668 | 0.067502 | 0.041668 | 69 | 0.02594 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Sumas Way JCT | BC_SMW_JCT | Sumas Way | BC_SMW_DSS |  |  | 686
| 60L048 | BC Hydro | British Columbia | 1 | ac | 2.04 | 1.2593 | 32.04 | 19.7778 | 69 | 12.3125 |  | 750 | 960 | 89.6336 | 114.731 | 0.9 | 80.6703 | 103.2579 | Sumas Way JCT | BC_SMW_JCT | Abbotsford | BC_ABB_DSS |  |  | 687
| 60L050 | BC Hydro | British Columbia | 1 | ac | 2.4225 | 1.4954 | 2.4225 | 1.4954 | 69 | 0.93093 |  | 450 | 480 | 53.7802 | 57.3655 | 0.9 | 48.4022 | 51.629 | Murrin | BC_MUR_DSS | Dal Grauer | BC_DGR_DSS |  |  | 688
| 60L051 | BC Hydro | British Columbia | 1 | ac | 2.4559 | 1.516 | 2.4559 | 1.516 | 69 | 0.94377 |  | 450 | 480 | 53.7802 | 57.3655 | 0.9 | 48.4022 | 51.629 | Murrin | BC_MUR_DSS | Dal Grauer | BC_DGR_DSS |  |  | 689
| 60L052 | BC Hydro | British Columbia | 1 | ac | 2.606 | 1.6086 | 2.606 | 1.6086 | 69 | 1.0014 |  | 450 | 480 | 53.7802 | 57.3655 | 0.9 | 48.4022 | 51.629 | Murrin | BC_MUR_DSS | Dal Grauer | BC_DGR_DSS |  |  | 690
| 60L053 | BC Hydro | British Columbia | 1 | ac | 2.4586 | 1.5176 | 2.4586 | 1.5176 | 69 | 0.94479 |  | 450 | 480 | 53.7802 | 57.3655 | 0.9 | 48.4022 | 51.629 | Murrin | BC_MUR_DSS | Dal Grauer | BC_DGR_DSS |  |  | 691
| 60L054 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 2.68 | 1.6543 | 69 | 1.0299 |  | 400 | 510 | 47.8046 | 60.9509 | 0.9 | 43.0241 | 54.8558 | Barnard | BC_BND_DSS | Simon Fraser University JCT | BC_SFU_JCT |  |  | 692
| 60L054SFU | BC Hydro | British Columbia | 1 | ac | 1.4764 | 0.91133 | 1.4764 | 0.91133 | 69 | 0.56734 |  | 500 | 600 | 59.7558 | 71.7069 | 0.9 | 53.7802 | 64.5362 | Simon Fraser University JCT | BC_SFU_JCT | Simon Fraser University | BC_SFU_DSS |  |  | 693
| 60L054 | BC Hydro | British Columbia | 1 | ac | 0.68 | 0.41975 | 2.68 | 1.6543 | 69 | 1.0299 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Simon Fraser University JCT | BC_SFU_JCT | Petro Canada Products | BC_PCP_ISS |  |  | 694
| 60L055 | BC Hydro | British Columbia | 1 | ac | 18.7048 | 11.5462 | 18.7048 | 11.5462 | 69 | 7.188 |  | 519 | 592 | 62.0265 | 70.7508 | 0.9 | 55.8238 | 63.6757 | Jamie Creek GS | BC_JME_GSS | Lajoie GS | BC_LAJ_DFS |  |  | 695
| 60L056 | BC Hydro | British Columbia | 1 | ac | 8.41 | 5.1914 | 8.41 | 5.1914 | 69 | 3.2318 |  | 590 | 610 | 70.5118 | 72.902 | 0.9 | 63.4606 | 65.6118 | Sperling | BC_SPG_DSS | University of BC | BC_UNY_DSS |  |  | 696
| 60L057 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 5.95 | 3.6728 | 69 | 2.2865 |  | 673 | 715 | 80.4312 | 85.4507 | 0.9 | 72.3881 | 76.9057 | Sperling | BC_SPG_DSS | Camosun | BC_CSN_DSS |  |  | 697
| 60L057 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 5.95 | 3.6728 | 69 | 2.2865 |  | 845 | 1010 | 100.9872 | 120.7066 | 0.9 | 90.8885 | 108.636 | Camosun | BC_CSN_DSS | South Campus JCT | BC_UNS_JCT |  |  | 698
| 60L057UNS | BC Hydro | British Columbia | 1 | ac | 0.41198 | 0.25431 | 0.41198 | 0.25431 | 69 | 0.15832 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | South Campus JCT | BC_UNS_JCT | South Campus | BC_UNS_DSS |  |  | 699
| 60L057 | BC Hydro | British Columbia | 1 | ac | 1.95 | 1.2037 | 5.95 | 3.6728 | 69 | 2.2865 |  | 463 | 490 | 55.3338 | 58.5606 | 0.9 | 49.8004 | 52.7046 | South Campus JCT | BC_UNS_JCT | University of BC | BC_UNY_DSS |  |  | 700
| 60L058 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 8 | 4.9383 | 69 | 3.0743 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Arnott | BC_ARN_DSS | Tsawassen JCT | BC_TSW_JCT |  |  | 701
| 60L058TSW | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 69 | 0.76857 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Tsawassen JCT | BC_TSW_JCT | Tsawassen | BC_TSW_DSS |  |  | 702
| 60L058 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 8 | 4.9383 | 69 | 3.0743 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Tsawassen JCT | BC_TSW_JCT | Delta Port Terminal JCT | BC_DPT_JCT |  |  | 703
| 60L058DPT | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 |  | 590 | 610 | 70.5118 | 72.902 | 0.9 | 63.4606 | 65.6118 | Delta Port Terminal JCT | BC_DPT_JCT | Delta Port Terminal | BC_DPT_DSS |  |  | 704
| 60L058WTL | BC Hydro | British Columbia | 1 | ac | 1.2038 | 0.74306 | 1.2038 | 0.74306 | 69 | 0.46259 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Delta Port Terminal JCT | BC_DPT_JCT | Westshore Terminals | BC_WTL_ISS |  |  | 706
| 60L059BCI | BC Hydro | British Columbia | 1 | ac | 0.4 | 0.24691 | 0.4 | 0.24691 | 69 | 0.15371 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Buckeye | BC_BCI_ISS | Lantic Real Property JCT | BC_LRP_JCT |  |  | 707
| 60L059LRP | BC Hydro | British Columbia | 1 | ac | 0.02 | 0.012346 | 0.02 | 0.012346 | 69 | 0.0076857 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Lantic Real Property JCT | BC_LRP_JCT | Lantic Real Property | BC_LRP_ISS |  |  | 707
| 60L059 | BC Hydro | British Columbia | 1 | ac | 0.5 | 0.30864 | 17.75 | 10.9568 | 69 | 6.8211 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Lantic Real Property JCT | BC_LRP_JCT | Lehigh Heidelberg JCT | BC_LNH_JCT |  |  | 708
| 60L059LNH | BC Hydro | British Columbia | 1 | ac | 0.2 | 0.12346 | 0.2 | 0.12346 | 69 | 0.076857 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Lehigh Heidelberg JCT | BC_LNH_JCT | Lehigh Heidelberg | BC_LNH_ISS |  |  | 708
| 60L059 | BC Hydro | British Columbia | 1 | ac | 1.1 | 0.67901 | 17.75 | 10.9568 | 69 | 6.8211 |  | 845 | 1010 | 100.9872 | 120.7066 | 0.9 | 90.8885 | 108.636 | Lehigh Heidelberg JCT | BC_LNH_JCT | Tilbury JCT | BC_TLB_JCT |  |  | 709
| 60L059TLB | BC Hydro | British Columbia | 1 | ac | 0.5 | 0.30864 | 0.5 | 0.30864 | 69 | 0.19214 |  | 845 | 1010 | 100.9872 | 120.7066 | 0.9 | 90.8885 | 108.636 | Tilbury JCT | BC_TLB_JCT | Tilbury | BC_TLB_ISS |  |  | 709
| 60L059 | BC Hydro | British Columbia | 1 | ac | 0.4 | 0.24691 | 17.75 | 10.9568 | 69 | 6.8211 |  | 845 | 1010 | 100.9872 | 120.7066 | 0.9 | 90.8885 | 108.636 | Tilbury JCT | BC_TLB_JCT | Canadian Auto Parts Toyota JCT | BC_CAN_JCT |  |  | 709
| 60L059CAN | BC Hydro | British Columbia | 1 | ac | 0.01 | 0.0061728 | 0.01 | 0.0061728 | 69 | 0.0038429 |  | 845 | 1010 | 100.9872 | 120.7066 | 0.9 | 90.8885 | 108.636 | Canadian Auto Parts Toyota JCT | BC_CAN_JCT | Canadian Auto Parts Toyota | BC_CAN_ISS |  |  | 709
| 60L059 | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 17.75 | 10.9568 | 69 | 6.8211 |  | 845 | 1010 | 100.9872 | 120.7066 | 0.9 | 90.8885 | 108.636 | Canadian Auto Parts Toyota JCT | BC_CAN_JCT | Arnott | BC_ARN_DSS |  |  | 710
| 60L059 | BC Hydro | British Columbia | 1 | ac | 5.75 | 3.5494 | 17.75 | 10.9568 | 69 | 6.8211 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Arnott | BC_ARN_DSS | Tsawassen JCT | BC_TSW_JCT |  |  | 711
| 60L059TSW | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 3 | 1.8519 | 69 | 1.1529 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Tsawassen JCT | BC_TSW_JCT | Tsawassen | BC_TSW_DSS |  |  | 712
| 60L059 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 17.75 | 10.9568 | 69 | 6.8211 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Tsawassen JCT | BC_TSW_JCT | Delta Port Terminal JCT | BC_DPT_JCT |  |  | 713
| 60L060 | BC Hydro | British Columbia | 1 | ac | 4.1662 | 2.5717 | 4.1662 | 2.5717 | 69 | 1.601 |  | 730 | 879 | 87.2434 | 105.0506 | 0.9 | 78.5191 | 94.5456 | Newell | BC_NEL_DSS | New Westminster | BC_NWR_DSS |  |  | 714
| 60L061 | BC Hydro | British Columbia | 1 | ac | 3.111 | 1.9204 | 3.111 | 1.9204 | 69 | 1.1955 |  | 847 | 1020 | 101.2262 | 121.9017 | 0.9 | 91.1036 | 109.7116 | Walters | BC_WLT_DSS | North Vancouver | BC_NVR_DSS |  |  | 715
| 60L062 | BC Hydro | British Columbia | 1 | ac | 2.39 | 1.4753 | 3.39 | 2.0926 | 69 | 1.3027 |  | 847 | 1020 | 101.2262 | 121.9017 | 0.9 | 91.1036 | 109.7116 | Walters | BC_WLT_DSS | Neptune Bulk Terminal JCT | BC_LCS_JCT |  |  | 716
| 60L062LCS | BC Hydro | British Columbia | 1 | ac | 0.12095 | 0.074659 | 0.12095 | 0.074659 | 69 | 0.046478 |  | 492 | 601 | 58.7997 | 71.8264 | 0.9 | 52.9197 | 64.6438 | Neptune Bulk Terminal JCT | BC_LCS_JCT | Neptune Bulk Terminal | BC_LCS_ISS |  |  | 717
| 60L062 | BC Hydro | British Columbia | 1 | ac | 0.5 | 0.30864 | 3.39 | 2.0926 | 69 | 1.3027 |  | 847 | 1020 | 101.2262 | 121.9017 | 0.9 | 91.1036 | 109.7116 | Neptune Bulk Terminal JCT | BC_LCS_JCT | Saskatchewan Wheat Pool JCT | BC_SWP_JCT |  |  | 718
| 60L062SWP | BC Hydro | British Columbia | 1 | ac | 0.42582 | 0.26285 | 0.42582 | 0.26285 | 69 | 0.16364 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Saskatchewan Wheat Pool JCT | BC_SWP_JCT | Saskatchewan Wheat Pool | BC_SWP_ISS |  |  | 719
| 60L062 | BC Hydro | British Columbia | 1 | ac | 0.5 | 0.30864 | 3.39 | 2.0926 | 69 | 1.3027 |  | 847 | 1020 | 101.2262 | 121.9017 | 0.9 | 91.1036 | 109.7116 | Saskatchewan Wheat Pool JCT | BC_SWP_JCT | North Vancouver | BC_NVR_DSS |  |  | 720
| 60L063 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 4.88 | 3.0123 | 69 | 1.8753 |  | 870 | 1050 | 103.975 | 125.4871 | 0.9 | 93.5775 | 112.9384 | North Vancouver | BC_NVR_DSS | James Richardson JCT | BC_JRI_JCT |  |  | 721
| 60L063JRI | BC Hydro | British Columbia | 1 | ac | 0.41808 | 0.25807 | 0.41808 | 0.25807 | 69 | 0.16066 |  | 500 | 590 | 59.7558 | 70.5118 | 0.9 | 53.7802 | 63.4606 | James Richardson JCT | BC_JRI_JCT | James Richardson | BC_JRI_DSS |  |  | 722
| 60L063 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 4.88 | 3.0123 | 69 | 1.8753 |  | 870 | 1050 | 103.975 | 125.4871 | 0.9 | 93.5775 | 112.9384 | James Richardson JCT | BC_JRI_JCT | Vancouver Dry Dock JCT | BC_VDK_JCT |  |  | 723
| 60L063VDK | BC Hydro | British Columbia | 1 | ac | 0.38845 | 0.23978 | 0.38845 | 0.23978 | 69 | 0.14927 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Vancouver Dry Dock JCT | BC_VDK_JCT | Vancouver Dry Dock | BC_VDK_ISS |  |  | 724
| 60L063 | BC Hydro | British Columbia | 1 | ac | 1.88 | 1.1605 | 4.88 | 3.0123 | 69 | 1.8753 |  | 870 | 1050 | 103.975 | 125.4871 | 0.9 | 93.5775 | 112.9384 | Vancouver Dry Dock JCT | BC_VDK_JCT | Vancouver Shipyards JCT | BC_VSY_JCT |  |  | 725
| 60L063VSY | BC Hydro | British Columbia | 1 | ac | 0.097914 | 0.060441 | 0.097914 | 0.060441 | 69 | 0.037627 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Vancouver Shipyards JCT | BC_VSY_JCT | Vancouver Shipyards | BC_VSY _ISS |  |  | 726
| 60L063 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 4.88 | 3.0123 | 69 | 1.8753 |  | 870 | 1050 | 103.975 | 125.4871 | 0.9 | 93.5775 | 112.9384 | Vancouver Shipyards JCT | BC_VSY_JCT | Northgate | BC_NOR_DSS |  |  | 727
| 60L064 | BC Hydro | British Columbia | 1 | ac | 8.8529 | 5.4647 | 8.8529 | 5.4647 | 69 | 3.402 |  | 777 | 965 | 92.8604 | 115.3286 | 0.9 | 83.5744 | 103.7957 | Capilano | BC_CAP_DSS | Walters | BC_WLT_DSS |  |  | 728
| 60L065 | BC Hydro | British Columbia | 1 | ac | 5.54 | 3.4198 | 7.54 | 4.6543 | 69 | 2.8975 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | John Lawson | BC_JLN_DSS | Hillcrest JCT | BC_HCT_JCT |  |  | 729
| 60L065HCT | BC Hydro | British Columbia | 1 | ac | 0.017163 | 0.010595 | 0.017163 | 0.010595 | 69 | 0.0065956 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Hillcrest JCT | BC_HCT_JCT | Hillcrest | BC_HCT_DSS |  |  | 730
| 60L065 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 7.54 | 4.6543 | 69 | 2.8975 |  | 1100 | 1505 | 131.4627 | 179.8648 | 0.9 | 118.3164 | 161.8783 | Hillcrest JCT | BC_HCT_JCT | Cypress | BC_CYP_DSS |  |  | 731
| 60L066 | BC Hydro | British Columbia | 1 | ac | 4.7836 | 2.9528 | 9.5672 | 5.9057 | 69 | 3.6765 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Capilano | BC_CAP_DSS | Capilano Pumps JCT | BC_CPS_JCT |  |  | 732
| 60L066CPS | BC Hydro | British Columbia | 1 | ac | 0.50982 | 0.3147 | 0.50982 | 0.3147 | 69 | 0.19592 |  | 540 | 570 | 64.5362 | 68.1216 | 0.9 | 58.0826 | 61.3094 | Capilano Pumps JCT | BC_CPS_JCT | Capilano Pumps | BC_CPS_DSS |  |  | 733
| 60L066 | BC Hydro | British Columbia | 1 | ac | 4.7836 | 2.9528 | 9.5672 | 5.9057 | 69 | 3.6765 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Capilano Pumps JCT | BC_CPS_JCT | Glenmore BCH | BC_GLR_DSS |  |  | 734
| 60L067 | BC Hydro | British Columbia | 1 | ac | 5.7904 | 3.5743 | 11.5807 | 7.1486 | 69 | 4.4503 |  | 730 | 879 | 87.2434 | 105.0506 | 0.9 | 78.5191 | 94.5456 | Newell | BC_NEL_DSS | Kruger Products JCT | BC_SCP_JCT |  |  | 735
| 60L067SCP | BC Hydro | British Columbia | 1 | ac | 0.037681 | 0.02326 | 0.037681 | 0.02326 | 69 | 0.01448 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Kruger Products JCT | BC_SCP_JCT | Kruger Products | BC_SCP_ISS |  |  | 736
| 60L067 | BC Hydro | British Columbia | 1 | ac | 5.7904 | 3.5743 | 11.5807 | 7.1486 | 69 | 4.4503 |  | 845 | 1021 | 100.9872 | 122.0212 | 0.9 | 90.8885 | 109.8191 | Kruger Products JCT | BC_SCP_JCT | Royal 2 | BC_RO2_DSS |  |  | 737
| 60L068 | BC Hydro | British Columbia | 1 | ac | 6.49 | 4.0062 | 11.49 | 7.0926 | 69 | 4.4154 |  | 845 | 1021 | 100.9872 | 122.0212 | 0.9 | 90.8885 | 109.8191 | Cheekye | BC_CKY_DSS | Mamquam JCT | BC_MAM_JCT |  |  | 738
| 60L068 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 11.49 | 7.0926 | 69 | 4.4154 |  | 845 | 1021 | 100.9872 | 122.0212 | 0.9 | 90.8885 | 109.8191 | Mamquam JCT | BC_MAM_JCT | Upper Mamquam JCT | BC_UMH_JCT |  |  | 739
| 60L068 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 11.49 | 7.0926 | 69 | 4.4154 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Upper Mamquam JCT | BC_UMH_JCT | Squamish | BC_SQH_DSS |  |  | 740
| 60L069 | BC Hydro | British Columbia | 1 | ac | 14.5 | 8.9506 | 44.5 | 27.4691 | 69 | 17.1007 |  | 845 | 1020 | 100.9872 | 121.9017 | 0.9 | 90.8885 | 109.7116 | Squamish | BC_SQH_DSS | Britannia JCT | BC_BTA_JCT |  |  | 741
| 60L069BTA | BC Hydro | British Columbia | 1 | ac | 0.17592 | 0.1086 | 0.17592 | 0.1086 | 69 | 0.067605 |  | 425 | 510 | 50.7924 | 60.9509 | 0.9 | 45.7132 | 54.8558 | Britannia JCT | BC_BTA_JCT | Britannia | BC_BTA_DSS |  |  | 742
| 60L069 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 44.5 | 27.4691 | 69 | 17.1007 |  | 845 | 1020 | 100.9872 | 121.9017 | 0.9 | 90.8885 | 109.7116 | Britannia JCT | BC_BTA_JCT | Furry Creek JCT | BC_FRC_JCT |  |  | 743
| 60L069FRC | BC Hydro | British Columbia | 1 | ac | 0.047808 | 0.029511 | 0.047808 | 0.029511 | 69 | 0.018372 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Furry Creek JCT | BC_FRC_JCT | Furry Creek | BC_FRC_DSS |  |  | 744
| 60L069 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 44.5 | 27.4691 | 69 | 17.1007 |  | 500 | 600 | 59.7558 | 71.7069 | 0.9 | 53.7802 | 64.5362 | Furry Creek JCT | BC_FRC_JCT | Furry Creek GS JCT | BC_FRI_JCT |  |  | 745
| 60L069FRI | BC Hydro | British Columbia | 1 | ac | 0.047808 | 0.029511 | 0.047808 | 0.029511 | 69 | 0.018372 |  | 267 | 450 | 31.9096 | 53.7802 | 0.9 | 28.7186 | 48.4022 | Furry Creek GS JCT | BC_FRI_JCT | Furry Creek GS | BC_FRI_GSS |  |  | 746
| 60L069 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 44.5 | 27.4691 | 69 | 17.1007 |  | 500 | 600 | 59.7558 | 71.7069 | 0.9 | 53.7802 | 64.5362 | Furry Creek GS JCT | BC_FRI_JCT | Porteau Cove JCT | BC_PTO_JCT |  |  | 747
| 60L069PTO | BC Hydro | British Columbia | 1 | ac | 0.013759 | 0.0084935 | 0.013759 | 0.0084935 | 69 | 0.0052876 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Porteau Cove JCT | BC_PTO_JCT | Porteau Cove | BC_PTO_DSS |  |  | 748
| 60L069 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 44.5 | 27.4691 | 69 | 17.1007 |  | 500 | 600 | 59.7558 | 71.7069 | 0.9 | 53.7802 | 64.5362 | Porteau Cove JCT | BC_PTO_JCT | Lions Bay JCT | BC_LBY_JCT |  |  | 749
| 60L069LBY | BC Hydro | British Columbia | 1 | ac | 0.025678 | 0.015851 | 0.025678 | 0.015851 | 69 | 0.0098678 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Lions Bay JCT | BC_LBY_JCT | Lions Bay | BC_LBY_DSS |  |  | 750
| 60L069 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 44.5 | 27.4691 | 69 | 17.1007 |  | 500 | 600 | 59.7558 | 71.7069 | 0.9 | 53.7802 | 64.5362 | Lions Bay JCT | BC_LBY_JCT | Horsheshoe Bay | BC_HSB_DSS |  |  | 751
| 60L070 | BC Hydro | British Columbia | 1 | ac | 7.02 | 4.3333 | 12.02 | 7.4198 | 69 | 4.6191 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Cheekye | BC_CKY_DSS | Mamquam JCT | BC_MAM_JCT |  |  | 752
| 60L070 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 12.02 | 7.4198 | 69 | 4.6191 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Mamquam JCT | BC_MAM_JCT | Upper Mamquam JCT | BC_UMH_JCT |  |  | 753
| 60L070 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 12.02 | 7.4198 | 69 | 4.6191 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Upper Mamquam JCT | BC_UMH_JCT | Squamish | BC_SQH_DSS |  |  | 754
| 60L071 | BC Hydro | British Columbia | 1 | ac | 4.3 | 2.6543 | 7.32 | 4.5185 | 69 | 2.813 |  | 810 | 940 | 96.8043 | 112.3408 | 0.9 | 87.1239 | 101.1067 | Big Bend | BC_BBS_DSS | Annacis Island JCT | BC_ANN_JCT |  |  | 755
| 60L071ANN | BC Hydro | British Columbia | 1 | ac | 0.054272 | 0.033501 | 0.054272 | 0.033501 | 69 | 0.020856 |  | 810 | 940 | 96.8043 | 112.3408 | 0.9 | 87.1239 | 101.1067 | Annacis Island JCT | BC_ANN_JCT | Annacis Island | BC_ANN_DSS |  |  | 756
| 60L071 | BC Hydro | British Columbia | 1 | ac | 0.2 | 0.12346 | 7.32 | 4.5185 | 69 | 2.813 |  | 810 | 940 | 96.8043 | 112.3408 | 0.9 | 87.1239 | 101.1067 | Annacis Island JCT | BC_ANN_JCT | Annacis Island Wastewater Treatment Plant JCT | BC_AWT_JCT |  |  | 757
| 60L071AWT | BC Hydro | British Columbia | 1 | ac | 1.5467 | 0.95474 | 1.5467 | 0.95474 | 69 | 0.59437 |  | 500 | 600 | 59.7558 | 71.7069 | 0.9 | 53.7802 | 64.5362 | Annacis Island Wastewater Treatment Plant JCT | BC_AWT_JCT | Annacis Island Wastewater Treatment Plant | BC_AWT_ISS |  |  | 758
| 60L071 | BC Hydro | British Columbia | 1 | ac | 2.82 | 1.7407 | 7.32 | 4.5185 | 69 | 2.813 |  | 810 | 940 | 96.8043 | 112.3408 | 0.9 | 87.1239 | 101.1067 | Annacis Island Wastewater Treatment Plant JCT | BC_AWT_JCT | Ingledow | BC_ING_DSS |  |  | 759
| 60L072 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 |  | 433 | 744 | 51.7485 | 88.9166 | 0.9 | 46.5736 | 80.0249 | Mamquam JCT | BC_MAM_JCT | Mamquam GS | BC_MAM_GSS |  |  | 760
| 60L073 | BC Hydro | British Columbia | 1 | ac | 6.04 | 3.7284 | 19.04 | 11.7531 | 69 | 7.3168 |  | 1050 | 1300 | 125.4871 | 155.365 | 0.9 | 112.9384 | 139.8285 | Ingledow | BC_ING_DSS | Surrey JCT | BC_SRY_JCT |  |  | 761
| 60L073SRY | BC Hydro | British Columbia | 1 | ac | 2.456 | 1.5161 | 2.456 | 1.5161 | 69 | 0.94382 |  | 215 | 290 | 25.695 | 34.6583 | 0.9 | 23.1255 | 31.1925 | Surrey JCT | BC_SRY_JCT | Surrey | BC_SRY_DSS |  |  | 762
| 60L073 | BC Hydro | British Columbia | 1 | ac | 13 | 8.0247 | 19.04 | 11.7531 | 69 | 7.3168 |  | 910 | 960 | 108.7555 | 114.731 | 0.9 | 97.8799 | 103.2579 | Surrey JCT | BC_SRY_JCT | White Rock | BC_WRK_DSS |  |  | 763
| 60L074 | BC Hydro | British Columbia | 1 | ac | 6.04 | 3.7284 | 15.04 | 9.284 | 69 | 5.7797 |  | 1050 | 1300 | 125.4871 | 155.365 | 0.9 | 112.9384 | 139.8285 | Ingledow | BC_ING_DSS | Surrey JCT | BC_SRY_JCT |  |  | 764
| 60L074SRY | BC Hydro | British Columbia | 1 | ac | 2.4459 | 1.5098 | 2.4459 | 1.5098 | 69 | 0.93991 |  | 215 | 290 | 25.695 | 34.6583 | 0.9 | 23.1255 | 31.1925 | Surrey JCT | BC_SRY_JCT | Surrey | BC_SRY_DSS |  |  | 765
| 60L074 | BC Hydro | British Columbia | 1 | ac | 9 | 5.5556 | 15.04 | 9.284 | 69 | 5.7797 |  | 845 | 1020 | 100.9872 | 121.9017 | 0.9 | 90.8885 | 109.7116 | Surrey JCT | BC_SRY_JCT | Nicomekl JCT | BC_NKL_JCT |  |  | 766
| 60L074NKL | BC Hydro | British Columbia | 1 | ac | 0.025894 | 0.015984 | 0.025894 | 0.015984 | 69 | 0.0099506 |  | 800 | 1018 | 95.6092 | 121.6627 | 0.9 | 86.0483 | 109.4964 | Nicomekl JCT | BC_NKL_JCT | Nicomekl | BC_NKL_DSS |  |  | 767
| 60L075 | BC Hydro | British Columbia | 1 | ac | 1.9597 | 1.2097 | 1.9597 | 1.2097 | 69 | 0.75307 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Chevron | BC_CVN_ISS | Shelburn | BC_SHL_DSS |  |  | 768
| 60L076 | BC Hydro | British Columbia | 1 | ac | 6.1721 | 3.8099 | 6.1721 | 3.8099 | 69 | 2.3718 |  | 400 | 510 | 47.8046 | 60.9509 | 0.9 | 43.0241 | 54.8558 | Horne Payne | BC_HPN_DSS | Chevron | BC_CVN_ISS |  |  | 769
| 60L077 | BC Hydro | British Columbia | 1 | ac | 3.225 | 1.9907 | 3.225 | 1.9907 | 69 | 1.2393 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | New Westminster | BC_NWR_DSS | Royal 2 | BC_RO2_DSS |  |  | 770
| 60L078 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 |  | 433 | 744 | 51.7485 | 88.9166 | 0.9 | 46.5736 | 80.0249 | Upper Mamquam JCT | BC_UMH_JCT | Upper Mamquam GS | BC_UMH_GSS |  |  | 771
| 60L079 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 18.01 | 11.1173 | 69 | 6.921 |  | 1070 | 1295 | 127.8773 | 154.7674 | 0.9 | 115.0896 | 139.2907 | Ingledow | BC_ING_DSS | Scott JCT | BC_SCT_JCT |  |  | 772
| 60L079SCT | BC Hydro | British Columbia | 1 | ac | 2.9804 | 1.8398 | 2.9804 | 1.8398 | 69 | 1.1453 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Scott JCT | BC_SCT_JCT | Scott | BC_SCT_DSS |  |  | 773
| 60L079 | BC Hydro | British Columbia | 1 | ac | 13 | 8.0247 | 18.01 | 11.1173 | 69 | 6.921 |  | 730 | 880 | 87.2434 | 105.1701 | 0.9 | 78.5191 | 94.6531 | Scott JCT | BC_SCT_JCT | Harvie Road JCT | BC_HRD_JCT |  |  | 774
| 60L079HRD | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Harvie Road JCT | BC_HRD_JCT | Harvie Road | BC_HRD_DSS |  |  | 775
| 60L079 | BC Hydro | British Columbia | 1 | ac | 4.01 | 2.4753 | 18.01 | 11.1173 | 69 | 6.921 |  | 730 | 880 | 87.2434 | 105.1701 | 0.9 | 78.5191 | 94.6531 | Harvie Road JCT | BC_HRD_JCT | Port Kells JCT | BC_PKL_JCT |  |  | 776
| 60L080 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 18.92 | 11.679 | 69 | 7.2707 |  | 1070 | 1295 | 127.8773 | 154.7674 | 0.9 | 115.0896 | 139.2907 | Ingledow | BC_ING_DSS | Scott JCT | BC_SCT_JCT |  |  | 777
| 60L080SCT | BC Hydro | British Columbia | 1 | ac | 3.0128 | 1.8597 | 3.0128 | 1.8597 | 69 | 1.1578 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Scott JCT | BC_SCT_JCT | Scott | BC_SCT_DSS |  |  | 778
| 60L080 | BC Hydro | British Columbia | 1 | ac | 15.92 | 9.8272 | 18.92 | 11.679 | 69 | 7.2707 |  | 730 | 880 | 87.2434 | 105.1701 | 0.9 | 78.5191 | 94.6531 | Scott JCT | BC_SCT_JCT | Port Kells Pumping JCT | BC_PKP_JCT |  |  | 779
| 60L080PKP | BC Hydro | British Columbia | 1 | ac | 0.36822 | 0.2273 | 0.36822 | 0.2273 | 69 | 0.1415 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Port Kells Pumping JCT | BC_PKP_JCT | Port Kells Pumping | BC_PKP_DSS |  |  | 780
| 60L080 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 18.92 | 11.679 | 69 | 7.2707 |  | 730 | 880 | 87.2434 | 105.1701 | 0.9 | 78.5191 | 94.6531 | Port Kells Pumping JCT | BC_PKP_JCT | Port Kells JCT | BC_PKL_JCT |  |  | 781
| 60L082 | BC Hydro | British Columbia | 1 | ac | 8.8812 | 5.4822 | 8.8812 | 5.4822 | 69 | 3.4129 |  | 731 | 880 | 87.3629 | 105.1701 | 0.9 | 78.6266 | 94.6531 | Ruskin GS | BC_RUS_GSS | Silverdale | BC_SVD_DSS |  |  | 782
| 60L083 | BC Hydro | British Columbia | 1 | ac | 8.8912 | 5.4884 | 8.8912 | 5.4884 | 69 | 3.4168 |  | 635 | 815 | 75.8898 | 97.4019 | 0.9 | 68.3008 | 87.6617 | Keating | BC_KTG_DSS | Sidney | BC_SNY_DSS |  |  | 783
| 60L085 | BC Hydro | British Columbia | 1 | ac | 9.4152 | 5.8119 | 9.4152 | 5.8119 | 69 | 3.6181 |  | 750 | 965 | 89.6336 | 115.3286 | 0.9 | 80.6703 | 103.7957 | Kidd #1 | BC_KI1_DSS | Big Bend | BC_BBS_DSS |  |  | 784
| 60L087 | BC Hydro | British Columbia | 1 | ac | 8.8741 | 5.4778 | 8.8741 | 5.4778 | 69 | 3.4102 |  | 645 | 820 | 77.0849 | 97.9994 | 0.9 | 69.3764 | 88.1995 | Keating | BC_KTG_DSS | Sidney | BC_SNY_DSS |  |  | 785
| 60L089 | BC Hydro | British Columbia | 1 | ac | 5.34 | 3.2963 | 5.34 | 3.2963 | 69 | 2.0521 |  | 370 | 470 | 44.2193 | 56.1704 | 0.9 | 39.7973 | 50.5534 | Cypress | BC_CYP_DSS | Horsheshoe Bay | BC_HSB_DSS |  |  | 786
| 60L090 | BC Hydro | British Columbia | 1 | ac | 0.45 | 0.27778 | 3.58 | 2.2099 | 69 | 1.3757 |  | 1355 | 1645 | 161.9381 | 196.5964 | 0.9 | 145.7443 | 176.9368 | Walters | BC_WLT_DSS | Canexus Corporation JCT | BC_NXC_JCT |  |  | 787
| 60L090 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 3.58 | 2.2099 | 69 | 1.3757 |  | 1070 | 1295 | 127.8773 | 154.7674 | 0.9 | 115.0896 | 139.2907 | Canexus Corporation JCT | BC_NXC_JCT | Deep Cove | BC_DCV_DSS |  |  | 789
| 60L090NXC | BC Hydro | British Columbia | 1 | ac | 0.8 | 0.49383 | 0.95 | 0.58642 | 69 | 0.36507 |  | 1070 | 1295 | 127.8773 | 154.7674 | 0.9 | 115.0896 | 139.2907 | Canexus Corporation JCT | BC_NXC_JCT | Erco Worldwide JCT | BC_ERW_JCT |  |  | 790
| 60L090NXC | BC Hydro | British Columbia | 1 | ac | 0.15 | 0.092593 | 0.95 | 0.58642 | 69 | 0.36507 |  | 1070 | 1295 | 127.8773 | 154.7674 | 0.9 | 115.0896 | 139.2907 | Erco Worldwide JCT | BC_ERW_JCT | Canexus Corporation | BC_NXC_ISS |  |  | 791
| 60L090 | BC Hydro | British Columbia | 1 | ac | 0.13 | 0.080247 | 3.58 | 2.2099 | 69 | 1.3757 |  | 1070 | 1295 | 127.8773 | 154.7674 | 0.9 | 115.0896 | 139.2907 | Erco Worldwide JCT | BC_ERW_JCT | Erco Worldwide | BC_ERW_ISS |  |  | 791
| 60L091 | BC Hydro | British Columbia | 1 | ac | 2.1103 | 1.3026 | 2.1103 | 1.3026 | 69 | 0.81094 |  | 849 | 1015 | 101.4653 | 121.3042 | 0.9 | 91.3187 | 109.1738 | Walters | BC_WLT_DSS | Canexus Corporation | BC_NXC_ISS |  |  | 792
| 60L092 | BC Hydro | British Columbia | 1 | ac | 3.9415 | 2.433 | 3.9415 | 2.433 | 69 | 1.5147 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Walters | BC_WLT_DSS | Deep Cove | BC_DCV_DSS |  |  | 793
| 60L093 | BC Hydro | British Columbia | 1 | ac | 5.7 | 3.5185 | 8.7 | 5.3704 | 69 | 3.3433 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Atchelitz | BC_ALZ_DSS | Wahleach JCT | BC_WAH_JCT |  | DELETIONS and CORRRECTIONS to 60L093 and related lines | 794
| 60L093 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 8.7 | 5.3704 | 69 | 3.3433 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Wahleach JCT | BC_WAH_JCT | Chilliwack | BC_CHK_DSS |  | DELETIONS and CORRRECTIONS to 60L093 and related lines | 795
| 60L093WAH | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 25 | 15.4321 | 69 | 9.6071 |  | 610 | 780 | 72.902 | 93.219 | 0.9 | 65.6118 | 83.8971 | Wahleach JCT | BC_WAH_JCT | Kent JCT | BC_KEN_JCT |  | DELETIONS and CORRRECTIONS to 60L093 and related lines | 796
| 60L093KEN | BC Hydro | British Columbia | 1 | ac | 10.7123 | 6.6125 | 10.7123 | 6.6125 | 69 | 4.1166 |  | 440 | 555 | 52.5851 | 66.3289 | 0.9 | 47.3266 | 59.696 | Kent JCT | BC_KEN_JCT | Kent | BC_KEN_DSS |  | DELETIONS and CORRRECTIONS to 60L093 and related lines | 797
| 60L093WAH | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 25 | 15.4321 | 69 | 9.6071 |  | 610 | 780 | 72.902 | 93.219 | 0.9 | 65.6118 | 83.8971 | Kent JCT | BC_KEN_JCT | Wahleach Pumping Station JCT | BC_WHP_JCT |  | DELETIONS and CORRRECTIONS to 60L093 and related lines | 798
| 60L093WAH | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 25 | 15.4321 | 69 | 9.6071 |  | 610 | 780 | 72.902 | 93.219 | 0.9 | 65.6118 | 83.8971 | Wahleach Pumping Station JCT | BC_WHP_JCT | Wahleach GS | BC_WAH_GSS |  | DELETIONS and CORRRECTIONS to 60L093 and related lines | 798
| 60L093WHP | BC Hydro | British Columbia | 1 | ac | 0.42469 | 0.26215 | 0.42469 | 0.26215 | 69 | 0.1632 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Wahleach Pumping Station JCT | BC_WHP_JCT | Wahleach Pumping Station | BC_WHP_DSS |  | DELETIONS and CORRRECTIONS to 60L093 and related lines | 799
| 60L094 | BC Hydro | British Columbia | 1 | ac | 8.6857 | 5.3616 | 8.6857 | 5.3616 | 69 | 3.3378 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Atchelitz | BC_ALZ_DSS | Chilliwack | BC_CHK_DSS |  | DELETIONS and CORRRECTIONS to 60L093 and related lines | 800
| 60L095 | BC Hydro | British Columbia | 1 | ac | 27.65 | 17.0679 | 28.65 | 17.6852 | 69 | 11.0098 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Wahleach GS | BC_WAH_GSS | Hope Pumping Station JCT | BC_HPS_JCT |  |  | 801
| 60L095HPS | BC Hydro | British Columbia | 1 | ac | 0.29676 | 0.18319 | 0.29676 | 0.18319 | 69 | 0.11404 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Hope Pumping Station JCT | BC_HPS_JCT | Hope Pumping Station | BC_HPS_DSS |  |  | 802
| 60L095 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 28.65 | 17.6852 | 69 | 11.0098 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Hope Pumping Station JCT | BC_HPS_JCT | Hope | BC_HOP_DSS |  |  | 803
| 60L097 | BC Hydro | British Columbia | 1 | ac | 3.402 | 2.1 | 3.402 | 2.1 | 69 | 1.3073 |  | 750 | 960 | 89.6336 | 114.731 | 0.9 | 80.6703 | 103.2579 | Northgate | BC_NOR_DSS | John Lawson | BC_JLN_DSS |  |  | 804
| 60L098 | BC Hydro | British Columbia | 1 | ac | 13.706 | 8.4605 | 13.706 | 8.4605 | 69 | 5.267 |  | 600 | 600 | 71.7069 | 71.7069 | 0.9 | 64.5362 | 64.5362 | Culliton Creek GS | BC_CTN_GSS | Cheekye | BC_CKY_DSS |  |  | 805
| 60L099 | BC Hydro | British Columbia | 1 | ac | 7.3964 | 4.5657 | 14.7929 | 9.1314 | 69 | 5.6847 |  | 1120 | 1440 | 133.8529 | 172.0966 | 0.9 | 120.4676 | 154.8869 | Cypress | BC_CYP_DSS | Hillcrest JCT | BC_HCT_JCT |  |  | 806
| 60L099HCT | BC Hydro | British Columbia | 1 | ac | 1.4654 | 0.90457 | 1.4654 | 0.90457 | 69 | 0.56314 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Hillcrest JCT | BC_HCT_JCT | Hillcrest | BC_HCT_DSS |  |  | 807
| 60L099 | BC Hydro | British Columbia | 1 | ac | 7.3964 | 4.5657 | 14.7929 | 9.1314 | 69 | 5.6847 |  | 730 | 940 | 87.2434 | 112.3408 | 0.9 | 78.5191 | 101.1067 | Hillcrest JCT | BC_HCT_JCT | Glenmore BCH | BC_GLR_DSS |  |  | 808
| 60L100 | BC Hydro | British Columbia | 1 | ac | 14.6017 | 9.0134 | 15.6017 | 9.6307 | 69 | 5.9955 |  | 1153 | 1383 | 137.7968 | 165.2844 | 0.9 | 124.0171 | 148.756 | McLellan | BC_MLN_DSS | Nicomekl JCT | BC_NKL_JCT |  |  | 809
| 60L100 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 15.6017 | 9.6307 | 69 | 5.9955 |  | 910 | 960 | 108.7555 | 114.731 | 0.9 | 97.8799 | 103.2579 | Nicomekl JCT | BC_NKL_JCT | Nicomekl | BC_NKL_DSS |  |  | 810
| 60L107 | BC Hydro | British Columbia | 1 | ac | 2.49 | 1.537 | 2.49 | 1.537 | 69 | 0.95687 |  | 800 | 1018 | 95.6092 | 121.6627 | 0.9 | 86.0483 | 109.4964 | Nicomekl JCT | BC_NKL_JCT | White Rock | BC_WRK_DSS |  |  | 811
| 60L128 | BC Hydro | British Columbia | 1 | ac | 30.0126 | 18.5263 | 30.0126 | 18.5263 | 69 | 11.5334 |  | 331 | 383 | 39.5583 | 45.7729 | 0.9 | 35.6025 | 41.1956 | Prevost | BC_PVO_DSS | Lake Cowichan | BC_LCW_DSS |  |  | 812
| 60L129 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 79.38 | 49 | 69 | 30.5046 |  | 505 | 601 | 60.3533 | 71.8264 | 0.9 | 54.318 | 64.6438 | Great Central | BC_GCL_DSS | Doran Taylor JCT | BC_DTR_JCT |  |  | 813
| 60L129DTR | BC Hydro | British Columbia | 1 | ac | 0.035985 | 0.022213 | 0.035985 | 0.022213 | 69 | 0.013829 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Doran Taylor JCT | BC_DTR_JCT | Doran Taylor GS | BC_DTR_GSS |  |  | 814
| 60L129 | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 79.38 | 49 | 69 | 30.5046 |  | 505 | 601 | 60.3533 | 71.8264 | 0.9 | 54.318 | 64.6438 | Doran Taylor JCT | BC_DTR_JCT | South Sutton JCT | BC_SSH_JCT |  |  | 815
| 60L129SSH | BC Hydro | British Columbia | 1 | ac | 0.52189 | 0.32215 | 0.52189 | 0.32215 | 69 | 0.20056 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | South Sutton JCT | BC_SSH_JCT | South Sutton GS | BC_SSH_GSS |  |  | 816
| 60L129 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 79.38 | 49 | 69 | 30.5046 |  | 505 | 601 | 60.3533 | 71.8264 | 0.9 | 54.318 | 64.6438 | South Sutton JCT | BC_SSH_JCT | Taylor River Rest Area JCT | BC_TRR_JCT |  |  | 817
| 60L129TRR | BC Hydro | British Columbia | 1 | ac | 0.015185 | 0.0093735 | 0.015185 | 0.0093735 | 69 | 0.0058354 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Taylor River Rest Area JCT | BC_TRR_JCT | Taylor River Rest Area | BC_TRR_DSS |  |  | 818
| 60L129 | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 79.38 | 49 | 69 | 30.5046 |  | 505 | 601 | 60.3533 | 71.8264 | 0.9 | 54.318 | 64.6438 | Taylor River Rest Area JCT | BC_TRR_JCT | Haa-Ak-Suuk JCT | BC_HAS_JCT |  |  | 819
| 60L129HAS | BC Hydro | British Columbia | 1 | ac | 0.19307 | 0.11918 | 0.19307 | 0.11918 | 69 | 0.074194 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Haa-Ak-Suuk JCT | BC_HAS_JCT | Haa-Ak-Suuk GS | BC_HAS_GSS |  |  | 820
| 60L129 | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 79.38 | 49 | 69 | 30.5046 |  | 505 | 601 | 60.3533 | 71.8264 | 0.9 | 54.318 | 64.6438 | Haa-Ak-Suuk JCT | BC_HAS_JCT | Marion 3 Creek JCT | BC_M3C_JCT |  |  | 821
| 60L129M3C | BC Hydro | British Columbia | 1 | ac | 0.16949 | 0.10462 | 0.16949 | 0.10462 | 69 | 0.065133 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Marion 3 Creek JCT | BC_M3C_JCT | Marion 3 Creek GS | BC_M3C_GSS |  |  | 822
| 60L129 | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 79.38 | 49 | 69 | 30.5046 |  | 505 | 601 | 60.3533 | 71.8264 | 0.9 | 54.318 | 64.6438 | Marion 3 Creek JCT | BC_M3C_JCT | Canoe Creek JCT | BC_CNK_JCT |  |  | 823
| 60L129CNK | BC Hydro | British Columbia | 1 | ac | 0.099541 | 0.061445 | 0.099541 | 0.061445 | 69 | 0.038252 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Canoe Creek JCT | BC_CNK_JCT | Canoe Creek GS | BC_CNK_GSS |  |  | 824
| 60L129 | BC Hydro | British Columbia | 1 | ac | 29.38 | 18.1358 | 79.38 | 49 | 69 | 30.5046 |  | 505 | 601 | 60.3533 | 71.8264 | 0.9 | 54.318 | 64.6438 | Canoe Creek JCT | BC_CNK_JCT | Long Beach | BC_LBH_DSS |  |  | 825
| 60L208 | BC Hydro | British Columbia | 1 | ac | 60 | 37.037 | 68.04 | 42 | 69 | 26.1468 |  | 230 | 420 | 27.4876 | 50.1948 | 0.9 | 24.7389 | 45.1753 | Vernon TS | BC_VNT_TSS | Westwold JCT | BC_WWD_JCT |  |  | 826
| 60L208WWD | BC Hydro | British Columbia | 1 | ac | 0.005186 | 0.0032012 | 0.005186 | 0.0032012 | 69 | 0.0019929 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Westwold JCT | BC_WWD_JCT | Westwold | BC_WWD_DSS |  |  | 827
| 60L208 | BC Hydro | British Columbia | 1 | ac | 8.04 | 4.963 | 68.04 | 42 | 69 | 26.1468 |  | 230 | 420 | 27.4876 | 50.1948 | 0.9 | 24.7389 | 45.1753 | Westwold JCT | BC_WWD_JCT | Monte Lake | BC_MTE_DSS |  |  | 828
| 60L209 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 30.71 | 18.9568 | 69 | 11.8014 |  | 239 | 384 | 28.5632 | 45.8924 | 0.9 | 25.7069 | 41.3032 | Salmon Arm | BC_SAM_DSS | Canoe Forest Products Ltd JCT | BC_FCO_JCT |  |  | 829
| 60L209FCO | BC Hydro | British Columbia | 1 | ac | 0.28566 | 0.17634 | 0.28566 | 0.17634 | 69 | 0.10978 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Canoe Forest Products Ltd JCT | BC_FCO_JCT | Canoe Forest Products Ltd | BC_FCO_ISS |  |  | 830
| 60L209 | BC Hydro | British Columbia | 1 | ac | 25.71 | 15.8704 | 30.71 | 18.9568 | 69 | 11.8014 |  | 259 | 363 | 30.9535 | 43.3827 | 0.9 | 27.8581 | 39.0444 | Canoe Forest Products Ltd JCT | BC_FCO_JCT | Sicamous | BC_SCM_DSS |  |  | 831
| 60L210 | BC Hydro | British Columbia | 1 | ac | 50 | 30.8642 | 101.19 | 62.463 | 69 | 38.8859 |  | 175 | 312 | 20.9145 | 37.2876 | 0.9 | 18.8231 | 33.5588 | Monashee | BC_MON_DSS | New Denver JCT | BC_NDR_JCT |  |  | 832
| 60L210NDR | BC Hydro | British Columbia | 1 | ac | 2.333 | 1.4401 | 2.333 | 1.4401 | 69 | 0.89655 |  | 175 | 312 | 20.9145 | 37.2876 | 0.9 | 18.8231 | 33.5588 | New Denver JCT | BC_NDR_JCT | Nakusp | BC_NAK_DSS |  |  | 833
| 60L210 | BC Hydro | British Columbia | 1 | ac | 51.19 | 31.5988 | 101.19 | 62.463 | 69 | 38.8859 |  | 175 | 312 | 20.9145 | 37.2876 | 0.9 | 18.8231 | 33.5588 | New Denver JCT | BC_NDR_JCT | New Denver | BC_NDR_DSS |  |  | 834
| 60L218 | BC Hydro | British Columbia | 1 | ac | 25.5336 | 15.7615 | 25.5336 | 15.7615 | 69 | 9.8122 |  | 828 | 1060 | 98.9555 | 126.6822 | 0.9 | 89.06 | 114.014 | Illecillewaet | BC_ILL_DSS | Walter Hardman GS | BC_WHN_GSS |  |  | 835
| 60L219 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 24.55 | 15.1543 | 69 | 9.4342 |  | 828 | 1060 | 98.9555 | 126.6822 | 0.9 | 89.06 | 114.014 | Walter Hardman GS | BC_WHN_GSS | South Cranberry JCT | BC_SCB_JCT |  |  | 836
| 60L219SCB | BC Hydro | British Columbia | 1 | ac | 0.2 | 0.12346 | 0.2 | 0.12346 | 69 | 0.076857 |  | 828 | 1060 | 98.9555 | 126.6822 | 0.9 | 89.06 | 114.014 | South Cranberry JCT | BC_SCB_JCT | South Cranberry GS | BC_SCB_GSS |  |  | 837
| 60L219 | BC Hydro | British Columbia | 1 | ac | 23.55 | 14.537 | 24.55 | 15.1543 | 69 | 9.4342 |  | 828 | 1060 | 98.9555 | 126.6822 | 0.9 | 89.06 | 114.014 | South Cranberry JCT | BC_SCB_JCT | Pingston GS | BC_PIN_GSS |  |  | 838
| 60L223 | BC Hydro | British Columbia | 1 | ac | 34.68 | 21.4074 | 64.68 | 39.9259 | 69 | 24.8556 |  | 490 | 627 | 58.5606 | 74.9337 | 0.9 | 52.7046 | 67.4403 | Mica GS | BC_MCA_GSS | Goldstream JCT | BC_GST_JCT |  | DELETED 60L223GST | 839
| 60L223 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 64.68 | 39.9259 | 69 | 24.8556 |  | 490 | 627 | 58.5606 | 74.9337 | 0.9 | 52.7046 | 67.4403 | Goldstream JCT | BC_GST_JCT | McCulloch Creek JCT | BC_MCK_JCT |  |  | 840
| 60L223MCK | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | McCulloch Creek JCT | BC_MCK_JCT | McCulloch Creek | BC_MCK_DSS |  |  | 841
| 60L223 | BC Hydro | British Columbia | 1 | ac | 20 | 12.3457 | 64.68 | 39.9259 | 69 | 24.8556 |  | 490 | 627 | 58.5606 | 74.9337 | 0.9 | 52.7046 | 67.4403 | McCulloch Creek JCT | BC_MCK_JCT | Goldstream Mine | BC_GSM_ISS |  |  | 842
| 60L270 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 130.61 | 80.6235 | 69 | 50.1916 |  | 349 | 453 | 41.7095 | 54.1387 | 0.9 | 37.5386 | 48.7248 | Kimberley | BC_KBY_DSS | Skookumchuck JCT | BC_SKU_JCT |  |  | 843
| 60L270SKU | BC Hydro | British Columbia | 1 | ac | 0.077463 | 0.047817 | 0.077463 | 0.047817 | 69 | 0.029768 |  | 231 | 380 | 27.6072 | 45.4144 | 0.9 | 24.8464 | 40.8729 | Skookumchuck JCT | BC_SKU_JCT | Skookumchuck | BC_SKU_DSS |  |  | 844
| 60L270CRS | BC Hydro | British Columbia | 1 | ac | 0.023553 | 0.014539 | 0.023553 | 0.014539 | 69 | 0.0090512 |  | 367 | 440 | 43.8607 | 52.5851 | 0.9 | 39.4747 | 47.3266 | Skookumchuck | BC_SKU_DSS | Crestbrook Skookumchuck | BC_CRS_DFS |  |  | 845
| 60L270 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 130.61 | 80.6235 | 69 | 50.1916 |  | 349 | 453 | 41.7095 | 54.1387 | 0.9 | 37.5386 | 48.7248 | Skookumchuck JCT | BC_SKU_JCT | Crestbrook Canal Flats JCT | BC_CRC_JCT |  |  | 846
| 60L270CRC | BC Hydro | British Columbia | 1 | ac | 0.072978 | 0.045048 | 0.072978 | 0.045048 | 69 | 0.028044 |  | 231 | 380 | 27.6072 | 45.4144 | 0.9 | 24.8464 | 40.8729 | Crestbrook Canal Flats JCT | BC_CRC_JCT | Crestbrook Canal Flats | BC_CRC_DSS |  |  | 847
| 60L270 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 130.61 | 80.6235 | 69 | 50.1916 |  | 349 | 453 | 41.7095 | 54.1387 | 0.9 | 37.5386 | 48.7248 | Crestbrook Canal Flats JCT | BC_CRC_JCT | Canal Flats JCT | BC_CNL_JCT |  |  | 848
| 60L270CNL | BC Hydro | British Columbia | 1 | ac | 0.026482 | 0.016347 | 0.026482 | 0.016347 | 69 | 0.010177 |  | 490 | 590 | 58.5606 | 70.5118 | 0.9 | 52.7046 | 63.4606 | Canal Flats JCT | BC_CNL_JCT | Canal Flats | BC_CNL_DSS |  |  | 849
| 60L270 | BC Hydro | British Columbia | 1 | ac | 27 | 16.6667 | 130.61 | 80.6235 | 69 | 50.1916 |  | 349 | 453 | 41.7095 | 54.1387 | 0.9 | 37.5386 | 48.7248 | Canal Flats JCT | BC_CNL_JCT | Fairmont JCT | BC_FMT_JCT |  |  | 850
| 60L270FMT | BC Hydro | British Columbia | 1 | ac | 0.044415 | 0.027417 | 0.044415 | 0.027417 | 69 | 0.017068 |  | 425 | 511 | 50.7924 | 61.0704 | 0.9 | 45.7132 | 54.9633 | Fairmont JCT | BC_FMT_JCT | Fairmont | BC_FMT_DSS |  |  | 851
| 60L270 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 130.61 | 80.6235 | 69 | 50.1916 |  | 349 | 453 | 41.7095 | 54.1387 | 0.9 | 37.5386 | 48.7248 | Fairmont JCT | BC_FMT_JCT | Athalmer JCT | BC_ATH_JCT |  |  | 852
| 60L270ATH | BC Hydro | British Columbia | 1 | ac | 0.14326 | 0.088431 | 0.14326 | 0.088431 | 69 | 0.055052 |  | 828 | 1003 | 98.9555 | 119.87 | 0.9 | 89.06 | 107.883 | Athalmer JCT | BC_ATH_JCT | Athalmer | BC_ATH_DSS |  |  | 853
| 60L270 | BC Hydro | British Columbia | 1 | ac | 10.61 | 6.5494 | 130.61 | 80.6235 | 69 | 50.1916 |  | 349 | 453 | 41.7095 | 54.1387 | 0.9 | 37.5386 | 48.7248 | Athalmer JCT | BC_ATH_JCT | Invermere | BC_INV_DSS |  |  | 854
| 60L271 | BC Hydro | British Columbia | 1 | ac | 12.52 | 7.7284 | 127.52 | 78.716 | 69 | 49.0041 |  | 629 | 957 | 75.1727 | 114.3725 | 0.9 | 67.6555 | 102.9353 | Invermere | BC_INV_DSS | Athalmer JCT | BC_ATH_JCT |  |  | 855
| 60L271ATH | BC Hydro | British Columbia | 1 | ac | 0.13871 | 0.085623 | 0.13871 | 0.085623 | 69 | 0.053304 |  | 433 | 829 | 51.7485 | 99.075 | 0.9 | 46.5736 | 89.1675 | Athalmer JCT | BC_ATH_JCT | Athalmer | BC_ATH_DSS |  |  | 856
| 60L271 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 127.52 | 78.716 | 69 | 49.0041 |  | 629 | 957 | 75.1727 | 114.3725 | 0.9 | 67.6555 | 102.9353 | Athalmer JCT | BC_ATH_JCT | Radium JCT | BC_RDM_JCT |  |  | 857
| 60L271RDM | BC Hydro | British Columbia | 1 | ac | 0.054046 | 0.033362 | 0.054046 | 0.033362 | 69 | 0.020769 |  | 265 | 492 | 31.6705 | 58.7997 | 0.9 | 28.5035 | 52.9197 | Radium JCT | BC_RDM_JCT | Radium | BC_RDM_DSS |  |  | 858
| 60L271 | BC Hydro | British Columbia | 1 | ac | 45 | 27.7778 | 127.52 | 78.716 | 69 | 49.0041 |  | 401 | 567 | 47.9241 | 67.763 | 0.9 | 43.1317 | 60.9867 | Radium JCT | BC_RDM_JCT | Spillimacheen JCT | BC_SPN_JCT |  |  | 859
| 60L271SPN | BC Hydro | British Columbia | 1 | ac | 3.7804 | 2.3336 | 3.7804 | 2.3336 | 69 | 1.4527 |  | 265 | 492 | 31.6705 | 58.7997 | 0.9 | 28.5035 | 52.9197 | Spillimacheen JCT | BC_SPN_JCT | Spillimacheen GS | BC_SPN_DFS |  |  | 860
| 60L271 | BC Hydro | British Columbia | 1 | ac | 25 | 15.4321 | 127.52 | 78.716 | 69 | 49.0041 |  | 401 | 567 | 47.9241 | 67.763 | 0.9 | 43.1317 | 60.9867 | Spillimacheen JCT | BC_SPN_JCT | Parson JCT | BC_PSN_JCT |  |  | 861
| 60L271PSN | BC Hydro | British Columbia | 1 | ac | 0.57605 | 0.35559 | 0.57605 | 0.35559 | 69 | 0.22137 |  | 265 | 492 | 31.6705 | 58.7997 | 0.9 | 28.5035 | 52.9197 | Parson JCT | BC_PSN_JCT | Parson | BC_PSN_DSS |  |  | 862
| 60L271 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 127.52 | 78.716 | 69 | 49.0041 |  | 401 | 567 | 47.9241 | 67.763 | 0.9 | 43.1317 | 60.9867 | Parson JCT | BC_PSN_JCT | Golden | BC_GDN_DSS |  |  | 863
| 60L272 | BC Hydro | British Columbia | 1 | ac | 3.0884 | 1.9064 | 3.0884 | 1.9064 | 69 | 1.1868 |  | 730 | 879 | 87.2434 | 105.0506 | 0.9 | 78.5191 | 94.5456 | Kicking Horse | BC_KHS_DSS | Golden | BC_GDN_DSS |  |  | 864
| 60L281 | BC Hydro | British Columbia | 1 | ac | 28.93 | 17.858 | 30.93 | 19.0926 | 69 | 11.886 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Fernie | BC_FNE_DSS | Sparwood JCT | BC_SPD_JCT |  |  | 865
| 60L281SPD | BC Hydro | British Columbia | 1 | ac | 0.34484 | 0.21287 | 0.34484 | 0.21287 | 69 | 0.13252 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Sparwood JCT | BC_SPD_JCT | Sparwood | BC_SPD_DSS |  |  | 866
| 60L281 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 30.93 | 19.0926 | 69 | 11.886 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Sparwood JCT | BC_SPD_JCT | Natal | BC_NTL_DSS |  |  | 867
| 60L283 | BC Hydro | British Columbia | 1 | ac | 15 | 9.2593 | 37.56 | 23.1852 | 69 | 14.4338 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Cranbrook | BC_CBK_DSS | Fort Steele JCT | BC_FST_JCT |  |  | 868
| 60L283FST | BC Hydro | British Columbia | 1 | ac | 0.077512 | 0.047847 | 0.077512 | 0.047847 | 69 | 0.029787 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Fort Steele JCT | BC_FST_JCT | Fort Steele | BC_FST_DSS |  |  | 869
| 60L283 | BC Hydro | British Columbia | 1 | ac | 20.56 | 12.6914 | 37.56 | 23.1852 | 69 | 14.4338 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Fort Steele JCT | BC_FST_JCT | Marysville JCT | BC_MVL_JCT |  |  | 870
| 60L283MVL | BC Hydro | British Columbia | 1 | ac | 0.072276 | 0.044615 | 0.072276 | 0.044615 | 69 | 0.027775 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Marysville JCT | BC_MVL_JCT | Marysville | BC_MVL_DSS |  |  | 871
| 60L283 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 37.56 | 23.1852 | 69 | 14.4338 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Marysville JCT | BC_MVL_JCT | Kimberley | BC_KBY_DSS |  |  | 872
| 60L284 | BC Hydro | British Columbia | 1 | ac | 12 | 7.4074 | 12 | 7.4074 | 69 | 4.6114 |  | 545 | 1041 | 65.1338 | 124.4115 | 0.9 | 58.6204 | 111.9703 | Cranbrook | BC_CBK_DSS | Moyie JCT | BC_MYE_JCT |  |  | 873
| 60L284MYE | BC Hydro | British Columbia | 1 | ac | 27.39 | 16.9074 | 27.39 | 16.9074 | 69 | 10.5256 |  | 141 | 248 | 16.8511 | 29.6389 | 0.9 | 15.166 | 26.675 | Moyie JCT | BC_MYE_JCT | Moyie | BC_MYE_DSS |  |  | 874
| 60L285 | BC Hydro | British Columbia | 1 | ac | 4.218 | 2.6037 | 4.218 | 2.6037 | 69 | 1.6209 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Natal | BC_NTL_DSS | Sparwood | BC_SPD_DSS |  |  | 875
| 60L287 | BC Hydro | British Columbia | 1 | ac | 1.1802 | 0.7285 | 1.1802 | 0.7285 | 69 | 0.45352 |  | 175 | 312 | 20.9145 | 37.2876 | 0.9 | 18.8231 | 33.5588 | Elko GS | BC_ELK_GSS | Crestbrook | BC_CFE_DSS |  |  | 876
| 60L288 | BC Hydro | British Columbia | 1 | ac | 2.4688 | 1.524 | 2.4688 | 1.524 | 69 | 0.94874 |  | 340 | 403 | 40.6339 | 48.1631 | 0.9 | 36.5705 | 43.3468 | Natal | BC_NTL_DSS | Elkview Coal | BC_EV1_ISS |  |  | 877
| 60L289 | BC Hydro | British Columbia | 1 | ac | 14.46 | 8.9259 | 16.46 | 10.1605 | 69 | 6.3253 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Cranbrook | BC_CBK_DSS | Bull River Mineral JCT | BC_BRM_JCT |  |  | 878
| 60L289BRM | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Bull River Mineral JCT | BC_BRM_JCT | Bull River Mineral | BC_BRM_ISS |  |  | 879
| 60L289 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 16.46 | 10.1605 | 69 | 6.3253 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Bull River Mineral JCT | BC_BRM_JCT | Wardner | BC_WAR_DSS |  | DELETED WARDNER JCT and ABERFELDIE JCT | 880
| 60L289 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 16.46 | 10.1605 | 69 | 6.3253 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Wardner | BC_WAR_DSS | Aberfeldie GS | BC_ABN_GSS |  |  | 881
| 60L290 | BC Hydro | British Columbia | 1 | ac | 3.8523 | 2.378 | 3.8523 | 2.378 | 69 | 1.4804 |  | 150 | 270 | 17.9267 | 32.2681 | 0.9 | 16.1341 | 29.0413 | Elko GS | BC_ELK_GSS | Windsor | BC_WIN_DSS |  |  | 882
| 60L292 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 16.6 | 10.2469 | 69 | 6.3791 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Natal | BC_NTL_DSS | Coal Mountain JCT | BC_CMO_JCT |  |  | 883
| 60L292CMO | BC Hydro | British Columbia | 1 | ac | 24.3511 | 15.0316 | 24.3511 | 15.0316 | 69 | 9.3578 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Coal Mountain JCT | BC_CMO_JCT | Coal Mountain | BC_CMO_DSS |  |  | 884
| 60L292 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 16.6 | 10.2469 | 69 | 6.3791 |  | 115 | 201 | 13.7438 | 24.0218 | 0.9 | 12.3694 | 21.6196 | Coal Mountain JCT | BC_CMO_JCT | Crowsnest TransCanada JCT | BC_CNT_JCT |  |  | 885
| 60L292CNT | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 69 | 0.76857 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Crowsnest TransCanada JCT | BC_CNT_JCT | Crowsnest TransCanada | BC_CNT_ISS |  |  | 886
| 60L292 | BC Hydro | British Columbia | 1 | ac | 3.6 | 2.2222 | 16.6 | 10.2469 | 69 | 6.3791 |  | 115 | 201 | 13.7438 | 24.0218 | 0.9 | 12.3694 | 21.6196 | Crowsnest TransCanada JCT | BC_CNT_JCT | Crowsnest Pass GS | BC_CRW_GSS |  |  | 887
| 60L294 | BC Hydro | British Columbia | 1 | ac | 32.0872 | 19.8069 | 64.1743 | 39.6138 | 69 | 24.6613 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Elko GS | BC_ELK_GSS | Windsor JCT | BC_WIN_JCT |  |  | 888
| 60L294WIN | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 3 | 1.8519 | 69 | 1.1529 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Windsor JCT | BC_WIN_JCT | Windsor | BC_WIN_DSS |  |  | 889
| 60L294 | BC Hydro | British Columbia | 1 | ac | 32.0872 | 19.8069 | 64.1743 | 39.6138 | 69 | 24.6613 |  | 265 | 488 | 31.6705 | 58.3216 | 0.9 | 28.5035 | 52.4895 | Windsor JCT | BC_WIN_JCT | Aberfeldie GS | BC_ABN_GSS |  |  | 890
| 60L295 | BC Hydro | British Columbia | 1 | ac | 11.6002 | 7.1606 | 11.9502 | 7.3766 | 69 | 4.5923 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Steeples JCT | BC_SPL_JCT | Joseph Creek | BC_JOE_DSS |  |  | 891
| 60L295 | BC Hydro | British Columbia | 1 | ac | 0.35 | 0.21605 | 11.9502 | 7.3766 | 69 | 4.5923 |  | 545 | 1041 | 65.1338 | 124.4115 | 0.9 | 58.6204 | 111.9703 | Steeples JCT | BC_SPL_JCT | Steeples | BC_SPL_DSS |  |  | 892
| 60L298 | BC Hydro | British Columbia | 1 | ac | 21.7664 | 13.4361 | 21.7664 | 13.4361 | 69 | 8.3645 |  | 435 | 822 | 51.9875 | 98.2385 | 0.9 | 46.7888 | 88.4146 | Joseph Creek | BC_JOE_DSS | Kimberley | BC_KBY_DSS |  |  | 893
| 60L299 | BC Hydro | British Columbia | 1 | ac | 18.2199 | 11.2468 | 18.2199 | 11.2468 | 69 | 7.0016 |  | 545 | 1041 | 65.1338 | 124.4115 | 0.9 | 58.6204 | 111.9703 | Cranbrook | BC_CBK_DSS | Joseph Creek | BC_JOE_DSS |  |  | 894
| 60L300 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 51.3 | 31.6667 | 69 | 19.7139 |  | 850 | 970 | 101.5848 | 115.9262 | 0.9 | 91.4263 | 104.3335 | Soda Creek | BC_SCK_DSS | Mount Polley Mining JCT | BC_MTP_JCT |  |  | 895
| 60L300MTP | BC Hydro | British Columbia | 1 | ac | 50 | 30.8642 | 58.5 | 36.1111 | 69 | 22.4807 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Mount Polley Mining JCT | BC_MTP_JCT | Gavin Lake JCT | BC_GVL_JCT |  |  | 896
| 60L300MTP | BC Hydro | British Columbia | 1 | ac | 8.5 | 5.2469 | 58.5 | 36.1111 | 69 | 22.4807 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Gavin Lake JCT | BC_GVL_JCT | Mount Polley Mining | BC_MTP_DSS |  |  | 897
| 60L300GVL | BC Hydro | British Columbia | 1 | ac | 0.02 | 0.012346 | 0.02 | 0.012346 | 69 | 0.0076857 |  | 493 | 625 | 58.9192 | 74.6947 | 0.9 | 53.0273 | 67.2252 | Gavin Lake JCT | BC_GVL_JCT | Gavin Lake | BC_GVL_DSS |  |  | 898
| 60L300 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 51.3 | 31.6667 | 69 | 19.7139 |  | 848 | 1016 | 101.3458 | 121.4237 | 0.9 | 91.2112 | 109.2813 | Mount Polley Mining JCT | BC_MTP_JCT | Marguerite JCT | BC_MGT_JCT |  |  | 899
| 60L300MGT | BC Hydro | British Columbia | 1 | ac | 0.25921 | 0.16001 | 0.25921 | 0.16001 | 69 | 0.099611 |  | 230 | 380 | 27.4876 | 45.4144 | 0.9 | 24.7389 | 40.8729 | Marguerite JCT | BC_MGT_JCT | Marguerite | BC_MGT_DSS |  |  | 900
| 60L300 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 51.3 | 31.6667 | 69 | 19.7139 |  | 848 | 1016 | 101.3458 | 121.4237 | 0.9 | 91.2112 | 109.2813 | Marguerite JCT | BC_MGT_JCT | Gibraltar Wells JCT | BC_GBW_JCT |  |  | 901
| 60L300GBW | BC Hydro | British Columbia | 1 | ac | 0.044097 | 0.02722 | 0.044097 | 0.02722 | 69 | 0.016946 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Gibraltar Wells JCT | BC_GBW_JCT | Gibraltar Wells | BC_GBW_ISS |  |  | 902
| 60L300 | BC Hydro | British Columbia | 1 | ac | 20.15 | 12.4383 | 51.3 | 31.6667 | 69 | 19.7139 |  | 230 | 380 | 27.4876 | 45.4144 | 0.9 | 24.7389 | 40.8729 | Gibraltar Wells JCT | BC_GBW_JCT | West Fraser Quesnel Plywood JCT | BC_WQL_JCT |  |  | 903
| 60L300WQL | BC Hydro | British Columbia | 1 | ac | 0.96 | 0.59259 | 0.96 | 0.59259 | 69 | 0.36891 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | West Fraser Quesnel Plywood JCT | BC_WQL_JCT | West Fraser Quesnel Plywood | BC_WQL_ISS |  |  | 904
| 60L300 | BC Hydro | British Columbia | 1 | ac | 20.15 | 12.4383 | 51.3 | 31.6667 | 69 | 19.7139 |  | 230 | 380 | 27.4876 | 45.4144 | 0.9 | 24.7389 | 40.8729 | West Fraser Quesnel Plywood JCT | BC_WQL_JCT | Barlow | BC_BLW_DSS |  |  | 905
| 60L301 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 101.24 | 62.4938 | 69 | 38.9051 |  | 265 | 441 | 31.6705 | 52.7046 | 0.9 | 28.5035 | 47.4341 | Carquille | BC_CRQ_DSS | Clinton JCT | BC_CLN_JCT |  |  | 906
| 60L301CLN | BC Hydro | British Columbia | 1 | ac | 0.97038 | 0.599 | 0.97038 | 0.599 | 69 | 0.3729 |  | 265 | 441 | 31.6705 | 52.7046 | 0.9 | 28.5035 | 47.4341 | Clinton JCT | BC_CLN_JCT | Clinton | BC_CLN_DSS |  |  | 907
| 60L301 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 101.24 | 62.4938 | 69 | 38.9051 |  | 265 | 441 | 31.6705 | 52.7046 | 0.9 | 28.5035 | 47.4341 | Clinton JCT | BC_CLN_JCT | Seventy Mile House JCT | BC_SMH_JCT |  |  | 908
| 60L301SMH | BC Hydro | British Columbia | 1 | ac | 0.11097 | 0.0685 | 0.11097 | 0.0685 | 69 | 0.042644 |  | 265 | 441 | 31.6705 | 52.7046 | 0.9 | 28.5035 | 47.4341 | Seventy Mile House JCT | BC_SMH_JCT | Seventy Mile House | BC_SMH_DSS |  |  | 909
| 60L301 | BC Hydro | British Columbia | 1 | ac | 40 | 24.6914 | 101.24 | 62.4938 | 69 | 38.9051 |  | 265 | 441 | 31.6705 | 52.7046 | 0.9 | 28.5035 | 47.4341 | Seventy Mile House JCT | BC_SMH_JCT | Ainsworth JCT | BC_AWL_JCT |  |  | 910
| 60L301AWL | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 |  | 317 | 379 | 37.8851 | 45.2949 | 0.9 | 34.0966 | 40.7654 | Ainsworth JCT | BC_AWL_JCT | Ainsworth | BC_AWL_DSS |  |  | 911
| 60L301 | BC Hydro | British Columbia | 1 | ac | 1.24 | 0.76543 | 101.24 | 62.4938 | 69 | 38.9051 |  | 265 | 441 | 31.6705 | 52.7046 | 0.9 | 28.5035 | 47.4341 | Ainsworth JCT | BC_AWL_JCT | Hundred Mile House | BC_HMH_DSS |  |  | 912
| 60L302 | BC Hydro | British Columbia | 1 | ac | 18 | 11.1111 | 21.73 | 13.4136 | 69 | 8.3505 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Soda Creek | BC_SCK_DSS | Timber West JCT | BC_TWT_JCT |  |  | 913
| 60L302TWT | BC Hydro | British Columbia | 1 | ac | 0.0086507 | 0.0053399 | 0.0086507 | 0.0053399 | 69 | 0.0033243 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Timber West JCT | BC_TWT_JCT | Timber West | BC_TWT_DSS |  |  | 914
| 60L302 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 21.73 | 13.4136 | 69 | 8.3505 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Timber West JCT | BC_TWT_JCT | West Fraser Williams Lake JCT | BC_WWL_JCT |  |  | 915
| 60L302WWL | BC Hydro | British Columbia | 1 | ac | 0.05539 | 0.034191 | 0.05539 | 0.034191 | 69 | 0.021285 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | West Fraser Williams Lake JCT | BC_WWL_JCT | West Fraser Williams Lake | BC_WWL_ISS |  |  | 916
| 60L302 | BC Hydro | British Columbia | 1 | ac | 1.73 | 1.0679 | 21.73 | 13.4136 | 69 | 8.3505 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | West Fraser Williams Lake JCT | BC_WWL_JCT | Tolko Lignum JCT | BC_LGW_JCT |  |  | 917
| 60L302LGW | BC Hydro | British Columbia | 1 | ac | 1.658 | 1.0234 | 1.658 | 1.0234 | 69 | 0.63713 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Tolko Lignum JCT | BC_LGW_JCT | Tolko Lignum | BC_LGW_DSS |  |  | 918
| 60L302 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 21.73 | 13.4136 | 69 | 8.3505 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Tolko Lignum JCT | BC_LGW_JCT | Williams Lake | BC_WLM_DSS |  |  | 919
| 60L303 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 6.7 | 4.1358 | 69 | 2.5747 |  | 580 | 830 | 69.3167 | 99.1945 | 0.9 | 62.385 | 89.2751 | Quesnel | BC_QNL_DSS | Cariboo Pulp JCT | BC_CBP_JCT |  |  | 920
| 60L303CBP | BC Hydro | British Columbia | 1 | ac | 0.49004 | 0.30249 | 0.49004 | 0.30249 | 69 | 0.18832 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Cariboo Pulp JCT | BC_CBP_JCT | Cariboo Pulp GS | BC_CBP_GSS |  |  | 921
| 60L303 | BC Hydro | British Columbia | 1 | ac | 2.7 | 1.6667 | 6.7 | 4.1358 | 69 | 2.5747 |  | 675 | 960 | 80.6703 | 114.731 | 0.9 | 72.6032 | 103.2579 | Cariboo Pulp JCT | BC_CBP_JCT | West Pine JCT | BC_WPN_JCT |  |  | 922
| 60L303WPN | BC Hydro | British Columbia | 1 | ac | 5.6613 | 3.4947 | 5.6613 | 3.4947 | 69 | 2.1756 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | West Pine JCT | BC_WPN_JCT | West Pine | BC_WPN_DSS |  |  | 923
| 60L303 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 6.7 | 4.1358 | 69 | 2.5747 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | West Pine JCT | BC_WPN_JCT | Barlow | BC_BLW_DSS |  |  | 924
| 60L306 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 6.66 | 4.1111 | 69 | 2.5593 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Quesnel | BC_QNL_DSS | West Fraser Quesnel JCT | BC_WFQ_JCT |  |  | 925
| 60L306WFQ | BC Hydro | British Columbia | 1 | ac | 0.12981 | 0.080132 | 0.12981 | 0.080132 | 69 | 0.049885 |  | 493 | 625 | 58.9192 | 74.6947 | 0.9 | 53.0273 | 67.2252 | West Fraser Quesnel JCT | BC_WFQ_JCT | West Fraser Quesnel | BC_WFQ_ISS |  |  | 926
| 60L306 | BC Hydro | British Columbia | 1 | ac | 5.66 | 3.4938 | 6.66 | 4.1111 | 69 | 2.5593 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | West Fraser Quesnel JCT | BC_WFQ_JCT | Barlow JCT | BC_BLW_JCT |  |  | 927
| 60L306BLW | BC Hydro | British Columbia | 1 | ac | 5.66 | 3.4938 | 5.66 | 3.4938 | 69 | 2.1751 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Barlow JCT | BC_BLW_JCT | Barlow | BC_BLW_DSS |  |  | 928
| 60L308 | BC Hydro | British Columbia | 1 | ac | 26.8299 | 16.5616 | 26.8299 | 16.5616 | 69 | 10.3103 |  | 460 | 780 | 54.9753 | 93.219 | 0.9 | 49.4778 | 83.8971 | Soda Creek | BC_SCK_DSS | Williams Lake | BC_WLM_DSS |  |  | 929
| 60L309 | BC Hydro | British Columbia | 1 | ac | 6.3824 | 3.9398 | 6.3824 | 3.9398 | 69 | 2.4527 |  | 828 | 1003 | 98.9555 | 119.87 | 0.9 | 89.06 | 107.883 | North West Energy | BC_NWE_ISS | Williams Lake | BC_WLM_DSS |  |  | 930
| 60L310 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 31.19 | 19.2531 | 69 | 11.9859 |  | 828 | 1060 | 98.9555 | 126.6822 | 0.9 | 89.06 | 114.014 | Soda Creek | BC_SCK_DSS | Gibraltar Capacitor JCT | BC_GBC_JCT |  |  | 931
| 60L310GBC | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Gibraltar Capacitor JCT | BC_GBC_JCT | Gibraltar Capacitor | BC_GBC_DSS |  |  | 932
| 60L310 | BC Hydro | British Columbia | 1 | ac | 1.19 | 0.73457 | 31.19 | 19.2531 | 69 | 11.9859 |  | 828 | 1060 | 98.9555 | 126.6822 | 0.9 | 89.06 | 114.014 | Gibraltar Capacitor JCT | BC_GBC_JCT | Gibraltar Mine | BC_GBR_ISS |  |  | 933
| 60L327 | BC Hydro | British Columbia | 1 | ac | 14.8 | 9.1358 | 14.8 | 9.1358 | 69 | 5.6874 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Williston | BC_WSN_DSS | Beaverley | BC_BVY_DSS |  |  | 934
| 60L329PLT | BC Hydro | British Columbia | 1 | ac | 0.2886 | 0.17815 | 0.2886 | 0.17815 | 69 | 0.11091 |  | 401 | 567 | 47.9241 | 67.763 | 0.9 | 43.1317 | 60.9867 | Canfor | BC_PLT_ISS | Canfor JCT | BC_PLT_JCT |  |  | 935
| 60L329 | BC Hydro | British Columbia | 1 | ac | 19 | 11.7284 | 22 | 13.5802 | 69 | 8.4543 |  | 401 | 567 | 47.9241 | 67.763 | 0.9 | 43.1317 | 60.9867 | Canfor JCT | BC_PLT_JCT | Tachick JCT | BC_TAC_JCT |  |  | 936
| 60L329TAC | BC Hydro | British Columbia | 1 | ac | 1.7361 | 1.0717 | 1.7361 | 1.0717 | 69 | 0.66717 |  | 828 | 1060 | 98.9555 | 126.6822 | 0.9 | 89.06 | 114.014 | Tachick JCT | BC_TAC_JCT | Tachick | BC_TAC_DSS |  |  | 937
| 60L329 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 22 | 13.5802 | 69 | 8.4543 |  | 347 | 488 | 41.4705 | 58.3216 | 0.9 | 37.3234 | 52.4895 | Tachick JCT | BC_TAC_JCT | Nechako Lumber JCT | BC_NLV_JCT |  |  | 938
| 60L329NLV | BC Hydro | British Columbia | 1 | ac | 0.057818 | 0.03569 | 0.057818 | 0.03569 | 69 | 0.022219 |  | 493 | 625 | 58.9192 | 74.6947 | 0.9 | 53.0273 | 67.2252 | Nechako Lumber JCT | BC_NLV_JCT | Nechako Lumber | BC_NLV_DSS |  |  | 939
| 60L329 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 22 | 13.5802 | 69 | 8.4543 |  | 347 | 488 | 41.4705 | 58.3216 | 0.9 | 37.3234 | 52.4895 | Nechako Lumber JCT | BC_NLV_JCT | Vanderhoof JCT | BC_VDF_JCT |  |  | 940
| 60L329VDF | BC Hydro | British Columbia | 1 | ac | 0.013853 | 0.0085512 | 0.013853 | 0.0085512 | 69 | 0.0053235 |  | 347 | 488 | 41.4705 | 58.3216 | 0.9 | 37.3234 | 52.4895 | Vanderhoof JCT | BC_VDF_JCT | Vanderhoof | BC_VDF_DSS |  |  | 941
| 60L330 | BC Hydro | British Columbia | 1 | ac | 6.2316 | 3.8467 | 6.2316 | 3.8467 | 69 | 2.3947 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Williston | BC_WSN_DSS | Pineview | BC_PVW_DSS |  |  | 942
| 60L331 | BC Hydro | British Columbia | 1 | ac | 14.598 | 9.0111 | 14.598 | 9.0111 | 69 | 5.6098 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Williston | BC_WSN_DSS | Patricia | BC_PCA_DSS |  |  | 943
| 60L332 | BC Hydro | British Columbia | 1 | ac | 6.41 | 3.9568 | 17.41 | 10.7469 | 69 | 6.6904 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Williston | BC_WSN_DSS | Pineview JCT | BC_PVW_JCT |  |  | 944
| 60L332PVW | BC Hydro | British Columbia | 1 | ac | 0.10207 | 0.063009 | 0.10207 | 0.063009 | 69 | 0.039226 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Pineview JCT | BC_PVW_JCT | Pineview | BC_PVW_DSS |  |  | 945
| 60L332 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 17.41 | 10.7469 | 69 | 6.6904 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Pineview JCT | BC_PVW_JCT | Canfor Rustad Division JCT | BC_NOS_JCT |  |  | 946
| 60L332NOS | BC Hydro | British Columbia | 1 | ac | 0.015576 | 0.009615 | 0.015576 | 0.009615 | 69 | 0.0059857 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Canfor Rustad Division JCT | BC_NOS_JCT | Canfor Rustad Division | BC_NOS_ISS |  |  | 947
| 60L332 | BC Hydro | British Columbia | 1 | ac | 6 | 3.7037 | 17.41 | 10.7469 | 69 | 6.6904 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Canfor Rustad Division JCT | BC_NOS_JCT | Patricia | BC_PCA_DSS |  |  | 948
| 60L336 | BC Hydro | British Columbia | 1 | ac | 13 | 8.0247 | 14.24 | 8.7901 | 69 | 5.4722 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Williston | BC_WSN_DSS | BC Chemical JCT | BC_BCM_JCT |  |  | 949
| 60L336BCM | BC Hydro | British Columbia | 1 | ac | 0.037444 | 0.023113 | 0.037444 | 0.023113 | 69 | 0.014389 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | BC Chemical JCT | BC_BCM_JCT | BC Chemical | BC_BCM_ISS |  |  | 950
| 60L336 | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 14.24 | 8.7901 | 69 | 5.4722 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | BC Chemical JCT | BC_BCM_JCT | FMC Prince George JCT | BC_FMC_JCT |  |  | 951
| 60L336FMC | BC Hydro | British Columbia | 1 | ac | 1.1579 | 0.71477 | 1.1579 | 0.71477 | 69 | 0.44497 |  | 500 | 600 | 59.7558 | 71.7069 | 0.9 | 53.7802 | 64.5362 | FMC Prince George JCT | BC_FMC_JCT | FMC Prince George | BC_FMC_ISS |  |  | 952
| 60L336 | BC Hydro | British Columbia | 1 | ac | 0.24 | 0.14815 | 14.24 | 8.7901 | 69 | 5.4722 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | FMC Prince George JCT | BC_FMC_JCT | Canreed | BC_CRD_DSS |  |  | 953
| 60L337 | BC Hydro | British Columbia | 1 | ac | 38.16 | 23.5556 | 68.16 | 42.0741 | 69 | 26.1929 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Williston | BC_WSN_DSS | Canadian National JCT | BC_CNG_JCT |  |  | 954
| 60L337CNG | BC Hydro | British Columbia | 1 | ac | 0.1062 | 0.065553 | 0.1062 | 0.065553 | 69 | 0.040809 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Canadian National JCT | BC_CNG_JCT | Canadian National | BC_CNG_ISS |  |  | 955
| 60L337 | BC Hydro | British Columbia | 1 | ac | 30 | 18.5185 | 68.16 | 42.0741 | 69 | 26.1929 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Canadian National JCT | BC_CNG_JCT | Upper Fraser | BC_UFR_DSS |  |  | 956
| 60L338 | BC Hydro | British Columbia | 1 | ac | 13.5 | 8.3333 | 14.97 | 9.2407 | 69 | 5.7528 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Williston | BC_WSN_DSS | BC Chemical JCT | BC_BCM_JCT |  |  | 957
| 60L338BCM | BC Hydro | British Columbia | 1 | ac | 0.049927 | 0.030819 | 0.049927 | 0.030819 | 69 | 0.019186 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | BC Chemical JCT | BC_BCM_JCT | BC Chemical | BC_BCM_ISS |  |  | 958
| 60L338 | BC Hydro | British Columbia | 1 | ac | 0.6 | 0.37037 | 14.97 | 9.2407 | 69 | 5.7528 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | BC Chemical JCT | BC_BCM_JCT | Prince George Pulp JCT | BC_HCR_JCT |  |  | 959
| 60L338HCR | BC Hydro | British Columbia | 1 | ac | 0.21217 | 0.13097 | 0.21217 | 0.13097 | 69 | 0.081535 |  | 493 | 625 | 58.9192 | 74.6947 | 0.9 | 53.0273 | 67.2252 | Prince George Pulp JCT | BC_HCR_JCT | Prince George Pulp | BC_HCR_ISS |  |  | 960
| 60L338 | BC Hydro | British Columbia | 1 | ac | 0.6 | 0.37037 | 14.97 | 9.2407 | 69 | 5.7528 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | Prince George Pulp JCT | BC_HCR_JCT | FMC Prince George JCT | BC_FMC_JCT |  |  | 961
| 60L338FMC | BC Hydro | British Columbia | 1 | ac | 1.1525 | 0.71143 | 1.1525 | 0.71143 | 69 | 0.4429 |  | 500 | 600 | 59.7558 | 71.7069 | 0.9 | 53.7802 | 64.5362 | FMC Prince George JCT | BC_FMC_JCT | FMC Prince George | BC_FMC_ISS |  |  | 962
| 60L338 | BC Hydro | British Columbia | 1 | ac | 0.27 | 0.16667 | 14.97 | 9.2407 | 69 | 5.7528 |  | 850 | 1020 | 101.5848 | 121.9017 | 0.9 | 91.4263 | 109.7116 | FMC Prince George JCT | BC_FMC_JCT | Canreed | BC_CRD_DSS |  |  | 963
| 60L339 | BC Hydro | British Columbia | 1 | ac | 55 | 33.9506 | 106.85 | 65.9568 | 69 | 41.0609 |  | 310 | 500 | 37.0486 | 59.7558 | 0.9 | 33.3437 | 53.7802 | Williston | BC_WSN_DSS | Pinnacle Pellets Meadowbank JCT | BC_PMB_JCT |  |  | 964
| 60L339PMB | BC Hydro | British Columbia | 1 | ac | 0.023904 | 0.014756 | 0.023904 | 0.014756 | 69 | 0.0091861 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Pinnacle Pellets Meadowbank JCT | BC_PMB_JCT | Pinnacle Pellets Meadowbank | BC_PMB_ISS |  |  | 965
| 60L339 | BC Hydro | British Columbia | 1 | ac | 12 | 7.4074 | 106.85 | 65.9568 | 69 | 41.0609 |  | 310 | 500 | 37.0486 | 59.7558 | 0.9 | 33.3437 | 53.7802 | Pinnacle Pellets Meadowbank JCT | BC_PMB_JCT | Colebank JCT | BC_CLB_JCT |  |  | 966
| 60L339CLB | BC Hydro | British Columbia | 1 | ac | 0.066812 | 0.041242 | 0.066812 | 0.041242 | 69 | 0.025675 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Colebank JCT | BC_CLB_JCT | Colebank | BC_CLB_DSS |  |  | 967
| 60L339 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 106.85 | 65.9568 | 69 | 41.0609 |  | 310 | 500 | 37.0486 | 59.7558 | 0.9 | 33.3437 | 53.7802 | Colebank JCT | BC_CLB_JCT | Dunkley Lumber JCT | BC_DKY_JCT |  |  | 968
| 60L339DKY | BC Hydro | British Columbia | 1 | ac | 0.28447 | 0.1756 | 0.28447 | 0.1756 | 69 | 0.10932 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Dunkley Lumber JCT | BC_DKY_JCT | Dunkley Lumber | BC_DKY_ISS |  |  | 969
| 60L339 | BC Hydro | British Columbia | 1 | ac | 36.85 | 22.7469 | 106.85 | 65.9568 | 69 | 41.0609 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Dunkley Lumber JCT | BC_DKY_JCT | Barlow | BC_BLW_DSS |  |  | 970
| 60L340 | BC Hydro | British Columbia | 1 | ac | 7.682 | 4.742 | 7.682 | 4.742 | 69 | 2.9521 |  | 830 | 1010 | 99.1945 | 120.7066 | 0.9 | 89.2751 | 108.636 | Canreed | BC_CRD_DSS | Northwood | BC_NWP_ISS |  |  | 971
| 60L341 | BC Hydro | British Columbia | 1 | ac | 9 | 5.5556 | 49.58 | 30.6049 | 69 | 19.0529 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Glenannan | BC_GLN_DSS | Fraser Lake JCT | BC_FSR_JCT |  |  | 972
| 60L341FSR | BC Hydro | British Columbia | 1 | ac | 0.097971 | 0.060476 | 0.097971 | 0.060476 | 69 | 0.037649 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Fraser Lake JCT | BC_FSR_JCT | Fraser Lake | BC_FSR_DSS |  |  | 973
| 60L341 | BC Hydro | British Columbia | 1 | ac | 7 | 4.321 | 49.58 | 30.6049 | 69 | 19.0529 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Fraser Lake JCT | BC_FSR_JCT | Fraser Lake Sawmill JCT | BC_FSS_JCT |  |  | 974
| 60L341FSS | BC Hydro | British Columbia | 1 | ac | 0.12564 | 0.077556 | 0.12564 | 0.077556 | 69 | 0.048282 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Fraser Lake Sawmill JCT | BC_FSS_JCT | Fraser Lake Sawmill | BC_FSS_ISS |  |  | 975
| 60L341 | BC Hydro | British Columbia | 1 | ac | 33.58 | 20.7284 | 49.58 | 30.6049 | 69 | 19.0529 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Fraser Lake Sawmill JCT | BC_FSS_JCT | Canfor JCT | BC_PLT_JCT |  |  | 976
| 60L344 | BC Hydro | British Columbia | 1 | ac | 61.1195 | 37.7281 | 61.1195 | 37.7281 | 69 | 23.4873 |  | 280 | 447 | 33.4632 | 53.4216 | 0.9 | 30.1169 | 48.0795 | Tachick | BC_TAC_DSS | Fort St James | BC_FM2_DSS |  |  | 977
| 60L351 | BC Hydro | British Columbia | 1 | ac | 15.0646 | 9.2991 | 15.0646 | 9.2991 | 69 | 5.7891 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Williston | BC_WSN_DSS | Beaverley | BC_BVY_DSS |  |  | 978
| 60L352 | BC Hydro | British Columbia | 1 | ac | 8.1097 | 5.006 | 8.1097 | 5.006 | 69 | 3.1164 |  | 725 | 925 | 86.6458 | 110.5481 | 0.9 | 77.9813 | 99.4933 | Glenannan | BC_GLN_DSS | Endako | BC_EKO_DSS |  |  | 979
| 60L354 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 22.63 | 13.9691 | 69 | 8.6964 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Beaverley | BC_BVY_DSS | Foothills JCT | BC_FHS_JCT |  |  | 980
| 60L354FHS | BC Hydro | British Columbia | 1 | ac | 1.4156 | 0.8738 | 1.4156 | 0.8738 | 69 | 0.54398 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Foothills JCT | BC_FHS_JCT | Foothills | BC_FHS_DSS |  |  | 981
| 60L354 | BC Hydro | British Columbia | 1 | ac | 12.63 | 7.7963 | 22.63 | 13.9691 | 69 | 8.6964 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Foothills JCT | BC_FHS_JCT | Chief Lake | BC_CHF_DSS |  |  | 982
| 60L357 | BC Hydro | British Columbia | 1 | ac | 10 | 6.1728 | 11.78 | 7.2716 | 69 | 4.5269 |  | 828 | 1060 | 98.9555 | 126.6822 | 0.9 | 89.06 | 114.014 | Beaverley | BC_BVY_DSS | Patricia JCT | BC_PCA_JCT |  |  | 983
| 60L357FHS | BC Hydro | British Columbia | 1 | ac | 2.2366 | 1.3806 | 2.2366 | 1.3806 | 69 | 0.85948 |  | 1050 | 1190 | 125.4871 | 142.2187 | 0.9 | 112.9384 | 127.9968 | Patricia JCT | BC_PCA_JCT | Foothills | BC_FHS_DSS |  |  | 984
| 60L357 | BC Hydro | British Columbia | 1 | ac | 1.78 | 1.0988 | 11.78 | 7.2716 | 69 | 4.5269 |  | 1050 | 1190 | 125.4871 | 142.2187 | 0.9 | 112.9384 | 127.9968 | Patricia JCT | BC_PCA_JCT | Patricia | BC_PCA_DSS |  |  | 985
| 60L358 | BC Hydro | British Columbia | 1 | ac | 28.51 | 17.5988 | 88.51 | 54.6358 | 69 | 34.0131 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Beaverley | BC_BVY_DSS | Isle Pierre JCT | BC_IPR_JCT |  |  | 986
| 60L358IPR | BC Hydro | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 69 | 0.38429 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Isle Pierre JCT | BC_IPR_JCT | Isle Pierre | BC_IPR_DSS |  |  | 987
| 60L358 | BC Hydro | British Columbia | 1 | ac | 60 | 37.037 | 88.51 | 54.6358 | 69 | 34.0131 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Isle Pierre JCT | BC_IPR_JCT | Vanderhoof JCT | BC_VDF_JCT |  |  | 988
| 60L359 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 5 | 3.0864 | 69 | 1.9214 |  | 360 | 535 | 43.0241 | 63.9387 | 0.9 | 38.7217 | 57.5448 | Fort St James | BC_FM2_DSS | Apollo Forest Products JCT | BC_AFP_JCT |  |  | 989
| 60L359AFP | BC Hydro | British Columbia | 1 | ac | 2.3735 | 1.4651 | 4.747 | 2.9302 | 69 | 1.8242 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Apollo Forest Products JCT | BC_AFP_JCT | Apollo Forest Products | BC_AFP_ISS |  |  | 990
| 60L359TFP | BC Hydro | British Columbia | 1 | ac | 2.35 | 1.4506 | 2.35 | 1.4506 | 69 | 0.90307 |  | 360 | 535 | 43.0241 | 63.9387 | 0.9 | 38.7217 | 57.5448 | Apollo Forest Products JCT | BC_AFP_JCT | Takla Forest Products | BC_TFP_DSS |  |  | 991
| 60L359AFP | BC Hydro | British Columbia | 1 | ac | 2.3735 | 1.4651 | 4.747 | 2.9302 | 69 | 1.8242 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Apollo Forest Products JCT | BC_AFP_JCT | Fort St James Green Energy GS | BC_FGE_GSS |  |  | 992
| 60L383 | BC Hydro | British Columbia | 1 | ac | 5 | 3.0864 | 13.53 | 8.3519 | 69 | 5.1994 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Skeena | BC_SKA_DSS | Terrace | BC_TER_DSS |  |  | 993
| 60L383 | BC Hydro | British Columbia | 1 | ac | 4.53 | 2.7963 | 13.53 | 8.3519 | 69 | 5.1994 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Terrace | BC_TER_DSS | Terrace Skeena Cellulose | BC_TSC_DSS |  |  | 994
| 60L383 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 13.53 | 8.3519 | 69 | 5.1994 |  | 280 | 450 | 33.4632 | 53.7802 | 0.9 | 30.1169 | 48.4022 | Terrace Skeena Cellulose | BC_TSC_DSS | Kalum | BC_KAL_DSS |  |  | 995
| 60L389 | BC Hydro | British Columbia | 1 | ac | 21.5486 | 13.3016 | 21.5486 | 13.3016 | 69 | 8.2808 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Skeena | BC_SKA_DSS | Dasque Creek GS | BC_DSQ_GSS |  |  | 996
| 60L390 | BC Hydro | British Columbia | 1 | ac | 4 | 2.4691 | 30.61 | 18.8951 | 69 | 11.763 |  | 230 | 380 | 27.4876 | 45.4144 | 0.9 | 24.7389 | 40.8729 | Rupert | BC_RUP_DSS | Diana Lake JCT | BC_DIL_JCT |  |  | 997
| 60L390DIL | BC Hydro | British Columbia | 1 | ac | 0.014135 | 0.0087254 | 0.014135 | 0.0087254 | 69 | 0.0054319 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Diana Lake JCT | BC_DIL_JCT | Diana Lake | BC_DIL_DSS |  |  | 998
| 60L390 | BC Hydro | British Columbia | 1 | ac | 2.61 | 1.6111 | 30.61 | 18.8951 | 69 | 11.763 |  | 230 | 380 | 27.4876 | 45.4144 | 0.9 | 24.7389 | 40.8729 | Diana Lake JCT | BC_DIL_JCT | Green River JCT | BC_GRR_JCT |  |  | 999
| 60L390GRR | BC Hydro | British Columbia | 1 | ac | 0.012543 | 0.0077425 | 0.012543 | 0.0077425 | 69 | 0.0048201 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Green River JCT | BC_GRR_JCT | Green River | BC_GRR_DSS |  |  | 1000
| 60L390 | BC Hydro | British Columbia | 1 | ac | 22 | 13.5802 | 30.61 | 18.8951 | 69 | 11.763 |  | 230 | 380 | 27.4876 | 45.4144 | 0.9 | 24.7389 | 40.8729 | Green River JCT | BC_GRR_JCT | Brown Lake JCT | BC_BRL_JCT |  |  | 1001
| 60L390BRL | BC Hydro | British Columbia | 1 | ac | 0.068721 | 0.04242 | 0.068721 | 0.04242 | 69 | 0.026408 |  | 340 | 340 | 40.6339 | 40.6339 | 0.9 | 36.5705 | 36.5705 | Brown Lake JCT | BC_BRL_JCT | Brown Lake GS | BC_BRL_GSS |  |  | 1002
| 60L390 | BC Hydro | British Columbia | 1 | ac | 2 | 1.2346 | 30.61 | 18.8951 | 69 | 11.763 |  | 230 | 380 | 27.4876 | 45.4144 | 0.9 | 24.7389 | 40.8729 | Brown Lake JCT | BC_BRL_JCT | Falls River GS | BC_FLS_GSS |  |  | 1003
| 60L391 | BC Hydro | British Columbia | 1 | ac | 8 | 4.9383 | 11.11 | 6.858 | 69 | 4.2694 |  | 430 | 745 | 51.3899 | 89.0361 | 0.9 | 46.251 | 80.1325 | Rupert | BC_RUP_DSS | Fareview Container Terminal JCT | BC_PRT_JCT |  |  | 1004
| 60L391PRT | BC Hydro | British Columbia | 1 | ac | 4.4241 | 2.7309 | 4.4241 | 2.7309 | 69 | 1.7001 | 3 |  |  | 0 | 0 | 0.9 | 36 | 39 | Fareview Container Terminal JCT | BC_PRT_JCT | Fareview Container Terminal | BC_PRT_ISS |  |  | 1005
| 60L391 | BC Hydro | British Columbia | 1 | ac | 3.11 | 1.9198 | 11.11 | 6.858 | 69 | 4.2694 |  | 430 | 745 | 51.3899 | 89.0361 | 0.9 | 46.251 | 80.1325 | Fareview Container Terminal JCT | BC_PRT_JCT | Oldfield | BC_OFD_DSS |  |  | 1006
| 60L392 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 10.71 | 6.6111 | 69 | 4.1157 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Rupert | BC_RUP_DSS | Port Edward JCT | BC_PED_JCT |  |  | 1007
| 60L392PED | BC Hydro | British Columbia | 1 | ac | 0.77786 | 0.48016 | 0.77786 | 0.48016 | 69 | 0.29892 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Port Edward JCT | BC_PED_JCT | Port Edward | BC_PED_DSS |  |  | 1008
| 60L392 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 10.71 | 6.6111 | 69 | 4.1157 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Port Edward JCT | BC_PED_JCT | Skeena Cellulose JCT | BC_SKL_JCT |  |  | 1009
| 60L392SKL | BC Hydro | British Columbia | 1 | ac | 0.61348 | 0.37869 | 0.61348 | 0.37869 | 69 | 0.23575 |  | 460 | 780 | 54.9753 | 93.219 | 0.9 | 49.4778 | 83.8971 | Skeena Cellulose JCT | BC_SKL_JCT | Skeena Cellulose | BC_SKL_ISS |  |  | 1010
| 60L392 | BC Hydro | British Columbia | 1 | ac | 3 | 1.8519 | 10.71 | 6.6111 | 69 | 4.1157 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Skeena Cellulose JCT | BC_SKL_JCT | Prince Rupert Grain JCT | BC_PRG_JCT |  |  | 1011
| 60L392PRG | BC Hydro | British Columbia | 1 | ac | 0.018987 | 0.01172 | 0.018987 | 0.01172 | 69 | 0.0072963 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Prince Rupert Grain JCT | BC_PRG_JCT | Prince Rupert Grain | BC_PRG_ISS |  |  | 1012
| 60L392 | BC Hydro | British Columbia | 1 | ac | 1.71 | 1.0556 | 10.71 | 6.6111 | 69 | 4.1157 |  | 450 | 760 | 53.7802 | 90.8287 | 0.9 | 48.4022 | 81.7459 | Prince Rupert Grain JCT | BC_PRG_JCT | Ridley Terminals Inc | BC_RTI_ISS |  |  | 1013
| 60L393 | BC Hydro | British Columbia | 1 | ac | 10.7804 | 6.6546 | 10.7804 | 6.6546 | 69 | 4.1428 |  | 430 | 745 | 51.3899 | 89.0361 | 0.9 | 46.251 | 80.1325 | Rupert | BC_RUP_DSS | Oldfield | BC_OFD_DSS |  |  | 1014
| 60L394 | BC Hydro | British Columbia | 1 | ac | 10.7257 | 6.6208 | 10.7257 | 6.6208 | 69 | 4.1217 |  | 390 | 650 | 46.6095 | 77.6825 | 0.9 | 41.9485 | 69.9142 | Skeena | BC_SKA_DSS | Kalum | BC_KAL_DSS |  |  | 1015
| 60L395 | BC Hydro | British Columbia | 1 | ac | 0.4739 | 0.29253 | 0.4739 | 0.29253 | 69 | 0.18211 |  | 754 | 949 | 90.1117 | 113.4164 | 0.9 | 81.1005 | 102.0748 | Rupert Gas | BC_RPG_GSS | Rupert | BC_RUP_DSS |  |  | 1016
| 1L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 63 | 0.38 | 3 | [5 empty] | 29.7675 | 32.5328 | Warfield | BC_WTS_DSS | Stoney Creek | BC_STY_DSS |  | STY used for Stoney Creek to avoid confusion with STC - Site C | 1017
| 6L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Brilliant SWS | BC_BSS_SWS | Blueberry JCT | BC_BLB_JCT |  | BLB used for Blueberry to avoid confusion with BLU - Blue River | 1018
| 6L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Blueberry JCT | BC_BLB_JCT | Ootischenia | BC_OOT_DSS |  | BLB used for Blueberry to avoid confusion with BLU - Blue River | 1019
| 6L | FortisBC | British Columbia | 1 | ac | 5 | 3.0864 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Ootischenia | BC_OOT_DSS | Blueberry | BC_BLB_DSS |  | BLB used for Blueberry to avoid confusion with BLU - Blue River | 1020
| 6L | FortisBC | British Columbia | 1 | ac | 2 | 1.2346 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Blueberry JCT | BC_BLB_JCT | Castlegar | BC_CAS_DSS |  | BLB used for Blueberry to avoid confusion with BLU - Blue River | 1021
| 6L | FortisBC | British Columbia | 1 | ac | 5.5 | 3.3951 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Castlegar | BC_CAS_DSS | Kraft GS | BC_KRA_GSS |  | Kraft refers to Celgar Green Energy | 1022
| 6L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Kraft GS | BC_KRA_GSS | Westar | BC_WST_DSS |  |  | 1023
| 7L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 2 | 1.2346 | 63 | 0.76 | 3 | [5 empty] | 29.7675 | 32.5328 | Brilliant TS | BC_BTS_TSS | Brilliant SWS | BC_BSS_SWS |  |  | 1024
| 7L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 2 | 1.2346 | 63 | 0.76 | 3 | [5 empty] | 29.7675 | 32.5328 | Brilliant SWS | BC_BSS_SWS | Brilliant GS | BC_BRD_GSS |  |  | 1025
| 8L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 2 | 1.2346 | 63 | 0.76 | 3 | [5 empty] | 29.7675 | 32.5328 | Brilliant TS | BC_BTS_TSS | Brilliant SWS | BC_BSS_SWS |  |  | 1026
| 8L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 2 | 1.2346 | 63 | 0.76 | 3 | [5 empty] | 29.7675 | 32.5328 | Brilliant SWS | BC_BSS_SWS | Brilliant GS | BC_BRD_GSS |  |  | 1027
| 9EL | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 53.5 | 33.0247 | 63 | 20.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Grand Forks TS | BC_GFT_TSS | Ruckles JCT | BC_RUC_JCT |  |  | 1028
| 9ELRUC | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 2.5 | 1.5432 | 63 | 0.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Ruckles JCT | BC_RUC_JCT | Bradford | BC_BRA_ISS |  |  | 1029
| 9ELRUC | FortisBC | British Columbia | 1 | ac | 1.5 | 0.92593 | 2.5 | 1.5432 | 63 | 0.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Bradford | BC_BRA_ISS | Ruckles | BC_RUC_DSS |  |  | 1030
| 9EL | FortisBC | British Columbia | 1 | ac | 17.5 | 10.8025 | 53.5 | 33.0247 | 63 | 20.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Ruckles JCT | BC_RUC_JCT | Christina Lake JCT | BC_CHR_JCT |  |  | 1031
| 9ELCHR | FortisBC | British Columbia | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 63 | 0.76 | 3 | [5 empty] | 29.7675 | 32.5328 | Christina Lake JCT | BC_CHR_JCT | Christina Lake | BC_CHR_DSS |  |  | 1032
| 9EL | FortisBC | British Columbia | 1 | ac | 32.5 | 20.0617 | 53.5 | 33.0247 | 63 | 20.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Christina Lake JCT | BC_CHR_JCT | Cascade JCT | BC_CSC_JCT |  |  | 1033
| 9EL | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 53.5 | 33.0247 | 63 | 20.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Cascade JCT | BC_CSC_JCT | Cascade | BC_CSC_DSS |  |  | 1034
| 9L | FortisBC | British Columbia | 1 | ac | 7.5 | 4.6296 | 7.5 | 4.6296 | 63 | 2.85 | 3 | [5 empty] | 29.7675 | 32.5328 | Cascade JCT | BC_CSC_JCT | Warfield | BC_WTS_DSS |  |  | 1035
| 10EL | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 53.5 | 33.0247 | 63 | 20.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Grand Forks TS | BC_GFT_TSS | Ruckles JCT | BC_RUC_JCT |  |  | 1036
| 10ELRUC | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 2.5 | 1.5432 | 63 | 0.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Ruckles JCT | BC_RUC_JCT | Bradford | BC_BRA_ISS |  |  | 1037
| 10ELRUC | FortisBC | British Columbia | 1 | ac | 1.5 | 0.92593 | 2.5 | 1.5432 | 63 | 0.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Bradford | BC_BRA_ISS | Ruckles | BC_RUC_DSS |  |  | 1038
| 10EL | FortisBC | British Columbia | 1 | ac | 17.5 | 10.8025 | 53.5 | 33.0247 | 63 | 20.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Ruckles JCT | BC_RUC_JCT | Christina Lake JCT | BC_CHR_JCT |  |  | 1039
| 10ELCHR | FortisBC | British Columbia | 1 | ac | 2 | 1.2346 | 2 | 1.2346 | 63 | 0.76 | 3 | [5 empty] | 29.7675 | 32.5328 | Christina Lake JCT | BC_CHR_JCT | Christina Lake | BC_CHR_DSS |  |  | 1040
| 10EL | FortisBC | British Columbia | 1 | ac | 32.5 | 20.0617 | 53.5 | 33.0247 | 63 | 20.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Christina Lake JCT | BC_CHR_JCT | Cascade JCT | BC_CSC_JCT |  |  | 1041
| 10EL | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 53.5 | 33.0247 | 63 | 20.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Cascade JCT | BC_CSC_JCT | Cascade | BC_CSC_DSS |  |  | 1042
| 10L | FortisBC | British Columbia | 1 | ac | 7.5 | 4.6296 | 7.5 | 4.6296 | 63 | 2.85 | 3 | [5 empty] | 29.7675 | 32.5328 | Cascade JCT | BC_CSC_JCT | Warfield | BC_WTS_DSS |  |  | 1043
| 11EL | FortisBC | British Columbia | 1 | ac | 60 | 37.037 | 60 | 37.037 | 161 | 27 | 3 | [5 empty] | 192.9603 | 212.4672 | Grand Forks TS | BC_GFT_TSS | AS Mawdsley TS | BC_ASM_TSS |  |  | 1044
| 11WL | FortisBC | British Columbia | 1 | ac | 35 | 21.6049 | 35 | 21.6049 | 161 | 15.75 | 3 | [5 empty] | 192.9603 | 212.4672 | Kettle Valley | BC_KET_DSS | Grand Forks TS | BC_GFT_TSS |  |  | 1045
| 12L (60L227) | FortisBC | British Columbia | 1 | ac | 0.74313 | 0.45872 | 0.74313 | 0.45872 | 63 | 0.28239 | 3 | [5 empty] | 29.7675 | 32.5328 | Kootenay Canal GS | BC_KCL_GSS | South Slocan GS | BC_SLC_GSS |  |  | 1046
| 13L (60L225) | FortisBC | British Columbia | 1 | ac | 0.42899 | 0.26481 | 0.42899 | 0.26481 | 63 | 0.16302 | 3 | [5 empty] | 29.7675 | 32.5328 | Kootenay Canal GS | BC_KCL_GSS | South Slocan GS | BC_SLC_GSS |  |  | 1047
| 14L | FortisBC | British Columbia | 1 | ac | 11 | 6.7901 | 11.5 | 7.0988 | 63 | 4.37 | 3 | [5 empty] | 29.7675 | 32.5328 | Emerald SWS | BC_ESS_SWS | Waneta SS | BC_WHS_TSS |  |  | 1048
| 14L | FortisBC | British Columbia | 1 | ac | 0.5 | 0.30864 | 11.5 | 7.0988 | 63 | 4.37 | 3 | [5 empty] | 29.7675 | 32.5328 | Waneta SS | BC_WHS_TSS | Waneta GS | BC_WAN_GSS |  |  | 1049
| 15L | FortisBC | British Columbia | 1 | ac | 11 | 6.7901 | 11.5 | 7.0988 | 63 | 4.37 | 3 | [5 empty] | 29.7675 | 32.5328 | Emerald SWS | BC_ESS_SWS | Waneta SS | BC_WHS_TSS |  |  | 1050
| 15L | FortisBC | British Columbia | 1 | ac | 0.5 | 0.30864 | 11.5 | 7.0988 | 63 | 4.37 | 3 | [5 empty] | 29.7675 | 32.5328 | Waneta SS | BC_WHS_TSS | Waneta GS | BC_WAN_GSS |  |  | 1051
| 16L | FortisBC | British Columbia | 1 | ac | 11 | 6.7901 | 11.5 | 7.0988 | 63 | 4.37 | 3 | [5 empty] | 29.7675 | 32.5328 | Emerald SWS | BC_ESS_SWS | Waneta SS | BC_WHS_TSS |  |  | 1052
| 16L | FortisBC | British Columbia | 1 | ac | 0.5 | 0.30864 | 11.5 | 7.0988 | 63 | 4.37 | 3 | [5 empty] | 29.7675 | 32.5328 | Waneta SS | BC_WHS_TSS | Waneta GS | BC_WAN_GSS |  |  | 1053
| 17L | FortisBC | British Columbia | 1 | ac | 11 | 6.7901 | 11.5 | 7.0988 | 63 | 4.37 | 3 | [5 empty] | 29.7675 | 32.5328 | Emerald SWS | BC_ESS_SWS | Waneta SS | BC_WHS_TSS |  |  | 1054
| 17L | FortisBC | British Columbia | 1 | ac | 0.5 | 0.30864 | 11.5 | 7.0988 | 63 | 4.37 | 3 | [5 empty] | 29.7675 | 32.5328 | Waneta SS | BC_WHS_TSS | Waneta GS | BC_WAN_GSS |  |  | 1055
| 18L | FortisBC | British Columbia | 1 | ac | 8.5 | 5.2469 | 8.5 | 5.2469 | 63 | 3.23 | 3 | [5 empty] | 29.7675 | 32.5328 | Waneta SS | BC_WHS_TSS | Beaver Park | BC_BEP_DSS |  |  | 1056
| 19L | FortisBC | British Columbia | 1 | ac | 12.5 | 7.716 | 40 | 24.6914 | 63 | 15.2 | 3 | [5 empty] | 29.7675 | 32.5328 | South Slocan GS | BC_SLC_GSS | Passmore | BC_PAS_DSS |  |  | 1057
| 19L | FortisBC | British Columbia | 1 | ac | 27.5 | 16.9753 | 40 | 24.6914 | 63 | 15.2 | 3 | [5 empty] | 29.7675 | 32.5328 | Passmore | BC_PAS_DSS | Valhalla | BC_VAL_DSS |  |  | 1058
| 20L | FortisBC | British Columbia | 1 | ac | 4.5 | 2.7778 | 42.5 | 26.2346 | 63 | 16.15 | 3 | [5 empty] | 29.7675 | 32.5328 | Warfield | BC_WTS_DSS | Glenmerry | BC_GLM_DSS |  |  | 1059
| 20L | FortisBC | British Columbia | 1 | ac | 5.5 | 3.3951 | 42.5 | 26.2346 | 63 | 16.15 | 3 | [5 empty] | 29.7675 | 32.5328 | Glenmerry | BC_GLM_DSS | Beaver Park | BC_BEP_DSS |  |  | 1060
| 20L | FortisBC | British Columbia | 1 | ac | 7.5 | 4.6296 | 42.5 | 26.2346 | 63 | 16.15 | 3 | [5 empty] | 29.7675 | 32.5328 | Beaver Park | BC_BEP_DSS | Fruitvale | BC_FRU_DSS |  |  | 1061
| 20L | FortisBC | British Columbia | 1 | ac | 7.5 | 4.6296 | 42.5 | 26.2346 | 63 | 16.15 | 3 | [5 empty] | 29.7675 | 32.5328 | Fruitvale | BC_FRU_DSS | Hearns | BC_HER_DSS |  |  | 1062
| 20L | FortisBC | British Columbia | 1 | ac | 17.5 | 10.8025 | 42.5 | 26.2346 | 63 | 16.15 | 3 | [5 empty] | 29.7675 | 32.5328 | Hearns | BC_HER_DSS | Salmo | BC_SLM_DSS |  | SLM used for Salmo to avoid confusion with SAL - Saltspring | 1063
| 21L | FortisBC | British Columbia | 1 | ac | 1.5 | 0.92593 | 1.5 | 0.92593 | 63 | 0.57 | 3 | [5 empty] | 29.7675 | 32.5328 | South Slocan GS | BC_SLC_GSS | Lower Bonnington GS | BC_LBO_GSS |  |  | 1064
| 22L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 2.5 | 1.5432 | 63 | 0.95 | 3 | [5 empty] | 29.7675 | 32.5328 | South Slocan GS | BC_SLC_GSS | Upper Bonnington SWS | BC_USS_SWS |  |  | 1065
| 23L | FortisBC | British Columbia | 1 | ac | 1.5 | 0.92593 | 4 | 2.4691 | 63 | 1.52 | 3 | [5 empty] | 29.7675 | 32.5328 | South Slocan GS | BC_SLC_GSS | Lower Bonnington GS | BC_LBO_GSS |  |  | 1066
| 23L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 4 | 2.4691 | 63 | 1.52 | 3 | [5 empty] | 29.7675 | 32.5328 | Lower Bonnington GS | BC_LBO_GSS | Upper Bonnington SWS | BC_USS_SWS |  |  | 1067
| 23L | FortisBC | British Columbia | 1 | ac | 1.5 | 0.92593 | 4 | 2.4691 | 63 | 1.52 | 3 | [5 empty] | 29.7675 | 32.5328 | Upper Bonnington SWS | BC_USS_SWS | Corra Linn GS | BC_COR_GSS |  |  | 1068
| 24L | FortisBC | British Columbia | 1 | ac | 4 | 2.4691 | 4 | 2.4691 | 63 | 1.52 | 3 | [5 empty] | 29.7675 | 32.5328 | South Slocan GS | BC_SLC_GSS | Corra Linn GS | BC_COR_GSS |  |  | 1069
| 25L | FortisBC | British Columbia | 1 | ac | 9 | 5.5556 | 16.5 | 10.1852 | 63 | 6.27 | 3 | [5 empty] | 29.7675 | 32.5328 | Brilliant SWS | BC_BSS_SWS | Tarrys | BC_TAR_DSS |  |  | 1070
| 25L | FortisBC | British Columbia | 1 | ac | 6.5 | 4.0123 | 16.5 | 10.1852 | 63 | 6.27 | 3 | [5 empty] | 29.7675 | 32.5328 | Tarrys | BC_TAR_DSS | Playmore | BC_PLA_DSS |  |  | 1071
| 25L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 16.5 | 10.1852 | 63 | 6.27 | 3 | [5 empty] | 29.7675 | 32.5328 | Playmore | BC_PLA_DSS | South Slocan GS | BC_SLC_GSS |  |  | 1072
| 26L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Brilliant SWS | BC_BSS_SWS | Blueberry JCT | BC_BLB_JCT |  | BLB used for Blueberry to avoid confusion with BLU - Blue River | 1073
| 26L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Blueberry JCT | BC_BLB_JCT | Ootischenia | BC_OOT_DSS |  | BLB used for Blueberry to avoid confusion with BLU - Blue River | 1074
| 26L | FortisBC | British Columbia | 1 | ac | 5 | 3.0864 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Ootischenia | BC_OOT_DSS | Blueberry | BC_BLB_DSS |  | BLB used for Blueberry to avoid confusion with BLU - Blue River | 1075
| 26L | FortisBC | British Columbia | 1 | ac | 2 | 1.2346 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Blueberry JCT | BC_BLB_JCT | Castlegar | BC_CAS_DSS |  | BLB used for Blueberry to avoid confusion with BLU - Blue River | 1076
| 26L | FortisBC | British Columbia | 1 | ac | 5.5 | 3.3951 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Castlegar | BC_CAS_DSS | Kraft GS | BC_KRA_GSS |  | Kraft refers to Celgar Green Energy | 1077
| 26L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Kraft GS | BC_KRA_GSS | Westar | BC_WST_DSS |  |  | 1078
| 27L | FortisBC | British Columbia | 1 | ac | 12.5 | 7.716 | 52.5 | 32.4074 | 63 | 19.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Salmo | BC_SLM_DSS | Ymir | BC_YMR_DSS |  | SLM used for Salmo to avoid confusion with SAL - Saltspring | 1079
| 27L | FortisBC | British Columbia | 1 | ac | 17.5 | 10.8025 | 52.5 | 32.4074 | 63 | 19.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Ymir | BC_YMR_DSS | Cottonwood | BC_COT_DSS |  |  | 1080
| 27L | FortisBC | British Columbia | 1 | ac | 10 | 6.1728 | 52.5 | 32.4074 | 63 | 19.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Cottonwood | BC_COT_DSS | Rosemont | BC_RSM_DSS |  |  | 1081
| 27L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 52.5 | 32.4074 | 63 | 19.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Rosemont | BC_RSM_DSS | Nelson | BC_NLS_DSS |  | Nelson represents all substations within Nelson Hydro | 1082
| 27L | FortisBC | British Columbia | 1 | ac | 10 | 6.1728 | 52.5 | 32.4074 | 63 | 19.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Nelson | BC_NLS_DSS | Corra Linn GS | BC_COR_GSS |  | DELETED - NELSON JCT | 1083
| 28L | FortisBC | British Columbia | 1 | ac | 10 | 6.1728 | 10 | 6.1728 | 63 | 3.8 | 3 | [5 empty] | 29.7675 | 32.5328 | Upper Bonnington GS | BC_UBO_GSS | Nelson | BC_NLS_DSS |  | Nelson represents all substations within Nelson Hydro | 1084
| 30L | FortisBC | British Columbia | 1 | ac | 57.5 | 35.4938 | 57.5 | 35.4938 | 63 | 21.85 | 3 | [5 empty] | 29.7675 | 32.5328 | South Slocan GS | BC_SLC_GSS | Coffee Creek | BC_COF_DSS |  |  | 1085
| 31L | FortisBC | British Columbia | 1 | ac | 5.5 | 3.3951 | 5.5 | 3.3951 | 63 | 2.09 | 3 | [5 empty] | 29.7675 | 32.5328 | AA Lambert | BC_AAL_DSS | Creston | BC_CRE_DSS |  |  | 1086
| 32L | FortisBC | British Columbia | 1 | ac | 67.5 | 41.6667 | 67.5 | 41.6667 | 63 | 25.65 | 3 | [5 empty] | 29.7675 | 32.5328 | AA Lambert | BC_AAL_DSS | Crawford Bay | BC_CRA_DSS |  |  | 1087
| 33L | FortisBC | British Columbia | 1 | ac | 0.5 | 0.30864 | 0.5 | 0.30864 | 63 | 0.19 | 3 | [5 empty] | 29.7675 | 32.5328 | Upper Bonnington SWS | BC_USS_SWS | Upper Bonnington GS | BC_UBO_GSS |  |  | 1088
| 34L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 63 | 0.38 | 3 | [5 empty] | 29.7675 | 32.5328 | AS Mawdsley TS | BC_ASM_TSS | Warfield | BC_WTS_DSS |  |  | 1089
| 37L | FortisBC | British Columbia | 1 | ac | 22.5 | 13.8889 | 22.5 | 13.8889 | 63 | 8.55 | 3 | [5 empty] | 29.7675 | 32.5328 | Coffee Creek | BC_COF_DSS | Kaslo | BC_KAS_DSS |  |  | 1090
| 38L | FortisBC | British Columbia | 1 | ac | 5 | 3.0864 | 5 | 3.0864 | 63 | 1.9 | 3 | [5 empty] | 29.7675 | 32.5328 | Crawford Bay | BC_CRA_DSS | Coffee Creek | BC_COF_DSS |  |  | 1091
| 40L | FortisBC | British Columbia | 1 | ac | 7.5 | 4.6296 | 7.5 | 4.6296 | 230 | 3.6 | 3 | [5 empty] | 402 | 435 | Bentley TS | BC_BEN_TSS | Vaseux Lake | BC_VAS_DSS |  |  | 1092
| 42L | FortisBC | British Columbia | 1 | ac | 17.5 | 10.8025 | 34 | 20.9877 | 63 | 12.92 | 3 | [5 empty] | 29.7675 | 32.5328 | Oliver | BC_OLI_DSS | OK Falls | BC_OKF_DSS |  |  | 1093
| 42L | FortisBC | British Columbia | 1 | ac | 7 | 4.321 | 34 | 20.9877 | 63 | 12.92 | 3 | [5 empty] | 29.7675 | 32.5328 | OK Falls | BC_OKF_DSS | Kaledon | BC_KAL2_DSS |  | KLD used for Kaledon to avoid confusion with KAL - Kalum | 1094
| 42L | FortisBC | British Columbia | 1 | ac | 9.5 | 5.8642 | 34 | 20.9877 | 63 | 12.92 | 3 | [5 empty] | 29.7675 | 32.5328 | Kaledon | BC_KAL2_DSS | Huth Avenue | BC_HUT_DSS |  | KLD used for Kaledon to avoid confusion with KAL - Kalum | 1095
| 43L | FortisBC | British Columbia | 1 | ac | 27.5 | 16.9753 | 85 | 52.4691 | 138 | 36.8536 | 3 | [5 empty] | 141 | 156 | Princeton | BC_PRI_DSS | BC Gas | BC_BCG_ISS |  |  | 1096
| 43L | FortisBC | British Columbia | 1 | ac | 6 | 3.7037 | 85 | 52.4691 | 138 | 36.8536 | 3 | [5 empty] | 141 | 156 | BC Gas | BC_BCG_ISS | Hedley | BC_HED_DSS |  |  | 1097
| 43L | FortisBC | British Columbia | 1 | ac | 27.5 | 16.9753 | 85 | 52.4691 | 138 | 36.8536 | 3 | [5 empty] | 141 | 156 | Hedley | BC_HED_DSS | Keremeos | BC_KER_DSS |  |  | 1098
| 43AL | FortisBC | British Columbia | 1 | ac | 4 | 2.4691 | 4 | 2.4691 | 138 | 1.7343 | 3 | [5 empty] | 141 | 156 | Hedley | BC_HED_DSS | Mascot Mines | BC_MAS_ISS |  |  | 1099
| 43L | FortisBC | British Columbia | 1 | ac | 24 | 14.8148 | 85 | 52.4691 | 138 | 36.8536 | 3 | [5 empty] | 141 | 156 | Keremeos | BC_KER_DSS | Bentley TS | BC_BEN_TSS |  |  | 1100
| 44L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Oliver | BC_OLI_DSS | Pine | BC_PNE_DSS |  | PNE used for Pine to avoid confusion with PIN - Pingston | 1101
| 44L | FortisBC | British Columbia | 1 | ac | 17.5 | 10.8025 | 18.5 | 11.4198 | 63 | 7.03 | 3 | [5 empty] | 29.7675 | 32.5328 | Pine | BC_PNE_DSS | Osoyoos | BC_OSO_DSS |  | PNE used for Pine to avoid confusion with PIN - Pingston | 1102
| 45L | FortisBC | British Columbia | 1 | ac | 3.5 | 2.1605 | 11 | 6.7901 | 63 | 4.18 | 3 | [5 empty] | 29.7675 | 32.5328 | RG Anderson | BC_RGA_DSS | Westminster | BC_WES_DSS |  |  | 1103
| 45L | FortisBC | British Columbia | 1 | ac | 7.5 | 4.6296 | 11 | 6.7901 | 63 | 4.18 | 3 | [5 empty] | 29.7675 | 32.5328 | Westminster | BC_WES_DSS | Arawana | BC_AWA_DSS |  |  | 1104
| 46L | FortisBC | British Columbia | 1 | ac | 11.5 | 7.0988 | 11.5 | 7.0988 | 138 | 4.9861 | 3 | [5 empty] | 141 | 156 | FA Lee TS | BC_LEE_TSS | Duck Lake | BC_DUC_DSS |  |  | 1105
| 47L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 2.5 | 1.5432 | 63 | 0.95 | 3 | [5 empty] | 29.7675 | 32.5328 | Huth Avenue | BC_HUT_DSS | Waterford | BC_WAT_DSS |  |  | 1106
| 48L | FortisBC | British Columbia | 1 | ac | 47.5 | 29.321 | 47.5 | 29.321 | 161 | 21.375 | 3 | [5 empty] | 192.9603 | 212.4672 | Bentley TS | BC_BEN_TSS | Grand Forks TS | BC_GFT_TSS |  |  | 1107
| 49L | FortisBC | British Columbia | 1 | ac | 3 | 1.8519 | 14 | 8.642 | 63 | 5.32 | 3 | [5 empty] | 29.7675 | 32.5328 | Huth Avenue | BC_HUT_DSS | West Bench | BC_WEB_DSS |  |  | 1108
| 49L | FortisBC | British Columbia | 1 | ac | 7.5 | 4.6296 | 14 | 8.642 | 63 | 5.32 | 3 | [5 empty] | 29.7675 | 32.5328 | West Bench | BC_WEB_DSS | Trout Creek | BC_TRC_DSS |  |  | 1109
| 49L | FortisBC | British Columbia | 1 | ac | 3.5 | 2.1605 | 14 | 8.642 | 63 | 5.32 | 3 | [5 empty] | 29.7675 | 32.5328 | Trout Creek | BC_TRC_DSS | Summerland | BC_SUM_DSS |  |  | 1110
| 50L | FortisBC | British Columbia | 1 | ac | 3.5 | 2.1605 | 14 | 8.642 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | FA Lee TS | BC_LEE_TSS | Sexsmith | BC_SEX_DSS |  |  | 1111
| 50L | FortisBC | British Columbia | 1 | ac | 5 | 3.0864 | 14 | 8.642 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Sexsmith | BC_SEX_DSS | Glenmore FBC | BC_GLE_DSS |  |  | 1112
| 50L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 14 | 8.642 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Glenmore FBC | BC_GLE_DSS | Recreation | BC_REC_DSS |  |  | 1113
| 50L | FortisBC | British Columbia | 1 | ac | 1.5 | 0.92593 | 14 | 8.642 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Recreation | BC_REC_DSS | Saucier | BC_SAU_DSS |  |  | 1114
| 50L | FortisBC | British Columbia | 1 | ac | 1.5 | 0.92593 | 14 | 8.642 | 138 | 6.07 | 3 | [5 empty] | 141 | 156 | Saucier | BC_SAU_DSS | Hollywood JCT | BC_HOL_JCT |  |  | 1115
| 51L | FortisBC | British Columbia | 1 | ac | 2 | 1.2346 | 4.5 | 2.7778 | 138 | 1.9511 | 3 | [5 empty] | 141 | 156 | Hollywood JCT | BC_HOL_JCT | Okanagan Mission | BC_OKM_DSS |  |  | 1116
| 51L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 4.5 | 2.7778 | 138 | 1.9511 | 3 | [5 empty] | 141 | 156 | Okanagan Mission | BC_OKM_DSS | Benvoulin | BC_BEV_DSS |  |  | 1117
| 52L | FortisBC | British Columbia | 1 | ac | 3.5 | 2.1605 | 3.5 | 2.1605 | 63 | 1.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Huth Avenue | BC_HUT_DSS | RG Anderson | BC_RGA_DSS |  |  | 1118
| 53L | FortisBC | British Columbia | 1 | ac | 3.5 | 2.1605 | 3.5 | 2.1605 | 63 | 1.33 | 3 | [5 empty] | 29.7675 | 32.5328 | Huth Avenue | BC_HUT_DSS | RG Anderson | BC_RGA_DSS |  |  | 1119
| 54L | FortisBC | British Columbia | 1 | ac | 11 | 6.7901 | 11 | 6.7901 | 138 | 4.7693 | 3 | [5 empty] | 141 | 156 | Black Mountain | BC_BLK_DSS | DG Bell | BC_DGB_DSS |  |  | 1120
| 55L | FortisBC | British Columbia | 1 | ac | 6.5 | 4.0123 | 12.5 | 7.716 | 138 | 5.4196 | 3 | [5 empty] | 141 | 156 | Hollywood JCT | BC_HOL_JCT | Hollywood | BC_HOL_DSS |  |  | 1121
| 55L | FortisBC | British Columbia | 1 | ac | 6 | 3.7037 | 12.5 | 7.716 | 138 | 5.4196 | 3 | [5 empty] | 141 | 156 | Hollywood | BC_HOL_DSS | FA Lee TS | BC_LEE_TSS |  |  | 1122
| 56L | FortisBC | British Columbia | 1 | ac | 5 | 3.0864 | 5 | 3.0864 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Princeton JCT | BC_PRI_JCT | Princeton | BC_PRI_DSS |  |  | 1123
| 57L | FortisBC | British Columbia | 1 | ac | 4 | 2.4691 | 40 | 24.6914 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | Black Mountain | BC_BLK_DSS | Joe Riche | BC_JRH_DSS |  | JRH used for Joe Riche to avoid confusion with JOR - Jordan River | 1124
| 57L | FortisBC | British Columbia | 1 | ac | 36 | 22.2222 | 40 | 24.6914 | 138 | 17.3429 | 3 | [5 empty] | 141 | 156 | Joe Riche | BC_JRH_DSS | Big White | BC_BWS_DSS |  | JRH used for Joe Riche to avoid confusion with JOR - Jordan River | 1125
| 58L | FortisBC | British Columbia | 1 | ac | 4 | 2.4691 | 4 | 2.4691 | 138 | 1.7343 | 3 | [5 empty] | 141 | 156 | FA Lee TS | BC_LEE_TSS | Black Mountain | BC_BLK_DSS |  |  | 1126
| 60L | FortisBC | British Columbia | 1 | ac | 2.5 | 1.5432 | 2.5 | 1.5432 | 138 | 1.0839 | 3 | [5 empty] | 141 | 156 | Benvoulin | BC_BEV_DSS | DG Bell | BC_DGB_DSS |  |  | 1127
| 61L | FortisBC | British Columbia | 1 | ac | 5 | 3.0864 | 5 | 3.0864 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Duck Lake | BC_DUC_DSS | Ellison | BC_ELL_DSS |  |  | 1128
| 62L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 63 | 0.38 | 3 | [5 empty] | 29.7675 | 32.5328 | Warfield | BC_WTS_DSS | Emerald SWS | BC_ESS_SWS |  |  | 1129
| 66L | FortisBC | British Columbia | 1 | ac | 20 | 12.3457 | 20 | 12.3457 | 63 | 7.6 | 3 | [5 empty] | 29.7675 | 32.5328 | Bentley TS | BC_BEN_TSS | Nk'Mip | BC_NKM_DSS |  |  | 1130
| 68L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 63 | 0.38 | 3 | [5 empty] | 29.7675 | 32.5328 | Bentley TS | BC_BEN_TSS | Oliver | BC_OLI_DSS |  |  | 1131
| 69L | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 1 | 0.61728 | 63 | 0.38 | 3 | [5 empty] | 29.7675 | 32.5328 | Bentley TS | BC_BEN_TSS | Oliver | BC_OLI_DSS |  |  | 1132
| 71L (2L277) | FortisBC | British Columbia | 1 | ac | 20 | 12.3457 | 21 | 12.963 | 230 | 10.08 | 3 | [5 empty] | 402 | 435 | Waneta SS | BC_WHS_TSS | Nelway | BC_NLY_DSS |  |  | 1133
| 71L (2L277) | FortisBC | British Columbia | 1 | ac | 1 | 0.61728 | 21 | 12.963 | 230 | 10.08 | [6 empty] | 450 | 450 | Nelway | BC_NLY_DSS | INT Nelway BPA | XX_BCUS2_INT |  |  | 1134
| 72L (2L263) | FortisBC | British Columbia | 1 | ac | 42.5 | 26.2346 | 42.5 | 26.2346 | 230 | 20.4 | 3 | [5 empty] | 402 | 435 | FA Lee TS | BC_LEE_TSS | Vernon TS | BC_VNT_TSS |  |  | 1135
| 73L | FortisBC | British Columbia | 1 | ac | 15 | 9.2593 | 57.5 | 35.4938 | 230 | 27.6 | 3 | [5 empty] | 402 | 435 | FA Lee TS | BC_LEE_TSS | DG Bell | BC_DGB_DSS |  |  | 1136
| 73L | FortisBC | British Columbia | 1 | ac | 42.5 | 26.2346 | 57.5 | 35.4938 | 230 | 27.6 | 3 | [5 empty] | 402 | 435 | DG Bell | BC_DGB_DSS | RG Anderson | BC_RGA_DSS |  |  | 1137
| 74L (2L264) | FortisBC | British Columbia | 1 | ac | 42.5 | 26.2346 | 42.5 | 26.2346 | 230 | 20.4 | 3 | [5 empty] | 402 | 435 | FA Lee TS | BC_LEE_TSS | Vernon TS | BC_VNT_TSS |  |  | 1138
| 75L | FortisBC | British Columbia | 1 | ac | 25 | 15.4321 | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | RG Anderson | BC_RGA_DSS | Vaseux Lake | BC_VAS_DSS |  |  | 1139
| 76L | FortisBC | British Columbia | 1 | ac | 25 | 15.4321 | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | RG Anderson | BC_RGA_DSS | Vaseux Lake | BC_VAS_DSS |  |  | 1140
| 77L | FortisBC | British Columbia | 1 | ac | 25 | 15.4321 | 25 | 15.4321 | 230 | 12 | 3 | [5 empty] | 402 | 435 | Warfield | BC_WTS_DSS | Brilliant TS | BC_BTS_TSS |  |  | 1141
| 79L (2L288) | FortisBC | British Columbia | 1 | ac | 15 | 9.2593 | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Brilliant TS | BC_BTS_TSS | Kootenay Canal GS | BC_KCL_GSS |  |  | 1142
| 81L (2L290) | FortisBC | British Columbia | 1 | ac | 15 | 9.2593 | 15 | 9.2593 | 230 | 7.2 | 3 | [5 empty] | 402 | 435 | Arrow Lakes GS | BC_ALH_GSS | Brilliant TS | BC_BTS_TSS |  |  | 1143
| 82L (2L289) | FortisBC | British Columbia | 1 | ac | 35 | 21.6049 | 35 | 21.6049 | 230 | 16.8 | 3 | [5 empty] | 402 | 435 | Brilliant TS | BC_BTS_TSS | Selkirk | BC_SEL_TSS |  |  | 1144
| 83L | FortisBC | British Columbia | 1 | ac | 3 | 1.8519 | 3 | 1.8519 | 230 | 1.44 | 3 | [5 empty] | 402 | 435 | Brilliant TS | BC_BTS_TSS | Brilliant Expansion GS | BC_BRX_GSS |  |  | 1145
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## Nodes
BC | EXISTING TRANSFORMERS
| Node Name | Node Code | Owner | Latitude | Longitude | Operating Region | Other References | Notes | Revisions | Count
| AA Lambert | BC_AAL_DSS | BC Hydro | 49.1402 | -116.5381 | British Columbia |  |  |  | 1
| Abbotsford | BC_ABB_DSS | BC Hydro | 49.0678 | -122.2978 | British Columbia |  |  |  | 2
| Aberfeldie GS | BC_ABN_GSS | BC Hydro | 49.4933 | -115.3624 | British Columbia |  |  | DELETED Aberfeldie JCT | 3
| Afton Mine | BC_AFN_ISS | BC Hydro | 50.6619 | -120.4997 | British Columbia |  |  |  | 4
| Afton Mine JCT | BC_AFN_JCT | BC Hydro | 50.6698 | -120.4992 | British Columbia |  |  |  | 5
| Ainsworth | BC_AWL_DSS | BC Hydro | 51.6539 | -121.3306 | British Columbia |  |  |  | 6
| Ainsworth JCT | BC_AWL_JCT | BC Hydro | 51.6598 | -121.304 | British Columbia |  |  |  | 7
| Aiyansh | BC_AYH_DSS | BC Hydro | 55.2809 | -128.9919 | British Columbia |  |  |  | 8
| Albreda | BC_ABA_DSS | BC Hydro | 52.6602 | -119.1928 | British Columbia |  |  |  | 9
| Albreda JCT | BC_ABA_JCT | BC Hydro | 52.664 | -119.1833 | British Columbia |  |  |  | 10
| Alouette GS | BC_ALU_GSS | BC Hydro | 49.371 | -122.3124 | British Columbia |  |  |  | 11
| Annacis Island | BC_ANN_DSS | BC Hydro | 49.1746 | -122.9363 | British Columbia |  |  |  | 12
| Annacis Island JCT | BC_ANN_JCT | BC Hydro | 49.1751 | -122.9352 | British Columbia |  |  |  | 13
| Annacis Island Wastewater Treatment Plant | BC_AWT_ISS | BC Hydro | 49.1666 | -122.9467 | British Columbia |  |  |  | 14
| Annacis Island Wastewater Treatment Plant JCT | BC_AWT_JCT | BC Hydro | 49.1745 | -122.9369 | British Columbia |  |  |  | 15
| Apollo Forest Products | BC_AFP_ISS | BC Hydro | 54.4909 | -124.2018 | British Columbia |  |  |  | 16
| Apollo Forest Products JCT | BC_AFP_JCT | BC Hydro | 54.4733 | -124.1903 | British Columbia |  |  |  | 17
| Arawana | BC_AWA_DSS | FortisBC | 49.5901 | -119.5801 | British Columbia |  |  |  | 18
| Armstrong | BC_ARM_DSS | BC Hydro | 50.4486 | -119.1836 | British Columbia |  |  |  | 19
| Armstrong JCT | BC_ARM_JCT | BC Hydro | 50.4484 | -119.1828 | British Columbia |  |  |  | 20
| Arnott | BC_ARN_DSS | BC Hydro | 49.0921 | -123.0417 | British Columbia |  |  |  | 21
| Arrow Lakes GS | BC_ALH_GSS | FortisBC | 49.343 | -117.7688 | British Columbia |  |  |  | 22
| AS Mawdsley TS | BC_ASM_TSS | FortisBC | 49.1011 | -117.7328 | British Columbia |  |  |  | 23
| Ash River GS | BC_ASH_GSS | BC Hydro | 49.3734 | -125.1506 | British Columbia |  |  |  | 24
| Ashcroft | BC_AFT_DSS | BC Hydro | 50.7365 | -121.2825 | British Columbia |  |  |  | 25
| Ashcroft JCT | BC_AFT_JCT | BC Hydro | 50.7368 | -121.2822 | British Columbia |  |  |  | 26
| Ashlu GS | BC_ASL_GSS | BC Hydro | 49.9143 | -123.325 | British Columbia |  |  |  | 27
| Ashlu JCT | BC_ASL_JCT | BC Hydro | 49.9156 | -123.2923 | British Columbia |  |  |  | 28
| Ashton Creek | BC_ACK_DSS | BC Hydro | 50.5614 | -118.9935 | British Columbia |  |  |  | 29
| Atchelitz | BC_ALZ_DSS | BC Hydro | 49.1136 | -122.0093 | British Columbia |  |  |  | 30
| Athalmer | BC_ATH_DSS | BC Hydro | 50.5151 | -116.0008 | British Columbia |  |  |  | 31
| Athalmer JCT | BC_ATH_JCT | BC Hydro | 50.5138 | -116.0008 | British Columbia |  |  |  | 32
| Avola | BC_AVO_DSS | BC Hydro | 51.7842 | -119.3269 | British Columbia |  |  |  | 33
| Avola JCT | BC_AVO_JCT | BC Hydro | 51.7842 | -119.3275 | British Columbia |  |  |  | 34
| Babine Lake | BC_BAB_DSS | BC Hydro | 54.8779 | -126.2044 | British Columbia |  |  |  | 35
| Balfour | BC_BAL_DSS | BC Hydro | 49.1042 | -122.5791 | British Columbia |  |  |  | 36
| Balfour JCT | BC_BAL_JCT | BC Hydro | 49.1305 | -122.5703 | British Columbia |  |  |  | 37
| Barlow | BC_BLW_DSS | BC Hydro | 53.0204 | -122.4296 | British Columbia |  |  |  | 38
| Barlow JCT | BC_BLW_JCT | BC Hydro | 53.0212 | -122.429 | British Columbia |  |  |  | 39
| Barnard | BC_BND_DSS | BC Hydro | 49.2621 | -122.9007 | British Columbia |  |  |  | 40
| Barriere | BC_BAR_DSS | BC Hydro | 51.1997 | -120.1337 | British Columbia |  |  |  | 41
| Barriere JCT | BC_BAR_JCT | BC Hydro | 51.2001 | -120.1306 | British Columbia |  |  |  | 42
| BC Chemical | BC_BCM_ISS | BC Hydro | 53.9253 | -122.6932 | British Columbia |  |  |  | 43
| BC Chemical JCT | BC_BCM_JCT | BC Hydro | 53.9259 | -122.6937 | British Columbia |  |  |  | 44
| BC Gas | BC_BCG_ISS | FortisBC | 49.3764 | -120.1441 | British Columbia |  |  |  | 45
| BC Rail | BC_BCR_ISS | BC Hydro | 55.1475 | -121.1326 | British Columbia |  |  |  | 46
| Bear Creek | BC_BRK_DSS | BC Hydro | 49.7519 | -123.5172 | British Columbia |  |  |  | 47
| Bear Mountain | BC_BMT_DSS | BC Hydro | 55.7637 | -120.4465 | British Columbia |  |  |  | 48
| Bear Mountain GS | BC_BMW_GSS | BC Hydro | 55.7041 | -120.4264 | British Columbia |  |  |  | 49
| Beaver Cove | BC_BVC_DSS | BC Hydro | 50.5196 | -126.882 | British Columbia |  |  |  | 50
| Beaver Cove JCT | BC_BVC_JCT | BC Hydro | 50.5195 | -126.8832 | British Columbia |  |  |  | 51
| Beaver Park | BC_BEP_DSS | FortisBC | 49.0708 | -117.609 | British Columbia |  |  |  | 52
| Beaverley | BC_BVY_DSS | BC Hydro | 53.8434 | -122.8348 | British Columbia |  |  |  | 53
| Bentley TS | BC_BEN_TSS | FortisBC | 49.1892 | -119.5301 | British Columbia |  |  |  | 54
| Benvoulin | BC_BEV_DSS | FortisBC | 49.8385 | -119.4533 | British Columbia |  |  |  | 55
| Big Bend | BC_BBS_DSS | BC Hydro | 49.1987 | -122.9928 | British Columbia |  |  |  | 56
| Big Silver GS | BC_BSV_GSS | BC Hydro | 49.693 | -121.8591 | British Columbia |  |  |  | 57
| Big White | BC_BWS_DSS | FortisBC | 49.7135 | -118.9636 | British Columbia |  |  |  | 58
| Bingham | BC_BMP_DSS | BC Hydro | 49.2476 | -122.9447 | British Columbia |  |  |  | 59
| Bingham JCT | BC_BMP_JCT | BC Hydro | 49.2597 | -122.9486 | British Columbia |  |  |  | 60
| Black Mountain | BC_BLK_DSS | FortisBC | 49.8697 | -119.332 | British Columbia |  |  |  | 61
| Blackpool | BC_BLP_DSS | BC Hydro | 51.5661 | -120.1614 | British Columbia |  |  |  | 62
| Blackpool JCT | BC_BLP_JCT | BC Hydro | 51.566 | -120.1678 | British Columbia |  |  |  | 63
| Blue River | BC_BLU_DSS | BC Hydro | 52.117 | -119.319 | British Columbia |  |  |  | 64
| Blue River JCT | BC_BLU_JCT | BC Hydro | 52.117 | -119.319 | British Columbia |  |  |  | 65
| Blue River Pumping Station | BC_BLE_DSS | BC Hydro | 52.1096 | -119.3062 | British Columbia |  |  |  | 66
| Blue River Pumping Station JCT | BC_BLE_JCT | BC Hydro | 52.117 | -119.319 | British Columbia |  |  |  | 67
| Blueberry | BC_BLB_DSS | FortisBC | 49.251 | -117.6574 | British Columbia |  |  |  | 68
| Blueberry JCT | BC_BLB_JCT | FortisBC | 49.3146 | -117.6331 | British Columbia |  |  |  | 69
| Bob Quinn | BC_BQN_DSS | BC Hydro | 56.9403 | -130.2656 | British Columbia |  |  |  | 70
| Bone Creek | BC_BET_DSS | BC Hydro | 52.2561 | -119.1812 | British Columbia |  |  |  | 71
| Bone Creek GS | BC_BNC_GSS | BC Hydro | 52.2553 | -119.1808 | British Columbia |  |  |  | 72
| Boston Bar | BC_BBR_DSS | BC Hydro | 49.8619 | -121.4415 | British Columbia |  |  |  | 73
| Boston Bar JCT | BC_BBR_JCT | BC Hydro | 49.4078 | -121.4484 | British Columbia |  | Location approximate |  | 74
| Boulder Creek GS | BC_BDH_GSS | BC Hydro | 50.6355 | -123.4059 | British Columbia |  |  |  | 75
| Boulder Creek JCT | BC_BDH_JCT | BC Hydro | 50.6354 | -123.4089 | British Columbia |  |  |  | 76
| Box Canyon GS | BC_BOX_GSS | BC Hydro | 49.6006 | -123.4267 | British Columbia |  |  |  | 77
| Box Canyon JCT | BC_BOX_JCT | BC Hydro | 49.5621 | -123.3999 | British Columbia |  |  |  | 78
| BP Noel 2 | BC_NL2_ISS | BC Hydro | 55.2782 | -120.2539 | British Columbia |  |  |  | 79
| BP Noel 3 | BC_NL3_ISS | BC Hydro | 55.3441 | -120.3566 | British Columbia |  |  |  | 80
| BP Noel 3 JCT | BC_NL3_JCT | BC Hydro | 55.3423 | -120.3586 | British Columbia |  |  |  | 81
| BP Noel 5 | BC_NL5_ISS | BC Hydro | 55.4145 | -120.4324 | British Columbia |  |  |  | 82
| BP Noel 5 JCT | BC_NL5_JCT | BC Hydro | 55.412 | -120.4288 | British Columbia |  |  |  | 83
| Bradford | BC_BRA_ISS | FortisBC | 49.0266 | -118.4274 | British Columbia |  |  |  | 84
| Bremner GS | BC_BRE_GSS | BC Hydro | 49.7042 | -122.0799 | British Columbia |  |  |  | 85
| Brenda Mines | BC_BDM_ISS | BC Hydro | 49.8704 | -119.9946 | British Columbia |  |  |  | 86
| Brenda Mines JCT | BC_BDM_JCT | BC Hydro | 49.8691 | -120.0043 | British Columbia |  |  |  | 87
| Bridge River 1 GS | BC_BR1_DFS | BC Hydro | 50.7299 | -122.24 | British Columbia |  |  |  | 88
| Bridge River 2 GS | BC_BR2_GSS | BC Hydro | 50.7299 | -122.24 | British Columbia |  |  |  | 89
| Bridge River TS | BC_BRT_TSS | BC Hydro | 50.7256 | -122.2523 | British Columbia |  |  |  | 90
| Brilliant Expansion GS | BC_BRX_GSS | FortisBC | 49.3231 | -117.6198 | British Columbia |  |  |  | 91
| Brilliant GS | BC_BRD_GSS | FortisBC | 49.3249 | -117.6207 | British Columbia |  |  |  | 92
| Brilliant SWS | BC_BSS_SWS | FortisBC | 49.3228 | -117.6128 | British Columbia |  |  |  | 93
| Brilliant TS | BC_BTS_TSS | FortisBC | 49.322 | -117.6128 | British Columbia |  |  |  | 94
| Britannia | BC_BTA_DSS | BC Hydro | 49.6216 | -123.2031 | British Columbia |  |  |  | 95
| Britannia JCT | BC_BTA_JCT | BC Hydro | 49.6218 | -123.2 | British Columbia |  |  |  | 96
| Britt Creek | BC_BCK_ISS | BC Hydro | 50.2479 | -114.9429 | British Columbia |  |  |  | 97
| Britt Creek JCT | BC_BCK_JCT | BC Hydro | 50.2477 | -114.9417 | British Columbia |  |  |  | 98
| Brocklehurst | BC_BKL_DSS | BC Hydro | 50.7089 | -120.3853 | British Columbia |  |  |  | 99
| Brown Lake GS | BC_BRL_GSS | BC Hydro | 54.0401 | -129.8345 | British Columbia |  |  |  | 100
| Brown Lake JCT | BC_BRL_JCT | BC Hydro | 54.0398 | -129.8349 | British Columbia |  |  |  | 101
| Brucejack Mine | BC_BJK_ISS | BC Hydro | 56.4656 | -130.1862 | British Columbia |  |  |  | 102
| Brucejack TS | BC_BJT_TSS | BC Hydro | 56.0584 | -130.0279 | British Columbia |  |  |  | 103
| Buckeye | BC_BCI_ISS | BC Hydro | 49.1434 | -123.0044 | British Columbia |  |  |  | 104
| Buckley Bay | BC_BKB_DSS | BC Hydro | 49.5478 | -124.8787 | British Columbia |  |  |  | 105
| Buckley Bay JCT | BC_BKB_JCT | BC Hydro | 49.5476 | -124.8808 | British Columbia |  |  |  | 106
| Bull River Mineral | BC_BRM_ISS | BC Hydro | 49.5013 | -115.377 | British Columbia |  |  |  | 107
| Bull River Mineral JCT | BC_BRM_JCT | BC Hydro | 49.4965 | -115.3746 | British Columbia |  |  |  | 108
| Bullmoose | BC_BLM_DSS | BC Hydro | 55.1392 | -121.4684 | British Columbia |  |  |  | 109
| Burnett | BC_BNT_DSS | BC Hydro | 48.4606 | -123.4437 | British Columbia |  |  |  | 110
| Burns Lake | BC_BRN_DSS | BC Hydro | 54.2403 | -125.7592 | British Columbia |  |  |  | 111
| Burns Lake JCT | BC_BRN_JCT | BC Hydro | 54.2597 | -125.7474 | British Columbia |  |  |  | 112
| Burrard | BC_BSY_TSS | BC Hydro | 49.2991 | -122.8908 | British Columbia |  | Burrard operates only as a synchronous condenser |  | 113
| Cache Creek | BC_CCW_DSS | BC Hydro | 50.7869 | -121.3137 | British Columbia |  |  |  | 114
| Cache Creek JCT | BC_CCW_JCT | BC Hydro | 50.7866 | -121.3137 | British Columbia |  |  |  | 115
| Cambie | BC_CAM_DSS | BC Hydro | 49.1909 | -123.0631 | British Columbia |  |  |  | 116
| Cambie JCT | BC_CAM_JCT | BC Hydro | 49.1901 | -123.0632 | British Columbia |  |  |  | 117
| Camosun | BC_CSN_DSS | BC Hydro | 49.2494 | -123.1977 | British Columbia |  |  |  | 118
| Campbell River | BC_CBL_DSS | BC Hydro | 50.0203 | -125.2537 | British Columbia |  |  |  | 119
| Campbell River JCT | BC_CBL_JCT | BC Hydro | 50.0138 | -125.3145 | British Columbia |  |  |  | 120
| Canadian Auto Parts Toyota | BC_CAN_ISS | BC Hydro | 49.1341 | -123.0235 | British Columbia |  |  |  | 121
| Canadian Auto Parts Toyota JCT | BC_CAN_JCT | BC Hydro | 49.1341 | -123.0237 | British Columbia |  |  |  | 122
| Canadian National | BC_CNG_ISS | BC Hydro | 54.0724 | -122.3671 | British Columbia |  | Location approximate |  | 123
| Canadian National JCT | BC_CNG_JCT | BC Hydro | 54.0751 | -122.3744 | British Columbia |  | Location approximate |  | 124
| Canal Flats | BC_CNL_DSS | BC Hydro | 50.1502 | -115.823 | British Columbia |  |  |  | 125
| Canal Flats JCT | BC_CNL_JCT | BC Hydro | 50.1505 | -115.823 | British Columbia |  |  |  | 126
| Canexus Corporation | BC_NXC_ISS | BC Hydro | 49.301 | -123.015 | British Columbia |  |  |  | 127
| Canexus Corporation JCT | BC_NXC_JCT | BC Hydro | 49.3077 | -123.0109 | British Columbia |  |  |  | 128
| Canfor | BC_PLT_ISS | BC Hydro | 54.0245 | -124.3345 | British Columbia |  |  |  | 129
| Canfor JCT | BC_PLT_JCT | BC Hydro | 54.0271 | -124.3353 | British Columbia |  |  |  | 130
| Canfor Rustad Division | BC_NOS_ISS | BC Hydro | 53.8496 | -122.7411 | British Columbia |  |  |  | 131
| Canfor Rustad Division JCT | BC_NOS_JCT | BC Hydro | 53.8495 | -122.742 | British Columbia |  |  |  | 132
| Canoe Creek GS | BC_CNK_GSS | BC Hydro | 49.1769 | -125.3956 | British Columbia |  |  |  | 133
| Canoe Creek JCT | BC_CNK_JCT | BC Hydro | 49.1772 | -125.3962 | British Columbia |  |  |  | 134
| Canoe Forest Products Ltd | BC_FCO_ISS | BC Hydro | 50.7593 | -119.2092 | British Columbia |  |  |  | 135
| Canoe Forest Products Ltd JCT | BC_FCO_JCT | BC Hydro | 50.7597 | -119.2074 | British Columbia |  |  |  | 136
| Canreed | BC_CRD_DSS | BC Hydro | 53.927 | -122.6935 | British Columbia |  |  |  | 137
| Cape Scott GS | BC_CSS_GSS | BC Hydro | 50.789 | -128.0033 | British Columbia |  |  |  | 138
| Capilano | BC_CAP_DSS | BC Hydro | 49.3348 | -123.1082 | British Columbia |  |  |  | 139
| Capilano Pumps | BC_CPS_DSS | BC Hydro | 49.3608 | -123.1134 | British Columbia |  |  |  | 140
| Capilano Pumps JCT | BC_CPS_JCT | BC Hydro | 49.3605 | -123.1174 | British Columbia |  |  |  | 141
| Cariboo Pulp GS | BC_CBP_GSS | BC Hydro | 52.997 | -122.4853 | British Columbia |  |  |  | 142
| Cariboo Pulp JCT | BC_CBP_JCT | BC Hydro | 52.9998 | -122.4608 | British Columbia |  |  |  | 143
| Carquille | BC_CRQ_DSS | BC Hydro | 50.8867 | -121.3988 | British Columbia |  |  |  | 144
| Cascade | BC_CSC_DSS | FortisBC | 49.0777 | -117.8251 | British Columbia |  |  |  | 145
| Cascade JCT | BC_CSC_JCT | FortisBC | 49.0774 | -117.8252 | British Columbia |  |  |  | 146
| Castlegar | BC_CAS_DSS | FortisBC | 49.3101 | -117.6594 | British Columbia |  |  |  | 147
| Catalyst Paper Crofton GS | BC_CFT_GSS | BC Hydro | 48.8757 | -123.65 | British Columbia |  |  |  | 148
| Cathedral Square | BC_CSQ_DSS | BC Hydro | 49.2826 | -123.1155 | British Columbia |  |  |  | 149
| Chappell Pumping Station | BC_CPL_DSS | BC Hydro | 52.3884 | -119.1769 | British Columbia |  |  |  | 150
| Chappell Pumping Station JCT | BC_CPL_JCT | BC Hydro | 52.3911 | -119.1538 | British Columbia |  |  |  | 151
| Chase | BC_CHS_DSS | BC Hydro | 50.8224 | -119.7051 | British Columbia |  |  |  | 152
| Chase JCT | BC_CHS_JCT | BC Hydro | 50.818 | -119.6922 | British Columbia |  |  |  | 153
| Cheakamus GS | BC_CMS_DFS | BC Hydro | 49.9337 | -123.291 | British Columbia |  |  |  | 154
| Cheekye | BC_CKY_DSS | BC Hydro | 49.7902 | -123.161 | British Columbia |  |  |  | 155
| Chetwynd | BC_CWD_DSS | BC Hydro | 55.7023 | -121.6306 | British Columbia |  |  |  | 156
| Chetwynd GS | BC_LAP_GSS | BC Hydro | 55.7235 | -121.565 | British Columbia |  |  |  | 157
| Chevron | BC_CVN_ISS | BC Hydro | 49.2912 | -122.9921 | British Columbia |  |  |  | 158
| Chief Lake | BC_CHF_DSS | BC Hydro | 54.009 | -122.8143 | British Columbia |  |  |  | 159
| Chilliwack | BC_CHK_DSS | BC Hydro | 49.1676 | -121.9532 | British Columbia |  |  |  | 160
| Christina Lake | BC_CHR_DSS | FortisBC | 49.0351 | -118.2125 | British Columbia |  |  |  | 161
| Christina Lake JCT | BC_CHR_JCT | FortisBC | 49.0101 | -118.2015 | British Columbia |  |  |  | 162
| Clayburn | BC_CBN_DSS | BC Hydro | 49.069 | -122.2971 | British Columbia |  |  |  | 163
| Clearwater | BC_CLW_DSS | BC Hydro | 51.6545 | -120.0344 | British Columbia |  |  |  | 164
| Clearwater JCT | BC_CLW_JCT | BC Hydro | 51.6657 | -120.0326 | British Columbia |  |  |  | 165
| Clinton | BC_CLN_DSS | BC Hydro | 51.0811 | -121.5895 | British Columbia |  |  |  | 166
| Clinton JCT | BC_CLN_JCT | BC Hydro | 51.0808 | -121.5756 | British Columbia |  |  |  | 167
| Clowhom GS | BC_COM_GSS | BC Hydro | 49.7112 | -123.5326 | British Columbia |  |  |  | 168
| Coal Mountain | BC_CMO_DSS | BC Hydro | 49.5131 | -114.656 | British Columbia |  |  |  | 169
| Coal Mountain JCT | BC_CMO_JCT | BC Hydro | 49.6765 | -114.7746 | British Columbia |  | Location approximate |  | 170
| Coffee Creek | BC_COF_DSS | FortisBC | 49.6993 | -116.9113 | British Columbia |  |  |  | 171
| Colebank | BC_CLB_DSS | BC Hydro | 53.2832 | -122.4926 | British Columbia |  |  |  | 172
| Colebank JCT | BC_CLB_JCT | BC Hydro | 53.2827 | -122.4932 | British Columbia |  |  |  | 173
| Colwood | BC_CLD_DSS | BC Hydro | 48.442 | -123.5099 | British Columbia |  |  |  | 174
| Como Lake | BC_COK_DSS | BC Hydro | 49.2623 | -122.797 | British Columbia |  |  |  | 175
| Comox | BC_CMX_DSS | BC Hydro | 49.7137 | -124.9683 | British Columbia |  |  |  | 176
| Comox JCT | BC_CMX_JCT | BC Hydro | 49.6835 | -125.045 | British Columbia |  |  |  | 177
| Confor Houston Sawmill | BC_NHS_ISS | BC Hydro | 54.3839 | -126.7111 | British Columbia |  |  |  | 178
| Continental Lime Limited | BC_CLL_ISS | BC Hydro | 50.8146 | -121.6506 | British Columbia |  |  |  | 179
| Continental Lime Limited JCT | BC_CLL_JCT | BC Hydro | 50.8133 | -121.651 | British Columbia |  |  |  | 180
| Conuma Coal | BC_MNK_ISS | BC Hydro | 55.393 | -121.8166 | British Columbia |  |  |  | 181
| Conuma Coal JCT | BC_MNK_JCT | BC Hydro | 55.4966 | -121.6143 | British Columbia |  |  |  | 182
| Conuma Hatchery | BC_CMH_ISS | BC Hydro | 49.8009 | -126.4192 | British Columbia |  |  |  | 183
| Conuma Hatchery JCT | BC_CMH_JCT | BC Hydro | 49.8012 | -126.4192 | British Columbia |  |  |  | 184
| Copper Mountain | BC_CUM_DSS | BC Hydro | 49.3459 | -120.5089 | British Columbia |  |  |  | 185
| Copper Mountain JCT | BC_CUM_JCT | BC Hydro | 49.3539 | -120.5479 | British Columbia |  |  |  | 186
| Coquitlam | BC_CQM_DSS | BC Hydro | 49.2613 | -122.7757 | British Columbia |  |  |  | 187
| Coquitlam JCT | BC_CQM_JCT | BC Hydro | 49.2609 | -122.7755 | British Columbia |  |  |  | 188
| Corra Linn GS | BC_COR_GSS | FortisBC | 49.4689 | -117.4686 | British Columbia |  |  |  | 189
| Cottonwood | BC_COT_DSS | FortisBC | 49.4279 | -117.2475 | British Columbia |  |  |  | 190
| Cranbrook | BC_CBK_DSS | BC Hydro | 49.5005 | -115.5805 | British Columbia |  |  |  | 191
| Crawford Bay | BC_CRA_DSS | FortisBC | 49.6846 | -116.843 | British Columbia |  |  |  | 192
| Crestbrook | BC_CFE_DSS | BC Hydro | 49.2724 | -115.101 | British Columbia |  |  |  | 193
| Crestbrook Canal Flats | BC_CRC_DSS | BC Hydro | 50.1547 | -115.804 | British Columbia |  |  |  | 194
| Crestbrook Canal Flats JCT | BC_CRC_JCT | BC Hydro | 50.1545 | -115.8054 | British Columbia |  |  |  | 195
| Crestbrook Skookumchuck | BC_CRS_DFS | BC Hydro | 49.5278 | -115.7581 | British Columbia |  |  |  | 196
| Creston | BC_CRE_DSS | FortisBC | 49.0906 | -116.5071 | British Columbia |  |  |  | 197
| Crowsnest Pass GS | BC_CRW_GSS | BC Hydro | 49.6488 | -114.7158 | British Columbia |  |  |  | 198
| Crowsnest TransCanada | BC_CNT_ISS | BC Hydro | 49.6481 | -114.7181 | British Columbia |  |  |  | 199
| Crowsnest TransCanada JCT | BC_CNT_JCT | BC Hydro | 49.649 | -114.7158 | British Columbia |  |  |  | 200
| Culliton Creek GS | BC_CTN_GSS | BC Hydro | 49.8772 | -123.1599 | British Columbia |  |  |  | 201
| Cypress | BC_CYP_DSS | BC Hydro | 49.3569 | -123.2321 | British Columbia |  |  |  | 202
| Dal Grauer | BC_DGR_DSS | BC Hydro | 49.2815 | -123.1252 | British Columbia |  |  |  | 203
| Darfield | BC_DFD_DSS | BC Hydro | 51.3128 | -120.1771 | British Columbia |  |  |  | 204
| Darfield JCT | BC_DFD_JCT | BC Hydro | 51.3152 | -120.19 | British Columbia |  |  |  | 205
| Dasque Creek GS | BC_DSQ_GSS | BC Hydro | 54.3835 | -128.9149 | British Columbia |  |  |  | 206
| Dawson Creek | BC_DAW_DSS | BC Hydro | 55.7789 | -120.2647 | British Columbia |  |  |  | 207
| Deep Cove | BC_DCV_DSS | BC Hydro | 49.3133 | -122.9872 | British Columbia |  |  | DELETED Deep Cove JCT BC_DCV_JCT | 208
| Delta Port Terminal | BC_DPT_DSS | BC Hydro | 49.0214 | -123.1566 | British Columbia |  |  |  | 209
| Delta Port Terminal JCT | BC_DPT_JCT | BC Hydro | 49.0305 | -123.1507 | British Columbia |  |  |  | 210
| DG Bell | BC_DGB_DSS | FortisBC | 49.8121 | -119.4468 | British Columbia |  |  |  | 211
| Diana Lake | BC_DIL_DSS | BC Hydro | 54.2295 | -130.0782 | British Columbia |  |  |  | 212
| Diana Lake JCT | BC_DIL_JCT | BC Hydro | 54.2291 | -130.0784 | British Columbia |  |  |  | 213
| Dokie | BC_DKT_DSS | BC Hydro | 55.823 | -122.1492 | British Columbia |  |  |  | 214
| Dokie GS | BC_DKW_GSS | BC Hydro | 55.8118 | -122.2474 | British Columbia |  |  |  | 215
| Domtar Kamloops | BC_WEY_ISS | BC Hydro | 50.691 | -120.3915 | British Columbia |  |  |  | 216
| Doran Taylor GS | BC_DTR_GSS | BC Hydro | 49.2962 | -125.2757 | British Columbia |  |  |  | 217
| Doran Taylor JCT | BC_DTR_JCT | BC Hydro | 49.2959 | -125.2758 | British Columbia |  |  |  | 218
| Douglas GS | BC_DGL_GSS | BC Hydro | 49.7676 | -122.151 | British Columbia |  |  |  | 219
| Douglas Street | BC_DUG_DSS | BC Hydro | 50.6673 | -120.3124 | British Columbia |  |  |  | 220
| Duck Lake | BC_DUC_DSS | FortisBC | 50.0099 | -119.3856 | British Columbia |  |  |  | 221
| Dunkley Lumber | BC_DKY_ISS | BC Hydro | 53.2763 | -122.4725 | British Columbia |  |  |  | 222
| Dunkley Lumber JCT | BC_DKY_JCT | BC Hydro | 53.2747 | -122.4768 | British Columbia |  |  |  | 223
| Dunsmuir | BC_DMR_DSS | BC Hydro | 49.3928 | -124.6716 | British Columbia |  |  |  | 224
| East Toba River GS | BC_ETR_GSS | BC Hydro | 50.6751 | -123.9603 | British Columbia |  |  |  | 225
| Elk Falls Mill | BC_EFM_ISS | BC Hydro | 50.0708 | -125.2801 | British Columbia |  |  |  | 226
| Elkford | BC_EFD_DSS | BC Hydro | 50.0286 | -114.9256 | British Columbia |  |  |  | 227
| Elkford JCT | BC_EFD_JCT | BC Hydro | 50.0377 | -114.93 | British Columbia |  |  |  | 228
| Elko GS | BC_ELK_GSS | BC Hydro | 49.2901 | -115.1046 | British Columbia |  |  |  | 229
| Elkview Coal | BC_EV1_ISS | BC Hydro | 49.7317 | -114.8532 | British Columbia |  |  |  | 230
| Ellison | BC_ELL_DSS | FortisBC | 49.9627 | -119.3872 | British Columbia |  |  |  | 231
| Ellsworth | BC_EWL_DSS | BC Hydro | 56.0147 | -129.1152 | British Columbia |  |  |  | 232
| Ellsworth JCT | BC_EWL_JCT | BC Hydro | 56.0145 | -129.1164 | British Columbia |  |  |  | 233
| Emerald SWS | BC_ESS_SWS | FortisBC | 49.1022 | -117.7322 | British Columbia |  |  |  | 234
| Encana 15-27 | BC_E15_ISS | BC Hydro | 55.8808 | -120.5692 | British Columbia |  |  |  | 235
| Encana 15-27 JCT | BC_E15_JCT | BC Hydro | 55.8761 | -120.571 | British Columbia |  |  |  | 236
| Encana 4-26 | BC_E42_ISS | BC Hydro | 55.7869 | -120.5286 | British Columbia |  |  |  | 237
| Encana 4-26 JCT | BC_E42_JCT | BC Hydro | 55.7885 | -120.5296 | British Columbia |  |  |  | 238
| Encana 9-27 | BC_KIS_ISS | BC Hydro | 55.8777 | -120.5605 | British Columbia |  |  |  | 239
| Encana Tower | BC_ET3_ISS | BC Hydro | 56.0029 | -120.6502 | British Columbia |  |  |  | 240
| Encana Tower JCT | BC_ET3_JCT | BC Hydro | 56.0288 | -120.5661 | British Columbia |  |  |  | 241
| Endako | BC_EKO_DSS | BC Hydro | 54.0724 | -125.0109 | British Columbia |  |  |  | 242
| Enderby | BC_END_DSS | BC Hydro | 50.5601 | -119.1447 | British Columbia |  |  |  | 243
| Enderby JCT | BC_END_JCT | BC Hydro | 50.5603 | -119.15 | British Columbia |  |  |  | 244
| Equity Silver | BC_EQU_ISS | BC Hydro | 54.3817 | -126.6234 | British Columbia |  |  |  | 245
| Erco Worldwide | BC_ERW_ISS | BC Hydro | 49.301 | -123.0106 | British Columbia |  |  |  | 246
| Erco Worldwide JCT | BC_ERW_JCT | BC Hydro | 49.3012 | -123.0123 | British Columbia |  |  |  | 247
| Esco Foundry | BC_ESC_ISS | BC Hydro | 49.256 | -122.7686 | British Columbia |  |  |  | 248
| Esco Foundry JCT | BC_ESC_JCT | BC Hydro | 49.2557 | -122.7689 | British Columbia |  |  |  | 249
| Esquimalt | BC_ESQ_DSS | BC Hydro | 48.4606 | -123.4437 | British Columbia |  |  |  | 250
| Eurocan | BC_EUR_ISS | BC Hydro | 54.0413 | -128.6998 | British Columbia |  |  |  | 251
| FA Lee TS | BC_LEE_TSS | FortisBC | 49.9068 | -119.3472 | British Columbia |  |  |  | 252
| Fairmont | BC_FMT_DSS | BC Hydro | 50.3193 | -115.8707 | British Columbia |  |  |  | 253
| Fairmont JCT | BC_FMT_JCT | BC Hydro | 50.319 | -115.8702 | British Columbia |  |  |  | 254
| Falls River GS | BC_FLS_GSS | BC Hydro | 53.9835 | -129.7342 | British Columbia |  |  |  | 255
| Fareview Container Terminal | BC_PRT_ISS | BC Hydro | 54.2864 | -130.3553 | British Columbia |  |  |  | 256
| Fareview Container Terminal JCT | BC_PRT_JCT | BC Hydro | 54.307 | -130.3053 | British Columbia |  |  |  | 257
| Fernie | BC_FNE_DSS | BC Hydro | 49.5025 | -115.0592 | British Columbia |  |  |  | 258
| Fiberco | BC_FBC_DSS | BC Hydro | 56.1439 | -120.6545 | British Columbia |  |  |  | 259
| Fiberco JCT | BC_FBC_JCT | BC Hydro | 56.1498 | -120.6663 | British Columbia |  |  |  | 260
| Finlay Forest Industries | BC_FFI_ISS | BC Hydro | 55.3214 | -123.1662 | British Columbia |  |  |  | 261
| Finn Pumping Station | BC_FPS_DSS | BC Hydro | 51.9136 | -119.3208 | British Columbia |  |  |  | 262
| Finn Pumping Station JCT | BC_FPS_JCT | BC Hydro | 51.934 | -119.3264 | British Columbia |  |  |  | 263
| Fire GS | BC_FRE_GSS | BC Hydro | 49.7834 | -122.2347 | British Columbia |  |  |  | 264
| Fleetwood | BC_FLW_DSS | BC Hydro | 49.1374 | -122.7877 | British Columbia |  |  |  | 265
| Fletcher Challenge | BC_FCC_ISS | BC Hydro | 55.2916 | -123.1572 | British Columbia |  |  |  | 266
| FMC Prince George | BC_FMC_ISS | BC Hydro | 53.9269 | -122.7086 | British Columbia |  |  |  | 267
| FMC Prince George JCT | BC_FMC_JCT | BC Hydro | 53.9277 | -122.7085 | British Columbia |  |  |  | 268
| Foothills | BC_FHS_DSS | BC Hydro | 53.907 | -122.8125 | British Columbia |  |  |  | 269
| Foothills JCT | BC_FHS_JCT | BC Hydro | 53.9073 | -122.7817 | British Columbia |  |  |  | 270
| Fording Coal | BC_FRO_ISS | BC Hydro | 50.2479 | -114.943 | British Columbia |  |  |  | 271
| Fording Coal JCT | BC_FRO_JCT | BC Hydro | 50.2479 | -114.9428 | British Columbia |  |  |  | 272
| Forest Kerr GS | BC_FKR_GSS | BC Hydro | 56.7172 | -130.6866 | British Columbia |  |  |  | 273
| Forest View | BC_FVW_DSS | BC Hydro | 49.8614 | -124.5303 | British Columbia |  |  |  | 274
| Forest View JCT | BC_FVW_JCT | BC Hydro | 49.8608 | -124.5297 | British Columbia |  |  |  | 275
| Fort Nelson GS | BC_FNG_GSS | BC Hydro | 58.6517 | -122.6931 | Alberta |  |  |  | 276
| Fort St James | BC_FM2_DSS | BC Hydro | 54.45 | -124.2503 | British Columbia |  |  |  | 277
| Fort St James Green Energy GS | BC_FGE_GSS | BC Hydro | 54.4893 | -124.2153 | British Columbia |  |  |  | 278
| Fort St. John | BC_FJN_DSS | BC Hydro | 56.2266 | -120.82 | British Columbia |  |  |  | 279
| Fort Steele | BC_FST_DSS | BC Hydro | 49.5925 | -115.6832 | British Columbia |  |  |  | 280
| Fort Steele JCT | BC_FST_JCT | BC Hydro | 49.5929 | -115.6837 | British Columbia |  |  |  | 281
| Fox Creek | BC_FOX_DSS | BC Hydro | 56.6784 | -120.974 | British Columbia |  |  |  | 282
| Fox Creek JCT | BC_FOX_JCT | BC Hydro | 56.3014 | -121.1898 | British Columbia |  |  |  | 283
| Fraser Lake | BC_FSR_DSS | BC Hydro | 54.0544 | -124.8501 | British Columbia |  |  |  | 284
| Fraser Lake JCT | BC_FSR_JCT | BC Hydro | 54.0468 | -124.8494 | British Columbia |  |  |  | 285
| Fraser Lake Sawmill | BC_FSS_ISS | BC Hydro | 54.065 | -124.7487 | British Columbia |  |  |  | 286
| Fraser Lake Sawmill JCT | BC_FSS_JCT | BC Hydro | 54.0477 | -124.7442 | British Columbia |  | Location approximate |  | 287
| Fruitvale | BC_FRU_DSS | FortisBC | 49.1131 | -117.5409 | British Columbia |  |  |  | 288
| Function Junction | BC_FCN_DSS | BC Hydro | 50.0904 | -123.0345 | British Columbia |  |  |  | 289
| Furry Creek | BC_FRC_DSS | BC Hydro | 49.5876 | -123.2211 | British Columbia |  |  |  | 290
| Furry Creek GS | BC_FRI_GSS | BC Hydro | 49.5793 | -123.202 | British Columbia |  |  |  | 291
| Furry Creek GS JCT | BC_FRI_JCT | BC Hydro | 49.586 | -123.2174 | British Columbia |  |  |  | 292
| Furry Creek JCT | BC_FRC_JCT | BC Hydro | 49.5875 | -123.2189 | British Columbia |  |  |  | 293
| Galiano | BC_GLS_DSS | BC Hydro | 48.9045 | -123.3617 | British Columbia |  |  |  | 294
| Galiano JCT | BC_GLS_JCT | BC Hydro | 48.9052 | -123.3622 | British Columbia |  |  |  | 295
| Gavin Lake | BC_GVL_DSS | BC Hydro | 52.4858 | -121.8059 | British Columbia |  |  |  | 296
| Gavin Lake JCT | BC_GVL_JCT | BC Hydro | 52.4857 | -121.8053 | British Columbia |  |  |  | 297
| George Dickie | BC_GDK_DSS | BC Hydro | 49.2306 | -123.1547 | British Columbia |  |  |  | 298
| George Tripp | BC_GTP_DSS | BC Hydro | 48.4738 | -123.36 | British Columbia |  |  |  | 299
| Gibraltar Capacitor | BC_GBC_DSS | BC Hydro | 52.5317 | -122.2859 | British Columbia |  |  |  | 300
| Gibraltar Capacitor JCT | BC_GBC_JCT | BC Hydro | 52.5313 | -122.2853 | British Columbia |  |  |  | 301
| Gibraltar Mine | BC_GBR_ISS | BC Hydro | 52.5302 | -122.2824 | British Columbia |  |  |  | 302
| Gibraltar Wells | BC_GBW_ISS | BC Hydro | 52.5058 | -122.4252 | British Columbia |  |  |  | 303
| Gibraltar Wells JCT | BC_GBW_JCT | BC Hydro | 52.5058 | -122.4244 | British Columbia |  |  |  | 304
| Gibsons | BC_GIB_DSS | BC Hydro | 49.4092 | -123.5141 | British Columbia |  |  |  | 305
| Glenannan | BC_GLN_DSS | BC Hydro | 54.0744 | -125.0157 | British Columbia |  |  |  | 306
| Glenmerry | BC_GLM_DSS | FortisBC | 49.0931 | -117.6751 | British Columbia |  |  |  | 307
| Glenmore BCH | BC_GLR_DSS | BC Hydro | 49.3601 | -123.133 | British Columbia |  |  |  | 308
| Glenmore FBC | BC_GLE_DSS | FortisBC | 49.8858 | -119.454 | British Columbia |  |  |  | 309
| Gloucester | BC_GLT_DSS | BC Hydro | 49.1094 | -122.4687 | British Columbia |  |  |  | 310
| Gloucester JCT | BC_GLT_JCT | BC Hydro | 49.1272 | -122.5178 | British Columbia |  |  |  | 311
| GM Shrum GS | BC_GMS_GSS | BC Hydro | 56.0139 | -122.1972 | British Columbia |  |  |  | 312
| Gold River | BC_GLD_DSS | BC Hydro | 49.7892 | -126.0643 | British Columbia |  |  |  | 313
| Gold River Pulp | BC_GRP_ISS | BC Hydro | 49.684 | -126.1258 | British Columbia |  |  |  | 314
| Golden | BC_GDN_DSS | BC Hydro | 51.2928 | -116.961 | British Columbia |  |  |  | 315
| Goldstream JCT | BC_GST_JCT | BC Hydro | 51.6936 | -118.641 | British Columbia |  |  | DELETED Goldstream BC_GST_DSS | 316
| Goldstream Mine | BC_GSM_ISS | BC Hydro | 51.632 | -118.4297 | British Columbia |  |  |  | 317
| Goward | BC_GOW_DSS | BC Hydro | 48.4901 | -123.4211 | British Columbia |  |  |  | 318
| Grand Forks TS | BC_GFT_TSS | FortisBC | 49.0475 | -118.4736 | British Columbia |  |  |  | 319
| Great Central | BC_GCL_DSS | BC Hydro | 49.3176 | -124.962 | British Columbia |  |  |  | 320
| Green River | BC_GRR_DSS | BC Hydro | 54.2063 | -129.9756 | British Columbia |  |  |  | 321
| Green River JCT | BC_GRR_JCT | BC Hydro | 54.2071 | -129.9762 | British Columbia |  |  |  | 322
| Greenhills | BC_GRH_ISS | BC Hydro | 50.0592 | -114.8561 | British Columbia |  |  |  | 323
| Greenhills JCT | BC_GRH_JCT | BC Hydro | 50.0445 | -114.9211 | British Columbia |  |  |  | 324
| Grief Point | BC_GPT_DSS | BC Hydro | 49.8054 | -124.5145 | British Columbia |  |  |  | 325
| Grief Point JCT | BC_GPT_JCT | BC Hydro | 49.821 | -124.4668 | British Columbia |  |  |  | 326
| GVRD Sapperton Pumps | BC_GSP_DSS | BC Hydro | 49.2222 | -122.8916 | British Columbia |  |  |  | 327
| GVRD Sapperton Pumps JCT | BC_GSP_JCT | BC Hydro | 49.2223 | -122.892 | British Columbia |  |  |  | 328
| Haa-Ak-Suuk GS | BC_HAS_GSS | BC Hydro | 49.2479 | -125.3837 | British Columbia |  |  |  | 329
| Haa-Ak-Suuk JCT | BC_HAS_JCT | BC Hydro | 49.25 | -125.3738 | British Columbia |  |  |  | 330
| Haney | BC_HNY_DSS | BC Hydro | 49.221 | -122.5522 | British Columbia |  |  |  | 331
| Harewood | BC_HWD_DSS | BC Hydro | 49.1345 | -123.9307 | British Columbia |  |  |  | 332
| Harewood JCT | BC_HWD_JCT | BC Hydro | 49.1327 | -123.9309 | British Columbia |  |  |  | 333
| Harewood West | BC_HWW_DSS | BC Hydro | 49.1225 | -123.9508 | British Columbia |  |  |  | 334
| Harewood West JCT | BC_HWW_JCT | BC Hydro | 49.0838 | -124.0763 | British Columbia |  |  |  | 335
| Harmac Pacific | BC_HMC_ISS | BC Hydro | 49.1355 | -123.8608 | British Columbia |  |  |  | 336
| Harvest Energy | BC_FNC_ISS | BC Hydro | 58.6453 | -120.0678 | Alberta |  |  |  | 337
| Harvest Energy JCT | BC_FNC_JCT | BC Hydro | 58.6382 | -120.087 | Alberta |  |  |  | 338
| Harvie Road | BC_HRD_DSS | BC Hydro | 49.1747 | -122.6969 | British Columbia |  |  |  | 339
| Harvie Road JCT | BC_HRD_JCT | BC Hydro | 49.1751 | -122.6975 | British Columbia |  |  |  | 340
| Hazelton | BC_HZN_DSS | BC Hydro | 55.242 | -127.6163 | British Columbia |  |  |  | 341
| Hearns | BC_HER_DSS | FortisBC | 49.1735 | -117.4903 | British Columbia |  |  |  | 342
| Hedley | BC_HED_DSS | FortisBC | 49.3501 | -120.0772 | British Columbia |  |  |  | 343
| Heffley | BC_HFY_DSS | BC Hydro | 50.8487 | -120.2678 | British Columbia |  |  |  | 344
| Heffley JCT | BC_HFY_JCT | BC Hydro | 50.8481 | -120.269 | British Columbia |  |  |  | 345
| Highland | BC_HLD_DSS | BC Hydro | 50.4074 | -120.8076 | British Columbia |  |  |  | 346
| Highland Valley Copper | BC_HVC_DSS | BC Hydro | 50.4707 | -121.0207 | British Columbia |  |  |  | 347
| Highland Valley Copper JCT | BC_HVC_JCT | BC Hydro | 50.4818 | -121.0168 | British Columbia |  |  |  | 348
| Hillcrest | BC_HCT_DSS | BC Hydro | 49.3466 | -123.2143 | British Columbia |  |  |  | 349
| Hillcrest JCT | BC_HCT_JCT | BC Hydro | 49.3598 | -123.214 | British Columbia |  |  |  | 350
| Hollywood | BC_HOL_DSS | FortisBC | 49.8728 | -119.3989 | British Columbia |  |  |  | 351
| Hollywood JCT | BC_HOL_JCT | FortisBC | 49.8763 | -119.4883 | British Columbia |  |  |  | 352
| Hope | BC_HOP_DSS | BC Hydro | 49.3796 | -121.4289 | British Columbia |  |  |  | 353
| Hope Pumping Station | BC_HPS_DSS | BC Hydro | 49.3736 | -121.4239 | British Columbia |  |  |  | 354
| Hope Pumping Station JCT | BC_HPS_JCT | BC Hydro | 49.3744 | -121.425 | British Columbia |  |  |  | 355
| Horne Payne | BC_HPN_DSS | BC Hydro | 49.2668 | -123.0179 | British Columbia |  |  |  | 356
| Horsey | BC_HSY_DSS | BC Hydro | 48.4426 | -123.3665 | British Columbia |  |  |  | 357
| Horsheshoe Bay | BC_HSB_DSS | BC Hydro | 49.3644 | -123.2769 | British Columbia |  |  |  | 358
| Houston | BC_HUS_DSS | BC Hydro | 54.3929 | -126.6685 | British Columbia |  |  |  | 359
| Houston Forest Products | BC_HFP_ISS | BC Hydro | 54.3776 | -126.713 | British Columbia |  |  |  | 360
| Howe Sound Pulp | BC_HSP_ISS | BC Hydro | 49.5236 | -123.49 | British Columbia |  |  |  | 361
| Huckleberry | BC_HML_DSS | BC Hydro | 53.6773 | -127.1667 | British Columbia |  |  |  | 362
| Hundred Mile House | BC_HMH_DSS | BC Hydro | 51.6575 | -121.2848 | British Columbia |  |  |  | 363
| Huth Avenue | BC_HUT_DSS | FortisBC | 49.4814 | -119.5977 | British Columbia |  |  |  | 364
| Illecillewaet | BC_ILL_DSS | BC Hydro | 50.9857 | -118.2045 | British Columbia |  |  |  | 365
| Ingledow | BC_ING_DSS | BC Hydro | 49.1589 | -122.8739 | British Columbia |  |  |  | 366
| INT Ingledow BPA | XX_BCUS1_INT | BC-US Border | 49.0021 | -122.724 | British Columbia |  |  |  | 367
| INT Nelway BPA | XX_BCUS2_INT | BC-US Border | 49.0002 | -117.3423 | British Columbia |  |  |  | 368
| Invermere | BC_INV_DSS | BC Hydro | 50.4951 | -116.1178 | British Columbia |  |  |  | 369
| Ioco Esso Petroleum | BC_IOC_ISS | BC Hydro | 49.3073 | -122.8845 | British Columbia |  |  |  | 370
| IPT Cranbrook Chapel Rock | PP_BCAB2_IPT | BC-AB Border | 49.6448 | -114.6619 | British Columbia |  |  |  | 371
| IPT Natal Coleman | PP_BCAB1_IPT | BC-AB Border | 49.6454 | -114.6618 | British Columbia |  |  |  | 372
| IPT Natal Pocaterra | PP_BCAB3_IPT | BC-AB Border | 50.5868 | -115.0705 | British Columbia |  |  |  | 373
| IPT Nelson Rainbow | PP_BCAB4_IPT | BC-AB Border | 58.5444 | -120 | British Columbia |  |  |  | 374
| Island GS | BC_ICG_GSS | BC Hydro | 50.0691 | -125.2819 | British Columbia |  |  |  | 375
| Island GS JCT | BC_ICG_JCT | BC Hydro | 50.0696 | -125.2798 | British Columbia |  |  |  | 376
| Island Paper Mill | BC_IPM_ISS | BC Hydro | 49.1687 | -122.9339 | British Columbia |  |  |  | 377
| Isle Pierre | BC_IPR_DSS | BC Hydro | 53.8651 | -123.2719 | British Columbia |  |  |  | 378
| Isle Pierre JCT | BC_IPR_JCT | BC Hydro | 53.8657 | -123.2719 | British Columbia |  |  |  | 379
| James Richardson | BC_JRI_DSS | BC Hydro | 49.3055 | -123.0656 | British Columbia |  |  |  | 380
| James Richardson JCT | BC_JRI_JCT | BC Hydro | 49.306 | -123.0664 | British Columbia |  |  |  | 381
| Jamie Creek GS | BC_JME_GSS | BC Hydro | 50.8282 | -123.0568 | British Columbia |  |  |  | 382
| Jeune Landing | BC_JUL_DSS | BC Hydro | 50.4405 | -127.4953 | British Columbia |  |  |  | 383
| Jimmie Creek GS | BC_JMC_GSS | BC Hydro | 50.604 | -124.0249 | British Columbia |  |  |  | 384
| Jinglepot | BC_JPT_DSS | BC Hydro | 49.1718 | -124.0214 | British Columbia |  |  |  | 385
| Joe Riche | BC_JRH_DSS | FortisBC | 49.8698 | -119.3321 | British Columbia |  |  |  | 386
| John Hart GS | BC_JHT_GSS | BC Hydro | 50.043 | -125.3104 | British Columbia |  |  |  | 387
| John Lawson | BC_JLN_DSS | BC Hydro | 49.3276 | -123.1611 | British Columbia |  |  |  | 388
| Jordan River GS | BC_JOR_DFS | BC Hydro | 48.4297 | -124.0523 | British Columbia |  |  |  | 389
| Joseph Creek | BC_JOE_DSS | BC Hydro | 49.5366 | -115.7552 | British Columbia |  |  |  | 390
| Kaledon | BC_KAL2_DSS | FortisBC | 49.3936 | -119.6063 | British Columbia |  |  |  | 391
| Kalum | BC_KAL_DSS | BC Hydro | 54.5194 | -128.6169 | British Columbia |  |  |  | 392
| Kamwood | BC_KWD_DSS | BC Hydro | 50.6858 | -120.3999 | British Columbia |  |  |  | 393
| Kaslo | BC_KAS_DSS | FortisBC | 49.9059 | -116.9157 | British Columbia |  |  |  | 394
| Keating | BC_KTG_DSS | BC Hydro | 48.567 | -123.412 | British Columbia |  |  |  | 395
| Kelly Lake | BC_KLY_DSS | BC Hydro | 51.0248 | -121.7391 | British Columbia |  |  |  | 396
| Kemano GS | BC_KMO_GSS | BC Hydro | 53.5632 | -127.9426 | British Columbia |  |  |  | 397
| Kemess Mine | BC_KMI_DSS | BC Hydro | 56.9942 | -126.7583 | British Columbia |  |  |  | 398
| Kennedy | BC_KDS_DSS | BC Hydro | 55.0704 | -122.7884 | British Columbia |  |  | DELETED Kennedy Capacitor Station - BC_KDY_DSS | 399
| Kent | BC_KEN_DSS | BC Hydro | 49.2476 | -121.7835 | British Columbia |  |  |  | 400
| Kent JCT | BC_KEN_JCT | BC Hydro | 49.1763 | -121.774 | British Columbia |  |  |  | 401
| Keogh | BC_KGH_DSS | BC Hydro | 50.6042 | -127.2917 | British Columbia |  |  |  | 402
| Keremeos | BC_KER_DSS | FortisBC | 49.2041 | -119.8284 | British Columbia |  |  |  | 403
| Kettle Valley | BC_KET_DSS | FortisBC | 49.0483 | -118.9339 | British Columbia |  |  |  | 404
| Kicking Horse | BC_KHS_DSS | BC Hydro | 51.2818 | -116.9944 | British Columbia |  |  |  | 405
| Kidd #1 | BC_KI1_DSS | BC Hydro | 49.2053 | -123.116 | British Columbia |  |  |  | 406
| Kidd #2 | BC_KI2_DSS | BC Hydro | 49.1982 | -123.1154 | British Columbia |  |  |  | 407
| Kimberley | BC_KBY_DSS | BC Hydro | 49.6638 | -115.9612 | British Columbia |  |  |  | 408
| Kitimat | BC_KIT_DSS | BC Hydro | 55.4431 | -129.4281 | British Columbia |  |  |  | 409
| Kokish GS | BC_KKS_GSS | BC Hydro | 50.5199 | -126.8755 | British Columbia |  |  |  | 410
| Kokish TS | BC_KTS_TSS | BC Hydro | 50.52 | -126.8755 | British Columbia |  |  |  | 411
| Koksilah | BC_KSH_DSS | BC Hydro | 48.7612 | -123.7118 | British Columbia |  |  |  | 412
| Koksilah JCT | BC_KSH_JCT | BC Hydro | 48.7353 | -123.7195 | British Columbia |  |  |  | 413
| Kootenay Canal GS | BC_KCL_GSS | FortisBC | 49.4533 | -117.5179 | British Columbia |  |  |  | 414
| Kraft GS | BC_KRA_GSS | FortisBC | 49.3361 | -117.7275 | British Columbia |  |  |  | 415
| Kruger Products | BC_SCP_ISS | BC Hydro | 49.2019 | -122.936 | British Columbia |  |  |  | 416
| Kruger Products JCT | BC_SCP_JCT | BC Hydro | 49.2022 | -122.9359 | British Columbia |  |  |  | 417
| Kwalsa | BC_KWL_TSS | BC Hydro | 49.7595 | -122.2058 | British Columbia |  |  |  | 418
| Kwoen | BC_KGP_ISS | BC Hydro | 55.3827 | -121.7046 | British Columbia |  |  |  | 419
| Kwoen JCT | BC_KGP_JCT | BC Hydro | 55.5015 | -121.6194 | British Columbia |  |  |  | 420
| Kwoiek Creek GS | BC_KCH_GSS | BC Hydro | 50.1051 | -121.5671 | British Columbia |  |  |  | 421
| Ladore Falls GS | BC_LDR_GSS | BC Hydro | 50.017 | -125.3909 | British Columbia |  |  |  | 422
| Ladysmith | BC_LDY_DSS | BC Hydro | 48.9834 | -123.8152 | British Columbia |  |  |  | 423
| Ladysmith JCT | BC_LDY_JCT | BC Hydro | 48.9752 | -123.8156 | British Columbia |  |  |  | 424
| Lafarge #1 | BC_LF1_ISS | BC Hydro | 49.159 | -123.0067 | British Columbia |  |  |  | 425
| Lafarge #2 | BC_LF2_ISS | BC Hydro | 50.6606 | -120.0631 | British Columbia |  |  |  | 426
| Lafarge #2 JCT | BC_LF2_JCT | BC Hydro | 50.6627 | -120.0629 | British Columbia |  |  |  | 427
| Lajoie GS | BC_LAJ_DFS | BC Hydro | 50.8397 | -122.8559 | British Columbia |  |  |  | 428
| Lake Buntzen #2 | BC_LB2_GSS | BC Hydro | 49.3706 | -122.8735 | British Columbia |  |  |  | 429
| Lake Buntzen GS | BC_LB1_DFS | BC Hydro | 49.3706 | -122.8736 | British Columbia |  |  |  | 430
| Lake Cowichan | BC_LCW_DSS | BC Hydro | 48.8214 | -124.0585 | British Columbia |  |  |  | 431
| Lamont GS | BC_LMN_GSS | BC Hydro | 49.569 | -122.3446 | British Columbia |  |  |  | 432
| Lantic Real Property | BC_LRP_ISS | BC Hydro | 49.1434 | -123.0119 | British Columbia |  |  |  | 433
| Lantic Real Property JCT | BC_LRP_JCT | BC Hydro | 49.1435 | -123.0108 | British Columbia |  |  |  | 434
| Lantzville | BC_LTZ_DSS | BC Hydro | 49.2266 | -124.075 | British Columbia |  |  |  | 435
| Lantzville JCT | BC_LTZ_JCT | BC Hydro | 49.2258 | -124.0755 | British Columbia |  |  |  | 436
| Lehigh Heidelberg | BC_LNH_ISS | BC Hydro | 49.1424 | -123.0208 | British Columbia |  |  |  | 437
| Lehigh Heidelberg JCT | BC_LNH_JCT | BC Hydro | 49.1421 | -123.0173 | British Columbia |  |  |  | 438
| Line Creek Coal | BC_LCC_ISS | BC Hydro | 49.8841 | -114.8509 | British Columbia |  |  |  | 439
| Line Creek Coal JCT | BC_LCC_JCT | BC Hydro | 49.8752 | -114.8854 | British Columbia |  |  |  | 440
| Lions Bay | BC_LBY_DSS | BC Hydro | 49.4535 | -123.2379 | British Columbia |  |  |  | 441
| Lions Bay JCT | BC_LBY_JCT | BC Hydro | 49.4537 | -123.2375 | British Columbia |  |  |  | 442
| Long Beach | BC_LBH_DSS | BC Hydro | 48.9967 | -125.5834 | British Columbia |  |  |  | 443
| Long Lake | BC_LNT_DSS | BC Hydro | 56.0041 | -129.9425 | British Columbia |  |  |  | 444
| Long Lake GS | BC_LNL_GSS | BC Hydro | 56.0623 | -130.0185 | British Columbia |  |  | DELETED Longo Developments BC_DVM_ISS | 445
| Lornex Low Level Dam | BC_LLD_ISS | BC Hydro | 50.558 | -121.1928 | British Columbia |  |  |  | 446
| Lougheed | BC_LOH_DSS | BC Hydro | 49.2604 | -122.9655 | British Columbia |  |  |  | 447
| Lougheed JCT | BC_LOH_JCT | BC Hydro | 49.2604 | -122.9644 | British Columbia |  |  |  | 448
| Lower Bear GS | BC_BHL_GSS | BC Hydro | 49.748 | -123.5159 | British Columbia |  |  |  | 449
| Lower Bonnington GS | BC_LBO_GSS | FortisBC | 49.4617 | -117.5004 | British Columbia |  |  |  | 450
| Lower Clowhom GS | BC_LCH_GSS | BC Hydro | 49.8176 | -123.3973 | British Columbia |  |  |  | 451
| Lumby #2 | BC_LU2_ISS | BC Hydro | 50.228 | -119.0144 | British Columbia |  |  |  | 452
| Lumby #2 JCT | BC_LU2_JCT | BC Hydro | 50.2285 | -119.0144 | British Columbia |  |  |  | 453
| Lynn Valley | BC_LYN_DSS | BC Hydro | 49.328 | -123.0442 | British Columbia |  |  |  | 454
| Mainwaring | BC_MAN_DSS | BC Hydro | 49.2268 | -123.0791 | British Columbia |  |  |  | 455
| Malaspina | BC_MSA_DSS | BC Hydro | 49.6688 | -123.9604 | British Columbia |  |  |  | 456
| Mamquam GS | BC_MAM_GSS | BC Hydro | 49.7214 | -123.0919 | British Columbia |  |  |  | 457
| Mamquam JCT | BC_MAM_JCT | BC Hydro | 49.7017 | -123.1466 | British Columbia |  |  |  | 458
| Maple Ridge | BC_MRG_DSS | BC Hydro | 49.2203 | -122.6234 | British Columbia |  |  |  | 459
| Maple Ridge JCT | BC_MRG_JCT | BC Hydro | 49.2207 | -122.6235 | British Columbia |  |  |  | 460
| Marble River Hatchery | BC_MRH_ISS | BC Hydro | 50.5234 | -127.4316 | British Columbia |  |  |  | 461
| Marble River Hatchery JCT | BC_MRH_JCT | BC Hydro | 50.5233 | -127.4319 | British Columbia |  |  |  | 462
| Marguerite | BC_MGT_DSS | BC Hydro | 52.5009 | -122.4282 | British Columbia |  |  |  | 463
| Marguerite JCT | BC_MGT_JCT | BC Hydro | 52.5011 | -122.4243 | British Columbia |  |  |  | 464
| Marion 3 Creek GS | BC_M3C_GSS | BC Hydro | 49.2342 | -125.3569 | British Columbia |  |  |  | 465
| Marion 3 Creek JCT | BC_M3C_JCT | BC Hydro | 49.236 | -125.3572 | British Columbia |  |  |  | 466
| Marysville | BC_MVL_DSS | BC Hydro | 49.6397 | -115.9286 | British Columbia |  |  |  | 467
| Marysville JCT | BC_MVL_JCT | BC Hydro | 49.6404 | -115.9277 | British Columbia |  |  |  | 468
| Mascot Mines | BC_MAS_ISS | FortisBC | 49.37 | -120.0227 | British Columbia |  |  |  | 469
| McCulloch Creek | BC_MCK_DSS | BC Hydro | 51.6476 | -118.5322 | British Columbia |  |  |  | 470
| McCulloch Creek JCT | BC_MCK_JCT | BC Hydro | 51.6426 | -118.5328 | British Columbia |  |  |  | 471
| McEwan | BC_MWN_DSS | BC Hydro | 54.4289 | -122.641 | British Columbia |  |  |  | 472
| McEwan JCT | BC_MWN_JCT | BC Hydro | 54.4291 | -122.5988 | British Columbia |  |  |  | 473
| McLellan | BC_MLN_DSS | BC Hydro | 49.099 | -122.6824 | British Columbia |  |  |  | 474
| McMahon Gas Plant | BC_MGP_ISS | BC Hydro | 56.1442 | -120.6689 | British Columbia |  |  |  | 475
| McMahon GS | BC_MCM_GSS | BC Hydro | 56.1463 | -120.6711 | British Columbia |  |  |  | 476
| McMahon JCT | BC_MCM_JCT | BC Hydro | 56.1496 | -120.6663 | British Columbia |  |  |  | 477
| Meikle GS | BC_MKL_GSS | BC Hydro | 55.2856 | -121.4691 | British Columbia |  |  |  | 478
| Meikle SWS | BC_MKT_SWS | BC Hydro | 55.2626 | -121.4951 | British Columbia |  |  |  | 479
| Meridian | BC_MDN_DSS | BC Hydro | 49.3097 | -122.8067 | British Columbia |  |  |  | 480
| Merritt | BC_MRT_DSS | BC Hydro | 50.1191 | -120.7743 | British Columbia |  |  |  | 481
| Merritt Green GS | BC_MIG_GSS | BC Hydro | 50.0971 | -120.7957 | British Columbia |  |  |  | 482
| Methanex | BC_MHX_ISS | BC Hydro | 54.0259 | -128.6839 | British Columbia |  | Location approximate |  | 483
| Meziadin | BC_MEZ_DSS | BC Hydro | 56.1084 | -129.3829 | British Columbia |  |  |  | 484
| Meziadin JCT | BC_MEZ_JCT | BC Hydro | 56.1093 | -129.3826 | British Columbia |  |  |  | 485
| Mica GS | BC_MCA_GSS | BC Hydro | 52.0759 | -118.5705 | British Columbia |  |  |  | 486
| Minette | BC_MIN_DSS | BC Hydro | 54.0324 | -128.7098 | British Columbia |  |  |  | 487
| Mission | BC_MIS_DSS | BC Hydro | 49.1409 | -122.3168 | British Columbia |  |  |  | 488
| Mission JCT | BC_MIS_JCT | BC Hydro | 49.1402 | -122.3163 | British Columbia |  |  |  | 489
| Monashee | BC_MON_DSS | BC Hydro | 49.9205 | -118.1477 | British Columbia |  |  |  | 490
| Monte Lake | BC_MTE_DSS | BC Hydro | 50.5237 | -119.8363 | British Columbia |  |  |  | 491
| Montrose Creek GS | BC_MTC_GSS | BC Hydro | 50.6231 | -124.1873 | British Columbia |  |  |  | 492
| Moose Lake GS | BC_MLW_GSS | BC Hydro | 55.2856 | -121.2986 | British Columbia |  |  |  | 493
| Moose Lake JCT | BC_MLW_JCT | BC Hydro | 55.279 | -121.3855 | British Columbia |  |  |  | 494
| Morfee | BC_MFE_DSS | BC Hydro | 55.3195 | -123.1125 | British Columbia |  |  |  | 495
| Mount Lehman | BC_MLE_DSS | BC Hydro | 49.0687 | -122.3916 | British Columbia |  |  |  | 496
| Mount Milligan | BC_MML_DSS | BC Hydro | 55.11 | -124.0218 | British Columbia |  |  |  | 497
| Mount Pleasant | BC_MPT_DSS | BC Hydro | 49.2655 | -123.1117 | British Columbia |  |  |  | 498
| Mount Polley Mining | BC_MTP_DSS | BC Hydro | 52.5443 | -121.633 | British Columbia |  |  |  | 499
| Mount Polley Mining JCT | BC_MTP_JCT | BC Hydro | 52.44 | -122.2813 | British Columbia |  |  |  | 500
| Moyie | BC_MYE_DSS | BC Hydro | 49.285 | -115.8307 | British Columbia |  |  |  | 501
| Moyie JCT | BC_MYE_JCT | BC Hydro | 49.5066 | -115.7391 | British Columbia |  |  |  | 502
| Murphy | BC_MHY_DSS | BC Hydro | 49.0376 | -123.8862 | British Columbia |  |  |  | 503
| Murphy JCT | BC_MHY_JCT | BC Hydro | 49.0377 | -123.8856 | British Columbia |  |  |  | 504
| Murrary River Coal | BC_MRC_ISS | BC Hydro | 55.0028 | -121.0454 | British Columbia |  | Location approximate |  | 505
| Murrary River Coal JCT | BC_MRC_JCT | BC Hydro | 55.0089 | -121.0386 | British Columbia |  | Location approximate |  | 506
| Murrin | BC_MUR_DSS | BC Hydro | 49.278 | -123.1013 | British Columbia |  |  |  | 507
| Nakusp | BC_NAK_DSS | BC Hydro | 50.238 | -117.7958 | British Columbia |  |  |  | 508
| Narrows Inlet GS | BC_NIT_GSS | BC Hydro | 49.8058 | -123.7158 | British Columbia |  |  |  | 509
| Narrows Inlet JCT | BC_NIT_JCT | BC Hydro | 49.7189 | -123.9688 | British Columbia |  | Location approximate |  | 510
| Natal | BC_NTL_DSS | BC Hydro | 49.7355 | -114.8583 | British Columbia |  |  |  | 511
| Nechako Lumber | BC_NLV_DSS | BC Hydro | 54.0138 | -124.0558 | British Columbia |  |  |  | 512
| Nechako Lumber JCT | BC_NLV_JCT | BC Hydro | 54.013 | -124.0518 | British Columbia |  |  |  | 513
| Nelson | BC_NLS_DSS | FortisBC | 49.4934 | -117.2962 | British Columbia |  |  | DELETED - Nelson JCT BC_NLS_JCT | 514
| Nelway | BC_NLY_DSS | BC Hydro | 49.0064 | -117.3415 | British Columbia |  |  |  | 515
| Neptune Bulk Terminal | BC_LCS_ISS | BC Hydro | 49.3054 | -123.0421 | British Columbia |  |  |  | 516
| Neptune Bulk Terminal JCT | BC_LCS_JCT | BC Hydro | 49.3065 | -123.0407 | British Columbia |  |  |  | 517
| New Denver | BC_NDR_DSS | BC Hydro | 49.9974 | -117.3697 | British Columbia |  |  |  | 518
| New Denver JCT | BC_NDR_JCT | BC Hydro | 50.219 | -117.7834 | British Columbia |  |  |  | 519
| New Westminster | BC_NWR_DSS | BC Hydro | 49.222 | -122.9157 | British Columbia |  |  |  | 520
| New Westminster JCT | BC_NWR_JCT | BC Hydro | 49.2631 | -122.8166 | British Columbia |  |  |  | 521
| Newell | BC_NEL_DSS | BC Hydro | 49.2178 | -122.9629 | British Columbia |  |  |  | 522
| Newstech Recycling | BC_NRG_ISS | BC Hydro | 49.23 | -122.8635 | British Columbia |  |  |  | 523
| Newstech Recycling JCT | BC_NRG_JCT | BC Hydro | 49.2322 | -122.8643 | British Columbia |  |  |  | 524
| Nexen | BC_NEX_ISS | BC Hydro | 49.1393 | -123.8662 | British Columbia |  |  |  | 525
| Nexen JCT | BC_NEX_JCT | BC Hydro | 49.1329 | -123.8668 | British Columbia |  |  |  | 526
| Nicola | BC_NIC_DSS | BC Hydro | 50.1802 | -120.3898 | British Columbia |  |  |  | 527
| Nicomekl | BC_NKL_DSS | BC Hydro | 49.0607 | -122.8002 | British Columbia |  |  |  | 528
| Nicomekl JCT | BC_NKL_JCT | BC Hydro | 49.1196 | -122.8123 | British Columbia |  |  |  | 529
| Nk'Mip | BC_NKM_DSS | FortisBC | 49.0392 | -119.4258 | British Columbia |  |  |  | 530
| North Vancouver | BC_NVR_DSS | BC Hydro | 49.3093 | -123.0646 | British Columbia |  |  |  | 531
| North West Energy | BC_NWE_ISS | BC Hydro | 52.1613 | -122.1714 | British Columbia |  |  |  | 532
| Northfield | BC_NFD_DSS | BC Hydro | 49.1908 | -123.9974 | British Columbia |  |  |  | 533
| Northgate | BC_NOR_DSS | BC Hydro | 49.3197 | -123.1353 | British Columbia |  |  |  | 534
| Northwest Stave GS | BC_NWS_GSS | BC Hydro | 49.6281 | -122.4625 | British Columbia |  |  |  | 535
| Northwood | BC_NWP_ISS | BC Hydro | 53.9802 | -122.696 | British Columbia |  |  |  | 536
| OK Falls | BC_OKF_DSS | FortisBC | 49.3376 | -119.5705 | British Columbia |  |  |  | 537
| Okanagan Mission | BC_OKM_DSS | FortisBC | 49.8552 | -119.4889 | British Columbia |  |  |  | 538
| Oldfield | BC_OFD_DSS | BC Hydro | 54.3096 | -130.3075 | British Columbia |  |  |  | 539
| Oliver | BC_OLI_DSS | FortisBC | 49.1901 | -119.5359 | British Columbia |  |  |  | 540
| Ootischenia | BC_OOT_DSS | FortisBC | 49.2895 | -117.6267 | British Columbia |  |  |  | 541
| Osoyoos | BC_OSO_DSS | FortisBC | 49.0278 | -119.4683 | British Columbia |  |  |  | 542
| Oyster River | BC_OYR_DSS | BC Hydro | 49.9027 | -125.2507 | British Columbia |  |  |  | 543
| Oyster River JCT | BC_OYR_JCT | BC Hydro | 49.9034 | -125.2568 | British Columbia |  |  |  | 544
| Parkland | BC_PLD_DSS | BC Hydro | 55.9109 | -120.4487 | British Columbia |  |  |  | 545
| Parkland JCT | BC_PLD_JCT | BC Hydro | 55.9099 | -120.4505 | British Columbia |  |  |  | 546
| Parksville | BC_PVL_DSS | BC Hydro | 49.3028 | -124.3225 | British Columbia |  |  |  | 547
| Parksville JCT | BC_PVL_JCT | BC Hydro | 49.3012 | -124.3225 | British Columbia |  |  |  | 548
| Parsnip | BC_PRS_DSS | BC Hydro | 55.3366 | -123.1811 | British Columbia |  |  |  | 549
| Parsnip JCT | BC_PRS_JCT | BC Hydro | 55.3245 | -123.1564 | British Columbia |  |  |  | 550
| Parson | BC_PSN_DSS | BC Hydro | 51.0697 | -116.6303 | British Columbia |  |  |  | 551
| Parson JCT | BC_PSN_JCT | BC Hydro | 51.0715 | -116.6231 | British Columbia |  |  |  | 552
| Passmore | BC_PAS_DSS | FortisBC | 49.5421 | -117.649 | British Columbia |  |  |  | 553
| Patricia | BC_PCA_DSS | BC Hydro | 53.905 | -122.7653 | British Columbia |  |  |  | 554
| Patricia JCT | BC_PCA_JCT | BC Hydro | 53.9054 | -122.7817 | British Columbia |  |  |  | 555
| Pavilion | BC_PAV_DSS | BC Hydro | 50.883 | -121.8281 | British Columbia |  | Location approximate |  | 556
| Pavilion JCT | BC_PAV_JCT | BC Hydro | 50.8822 | -121.8264 | British Columbia |  | Location approximate |  | 557
| Peace Canyon GS | BC_PCN_GSS | BC Hydro | 55.9826 | -121.995 | British Columbia |  |  |  | 558
| Pemberton | BC_PEM_DSS | BC Hydro | 50.3219 | -122.8044 | British Columbia |  |  |  | 559
| Pemberton JCT | BC_PEM_JCT | BC Hydro | 50.3219 | -122.8001 | British Columbia |  |  |  | 560
| Pender Harbour | BC_PHR_DSS | BC Hydro | 49.6401 | -123.9655 | British Columbia |  |  |  | 561
| Pennask GS | BC_PSW_GSS | BC Hydro | 49.9256 | -120.1093 | British Columbia |  |  |  | 562
| Pennask JCT | BC_PSW_JCT | BC Hydro | 49.9106 | -120.1104 | British Columbia |  |  |  | 563
| Petro Canada Products | BC_PCP_ISS | BC Hydro | 49.2783 | -122.8849 | British Columbia |  |  |  | 564
| PetroCan | BC_KLC_DSS | BC Hydro | 58.6279 | -122.2526 | Alberta |  |  |  | 565
| PetroCan JCT | BC_KLC_JCT | BC Hydro | 58.6283 | -122.2526 | Alberta |  |  |  | 566
| Pike Lake | BC_PIK_DSS | BC Hydro | 48.4906 | -123.4581 | British Columbia |  |  |  | 567
| Pine | BC_PNE_DSS | FortisBC | 49.1786 | -119.5434 | British Columbia |  |  |  | 568
| Pineview | BC_PVW_DSS | BC Hydro | 53.8453 | -122.6952 | British Columbia |  |  |  | 569
| Pineview JCT | BC_PVW_JCT | BC Hydro | 53.8439 | -122.6962 | British Columbia |  |  |  | 570
| Pingston GS | BC_PIN_GSS | BC Hydro | 50.7716 | -118.1041 | British Columbia |  |  |  | 571
| Pinnacle Pellets | BC_PBL_ISS | BC Hydro | 54.1543 | -125.45 | British Columbia |  |  |  | 572
| Pinnacle Pellets JCT | BC_PBL_JCT | BC Hydro | 54.1542 | -125.4475 | British Columbia |  |  |  | 573
| Pinnacle Pellets Meadowbank | BC_PMB_ISS | BC Hydro | 53.3027 | -122.5257 | British Columbia |  |  |  | 574
| Pinnacle Pellets Meadowbank JCT | BC_PMB_JCT | BC Hydro | 53.3023 | -122.5265 | British Columbia |  |  |  | 575
| Playmore | BC_PLA_DSS | FortisBC | 49.4473 | -117.5338 | British Columbia |  |  |  | 576
| Plutonic TS | BC_PSY_TSS | BC Hydro | 49.7877 | -124.1763 | British Columbia |  |  |  | 577
| Port Alberni | BC_PAL_DSS | BC Hydro | 49.2506 | -124.8104 | British Columbia |  |  |  | 578
| Port Edward | BC_PED_DSS | BC Hydro | 54.2287 | -130.2931 | British Columbia |  | Location approximate |  | 579
| Port Edward JCT | BC_PED_JCT | BC Hydro | 54.2407 | -130.2728 | British Columbia |  |  |  | 580
| Port Hardy | BC_PHY_DSS | BC Hydro | 50.7139 | -127.4984 | British Columbia |  |  |  | 581
| Port Kells | BC_PKL_DSS | BC Hydro | 49.1766 | -122.6303 | British Columbia |  |  |  | 582
| Port Kells JCT | BC_PKL_JCT | BC Hydro | 49.1754 | -122.6304 | British Columbia |  |  |  | 583
| Port Kells Pumping | BC_PKP_DSS | BC Hydro | 49.1777 | -122.6998 | British Columbia |  |  |  | 584
| Port Kells Pumping JCT | BC_PKP_JCT | BC Hydro | 49.1752 | -122.7018 | British Columbia |  |  |  | 585
| Port McNeil | BC_PML_DSS | BC Hydro | 50.5724 | -127.0788 | British Columbia |  |  |  | 586
| Port McNeil JCT | BC_PML_JCT | BC Hydro | 50.5711 | -127.0789 | British Columbia |  |  |  | 587
| Portage Pass | BC_PPS_DSS | BC Hydro | 56.0164 | -122.0904 | British Columbia |  |  |  | 588
| Portage Pass JCT | BC_PPS_JCT | BC Hydro | 56.0155 | -122.091 | British Columbia |  |  |  | 589
| Porteau Cove | BC_PTO_DSS | BC Hydro | 49.5456 | -123.2398 | British Columbia |  |  |  | 590
| Porteau Cove JCT | BC_PTO_JCT | BC Hydro | 49.5456 | -123.24 | British Columbia |  |  |  | 591
| Powell | BC_POW_DSS | BC Hydro | 49.8776 | -124.5523 | British Columbia |  |  |  | 592
| Prevost | BC_PVO_DSS | BC Hydro | 48.8239 | -123.7378 | British Columbia |  |  |  | 593
| Prince George Pulp | BC_HCR_ISS | BC Hydro | 53.9229 | -122.6878 | British Columbia |  |  |  | 594
| Prince George Pulp JCT | BC_HCR_JCT | BC Hydro | 53.9231 | -122.6896 | British Columbia |  |  |  | 595
| Prince Rupert Grain | BC_PRG_ISS | BC Hydro | 54.2347 | -130.3288 | British Columbia |  |  |  | 596
| Prince Rupert Grain JCT | BC_PRG_JCT | BC Hydro | 54.2405 | -130.2743 | British Columbia |  |  |  | 597
| Princeton | BC_PRI_DSS | FortisBC | 49.4573 | -120.502 | British Columbia |  |  |  | 598
| Princeton JCT | BC_PRI_JCT | BC Hydro | 49.4408 | -120.566 | British Columbia |  |  |  | 599
| Puntledge GS | BC_PUN_DFS | BC Hydro | 49.665 | -125.0939 | British Columbia |  |  |  | 600
| Qualicum | BC_QLC_DSS | BC Hydro | 49.3313 | -124.4397 | British Columbia |  |  |  | 601
| Qualicum JCT | BC_QLC_JCT | BC Hydro | 49.3306 | -124.4397 | British Columbia |  |  |  | 602
| Quality GS | BC_QTY_GSS | BC Hydro | 55.1846 | -120.8547 | British Columbia |  |  |  | 603
| Quesnel | BC_QNL_DSS | BC Hydro | 52.995 | -122.5023 | British Columbia |  |  |  | 604
| Quesnel River Pulp | BC_QRP_ISS | BC Hydro | 53.0072 | -122.4966 | British Columbia |  |  |  | 605
| Quintette | BC_QNT_DSS | BC Hydro | 54.9934 | -120.9987 | British Columbia |  |  |  | 606
| Radium | BC_RDM_DSS | BC Hydro | 50.63 | -116.074 | British Columbia |  |  |  | 607
| Radium JCT | BC_RDM_JCT | BC Hydro | 50.63 | -116.0747 | British Columbia |  |  |  | 608
| Rainbow | BC_RBW_DSS | BC Hydro | 50.1328 | -122.9545 | British Columbia |  |  |  | 609
| Rainbow JCT | BC_RBW_JCT | BC Hydro | 50.1348 | -122.9601 | British Columbia |  |  |  | 610
| Rearguard Pumping Station | BC_REG_DSS | BC Hydro | 52.9712 | -119.3489 | British Columbia |  |  |  | 611
| Recreation | BC_REC_DSS | FortisBC | 49.8972 | -119.4889 | British Columbia |  |  |  | 612
| Red Bluff | BC_RBF_DSS | BC Hydro | 52.9798 | -122.4661 | British Columbia |  |  |  | 613
| Red Chris Mine | BC_RDC_ISS | BC Hydro | 57.7333 | -129.7673 | British Columbia |  |  |  | 614
| Revelstoke GS | BC_REV_GSS | BC Hydro | 51.0486 | -118.1939 | British Columbia |  |  |  | 615
| RG Anderson | BC_RGA_DSS | FortisBC | 49.4801 | -119.5523 | British Columbia |  |  |  | 616
| Richmond | BC_RIM_DSS | BC Hydro | 49.1633 | -123.1288 | British Columbia |  |  |  | 617
| Richmond Steel Recycling | BC_RSR_ISS | BC Hydro | 49.2009 | -123.0881 | British Columbia |  |  |  | 618
| Ridley Terminals Inc | BC_RTI_ISS | BC Hydro | 54.2245 | -130.3253 | British Columbia |  |  |  | 619
| Riverside | BC_RVS_DSS | BC Hydro | 50.394 | -119.2272 | British Columbia |  |  |  | 620
| Riverside JCT | BC_RVS_JCT | BC Hydro | 50.3941 | -119.2278 | British Columbia |  |  |  | 621
| Rosedale | BC_ROS_DSS | BC Hydro | 49.1764 | -121.7755 | British Columbia |  |  |  | 622
| Rosemont | BC_RSM_DSS | FortisBC | 49.4845 | -117.3029 | British Columbia |  |  |  | 623
| Royal 2 | BC_RO2_DSS | BC Hydro | 49.2017 | -122.9163 | British Columbia |  |  |  | 624
| Ruckles | BC_RUC_DSS | FortisBC | 49.027 | -118.436 | British Columbia |  |  |  | 625
| Ruckles JCT | BC_RUC_JCT | FortisBC | 49.0464 | -118.4361 | British Columbia |  |  |  | 626
| Rupert | BC_RUP_DSS | BC Hydro | 54.2568 | -130.2317 | British Columbia |  |  |  | 627
| Rupert Gas | BC_RPG_GSS | BC Hydro | 54.3143 | -130.2944 | British Columbia |  |  |  | 628
| Ruskin GS | BC_RUS_GSS | BC Hydro | 49.195 | -122.4083 | British Columbia |  |  |  | 629
| Rutherford Creek GS | BC_RUT_GSS | BC Hydro | 50.2727 | -122.867 | British Columbia |  |  |  | 630
| Rutherford Creek JCT | BC_RUT_JCT | BC Hydro | 50.2721 | -122.8646 | British Columbia |  |  |  | 631
| Sachteen | BC_SAC_DSS | BC Hydro | 49.9929 | -122.4585 | British Columbia |  |  |  | 632
| Sahtlam | BC_SAT_DSS | BC Hydro | 48.8068 | -123.8009 | British Columbia |  |  |  | 633
| Salmo | BC_SLM_DSS | FortisBC | 49.1936 | -117.2768 | British Columbia |  |  |  | 634
| Salmon Arm | BC_SAM_DSS | BC Hydro | 50.6916 | -119.2516 | British Columbia |  |  |  | 635
| Salmon Valley | BC_SVY_DSS | BC Hydro | 54.1442 | -122.621 | British Columbia |  |  |  | 636
| Saltery Bay | BC_SAY_DSS | BC Hydro | 49.7871 | -124.1772 | British Columbia |  |  |  | 637
| Saltspring | BC_SAL_DSS | BC Hydro | 48.8574 | -123.5157 | British Columbia |  |  |  | 638
| Saltspring JCT | BC_SAL_JCT | BC Hydro | 48.8574 | -123.5228 | British Columbia |  |  |  | 639
| Saskatchewan Wheat Pool | BC_SWP_ISS | BC Hydro | 49.3068 | -123.0537 | British Columbia |  |  |  | 640
| Saskatchewan Wheat Pool JCT | BC_SWP_JCT | BC Hydro | 49.3085 | -123.0522 | British Columbia |  |  |  | 641
| Saucier | BC_SAU_DSS | FortisBC | 49.8824 | -119.488 | British Columbia |  |  |  | 642
| Savona | BC_SVA_DSS | BC Hydro | 50.7549 | -120.8005 | British Columbia |  |  |  | 643
| Scott | BC_SCT_DSS | BC Hydro | 49.183 | -122.8892 | British Columbia |  |  |  | 644
| Scott JCT | BC_SCT_JCT | BC Hydro | 49.1619 | -122.8862 | British Columbia |  |  |  | 645
| Sea Island | BC_SEA_DSS | BC Hydro | 49.1871 | -123.1514 | British Columbia |  |  |  | 646
| Sea Island JCT | BC_SEA_JCT | BC Hydro | 49.1921 | -123.1246 | British Columbia |  |  |  | 647
| Sechelt | BC_SEC_DSS | BC Hydro | 49.4767 | -123.7522 | British Columbia |  |  |  | 648
| Sechelt Creek GS | BC_SCG_GSS | BC Hydro | 49.6775 | -123.5481 | British Columbia |  |  |  | 649
| Sechelt Creek GS JCT | BC_SCG_JCT | BC Hydro | 49.6783 | -123.5524 | British Columbia |  |  |  | 650
| Selkirk | BC_SEL_TSS | BC Hydro | 49.0596 | -117.5133 | British Columbia |  |  |  | 651
| Septimus | BC_SEP_DSS | BC Hydro | 56.0337 | -120.8749 | British Columbia |  |  |  | 652
| Septimus JCT | BC_SEP_JCT | BC Hydro | 56.0507 | -120.5947 | British Columbia |  |  |  | 653
| Seton Lake GS | BC_SON_DFS | BC Hydro | 50.6727 | -121.9241 | British Columbia |  |  |  | 654
| Seven Mile GS | BC_SEV_GSS | BC Hydro | 49.0302 | -117.5041 | British Columbia |  |  |  | 655
| Seventy Mile House | BC_SMH_DSS | BC Hydro | 51.3001 | -121.3963 | British Columbia |  |  |  | 656
| Seventy Mile House JCT | BC_SMH_JCT | BC Hydro | 51.2999 | -121.3952 | British Columbia |  |  |  | 657
| Sexsmith | BC_SEX_DSS | FortisBC | 49.9185 | -119.3944 | British Columbia |  |  |  | 658
| Shawnigan | BC_SHA_DSS | BC Hydro | 48.6484 | -123.5958 | British Columbia |  |  |  | 659
| Shawnigan JCT | BC_SHA_JCT | BC Hydro | 48.6483 | -123.5973 | British Columbia |  |  |  | 660
| Shelburn | BC_SHL_DSS | BC Hydro | 49.2829 | -122.974 | British Columbia |  |  |  | 661
| Shell Groundbirch | BC_SGB_ISS | BC Hydro | 55.7455 | -121.139 | British Columbia |  |  |  | 662
| Shell Saturn Gas Plant | BC_SRN_ISS | BC Hydro | 55.9591 | -121.0663 | British Columbia |  |  |  | 663
| Shell Saturn Gas Plant JCT | BC_SRN_JCT | BC Hydro | 55.9336 | -121.0224 | British Columbia |  |  |  | 664
| Shell Sunset Prairie | BC_SST_ISS | BC Hydro | 55.9253 | -120.7846 | British Columbia |  | Location approximate |  | 665
| Sicamous | BC_SCM_DSS | BC Hydro | 50.8442 | -118.9735 | British Columbia |  |  |  | 666
| Sidney | BC_SNY_DSS | BC Hydro | 48.629 | -123.4166 | British Columbia |  |  |  | 667
| Silverdale | BC_SVD_DSS | BC Hydro | 49.141 | -122.3573 | British Columbia |  |  |  | 668
| Similco | BC_SCO_DSS | BC Hydro | 49.3531 | -120.5516 | British Columbia |  |  |  | 669
| Simon Fraser University | BC_SFU_DSS | BC Hydro | 49.2755 | -122.9153 | British Columbia |  |  |  | 670
| Simon Fraser University JCT | BC_SFU_JCT | BC Hydro | 49.2751 | -122.896 | British Columbia |  |  |  | 671
| Site C GS | BC_STC_GSS | BC Hydro | 56.1966 | -120.914 | British Columbia |  |  |  | 672
| Site C JCT | BC_STC_JCT | BC Hydro | 56.1726 | -120.9244 | British Columbia |  |  |  | 673
| Skeena | BC_SKA_DSS | BC Hydro | 54.4523 | -128.6328 | British Columbia |  |  |  | 674
| Skeena Cellulose | BC_SKL_ISS | BC Hydro | 54.2395 | -130.2949 | British Columbia |  |  |  | 675
| Skeena Cellulose JCT | BC_SKL_JCT | BC Hydro | 54.2407 | -130.2742 | British Columbia |  |  |  | 676
| Skookum Creek GS | BC_SKO_GSS | BC Hydro | 49.7205 | -122.9956 | British Columbia |  |  |  | 677
| Skookumchuck | BC_SKU_DSS | BC Hydro | 49.9036 | -115.7388 | British Columbia |  |  |  | 678
| Skookumchuck JCT | BC_SKU_JCT | BC Hydro | 49.9037 | -115.7379 | British Columbia |  |  |  | 679
| Smithers | BC_SRS_DSS | BC Hydro | 54.7713 | -127.1458 | British Columbia |  |  |  | 680
| Soda Creek | BC_SCK_DSS | BC Hydro | 52.3056 | -122.2155 | British Columbia |  |  |  | 681
| Solex Gas | BC_NGL_ISS | BC Hydro | 56.1487 | -120.6669 | British Columbia |  |  |  | 682
| Sooke | BC_SOO_DSS | BC Hydro | 48.3909 | -123.6989 | British Columbia |  |  |  | 683
| Sooke JCT | BC_SOO_JCT | BC Hydro | 48.3955 | -123.6837 | British Columbia |  |  |  | 684
| Sorrento | BC_STO_DSS | BC Hydro | 50.8677 | -119.4619 | British Columbia |  |  |  | 685
| Sorrento JCT | BC_STO_JCT | BC Hydro | 50.8696 | -119.4621 | British Columbia |  |  |  | 686
| South Bank | BC_SBK_DSS | BC Hydro | 56.1808 | -120.9094 | British Columbia |  |  |  | 687
| South Campus | BC_UNS_DSS | BC Hydro | 49.2465 | -123.2286 | British Columbia |  |  |  | 688
| South Campus JCT | BC_UNS_JCT | BC Hydro | 49.2499 | -123.2292 | British Columbia |  |  |  | 689
| South Cranberry GS | BC_SCB_GSS | BC Hydro | 50.7716 | -118.1041 | British Columbia |  |  |  | 690
| South Cranberry JCT | BC_SCB_JCT | BC Hydro | 50.7686 | -118.0997 | British Columbia |  |  |  | 691
| South Slocan GS | BC_SLC_GSS | FortisBC | 49.4555 | -117.5197 | British Columbia |  |  |  | 692
| South Sutton GS | BC_SSH_GSS | BC Hydro | 49.2876 | -125.3092 | British Columbia |  |  |  | 693
| South Sutton JCT | BC_SSH_JCT | BC Hydro | 49.2918 | -125.3071 | British Columbia |  |  |  | 694
| South Wellington | BC_SWN_DSS | BC Hydro | 49.0778 | -123.9083 | British Columbia |  |  |  | 695
| South Wellington JCT | BC_SWN_JCT | BC Hydro | 49.0779 | -123.9097 | British Columbia |  |  |  | 696
| Sparwood | BC_SPD_DSS | BC Hydro | 49.7091 | -114.8927 | British Columbia |  |  |  | 697
| Sparwood JCT | BC_SPD_JCT | BC Hydro | 49.7091 | -114.8877 | British Columbia |  |  |  | 698
| Spatsum | BC_STL_DSS | BC Hydro | 50.5579 | -121.2955 | British Columbia |  |  |  | 699
| Spences Bridge | BC_SBR_DSS | BC Hydro | 50.4278 | -121.3261 | British Columbia |  |  |  | 700
| Sperling | BC_SPG_DSS | BC Hydro | 49.2497 | -123.1525 | British Columbia |  |  |  | 701
| Spillimacheen GS | BC_SPN_DFS | BC Hydro | 50.9034 | -116.4089 | British Columbia |  |  |  | 702
| Spillimacheen JCT | BC_SPN_JCT | BC Hydro | 50.9063 | -116.3661 | British Columbia |  |  |  | 703
| Spuzzum | BC_SZM_DSS | BC Hydro | 49.6984 | -121.4099 | British Columbia |  |  |  | 704
| Squamish | BC_SQH_DSS | BC Hydro | 49.7022 | -123.1486 | British Columbia |  |  |  | 705
| St Leon Creek | BC_SLK_DSS | BC Hydro | 49.2887 | -122.3421 | British Columbia |  |  |  | 706
| St Leon Creek JCT | BC_SLK_JCT | BC Hydro | 49.289 | -122.3421 | British Columbia |  |  |  | 707
| Stave Falls GS | BC_SFL_GSS | BC Hydro | 49.2288 | -122.3561 | British Columbia |  |  |  | 708
| Steeples | BC_SPL_DSS | BC Hydro | 49.507 | -115.7484 | British Columbia |  |  |  | 709
| Steeples JCT | BC_SPL_JCT | BC Hydro | 49.5 | -115.7514 | British Columbia |  |  |  | 710
| Steveston | BC_STV_DSS | BC Hydro | 49.1326 | -123.1469 | British Columbia |  |  |  | 711
| Stewart | BC_STW_DSS | BC Hydro | 55.9478 | -129.9806 | British Columbia |  |  |  | 712
| Stokke GS | BC_SKK_GSS | BC Hydro | 49.7111 | -122.0343 | British Columbia |  |  |  | 713
| Stoney Creek | BC_STY_DSS | FortisBC | 49.1146 | -117.7267 | British Columbia |  |  |  | 714
| Strathcona GS | BC_SCA_GSS | BC Hydro | 49.9981 | -125.5856 | British Columbia |  |  |  | 715
| Strawberry Hill | BC_SYH_DSS | BC Hydro | 49.1364 | -122.8752 | British Columbia |  |  |  | 716
| Strawberry Hill JCT | BC_SYH_JCT | BC Hydro | 49.137 | -122.8751 | British Columbia |  |  |  | 717
| Stump | BC_STM_ISS | BC Hydro | 50.3255 | -120.4471 | British Columbia |  |  |  | 718
| Stump JCT | BC_STM_JCT | BC Hydro | 50.3189 | -120.4463 | British Columbia |  |  |  | 719
| Sukunka | BC_SNK_DSS | BC Hydro | 55.5021 | -121.6179 | British Columbia |  |  |  | 720
| Sumas Way | BC_SMW_DSS | BC Hydro | 49.0319 | -122.2701 | British Columbia |  |  |  | 721
| Sumas Way JCT | BC_SMW_JCT | BC Hydro | 49.0321 | -122.2707 | British Columbia |  |  |  | 722
| Summerland | BC_SUM_DSS | FortisBC | 49.6004 | -119.6757 | British Columbia |  |  |  | 723
| Sundance Lake | BC_SLS_DSS | BC Hydro | 55.7141 | -121.3519 | British Columbia |  |  |  | 724
| Surrey | BC_SRY_DSS | BC Hydro | 49.1048 | -122.8295 | British Columbia |  |  |  | 725
| Surrey JCT | BC_SRY_JCT | BC Hydro | 49.1257 | -122.8314 | British Columbia |  |  |  | 726
| Tachick | BC_TAC_DSS | BC Hydro | 54.0007 | -124.0728 | British Columbia |  |  |  | 727
| Tachick JCT | BC_TAC_JCT | BC Hydro | 53.9987 | -124.0728 | British Columbia |  |  |  | 728
| Tahsis Village | BC_TSV_DSS | BC Hydro | 49.9233 | -126.6511 | British Columbia |  |  |  | 729
| Takla Forest Products | BC_TFP_DSS | BC Hydro | 54.469 | -124.1658 | British Columbia |  |  |  | 730
| Tarrys | BC_TAR_DSS | FortisBC | 49.3927 | -117.5517 | British Columbia |  |  |  | 731
| Tatogga | BC_TAT_DSS | BC Hydro | 57.713 | -129.987 | British Columbia |  |  |  | 732
| Taylor | BC_TAY_DSS | BC Hydro | 56.1818 | -120.7207 | British Columbia |  |  |  | 733
| Taylor River Rest Area | BC_TRR_DSS | BC Hydro | 49.2951 | -125.2999 | British Columbia |  |  |  | 734
| Taylor River Rest Area JCT | BC_TRR_JCT | BC Hydro | 49.2934 | -125.2994 | British Columbia |  |  |  | 735
| Telkwa | BC_TKW_DSS | BC Hydro | 54.5153 | -126.7655 | British Columbia |  |  |  | 736
| Terrace | BC_TER_DSS | BC Hydro | 54.5109 | -128.5582 | British Columbia |  |  |  | 737
| Terrace Skeena Cellulose | BC_TSC_DSS | BC Hydro | 54.5137 | -128.6056 | British Columbia |  |  | DELETED - Terrace Skeena Cellulose JCT BC_TSC_JCT | 738
| Texaco | BC_TXB_DSS | BC Hydro | 56.338 | -120.1383 | British Columbia |  |  |  | 739
| Tilbury | BC_TLB_ISS | BC Hydro | 49.14 | -123.0294 | British Columbia |  |  |  | 740
| Tilbury JCT | BC_TLB_JCT | BC Hydro | 49.1371 | -123.0257 | British Columbia |  |  |  | 741
| Timber West | BC_TWT_DSS | BC Hydro | 52.1651 | -122.1719 | British Columbia |  |  |  | 742
| Timber West JCT | BC_TWT_JCT | BC Hydro | 52.164 | -122.1667 | British Columbia |  |  |  | 743
| Timbernorth | BC_TBN_DSS | BC Hydro | 55.2955 | -123.1585 | British Columbia |  |  |  | 744
| Timbernorth JCT | BC_TBN_JCT | BC Hydro | 55.2946 | -123.1535 | British Columbia |  |  |  | 745
| Tipella GS | BC_TPA_GSS | BC Hydro | 49.7409 | -122.1622 | British Columbia |  |  |  | 746
| Tisdall | BC_TIS_DSS | BC Hydro | 50.2795 | -122.8593 | British Columbia |  |  |  | 747
| Tolko Armstrong GS | BC_RVG_GSS | BC Hydro | 50.3939 | -119.2272 | British Columbia |  |  |  | 748
| Tolko Armstrong JCT | BC_RVG_JCT | BC Hydro | 50.3936 | -119.2285 | British Columbia |  |  |  | 749
| Tolko Industries Heffley | BC_TOK_DSS | BC Hydro | 50.8431 | -120.2724 | British Columbia |  |  |  | 750
| Tolko Industries Heffley JCT | BC_TOK_JCT | BC Hydro | 50.8424 | -120.2721 | British Columbia |  |  |  | 751
| Tolko Industries Lavington | BC_TIL_DSS | BC Hydro | 50.2329 | -119.0939 | British Columbia |  |  |  | 752
| Tolko Industries Lavington JCT | BC_TIL_JCT | BC Hydro | 50.2356 | -119.0937 | British Columbia |  |  |  | 753
| Tolko Lignum | BC_LGW_DSS | BC Hydro | 52.1581 | -122.1808 | British Columbia |  |  |  | 754
| Tolko Lignum JCT | BC_LGW_JCT | BC Hydro | 52.1566 | -122.1755 | British Columbia |  |  |  | 755
| Topley | BC_TPY_DSS | BC Hydro | 54.5205 | -126.2937 | British Columbia |  |  |  | 756
| Trans Mountain | BC_TMO_DSS | BC Hydro | 49.0646 | -122.159 | British Columbia |  |  |  | 757
| Trans Mountain JCT | BC_TMO_JCT | BC Hydro | 49.0604 | -122.0756 | British Columbia |  |  |  | 758
| TransMountain Kamloops | BC_TMT_DSS | BC Hydro | 50.6634 | -120.413 | British Columbia |  |  |  | 759
| TransMountain Kamloops JCT | BC_TMT_JCT | BC Hydro | 50.668 | -120.4173 | British Columbia |  |  |  | 760
| TransMountain McMurphy | BC_TMM_DSS | BC Hydro | 51.6765 | -119.4473 | British Columbia |  |  |  | 761
| TransMountain McMurphy JCT | BC_TMM_JCT | BC Hydro | 51.6776 | -119.4484 | British Columbia |  |  |  | 762
| Tree Island Industries | BC_TII_DSS | BC Hydro | 49.1861 | -122.9573 | British Columbia |  |  |  | 763
| Tree Island Industries JCT | BC_TII_JCT | BC Hydro | 49.1925 | -122.9427 | British Columbia |  |  |  | 764
| Tretheway GS | BC_TWY_GSS | BC Hydro | 49.7038 | -122.0796 | British Columbia |  |  |  | 765
| Trio GS | BC_TRE_GSS | BC Hydro | 49.6284 | -122.0329 | British Columbia |  |  |  | 766
| Trout Creek | BC_TRC_DSS | FortisBC | 49.5708 | -119.6587 | British Columbia |  |  |  | 767
| Tsawassen | BC_TSW_DSS | BC Hydro | 49.0361 | -123.075 | British Columbia |  |  |  | 768
| Tsawassen JCT | BC_TSW_JCT | BC Hydro | 49.0601 | -123.0759 | British Columbia |  |  |  | 769
| Tumbler Ridge | BC_TLR_DSS | BC Hydro | 55.1484 | -121.1339 | British Columbia |  |  |  | 770
| Tyax Lake | BC_TXL_DSS | BC Hydro | 50.9102 | -122.743 | British Columbia |  | Location approximate |  | 771
| Tyax Lake JCT | BC_TXL_JCT | BC Hydro | 50.9097 | -122.7429 | British Columbia |  | Location approximate |  | 772
| University of BC | BC_UNY_DSS | BC Hydro | 49.2612 | -123.2447 | British Columbia |  |  |  | 773
| Upper Bear GS | BC_BHU_GSS | BC Hydro | 49.7954 | -123.5721 | British Columbia |  |  |  | 774
| Upper Bonnington GS | BC_UBO_GSS | FortisBC | 49.4601 | -117.4842 | British Columbia |  |  |  | 775
| Upper Bonnington SWS | BC_USS_SWS | FortisBC | 49.461 | -117.4833 | British Columbia |  |  |  | 776
| Upper Clowhom GS | BC_UCH_GSS | BC Hydro | 49.8543 | -123.4461 | British Columbia |  |  |  | 777
| Upper Fraser | BC_UFR_DSS | BC Hydro | 54.118 | -121.9453 | British Columbia |  |  |  | 778
| Upper Harrison | BC_UHT_DSS | BC Hydro | 49.7591 | -122.2052 | British Columbia |  |  |  | 779
| Upper Lillooet River GS | BC_ULR_GSS | BC Hydro | 50.657 | -123.4476 | British Columbia |  |  |  | 780
| Upper Mamquam GS | BC_UMH_GSS | BC Hydro | 49.7178 | -123.0546 | British Columbia |  |  |  | 781
| Upper Mamquam JCT | BC_UMH_JCT | BC Hydro | 49.7016 | -123.1471 | British Columbia |  |  |  | 782
| Upper Stave River GS | BC_USR_GSS | BC Hydro | 49.566 | -122.3503 | British Columbia |  |  |  | 783
| Valemount | BC_VLM_DSS | BC Hydro | 52.7824 | -119.282 | British Columbia |  |  |  | 784
| Valhalla | BC_VAL_DSS | FortisBC | 49.7597 | -117.4681 | British Columbia |  |  |  | 785
| Valleyview | BC_VVW_DSS | BC Hydro | 50.6801 | -120.2827 | British Columbia |  |  |  | 786
| Vancouver Dry Dock | BC_VDK_ISS | BC Hydro | 49.3092 | -123.076 | British Columbia |  |  |  | 787
| Vancouver Dry Dock JCT | BC_VDK_JCT | BC Hydro | 49.3122 | -123.074 | British Columbia |  |  |  | 788
| Vancouver International Airport | BC_YVR_ISS | BC Hydro | 49.187 | -123.1519 | British Columbia |  |  |  | 789
| Vancouver Island TS | BC_VIT_TSS | BC Hydro | 48.8273 | -123.7164 | British Columbia |  |  |  | 790
| Vancouver Shipyards | BC_VSY _ISS | BC Hydro | 49.3131 | -123.1085 | British Columbia |  |  |  | 791
| Vancouver Shipyards JCT | BC_VSY_JCT | BC Hydro | 49.3132 | -123.1076 | British Columbia |  |  |  | 792
| Vanderhoof | BC_VDF_DSS | BC Hydro | 54.0083 | -124.0151 | British Columbia |  |  |  | 793
| Vanderhoof JCT | BC_VDF_JCT | BC Hydro | 54.0086 | -124.0151 | British Columbia |  |  |  | 794
| Vaseux Lake | BC_VAS_DSS | BC Hydro | 49.2511 | -119.5196 | British Columbia |  |  |  | 795
| Vavenby | BC_VBY_DSS | BC Hydro | 51.5904 | -119.7537 | British Columbia |  |  |  | 796
| Vavenby JCT | BC_VBY_JCT | BC Hydro | 51.5907 | -119.7536 | British Columbia |  |  |  | 797
| Vernon TS | BC_VNT_TSS | BC Hydro | 50.2518 | -119.2289 | British Columbia |  |  |  | 798
| Wahleach GS | BC_WAH_GSS | BC Hydro | 49.2366 | -121.6807 | British Columbia |  |  |  | 799
| Wahleach Hope JCT | BC_WHO_JCT | BC Hydro | 49.317 | -121.6643 | British Columbia |  |  |  | 800
| Wahleach JCT | BC_WAH_JCT | BC Hydro | 49.1458 | -121.9564 | British Columbia |  |  |  | 801
| Wahleach Pumping Station | BC_WHP_DSS | BC Hydro | 49.1947 | -121.7313 | British Columbia |  |  |  | 802
| Wahleach Pumping Station JCT | BC_WHP_JCT | BC Hydro | 49.2084 | -121.7081 | British Columbia |  |  |  | 803
| Walden North GS | BC_WDN_GSS | BC Hydro | 50.6605 | -121.9833 | British Columbia |  |  |  | 804
| Walden North JCT | BC_WDN_JCT | BC Hydro | 50.67 | -121.9802 | British Columbia |  |  |  | 805
| Walter Hardman GS | BC_WHN_GSS | BC Hydro | 50.8139 | -118.06 | British Columbia |  |  |  | 806
| Walters | BC_WLT_DSS | BC Hydro | 49.31 | -123.0261 | British Columbia |  |  |  | 807
| Waneta Expansion GS | BC_WAX_GSS | FortisBC | 49.0047 | -117.616 | British Columbia |  |  |  | 808
| Waneta GS | BC_WAN_GSS | FortisBC | 49.0041 | -117.6129 | British Columbia |  |  |  | 809
| Waneta SS | BC_WHS_TSS | FortisBC | 49.0068 | -117.6131 | British Columbia |  |  |  | 810
| Wardner | BC_WAR_DSS | BC Hydro | 49.4934 | -115.3617 | British Columbia |  |  | DELETED Wardner JCT | 811
| Warfield | BC_WTS_DSS | FortisBC | 49.1052 | -117.7397 | British Columbia |  |  |  | 812
| Waterford | BC_WAT_DSS | FortisBC | 49.4611 | -119.5891 | British Columbia |  |  |  | 813
| Wescup | BC_WSP_DSS | BC Hydro | 58.7242 | -122.7016 | Alberta |  |  |  | 814
| West Bench | BC_WEB_DSS | FortisBC | 49.5084 | -119.6216 | British Columbia |  |  |  | 815
| West Fraser Quesnel | BC_WFQ_ISS | BC Hydro | 52.9961 | -122.5013 | British Columbia |  |  |  | 816
| West Fraser Quesnel JCT | BC_WFQ_JCT | BC Hydro | 52.9961 | -122.4623 | British Columbia |  |  |  | 817
| West Fraser Quesnel Plywood | BC_WQL_ISS | BC Hydro | 52.9459 | -122.4826 | British Columbia |  |  |  | 818
| West Fraser Quesnel Plywood JCT | BC_WQL_JCT | BC Hydro | 52.9465 | -122.4684 | British Columbia |  |  |  | 819
| West Fraser Williams Lake | BC_WWL_ISS | BC Hydro | 52.1598 | -122.1836 | British Columbia |  |  |  | 820
| West Fraser Williams Lake JCT | BC_WWL_JCT | BC Hydro | 52.1537 | -122.1756 | British Columbia |  |  |  | 821
| West Kamloops | BC_WKA_DSS | BC Hydro | 50.674 | -120.3839 | British Columbia |  |  |  | 822
| West Pine | BC_WPN_DSS | BC Hydro | 53.0128 | -122.5181 | British Columbia |  |  |  | 823
| West Pine JCT | BC_WPN_JCT | BC Hydro | 53.0154 | -122.4413 | British Columbia |  |  |  | 824
| Westar | BC_WST_DSS | FortisBC | 49.3369 | -117.738 | British Columbia |  |  |  | 825
| Westbank | BC_WBK_DSS | BC Hydro | 49.8484 | -119.6193 | British Columbia |  |  |  | 826
| Westcoast Cellufibre | BC_WCF_ISS | BC Hydro | 49.2064 | -123.1072 | British Columbia |  |  |  | 827
| Westcoast Cellufibre JCT | BC_WCF_JCT | BC Hydro | 49.2067 | -123.1071 | British Columbia |  |  |  | 828
| Westmin Resources | BC_WNR_ISS | BC Hydro | 55.9529 | -129.968 | British Columbia |  |  |  | 829
| Westmin Resources JCT | BC_WNR_JCT | BC Hydro | 55.9547 | -129.9722 | British Columbia |  |  |  | 830
| Westminster | BC_WES_DSS | FortisBC | 49.5009 | -119.5869 | British Columbia |  |  |  | 831
| Westshore Terminals | BC_WTL_ISS | BC Hydro | 49.0198 | -123.1702 | British Columbia |  |  | DELETED - Westshore Terminals JCT | 832
| Westwold | BC_WWD_DSS | BC Hydro | 50.4763 | -119.7575 | British Columbia |  |  |  | 833
| Westwold JCT | BC_WWD_JCT | BC Hydro | 50.4765 | -119.7574 | British Columbia |  |  |  | 834
| Whalley | BC_WHY_DSS | BC Hydro | 49.1901 | -122.8366 | British Columbia |  |  |  | 835
| Whatshan GS | BC_WGS_GSS | BC Hydro | 49.9106 | -118.0718 | British Columbia |  |  |  | 836
| White Rock | BC_WRK_DSS | BC Hydro | 49.0306 | -122.7898 | British Columbia |  |  | DELETED - Whonnock BC_WNK_DSS and Whonnock BC_WNK_JCT | 837
| Williams Lake | BC_WLM_DSS | BC Hydro | 52.1335 | -122.1385 | British Columbia |  |  |  | 838
| Williston | BC_WSN_DSS | BC Hydro | 53.8502 | -122.609 | British Columbia |  |  |  | 839
| Windsor | BC_WIN_DSS | BC Hydro | 49.3058 | -115.1283 | British Columbia |  |  |  | 840
| Windsor JCT | BC_WIN_JCT | BC Hydro | 49.3072 | -115.1288 | British Columbia |  |  |  | 841
| Woodfibre | BC_WFR_DSS | BC Hydro | 49.6671 | -123.2547 | British Columbia |  |  |  | 842
| Woodfibre JCT | BC_WFR_JCT | BC Hydro | 49.6717 | -123.258 | British Columbia |  |  |  | 843
| Woss | BC_WOS_DSS | BC Hydro | 50.2176 | -126.5945 | British Columbia |  |  |  | 844
| Woss JCT | BC_WOS_JCT | BC Hydro | 50.218 | -126.5945 | British Columbia |  |  |  | 845
| Ymir | BC_YMR_DSS | FortisBC | 49.2868 | -117.225 | British Columbia |  |  |  | 846
| Zeballos Lake GS | BC_ZBL_GSS | BC Hydro | 50.0535 | -126.7797 | British Columbia |  |  |  | 847
| Zeballos Lake TS | BC_ZBT_TSS | BC Hydro | 49.9238 | -126.6597 | British Columbia |  |  |  | 848
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## HydroExisting
BC | EXISTING STORAGE HYDROELECTRIC | [24 empty] | RESERVOIR
| Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Renewal Year | Dam Type | Penstock | Rated Head | Maximum Head | Minimum Head | Average Flow (Facility) | Rated Discharge (Unit) | Rated Discharge (Facility) | Upstream Reservoir Area | Upstream Reservoir Storage | Turbine Type | Station Flow | Upper Storage Name | Upper Storage Level | Lower Storage Name | Lower Storage Level | Upper Storage Name | Minimum Level | Maximum Level | Initial Level | Low Volume | High Volume | Live Storage | M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10 | M11 | M12 | Other References | Notes
|  |  | (MW) | (%) | (MW) | (%) | (GWh/year) |  |  |  | (m) | (m) | (m) | (m) | (m3/s) | (m3/s) | (m3/s) | (km2) | (hours) |  | (WSC#) |  | (WSC#) |  | (WSC#) |  | (m) | (m) | (m) | (m3) | (m3) | (m3) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s)
| Aberfeldie | Hydro_daily | 24 | 100% | 24 | 33.12% | 69.6228 | 2 | 2009 | [12 empty] | Aberfeldie |  |  |  | Aberfeldie | 876.15 | 876.67 | 876.67 |  |  |  | 7.66 | 7.34 | 9.25 | 30.8 | 96.8 | 109 | 52 | 21.5 | 15.6 | 14.4 | 12.8 | 9.32
| Alouette | Hydro_daily | 9 | 100% | 9 | 33.12% | 26.1086 | 1 | [13 empty] | Allouette |  | Stave |  | Allouette | 112.6 | 125.5 | 122.92 |  |  |  | 10.0525 | 8.6512 | 8.9568 | 13.2824 | 32.3897 | 49.7957 | 38.2854 | 23.594 | 15.0539 | 14.8909 | 14.3813 | 10.6664
| Arrow Lakes | Hydro_daily | 185 | 100% | 185 | 47.33% | 767 | 2 | [13 empty] | Arrow | 08NE102 | Columbia (U.S.) | 08NE049 | Arrow | 418.64 | 440.1 | 435.808 |  |  |  | 130 | 117 | 131 | 293 | 771 | 987 | 691 | 367 | 250 | 202 | 178 | 139 |  | 08NE049 is flow and level data
| Ash | Hydro_daily | 28 | 100% | 28 | 33.12% | 81.2266 | 1 | [13 empty] | Elsie |  |  |  | Elsie | 320 | 330.71 | 328.568 |  |  |  | 25 | 24 | 21 | 24 | 28 | 24 | 13 | 7 | 7 | 21 | 32 | 29
| Bridge | Hydro_daily | 480 | 100% | 480 | 33.12% | 1392.4559 | 8 | [13 empty] | Anderson Lake |  | Seton |  | Carpenter | 606.55 | 651.08 | 642.174 |  |  |  | 16 | 14 | 14 | 21 | 78 | 159 | 128 | 73 | 38 | 31 | 25 | 19
| Brilliant Expansion | Hydro_daily | 127.5 | 100% | 127.5 | 38.38% | 428.67 | 1 | [13 empty] | Brilliant |  | Columbia (U.S.) | 08NE049 | Brilliant | [19 empty] | 08NE049 is flow and level data
| Brilliant | Hydro_daily | 150 | 100% | 150 | 33.12% | 435.1427 | 4 | [13 empty] | Brilliant |  | Columbia (U.S.) | 08NE049 | Brilliant | [19 empty] | 08NE049 is flow and level data
| Brown Lake | Hydro_daily | 7.2 | 100% | 7.2 | 90.37% | 57 | 1
| Buntzen Lake | Hydro_daily | 55 | 100% | 55 | 33.12% | 159.5523 | 1 | 1951 | [12 empty] | Buntzen Lake |  |  |  | Buntzen Lake
| Cheakamus | Hydro_daily | 158 | 100% | 158 | 37.73% | 522.1712 | 2 | [13 empty] | Daisy |  |  |  | Daisy | 362.1 | 373.5 | 371.22 |  |  |  | 20 | 21 | 22 | 33 | 75 | 115 | 105 | 68 | 41 | 43 | 40 | 25
| Clowhom | Hydro_daily | 33 | 100% | 33 | 45.16% | 130.5428 | 1 | [12 empty] | 08GB013 | Clowhom Lake |  |  |  | Clowhom | 45 | 52.5 | 51 |  |  |  | 25 | 26 | 24 | 29 | 56 | 70 | 55 | 29 | 24 | 39 | 42 | 30 |  | 08GB013 located at upper end of reservoir
| Corra Linn | Hydro_daily | 51 | 100% | 51 | 33.12% | 147.9485 | 3 | [12 empty] | 08NJ158 | Kootenay Lake |  | Upper Bonnington |  | Kootenay Lake
| Diversion (not powered) | [20 empty] | Diversion |  | Elliot |  | Diversion | 358.68 | 386.2 | 380 |  |  |  | 23 | 21 | 16 | 12 | 7 | 3 | 2 | 1 | 3 | 11 | 25 | 25
| Eldorado Reservoir | Hydro_daily | 1.13 | 100% | 1.13 | 40.41% | 4 | 1
| Elko | Hydro_daily | 12 | 100% | 12 | 33.12% | 34.8114 | 2
| Falls River | Hydro_daily | 7 | 100% | 7 | 33.12% | 20.3067 | 2
| G.M. Shrum | Hydro_monthly | 3050 | 100% | 3050 | 60.06% | 16047.45 | 10 | [13 empty] | Williston | 07EF003 | Dinosaur |  | Williston | 642.03 | 672.08 | 666.07 |  |  | 39471000000 | 300 | 255 | 245 | 517 | 2475 | 3706 | 1974 | 990 | 787 | 795 | 546 | 351
| John Hart | Hydro_daily | 138 | 100% | 138 | 33.12% | 400.3313 | 3 | 2019 | [11 empty] | 08HD003 | John Hart |  |  |  | John Hart | 133.43 | 140.06 | 139.44 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Jordan River | Hydro_daily | 170 | 100% | 170 | 33.12% | 493.1617 | 1 | 1971 | [12 empty] | Elliott |  |  |  | Elliott | 311.51 | 335.89 | 330 |  |  |  | 23 | 21 | 16 | 12 | 7 | 3 | 2 | 1 | 3 | 11 | 25 | 25
| Kemano | Hydro_monthly | 900 | 100% | 900 | 41.95% | 3307 | 8 | 2010 | [11 empty] | 08FE002 | Nechako |  |  |  | Nachako
| Kootenay Canal | Hydro_daily | 591 | 100% | 591 | 33.12% | 1714.4622 | 4 | [13 empty] | Corra Linn |  | Brilliant |  | Corra Linn
| Ladore | Hydro_daily | 47 | 100% | 47 | 33.12% | 136.3447 | 2 | [13 empty] | Lower Campbell Lake |  | John Hart |  | Lower | 163.65 | 178.3 | 176.8 |  |  |  | 13 | 10 | 10 | 12 | 16 | 12 | 5 | 2 | 3 | 12 | 17 | 12
| Lajoie | Hydro_daily | 25 | 100% | 25 | 33.12% | 72.5238 | 1 | [13 empty] | Downton Lake |  | Carpenter |  | Downton | 707.67 | 749.81 | 741.382 |  |  |  | 7 | 7 | 7 | 11 | 39 | 101 | 123 | 104 | 55 | 26 | 12 | 7
| Long Lake | Hydro_daily | 31 | 100% | 31 | 56.73% | 154.068 | 2
| Lower Bonnington | Hydro_daily | 46 | 100% | 46 | 33.11% | 133.44 | 3 | 1924 | [12 empty] | Lower Bonnington |  | South Slocan |  | Lower Bonnington
| Mica | Hydro_monthly | 2971 | 100% | 2971 | 44.94% | 11695.8911 | 6 | [13 empty] | Kinbasket | 08ND017 | Revelstoke |  | Kinbasket | 707.41 | 754.38 | 744.986 |  |  |  | 108 | 103 | 104 | 219 | 819 | 1611 | 1600 | 1104 | 581 | 314 | 196 | 132
| Peace Canyon | Hydro_monthly | 700 | 100% | 700 | 62.2% | 3814.4101 | 4 | [12 empty] | 07EF001 | Dinosaur |  | Site C | 07EF001 | Dinosaur | 500 | 502.92 | 502.336 |  |  | 24690000 | 4.021 | 3.4605 | 3.5827 | 5.313 | 12.9559 | 19.9183 | 15.3141 | 9.4376 | 6.0215 | 5.9564 | 5.7525 | 4.2665 |  | 07EF001 Level is prior to Site C reservoir
| Puntledge | Hydro_daily | 24 | 100% | 24 | 33.12% | 69.6228 | 1 | 1955
| Raging River | Hydro_daily | 8 | 100% | 8 | 56.73% | 39.7592 | 2
| Revelstoke | Hydro_monthly | 2500 | 100% | 2500 | 40.18% | 8799.8518 | 5 | [12 empty] | 08ND025 | Revelstoke |  | Arrow |  | Revelstoke | 554.54 | 573.02 | 572.716 |  |  |  | 47 | 44 | 48 | 125 | 454 | 700 | 554 | 339 | 200 | 143 | 100 | 66
| Ruskin | Hydro_daily | 115 | 100% | 115 | 33.11% | 333.5804 | 3 | [13 empty] | Hayward | 08MH167 |  |  | Hayward | 41.1 | 42.8 | 42.46 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Seton | Hydro_daily | 48 | 100% | 48 | 33.12% | 139.2457 | 1 | [12 empty] | 08ME003 | Seton (+ Carpenter) |  |  |  | Seton | 235.76 | 236.36 | 236.24 |  |  |  | 8 | 7 | 7 | 8 | 20 | 47 | 41 | 24 | 15 | 12 | 11 | 9
| Seven Mile | Hydro_daily | 805 | 100% | 805 | 33.12% | 2335.2657 | 4 | [13 empty] | Seven Mile |  | Waneta |  | Seven Mile | 514.8 | 527.3 | 524.8 |  |  |  | 484 | 497 | 616 | 892 | 1303 | 1438 | 707 | 367 | 425 | 615 | 611 | 522
| Shuswap | Hydro_daily | 6 | 100% | 6 | 33.12% | 17.41 | 1 | [13 empty] | Shuswap Lake |  |  |  | Shuswap Lake
| Site C | Hydro_monthly | 1132 | 100% | 1132 | 54.1% | 5364.4221 | 6 | [12 empty] | 07FA004 | Site C |  |  |  | SiteC Res | 460.011 | 461.8 | 461.4419 |  |  | 165000000 | 13.92 | 12.1 | 12.51 | 34.74 | 169 | 311.7 | 199.1 | 94.03 | 64.18 | 45.06 | 25.22 | 17.97 |  | 07FA004 Flow is prior to Site C generation
| South Slocan | Hydro_daily | 57 | 100% | 57 | 33.12% | 165.3542 | 3 | [13 empty] | South Slocan |  | Brilliant
| Stave Falls | Hydro_daily | 91 | 100% | 91 | 33.12% | 263.9865 | 2 | 2000 | [12 empty] | Stave Lake |  | Hayward | 08MH167 | Stave Lake | 73 | 82.08 | 80.264 |  |  |  | 50.77 | 43.69 | 45.23 | 67.08 | 163.57 | 251.47 | 193.34 | 119.15 | 76.02 | 75.2 | 72.63 | 53.87
| Strathcona | Hydro_daily | 65 | 100% | 65 | 33.12% | 188.5618 | 2 | [13 empty] | Upper Campbell Lake | 08HD031 | Lower Campbell Lake |  | Upper Campbell Lake | 210 | 221 | 219.6 |  |  |  | 86 | 68 | 63 | 67 | 106 | 114 | 72 | 36 | 32 | 80 | 116 | 89
| Tyson Creek | Hydro_daily | 9.3 | 100% | 9.3 | 56.73% | 46.2201 | 1
| Upper Bonnington | Hydro_daily | 63 | 100% | 63 | 33.12% | 182.7599 | 6 | 1939 | [12 empty] | Upper Bonnington |  | Lower Bonnington
| Wahleach | Hydro_daily | 65 | 100% | 65 | 33.12% | 188.5618 | 1 | [13 empty] | Jones Lake |  |  |  | Jones | 45 | 52.5 | 51 |  |  |  | 5 | 5 | 4 | 5 | 10 | 12 | 9 | 5 | 4 | 5 | 7 | 6
| Walter Hardman | Hydro_daily | 8 | 100% | 8 | 33.12% | 23.2076 | 2 | [13 empty] | Walter Hardman |  | Arrow |  | Walter Hardman | 698 | 701.95 | 701.16 |  |  |  | 4.021 | 3.4605 | 3.5827 | 5.313 | 12.9559 | 19.9183 | 15.3141 | 9.4376 | 6.0215 | 5.9564 | 5.7525 | 4.2665
| Waneta | Hydro_daily | 480 | 100% | 480 | 33.12% | 1392.4565 | 4 | [13 empty] | Waneta |  | Columbia (U.S.) | 08NE058 | Waneta | 458.1 | 462.7 | 461.78 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 08NE058 is flow at the international border
| Waneta Expansion | Hydro_daily | 335 | 100% | 335 | 56.73% | 1664.9186 | 2 | [13 empty] | Waneta |  | Columbia (U.S.) | 08NE058 | [20 empty] | 08NE058 is flow at the international border
| Whatshan | Hydro_daily | 54 | 100% | 54 | 33.12% | 156.6514 | 1 | [13 empty] | Whatshan |  | Arrow |  | Whatshan | 634 | 641.3 | 639.58 |  |  |  | 4.021 | 3.4605 | 3.5827 | 5.313 | 12.9559 | 19.9183 | 15.3141 | 9.4376 | 6.0215 | 5.9564 | 5.7525 | 4.2665
| Zeballos Lake | Hydro_daily | 21.85 | 100% | 21.85 | 56.73% | 108.59 | 3 | 1972
General Notes:
Hydroelectric generation type has been estimated based on available information concerning operations, reservoir size and operations, facility location and design flows.
The WSC# refers to the Water Survey of Canada Hydrometric station

## HydroRenewals
BC | HYDROELECTRIC RENEWAL |  | Existing Design | [7 empty] | Renewal Design | [14 empty] | Costs |  | 1.77% | 1.05 |  |  | 7% | 70
| Existing Project Name | Owner | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Start Year | Renewal Project Name | Renewal Project Code | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Additional Annual Energy | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed Cost Existing Project | Fixed Cost Renewed Project | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
|  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) | [5 empty] | dd.dddd | dd.dddd |  |  |  |  | (km) |  |  | (MW) | (MW) | (GWh/year) | ($2017M) | ($2018M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M/year) | ($/kW-year) | ($/year) | ($/year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
| Shuswap | BC Hydro | hydro_daily | 6 | 100% | 6 | 33.12% | 17.41 | 1 | 1929 | Shushwap Refurbishment | RN_SHU | Kamloops | 50.296 | -118.8133 | BritishColumbia.a | Ashton Creek | BC_ACK_SUB | 2.4 | 0 | hydro_daily | hydro_daily | 3 | 3 |  | 6 | 6.138 | 0.10864 | 1.0019 | 7.2485 | 0.73135 | 7.9799 | 0.56354 | 187.8454 | 1059814.91 | 1276085.6407 | 72090.2436 | 9.2375 | 6.428 | 15.6655 | 85 |  | 5 | 8
| Falls River | BC Hydro | hydro_daily | 7 | 100% | 7 | 33.12% | 20.3067 | 2 | 1930 | Falls River Redevelopment | RN_FSR | North Coast | 53.9835 | -129.7342 | BritishColumbia.a | Falls River GS | BC_FLS_GEN | 6.6 | 0 | hydro_daily | hydro_daily | 24 | 24 | 170 | 260 | 265.9816 | 4.7079 | 43.4139 | 314.1033 | 9.4308 | 323.5341 | 22.8478 | 951.9927 | 1137343.5126 | 2248435.3682 | 46295.494 | 4.1656 | 6.428 | 10.5936 | 381 | 54 | 5 | 8 | Requires raising height of dam
| Alouette | BC Hydro | Hydro_daily | 9 | 100% | 9 | 33.12% | 26.1086 | 1 | 1928 | Alouette Redevelopment | RN_ALO | Lower Mainland | 49.3721 | -122.3124 | BritishColumbia.a | Alouette GS | BC_ALU_GEN | 6.8 | 0 | hydro_daily | hydro_daily | 21 | 21 | 61 | 160 | 163.681 | 2.8972 | 26.7162 | 193.2944 | 6.7843 | 200.0786 | 14.1295 | 672.8314 | 1276085.6407 | 2214921.2361 | 44706.4569 | 4.3841 | 6.428 | 10.8121 | 103 | 35 | 5 | 8 | CHECK for 2018 update study
| Elko | BC Hydro | hydro_daily | 12 | 100% | 12 | 33.12% | 34.8114 | 2 | 1924 | Elko Redevelopment | RN_ELK | Columbia | 49.2901 | -115.1046 | BritishColumbia.a | Elko GS | BC_ELK_GEN | 6.6 | 0 | hydro_daily | hydro_daily | 21 | 21 | 125 | 180.1 | 184.2434 | 3.2611 | 30.0725 | 217.577 | 7.3514 | 224.9284 | 15.8843 | 756.3969 | 1455800.1611 | 2313748.429 | 40854.6794 | 4.3841 | 6.428 | 10.8121 | 395 | 66 | 5 | 8
| Puntledge | BC Hydro | hydro_daily | 24 | 100% | 24 | 33.12% | 69.6228 | 1 | 1912 | Puntledge Additional Unit | RN_PUN | Vancouver Island | 49.665 | -125.0939 | BritishColumbia.a | Puntledge GS | BC_PUN_GEN | 13.8 | 0 | hydro_daily | hydro_daily | 10 | 10 | 18 | 115 | 117.6457 | 2.0823 | 19.2023 | 138.9303 | 5.4226 | 144.3529 | 10.1941 | 1019.4134 | 1999739.8499 | 2345600.7748 | 34586.0925 | 5.825 | 6.428 | 12.253 | 89 | 49 | 5 | 8
| Lajoie | BC Hydro | hydro_daily | 25 | 100% | 25 | 33.12% | 72.5238 | 1 | 1957 | Lajoie Additional Unit | RN_LAJ | Lillooet | 50.8397 | -122.8559 | BritishColumbia.a | Lajoie GS | BC_LAJ_GEN | 13.8 | 0 | hydro_daily | hydro_daily | 30 | 30 | 80 | 340 | 347.8221 | 6.1565 | 56.772 | 410.7505 | 11.3132 | 422.0637 | 29.8059 | 993.5313 | 2037479.6341 | 2923633.0602 | 29538.4475 | 3.8243 | 6.428 | 10.2523 | 211 | 79 | 5 | 8
| Ash River | BC Hydro | hydro_daily | 28 | 100% | 28 | 33.12% | 81.2266 | 1 | 1958 | Ash River Additional Unit | RN_ASH | Vancouver Island | 49.3734 | -125.1506 | BritishColumbia.a | Ash River GS | BC_ASH_GEN | 13.8 | 0 | hydro_daily | hydro_daily | 9 | 9 | 30 | 101 | 103.3236 | 1.8288 | 16.8646 | 122.0171 | 4.9655 | 126.9825 | 8.9674 | 996.383 | 2146026.7484 | 2438221.4187 | 32466.0745 | 6.0648 | 6.428 | 12.4928 | 188 | 56 | 5 | 8
| Ladore | BC Hydro | hydro_daily | 47 | 100% | 47 | 33.12% | 136.3447 | 2 | 1956 | Ladore Additional Unit | RN_LAD | Vancouver Island | 50.0173 | -125.393 | BritishColumbia.a | Ladore Falls GS | BC_LDR_GEN | 13.8 | 0 | hydro_daily | hydro_daily | 9 | 9 | 8 | 11 | 11.2531 | 0.19918 | 1.8367 | 13.289 | 1.1033 | 14.3923 | 1.0164 | 112.931 | 2720555.3829 | 2947860.0994 | 25256.0796 | 6.0648 | 6.428 | 12.4928 | 188 | 170 | 5 | 8
| Seton | BC Hydro | hydro_daily | 48 | 100% | 48 | 33.12% | 139.2457 | 1 | 1956 | Seton Unit Upgrade | RN_SET | Lillooet | 50.6727 | -121.9241 | BritishColumbia.a | Seton Lake GS | BC_SON_GEN | 13.8 | 0 | hydro_daily | hydro_daily | 2 | 2 |  | 20 | 20.4601 | 0.36214 | 3.3395 | 24.1618 | 1.6552 | 25.817 | 1.8232 | 911.5916 | 2746915.1153 | 2798755.8503 | 25920.3675 | 10.7895 | 6.428 | 17.2175 | 420 |  | 5 | 8
| Wahleach | BC Hydro | hydro_daily | 65 | 100% | 65 | 33.12% | 188.5618 | 1 | 1952 | Wahleach Additional Units | RN_WAH | Lower Mainland | 49.2366 | -121.6807 | BritishColumbia.a | Wahleach GS | BC_WAH_GEN | 13.8 | 0 | hydro_daily | hydro_daily | 14 | 14 |  | 5.8 | 5.9334 | 0.10502 | 0.96846 | 7.0069 | 0.71472 | 7.7216 | 0.5453 | 38.9499 | 3156102.2857 | 3451039.7387 | 21066.9609 | 5.1207 | 6.428 | 11.5487 | 21 |  | 5 | 8
| Seven Mile | BC Hydro | hydro_daily | 805 | 100% | 805 | 33.12% | 2335.2657 | 4 | 1979 | Seven Mile Turbine Upgrades | RN_SEV | Columbia | 49.0302 | -117.5041 | BritishColumbia.a | Seven Mile GS | BC_SEV_GEN | 13.8 | 0 | hydro_daily | hydro_daily | 48 | 48 | 89 | 137 | 140.1518 | 2.4807 | 22.8758 | 165.5083 | 6.1063 | 171.6146 | 12.1193 | 252.4863 | 9992893.6544 | 10261513.2129 | 5596.2408 | 3.1943 | 6.428 | 9.6223 | 120 | 65 | 5 | 8
| Revelstoke | BC Hydro | hydro_monthly | 2500 | 100% | 2500 | 40.18% | 8799.8518 | 6 | 1984 | Revelstoke 6 | RN_REV | Columbia | 51.0486 | -118.1939 | BritishColumbia.a | Revelstoke GS | BC_REV_GEN | 16 | 0 | hydro_monthly | hydro_monthly | 488 | 488 | 26 | 669 | 684.3911 | 12.1137 | 111.7072 | 808.2121 | 17.906 | 826.118 | 58.3401 | 119.5493 | 16791646.2501 | 18220532.4528 | 2928.0455 | 1.3141 | 6.428 | 7.7421 | 46 | n/a | 5 | 8
| G.M. Shrum | BC Hydro | hydro_monthly | 3050 | 100% | 3050 | 60.06% | 16047.45 | 10 | 1968 | GMS Units 1-5 Capacity Increase | RN_GMS | Peace River | 56.0148 | -122.1957 | BritishColumbia.a | GM Shrum GS | BC_GMS_GEN | 13.8 | 0 | hydro_monthly | hydro_monthly | 100 | 100 | 0 | 41.9545 | 42.9198 | 0.75968 | 7.0054 | 50.6849 | 2.736 | 53.4209 | 3.7726 | 37.7256 | 18392725.0558 | 18666503.9288 | 2737.7887 | 2.4115 | 6.428 | 8.8395 | 39 | n/a | 5 | 8 | Direct Capital Cost ratiod from 220 MW UCC
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroGreenfield
BC | HYDROELECTRIC GREENFIELD | [10 empty] | DESIGN | [6 empty] | COSTS |  | 2% | 1.05 |  |  | 7% | 70
| Project Name | Project Code | Owner | Location (River) | Latitude | Longitude | COPPER Balancing Area | Distance to Market Grid | Connecting Node Name | Connecting Node Code | Substation Voltage | Generation Type | Generation Type - COPPER | Installed Capacity | Effective Capacity | Average Annual Energy - Plant | Capacity Factor | # of units | Total Capital Cost | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Construction Time | Development Time | Notes
[8 empty] | (km) |  |  | (kV) |  |  | (MW) | (MW) | (GWh/year) | (%) |  | ($2008M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | (years) | (years)
| Beavercrow | GF_BVR | BC Hydro | Liard River |  |  | British Columbia.a | 700 |  |  |  | hydro_monthly | hydro_monthly | 1128 | 1128 | 6485 | 65.63% | 6 | 7647.4 | 12502.0795 | 250.0416 | 4541.0611 | 17293.1821 | 715.2818 | 18008.4639 | 1271.7492 | 1127.4372 | 10339.1591 | 0.95337 | 6.428 | 7.3814 | 11 | 20 | Average annual energy proportioned
| Border | GF_BOR | BC Hydro | Columbia River |  |  | British Columbia.a | 25 |  |  |  | hydro_daily | hydro_daily | 275 | 275 | 1418 | 58.86% | 5 | 1803.4 | 2948.2242 | 58.9645 | 964.3414 | 3971.5302 | 263.6549 | 4235.1851 | 299.0868 | 1087.5882 | 22218.6891 | 1.6369 | 6.428 | 8.0649 | 10 | 18
| Devil's Gorge | GF_DEV | BC Hydro | Liard River |  |  | British Columbia.a | 700 |  |  |  | hydro_monthly | hydro_monthly | 2490 | 2490 | 14315 | 65.63% | 6 | 6986.5 | 11421.6307 | 228.4326 | 4148.6156 | 15798.6789 | 672.7399 | 16471.4188 | 1163.2038 | 467.1501 | 6731.2653 | 0.70396 | 6.428 | 7.132 | 11 | 20 | Average annual energy proportioned
| Duncan Dam | GF_DUN | BC Hydro | Kootenay River |  |  | British Columbia.a | 25 |  |  |  | hydro_daily | hydro_daily | 30 | 30 | 103 | 39.19% | 0 | 250 | 255.7515 | 0 | 41.0181 | 296.7696 | 45.3724 | 342.1421 | 24.1619 | 805.397 | 73830.7079 | 3.8243 | 6.428 | 10.2523 | 5 | 8 | Project not currently powered
| Elaho River | GF_ELA | BC Hydro | Elaho River |  |  | British Columbia.a | 50 |  |  |  | hydro_daily | hydro_daily | 200 | 200 | 945 | 53.94% | 2 | 1116.8 | 1825.7607 | 36.5152 | 298.6766 | 2160.9525 | 174.4722 | 2335.4247 | 164.9266 | 824.6329 | 26404.5332 | 1.8493 | 6.428 | 8.2773 | 5 | 9
| Hell's Gate | GF_HGT | BC Hydro | Liard River |  |  | British Columbia.a | 700 |  |  |  | hydro_monthly | hydro_monthly | 700 | 700 | 4024 | 65.62% | 4 | 2065 | 3375.8917 | 67.5178 | 762.0309 | 4205.4404 | 274.0921 | 4479.5325 | 316.3425 | 451.9178 | 13390.402 | 1.1445 | 6.428 | 7.5725 | 7 | 13 | Average annual energy proportioned
| Iskut Canyon | GF_ISK | BC Hydro | Iskut River |  |  | British Columbia.a | 150 |  |  |  | hydro_daily | hydro_daily | 810 | 810 | 3548 | 50% | 3 | 2596.4 | 4244.6321 | 84.8926 | 958.1293 | 5287.654 | 320.1581 | 5607.8121 | 396.021 | 488.9149 | 12371.9419 | 1.0823 | 6.428 | 7.5103 | 7 | 13
| McGregor | GF_MCG | BC Hydro | McGregor River |  |  | British Columbia.a | 50 |  |  |  | hydro_monthly | hydro_monthly | 360 | 360 | 1673 | 53.05% | 2 | 1117.4 | 1826.7416 | 36.5348 | 354.6462 | 2217.9227 | 177.5795 | 2395.5022 | 169.1692 | 469.9145 | 19200.8651 | 1.4765 | 6.428 | 7.9045 | 6 | 11 | Average annual energy proportioned
| More Creek | GF_MRC | BC Hydro | Iskut River |  |  | British Columbia.a | 150 |  |  |  | hydro_daily | hydro_daily | 170 | 170 | 745 | 50.03% | 2 | 923.5 | 1509.7511 | 30.195 | 293.1052 | 1833.0513 | 156.0416 | 1989.093 | 140.4688 | 826.2871 | 28835.8951 | 1.968 | 6.428 | 8.396 | 6 | 11
| Mosley Creek | GF_MOS | BC Hydro | Homathko River |  |  | British Columbia.a | 150 |  |  |  | hydro_daily | hydro_daily | 290 | 290 | 1477 | 58.14% | 2 | 1757 | 2872.3689 | 57.4474 | 742.1826 | 3671.9989 | 249.9958 | 3921.9947 | 276.9694 | 955.0669 | 21588.2301 | 1.604 | 6.428 | 8.032 | 8 | 14
| Murphy Creek | GF_MUR | BC Hydro | Columbia River |  |  | British Columbia.a | 25 |  |  |  | hydro_daily | hydro_daily | 275 | 275 | 1794 | 74.47% | 5 | 1543.8 | 2523.8264 | 50.4765 | 652.1238 | 3226.4268 | 228.9917 | 3455.4185 | 244.02 | 887.3455 | 22218.6891 | 1.6369 | 6.428 | 8.0649 | 8 | 14
| Nude Canyon | GF_NUD | BC Hydro | Homathko River |  |  | British Columbia.a | 150 |  |  |  | hydro_daily | hydro_daily | 185 | 185 | 942 | 58.13% | 1 | 926.4 | 1514.492 | 30.2898 | 294.0257 | 1838.8075 | 156.3739 | 1995.1814 | 140.8988 | 761.615 | 27544.1691 | 1.9053 | 6.428 | 8.3333 | 6 | 11 | Average annual energy proportioned
| Site E | GF_STE | BC Hydro | Peace River |  |  | British Columbia.a | 50 |  |  |  | hydro_daily | hydro_daily | 675 | 675 | 3210 | 54.29% | 6 | 2547.7 | 4165.0166 | 83.3003 | 1076.1859 | 5324.5029 | 321.67 | 5646.1729 | 398.7301 | 590.7112 | 13656.9622 | 1.1606 | 6.428 | 7.5886 | 8 | 14
| Waddington | GF_WAD | BC Hydro | Homathko River |  |  | British Columbia.a | 150 |  |  |  | hydro_daily | hydro_daily | 420 | 420 | 2139 | 58.14% | 2 | 1655 | 2705.6178 | 54.1124 | 699.0963 | 3458.8265 | 240.0558 | 3698.8822 | 261.2133 | 621.9365 | 17661.8274 | 1.3918 | 6.428 | 7.8198 | 8 | 14 | Average annual energy proportioned
[19 empty] | Inflation rate: | 1.6348
| Site C - 2008 | [10 empty] | hydro_daily |  | 1132 | 1132 | 5100 |  |  | 4893.5219 | 4893.5219 | 97.8704 | 1264.4222 | 6255.8146 | 358.8408 | 6614.6554 | 467.1238 | 412.6536 | 10319.3416 | 0.95207 | 6.428 | 7.3801 | 8 | 14
| Site C - 2018 | [10 empty] | hydro_daily |  | 1132 | 1132 | 5100 |  |  |  | 8000 | 160 | 2067.0956 | 10227.0956 | 500.8628 | 10727.9585 | 757.6034 | 669.2609 | 10319.3416 | 0.95207 | 6.428 | 7.3801 | 8 | 14
Specific Notes:
Total capital costs for the above lare-scale projects inflated from 2008 to 2018 similarly to increase in Site C total costs from $6.6 billion to $10.7 billion over the same period, or 63% of total capital cost in 2008.
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to didtance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume Hydro_daily and Hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 2.00% of total capital costs (inclusive of contingencies, as they are above)
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroPS
BC | HYDROELECTRIC PUMPED STORAGE |  | Existing Design | [7 empty] | Pumped Storage Design | [14 empty] | Reservoir Design | [13 empty] | COSTS | 1.77% | 1.05 |  |  | 7% | 70
| Existing Project Name | Owner | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Start Year | Pumped Storage Project Name | Project Code | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Estimated Round Trip Efficiency | Salt/Fresh | Reservoir Types | Reservoir Storage | Storage Requirement | Gross Head | Penstock | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping), 70% of Generation Flow | Turbine Type | Pump Type | Pumping Duration at Peak Output | Generation Duration at Peak Output | Total Footprint | Total Capital Cost | Capital Overhead | Interest During Construction | Loaded Capital (Implementation) Cost | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per KW | Fixed Cost | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Cost of Capacity | Unit Cost of Stored Energy | Levelized Cost | Construction Time | Development Time | Notes
|  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) | [5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) |  |  |  | (m3) | (MWh) | (m) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($2018M) | ($M) | ($M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($M/year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2018/MW) | ($2018/MWh) | ($2018/kW-year) | (years) | (years)
| Mica | BC Hydro | Hydro_monthly | 2971 | 100% | 2971 | 44.94% | 11695.8911 | 6 |  | Mica Pumped Storage | PS_MIC | MICA | 52.0759 | -118.5705 | British Columbia.a | Mica GS | BC_MCA_GEN | 500 | 25 | Hydro_pump | hydro_pump | 500 | 465 | 80% | Fresh | Lake to Lake | [12 empty] | 752.8302 | 13.3251 | 122.878 | 889.0333 | 19.102 | 908.1353 | 64.1321 | 128.2642 | 3.9557 | 7911.4456 | 1 | 0 | 1 |  |  |  | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Alberni Inlet | PS_BC001 | Vancouver Island | 48.9998 | -124.8961 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 5536332 | 6000 | 500 |  | 0.26 | 256 | 179 | Single-Stage | Single-Stage | 8.6 | 6 | 299 | 2755.9573 |  |  | 3131.9861 | 112.2114 | 3244.1976 | 229.1037 | 229.1037 | 55.1191 | 55119.1462 | 1 | 0 | 1 | 3131985.7315 | 521997.6219 | 191.2566 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Albert | PS_BC002 | Lower Mainland | 50.1903 | -123.9383 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 1657584 | 6000 | 1670 |  | 0.73 | 77 | 54 | Multi-Stage | Multi-Stage | 8.6 | 6 | 43 | 2104.5968 |  |  | 2391.7526 | 93.4532 | 2485.2057 | 175.5041 | 175.5041 | 42.0919 | 42091.9365 | 1 | 0 | 1 | 2391752.8963 | 398625.6736 | 145.4466 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Alouette-Stave | PS_BC003 | Lower Mainland | 49.382 | -122.3038 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 68528941 | 6000 | 42 |  | 0.03 | 3173 | 2221 | Single-Stage | Single-Stage | 8.6 | 6 | 35.6 | 3045.5828 |  |  | 3461.1288 | 120.0821 | 3581.2109 | 252.9034 | 252.9034 | 30.4558 | 30455.8288 | 1 | 0 | 1 | 3461129.1484 | 576855.0489 | 211.2984 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Altwood | PS_BC004 | Lower Mainland | 50.3169 | -124.6654 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 6291287 | 6000 | 440 |  | 0.34 | 291 | 204 | Single-Stage | Single-Stage | 8.6 | 6 | 30 | 2008.3905 |  |  | 2282.4197 | 90.5333 | 2372.953 | 167.5768 | 167.5768 | 40.1678 | 40167.8106 | 1 | 0 | 1 | 2282419.4101 | 380403.6168 | 139.7204 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Amor | PS_BC005 | Lower Mainland | 50.5649 | -124.9921 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2563117 | 6000 | 1080 |  | 0.45 | 119 | 83 | Multi-Stage | Multi-Stage | 8.6 | 6 | 59 | 1985.1155 |  |  | 2255.9689 | 89.8202 | 2345.7891 | 165.6585 | 165.6585 | 39.7023 | 39702.3092 | 1 | 0 | 1 | 2255968.7393 | 375994.4081 | 137.4299 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Andesite-16 | PS_BC006 | 2L99 | 54.409 | -129.268 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 10964631 | 16000 | 700 |  | 0.12 | 190 | 133 | Single-Stage | Single-Stage | 22.9 | 16 | 102 | 1811.7265 |  |  | 2058.9225 | 84.4202 | 2143.3426 | 151.3618 | 151.3618 | 18.0913 | 18091.2694 | 1 | 0 | 1 | 1811726.6528 | 113233.059 | 125.6338 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Andesite-48 | PS_BC007 | 2L99 | 54.384 | -129.186 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 16446946 | 24000 | 700 |  | 0.12 | 95 | 67 | Single‐Stage | Single‐Stage | 68.6 | 48 | 175.3 | 2742.5168 |  |  | 3116.7117 | 111.8399 | 3228.5516 | 227.9988 | 455.9976 | 41.0888 | 82177.5709 | 1 | 0 | 1 | 5485033.7926 | 114271.7998 | 380.4517 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Annis | PS_BC008 | Lower Mainland | 49.7497 | -124.0434 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 8650519 | 6000 | 320 |  | 0.64 | 400 | 280 | Single-Stage | Single-Stage | 8.6 | 6 | 62 | 2062.7473 |  |  | 2344.1931 | 92.1884 | 2436.3815 | 172.0561 | 172.0561 | 41.2549 | 41254.9462 | 1 | 0 | 1 | 2344192.9959 | 390699.4053 | 143.1561 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Antimony - John George | PS_BC009 | Lower Mainland | 50.1307 | -121.8491 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3853033 | 6000 | 747 |  | 0.17 | 178 | 125 | Multi-Stage | Multi-Stage | 8.6 | 6 | 35.4 | 1474.4824 |  |  | 1675.664 | 73.411 | 1749.075 | 123.5188 | 123.5188 | 14.7448 | 14744.8243 | 1 | 0 | 1 | 1675664.2003 | 279276.985 | 102.2707 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Appleton | PS_BC010 | Lower Mainland | 49.95 | -124.5491 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Man Made | 7495353 | 6000 | 384 |  | 0.77 | 347 | 243 | Single-Stage | Single-Stage | 8.6 | 6 | 34.5 | 1956.6031 |  |  | 2223.5663 | 88.943 | 2312.5093 | 163.3083 | 163.3083 | 19.566 | 19566.0306 | 1 | 0 | 1 | 2223566.2094 | 370594.5591 | 135.712 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Appolina | PS_BC011 | Lower Mainland | 50.9128 | -126.3244 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2611477 | 6000 | 1060 |  | 0.96 | 121 | 85 | Multi-Stage | Multi-Stage | 8.6 | 6 | 48 | 1968.513 |  |  | 2237.1012 | 89.3099 | 2326.4111 | 164.29 | 164.29 | 39.3703 | 39370.2592 | 1 | 0 | 1 | 2237100.762 | 372850.6996 | 136.2846 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Aveling | PS_BC012 | 2L99 | 54.221 | -128.883 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 11629154 | 16000 | 660 |  | 0.24 | 202 | 141 | Single-Stage | Single-Stage | 22.9 | 16 | 172.1 | 2302.5778 |  |  | 2616.7465 | 99.3304 | 2716.077 | 191.8081 | 191.8081 | 23.0058 | 23005.7619 | 1 | 0 | 1 | 2302578.083 | 143910.8439 | 159.7622 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Battle - Fraser | PS_BC013 | Lower Mainland | 50.6918 | -126.3272 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 12513980 | 6000 | 230 |  | 0.06 | 579 | 406 | Single-Stage | Single-Stage | 8.6 | 6 | 38.5 | 1911.9146 |  |  | 2172.7804 | 87.5597 | 2260.3401 | 159.6242 | 159.6242 | 19.1191 | 19119.1464 | 1 | 0 | 1 | 2172780.1425 | 362130.0238 | 132.6198 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Battle - Loose | PS_BC014 | Lower Mainland | 50.7503 | -126.3794 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 10466238 | 6000 | 275 |  | 0.1 | 485 | 339 | Single-Stage | Single-Stage | 8.6 | 6 | 29.4 | 1734.2806 |  |  | 1970.9096 | 81.9549 | 2052.8645 | 144.9723 | 144.9723 | 17.3428 | 17342.8056 | 1 | 0 | 1 | 1970909.3921 | 328484.8987 | 120.2511 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Beavertail - Campbell | PS_BC015 | Vancouver Island | 50.0119 | -125.5207 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 15148503 | 3000 | 95 |  | 0.03 | 701 | 491 | Single-Stage | Single-Stage | 8.6 | 6 | 37.8 | 1755.2382 |  |  | 1994.7267 | 82.6254 | 2077.3521 | 146.7016 | 293.4033 | 26.3286 | 52657.1449 | 1 | 0 | 1 | 3989453.1258 | 664908.6634 | 243.4799 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Berkeley - Heydon | PS_BC016 | Lower Mainland | 50.556 | -125.6416 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3777186 | 6000 | 762 |  | 0.17 | 175 | 122 | Multi-Stage | Multi-Stage | 8.6 | 6 | 24.1 | 1753.0737 |  |  | 1992.2669 | 82.5563 | 2074.8232 | 146.523 | 146.523 | 17.5307 | 17530.7376 | 1 | 0 | 1 | 1992267.1407 | 332044.3326 | 121.6254 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Berkely - Glendale | PS_BC017 | Lower Mainland | 50.6159 | -125.6375 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3969952 | 6000 | 725 |  | 0.18 | 184 | 129 | Multi-Stage | Multi-Stage | 8.6 | 6 | 27.2 | 1422.2287 |  |  | 1616.2806 | 71.6359 | 1687.9165 | 119.1999 | 119.1999 | 14.2223 | 14222.2861 | 1 | 0 | 1 | 1616280.7493 | 269379.7431 | 98.6059 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Big Falls | PS_BC018 | 2L101 | 53.976 | -129.557 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 95940517 | 24000 | 120 |  | 0.01 | 555 | 389 | Single‐Stage | Single‐Stage | 68.6 | 48 | 253.5 | 2361.7597 |  |  | 2684.0033 | 101.0553 | 2785.0587 | 196.6795 | 393.3591 | 35.3868 | 70773.6395 | 1 | 0 | 1 | 4723519.9405 | 98406.6654 | 327.6557 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Blinch - Stave | PS_BC019 | Lower Mainland | 49.4385 | -122.2268 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4195649 | 6000 | 686 |  | 0.18 | 194 | 136 | Single-Stage | Single-Stage | 8.6 | 6 | 25.1 | 1342.3669 |  |  | 1525.5224 | 68.8817 | 1594.4041 | 112.5961 | 112.5961 | 13.4237 | 13423.6685 | 1 | 0 | 1 | 1525522.0567 | 254253.2944 | 93.1087 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Bobs | PS_BC020 | Lower Mainland | 49.6206 | -124.2702 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 4325260 | 6000 | 640 |  | 0.28 | 200 | 140 | Single-Stage | Single-Stage | 8.6 | 6 | 65 | 1769.9493 |  |  | 2011.445 | 83.0946 | 2094.5396 | 147.9154 | 147.9154 | 35.399 | 35398.9857 | 1 | 0 | 1 | 2011445.4804 | 335240.7225 | 122.5416 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Bookhout - Great Central | PS_BC021 | Vancouver Island | 49.3301 | -125.1041 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3327417 | 6000 | 865 |  | 0.46 | 154 | 108 | Multi-Stage | Multi-Stage | 8.6 | 6 | 46.3 | 1697.9706 |  |  | 1929.6455 | 80.7869 | 2010.4323 | 141.9758 | 141.9758 | 16.9797 | 16979.7067 | 1 | 0 | 1 | 1929644.9254 | 321607.6784 | 117.7316 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Bookhout 2 | PS_BC022 | Vancouver Island | 49.3267 | -125.0592 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 4082575 | 6000 | 705 |  | 0.54 | 189 | 132 | Multi-Stage | Multi-Stage | 8.6 | 6 | 45.5 | 1422.6491 |  |  | 1616.7584 | 71.6502 | 1688.4086 | 119.2346 | 119.2346 | 14.2265 | 14226.4903 | 1 | 0 | 1 | 1616758.3181 | 269459.9106 | 98.7205 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Boomerang - Hibbard | PS_BC023 | Lower Mainland | 51.0345 | -127.0308 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 28782155 | 6000 | 100 |  | 0.04 | 1333 | 933 | Single-Stage | Single-Stage | 8.6 | 6 | 52.8 | 2423.9105 |  |  | 2754.6342 | 102.8519 | 2857.486 | 201.7943 | 201.7943 | 24.2391 | 24239.1057 | 1 | 0 | 1 | 2754634.2033 | 459105.1279 | 168.1226 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Bradburn - Forbes1 | PS_BC024 | Lower Mainland | 50.2587 | -124.4771 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 7106705 | 6000 | 405 |  | 0.17 | 329 | 230 | Single-Stage | Single-Stage | 8.6 | 6 | 29.9 | 1498.3415 |  |  | 1702.7785 | 74.2148 | 1776.9933 | 125.4904 | 125.4904 | 14.9834 | 14983.4152 | 1 | 0 | 1 | 1702777.9704 | 283796.1375 | 103.8741 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Bradburn - Forbes2 | PS_BC025 | Lower Mainland | 50.2601 | -124.4591 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 9022619 | 6000 | 319 |  | 0.11 | 418 | 292 | Single-Stage | Single-Stage | 8.6 | 6 | 39.6 | 1680.2787 |  |  | 1909.5396 | 80.2149 | 1989.7545 | 140.5155 | 140.5155 | 16.8028 | 16802.7875 | 1 | 0 | 1 | 1909540.0793 | 318256.6799 | 116.5863 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Bradburn - Powell | PS_BC026 | Lower Mainland | 50.2029 | -124.4044 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2692437 | 6000 | 1069 |  | 0.18 | 125 | 87 | Multi-Stage | Multi-Stage | 8.6 | 6 | 27.9 | 1653.5724 |  |  | 1879.1894 | 79.3477 | 1958.5371 | 138.311 | 138.311 | 16.5357 | 16535.7235 | 1 | 0 | 1 | 1879189.8356 | 313198.1151 | 114.6394 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Breg | PS_BC027 | Lower Mainland | 50.3133 | -124.8196 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 3295436 | 6000 | 840 |  | 0.53 | 153 | 107 | Multi-Stage | Multi-Stage | 8.6 | 6 | 56 | 2005.6081 |  |  | 2279.2577 | 90.4482 | 2369.7059 | 167.3475 | 167.3475 | 40.1122 | 40112.1629 | 1 | 0 | 1 | 2279257.3776 | 379876.8022 | 138.5751 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Burley | PS_BC028 | Lower Mainland | 50.9002 | -126.7642 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 3075740 | 6000 | 900 |  | 1 | 142 | 100 | Multi-Stage | Multi-Stage | 8.6 | 6 | 46 | 1885.9119 |  |  | 2143.2298 | 86.7501 | 2229.9799 | 157.4801 | 157.4801 | 37.7182 | 37718.2375 | 1 | 0 | 1 | 2143229.2826 | 357205.4531 | 130.5584 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Burwell - Seymour | PS_BC029 | Lower Mainland | 49.4474 | -122.9689 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 6085022 | 6000 | 473 |  | 0.24 | 282 | 197 | Single-Stage | Single-Stage | 8.6 | 6 | 27 | 1347.9627 |  |  | 1531.8817 | 69.0764 | 1600.9581 | 113.0589 | 113.0589 | 13.4796 | 13479.6265 | 1 | 0 | 1 | 1531881.6244 | 255313.7949 | 93.4523 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Butchart - Goldstream | PS_BC030 | Vancouver Island | 48.5146 | -123.6329 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 12735467 | 3000 | 113 |  | 0.05 | 590 | 413 | Single-Stage | Single-Stage | 8.6 | 6 | 52.6 | 1693.3155 |  |  | 1924.3552 | 80.6366 | 2004.9918 | 141.5916 | 283.1831 | 25.3997 | 50799.4662 | 1 | 0 | 1 | 3848710.0406 | 641451.6734 | 234.8906 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Butchart - Sooke | PS_BC031 | Vancouver Island | 48.5664 | -123.6772 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 7437249 | 6000 | 387 |  | 0.12 | 344 | 241 | Single-Stage | Single-Stage | 8.6 | 6 | 26.8 | 1588.7794 |  |  | 1805.5559 | 77.225 | 1882.7809 | 132.9611 | 132.9611 | 15.8878 | 15887.7943 | 1 | 0 | 1 | 1805556.0512 | 300925.6268 | 110.173 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Calder | PS_BC032 | Lower Mainland | 49.9015 | -123.9536 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 3504008 | 6000 | 790 |  | 0.56 | 162 | 114 | Multi-Stage | Multi-Stage | 8.6 | 6 | 56 | 2008.8725 |  |  | 2282.9674 | 90.548 | 2373.5155 | 167.6165 | 167.6165 | 40.1775 | 40177.4501 | 1 | 0 | 1 | 2282967.9844 | 380494.0914 | 139.7204 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Camp | PS_BC033 | Lower Mainland | 50.6404 | -125.9618 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2768166 | 6000 | 1000 |  | 0.83 | 128 | 90 | Multi-Stage | Multi-Stage | 8.6 | 6 | 47 | 2043.9476 |  |  | 2322.8283 | 91.6176 | 2414.4459 | 170.507 | 170.507 | 40.879 | 40878.9529 | 1 | 0 | 1 | 2322828.3758 | 387137.6809 | 142.0109 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Camp Cove | PS_BC034 | Lower Mainland | 49.3698 | -121.8394 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 7800042 | 6000 | 369 |  | 0.34 | 361 | 253 | Single-Stage | Single-Stage | 8.6 | 6 | 65.9 | 1439.0703 |  |  | 1635.4202 | 72.2103 | 1707.6305 | 120.5921 | 120.5921 | 14.3907 | 14390.703 | 1 | 0 | 1 | 1635420.1505 | 272570.4068 | 99.8657 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Caren | PS_BC035 | Lower Mainland | 49.6212 | -123.8427 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 3145643 | 6000 | 880 |  | 0.33 | 146 | 102 | Multi-Stage | Multi-Stage | 8.6 | 6 | 409 | 3362.3519 |  |  | 3821.1185 | 128.4195 | 3949.5379 | 278.9145 | 278.9145 | 67.247 | 67247.0376 | 1 | 0 | 1 | 3821118.7018 | 636853.4987 | 233.6308 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Carpenter - Seton | PS_BC036 | Lower Mainland | 50.7309 | -122.2383 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4321645 | 6000 | 666 |  | 0.14 | 200 | 140 | Single-Stage | Single-Stage | 8.6 | 6 | 20.9 | 1449.8982 |  |  | 1647.7255 | 72.5784 | 1720.3039 | 121.487 | 121.487 | 14.499 | 14498.9817 | 1 | 0 | 1 | 1647725.851 | 274620.4025 | 100.5529 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Cataract Lake | PS_BC037 | Vancouver Island | 48.9884 | -125.1954 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 5126233 | 6000 | 540 |  | 0.22 | 237 | 166 | Single-Stage | Single-Stage | 8.6 | 6 | 190 | 2337.6783 |  |  | 2656.6362 | 100.3552 | 2756.9913 | 194.6974 | 194.6974 | 46.7536 | 46753.5649 | 1 | 0 | 1 | 2656636.3918 | 442772.732 | 162.6254 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Centre - Lower Eldrid | PS_BC038 | Lower Mainland | 50.1603 | -124.143 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3128495 | 6000 | 920 |  | 0.46 | 145 | 101 | Multi-Stage | Multi-Stage | 8.6 | 6 | 35.2 | 1593.6526 |  |  | 1811.0941 | 77.3856 | 1888.4797 | 133.3635 | 133.3635 | 15.9365 | 15936.5269 | 1 | 0 | 1 | 1811094.4754 | 301848.6975 | 110.5165 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Chickwat - Lower Tzoonie | PS_BC039 | Lower Mainland | 49.879 | -123.6216 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2361128 | 6000 | 1219 |  | 0.37 | 109 | 77 | Multi-Stage | Multi-Stage | 8.6 | 6 | 32 | 1546.9392 |  |  | 1758.0069 | 75.8394 | 1833.8463 | 129.5054 | 129.5054 | 15.4694 | 15469.3913 | 1 | 0 | 1 | 1758006.4581 | 293001.649 | 107.3098 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Chimdemash-16 | PS_BC040 | 2L99 | 54.615 | -128.22 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 12792069 | 16000 | 600 |  | 0.2 | 222 | 155 | Single-Stage | Single-Stage | 22.9 | 16 | 115.4 | 1962.8619 |  |  | 2230.679 | 89.1359 | 2319.8149 | 163.8242 | 163.8242 | 19.6085 | 19608.4952 | 1 | 0 | 1 | 1962861.7274 | 122679.0727 | 136.1701 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Chimdemash-48 | PS_BC041 | 2L99 | 54.593 | -128.195 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 19188103 | 24000 | 600 |  | 0.2 | 111 | 78 | Single‐Stage | Single‐Stage | 68.6 | 48 | 211.3 | 3463.037 |  |  | 3935.5413 | 131.0159 | 4066.5572 | 287.1783 | 574.3567 | 51.8867 | 103773.3022 | 1 | 0 | 1 | 6926074.2665 | 144293.357 | 480.432 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Chusan - Daniels | PS_BC042 | Lower Mainland | 50.4107 | -124.3022 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 11795965 | 6000 | 244 |  | 0.19 | 546 | 382 | Single-Stage | Single-Stage | 8.6 | 6 | 33.1 | 1556.6662 |  |  | 1769.0612 | 76.1626 | 1845.2237 | 130.3088 | 130.3088 | 15.5667 | 15566.663 | 1 | 0 | 1 | 1769061.5467 | 294843.2094 | 107.997 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Chusan - Upper Powell | PS_BC043 | Lower Mainland | 50.4104 | -124.2566 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 13263666 | 6000 | 217 |  | 0.06 | 614 | 430 | Single-Stage | Single-Stage | 8.6 | 6 | 44.5 | 2020.1752 |  |  | 2295.8123 | 90.8933 | 2386.7057 | 168.548 | 168.548 | 20.2018 | 20201.7526 | 1 | 0 | 1 | 2295811.9519 | 382635.7071 | 140.064 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Clover - Powell | PS_BC044 | Lower Mainland | 50.0758 | -124.4829 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 37379422 | 6000 | 77 |  | 0.06 | 1731 | 1211 | Single-Stage | Single-Stage | 8.6 | 6 | 64.8 | 2652.243 |  |  | 3014.1208 | 109.329 | 3123.4498 | 220.5765 | 220.5765 | 26.5224 | 26522.4299 | 1 | 0 | 1 | 3014121.2856 | 502353.1659 | 183.927 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Clowhom 1 | PS_BC045 | Lower Mainland | 49.7166 | -123.5418 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3671193 | 6000 | 784 |  | 0.3 | 170 | 119 | Multi-Stage | Multi-Stage | 8.6 | 6 | 36.7 | 1866.1106 |  |  | 2120.7268 | 86.1311 | 2206.8579 | 155.8473 | 155.8473 | 18.6611 | 18661.1052 | 1 | 0 | 1 | 2120726.2851 | 353454.7626 | 129.4131 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Colvin | PS_BC046 | Lower Mainland | 49.4898 | -123.9073 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 15378700 | 6000 | 180 |  | 0.13 | 712 | 498 | Single-Stage | Single-Stage | 8.6 | 6 | 160 | 2799.4824 |  |  | 3181.4498 | 113.4106 | 3294.8605 | 232.6815 | 232.6815 | 55.9896 | 55989.6477 | 1 | 0 | 1 | 3181450.181 | 530241.1242 | 194.6923 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Comox 1 | PS_BC047 | Vancouver Island | 49.588 | -125.1734 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3657199 | 6000 | 787 |  | 0.3 | 169 | 119 | Multi-Stage | Multi-Stage | 8.6 | 6 | 46.6 | 2105.3827 |  |  | 2392.6457 | 93.4768 | 2486.1225 | 175.5688 | 175.5688 | 21.0538 | 21053.827 | 1 | 0 | 1 | 2392646.1905 | 398774.556 | 146.0192 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Cosby | PS_BC048 | Lower Mainland | 50.5429 | -125.5644 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 5536332 | 6000 | 500 |  | 0.45 | 256 | 179 | Single-Stage | Single-Stage | 8.6 | 6 | 42 | 1810.5794 |  |  | 2057.6188 | 84.3839 | 2142.0027 | 151.2672 | 151.2672 | 36.2116 | 36211.588 | 1 | 0 | 1 | 2057618.4843 | 342936.7958 | 125.9774 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Crucil | PS_BC049 | Lower Mainland | 49.5458 | -123.7586 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2611477 | 6000 | 1060 |  | 0.23 | 121 | 85 | Multi-Stage | Multi-Stage | 8.6 | 6 | 169 | 2562.1513 |  |  | 2911.7368 | 106.7957 | 3018.5325 | 213.1673 | 213.1673 | 51.243 | 51243.0258 | 1 | 0 | 1 | 2911737.1704 | 485288.9558 | 177.5136 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Davie | PS_BC050 | Lower Mainland | 49.598 | -124.38 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 9227220 | 6000 | 300 |  | 0.2 | 427 | 299 | Single-Stage | Single-Stage | 8.6 | 6 | 84 | 2195.3097 |  |  | 2494.8425 | 96.1672 | 2591.0097 | 182.9759 | 182.9759 | 43.9062 | 43906.1942 | 1 | 0 | 1 | 2494842.4848 | 415806.6991 | 152.3181 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Deserted - Un-named | PS_BC051 | Lower Mainland | 50.1687 | -123.6691 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2756911 | 6000 | 1044 |  | 0.2 | 128 | 89 | Multi-Stage | Multi-Stage | 8.6 | 6 | 33.5 | 1699.1846 |  |  | 1931.025 | 80.8261 | 2011.851 | 142.076 | 142.076 | 16.9918 | 16991.8452 | 1 | 0 | 1 | 1931024.9505 | 321837.8735 | 117.8461 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Diana-16 | PS_BC052 | 2L101 | 54.206 | -130.15 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 1000 | 80% | Fresh | Not stated | 11992565 | 16000 | 320 |  | 0.27 | 208 | 146 | Single-Stage | Single-Stage | 22.9 | 16 | 53.7 | 1044.5092 |  |  | 1187.0244 | 58.1014 | 1245.1257 | 87.9302 | 175.8604 | 20.8619 | 41723.7115 | 1 | 0 | 1 | 2089018.9213 | 130564.112 | 144.874 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Diana-48 | PS_BC053 | 2L101 | 54.205 | -130.168 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 35977694 | 24000 | 320 |  | 0.27 | 208 | 146 | Single‐Stage | Single‐Stage | 68.6 | 48 | 215.2 | 1493.9681 |  |  | 1697.8084 | 74.0678 | 1771.8762 | 125.1291 | 250.2581 | 22.3873 | 44774.6548 | 1 | 0 | 1 | 2987936.3125 | 62248.8641 | 207.2901 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Dinner | PS_BC054 | Lower Mainland | 49.9485 | -124.7192 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 13840830 | 6000 | 200 |  | 0.13 | 641 | 449 | Single-Stage | Single-Stage | 8.6 | 6 | 94 | 2636.35 |  |  | 2996.0593 | 108.8841 | 3104.9435 | 219.2696 | 219.2696 | 52.727 | 52727.0005 | 1 | 0 | 1 | 2996059.5637 | 499343.4515 | 183.2398 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Dodd - Powell | PS_BC055 | Lower Mainland | 50.0209 | -124.3289 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 22140119 | 6000 | 130 |  | 0.03 | 1025 | 718 | Single-Stage | Single-Stage | 8.6 | 6 | 32.8 | 2358.0744 |  |  | 2679.8152 | 100.9483 | 2780.7635 | 196.3762 | 196.3762 | 23.5807 | 23580.7444 | 1 | 0 | 1 | 2679815.0863 | 446635.6568 | 163.5416 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Dodd-Goat | PS_BC056 | Lower Mainland | 50.0247 | -124.2965 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 22140119 | 6000 | 130 |  | 0.03 | 1025 | 718 | Single-Stage | Single-Stage | 8.6 | 6 | 27.7 | 2362.1934 |  |  | 2684.4962 | 101.0679 | 2785.5641 | 196.7152 | 196.7152 | 23.6219 | 23621.9345 | 1 | 0 | 1 | 2684495.7189 | 447415.5714 | 163.8851 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Doran - Great Central | PS_BC057 | Vancouver Island | 49.3424 | -125.289 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4953899 | 6000 | 581 |  | 0.21 | 229 | 161 | Single-Stage | Single-Stage | 8.6 | 6 | 25.5 | 1643.0628 |  |  | 1867.2458 | 79.0052 | 1946.2511 | 137.4433 | 137.4433 | 16.4306 | 16430.6274 | 1 | 0 | 1 | 1867246.0338 | 311207.6723 | 113.9523 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Doran Neighbour | PS_BC058 | Vancouver Island | 49.345 | -125.264 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3685295 | 6000 | 781 |  | 0.33 | 171 | 119 | Multi-Stage | Multi-Stage | 8.6 | 6 | 40.4 | 1755.647 |  |  | 1995.1912 | 82.6385 | 2077.8297 | 146.7354 | 146.7354 | 17.5565 | 17556.469 | 1 | 0 | 1 | 1995190.9614 | 332532.2086 | 121.74 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Downie | PS_BC059 | Lower Mainland | 50.4481 | -125.0482 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 8388382 | 6000 | 330 |  | 0.24 | 388 | 272 | Single-Stage | Single-Stage | 8.6 | 6 | 62 | 1923.6109 |  |  | 2186.0726 | 87.9228 | 2273.9954 | 160.5885 | 160.5885 | 38.4722 | 38472.219 | 1 | 0 | 1 | 2186073.0477 | 364344.9353 | 133.9941 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Elephant - Lois | PS_BC060 | Lower Mainland | 49.8357 | -124.2442 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3718625 | 6000 | 774 |  | 0.22 | 172 | 121 | Multi-Stage | Multi-Stage | 8.6 | 6 | 48.9 | 1857.5208 |  |  | 2110.965 | 85.862 | 2196.8269 | 155.1389 | 155.1389 | 18.5752 | 18575.2081 | 1 | 0 | 1 | 2110965.3278 | 351827.3638 | 128.8405 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Elk Bay | PS_BC061 | Vancouver Island | 50.2786 | -125.4392 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 11072664 | 6000 | 250 |  | 0.06 | 513 | 359 | Single-Stage | Single-Stage | 8.6 | 6 | 190 | 2925.1497 |  |  | 3324.2635 | 116.8399 | 3441.1034 | 243.0091 | 243.0091 | 58.503 | 58502.9939 | 1 | 0 | 1 | 3324263.8764 | 554043.9794 | 202.7091 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Elk Bay South | PS_BC062 | Vancouver Island | 50.2013 | -125.3846 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 3740765 | 6000 | 740 |  | 0.13 | 173 | 121 | Multi-Stage | Multi-Stage | 8.6 | 6 | 152 | 2226.0726 |  |  | 2529.8028 | 97.0793 | 2626.8822 | 185.5092 | 185.5092 | 44.5215 | 44521.4529 | 1 | 0 | 1 | 2529802.3558 | 421633.726 | 154.6086 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Elsie - Ash | PS_BC063 | Vancouver Island | 49.4245 | -125.1069 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 10985555 | 3000 | 131 |  | 0.04 | 509 | 356 | Single-Stage | Single-Stage | 8.6 | 6 | 38.7 | 1594.4721 |  |  | 1812.0254 | 77.4126 | 1889.438 | 133.4312 | 266.8624 | 23.9171 | 47834.1646 | 1 | 0 | 1 | 3624051.1256 | 604008.9027 | 221.1476 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Fawn | PS_BC064 | Lower Mainland | 50.4823 | -125.1136 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 5375080 | 6000 | 515 |  | 0.4 | 249 | 174 | Single-Stage | Single-Stage | 8.6 | 6 | 75 | 1714.6481 |  |  | 1948.5984 | 81.3243 | 2029.9227 | 143.3522 | 143.3522 | 34.293 | 34292.9615 | 1 | 0 | 1 | 1948598.7964 | 324766.2752 | 119.1059 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Florence - Stave | PS_BC065 | Lower Mainland | 49.3579 | -122.3169 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 10063691 | 6000 | 286 |  | 0.37 | 466 | 326 | Single-Stage | Single-Stage | 8.6 | 6 | 41.5 | 1815.3347 |  |  | 2063.023 | 84.5342 | 2147.5572 | 151.6595 | 151.6595 | 18.1533 | 18153.3476 | 1 | 0 | 1 | 2063022.9143 | 343836.9615 | 125.8629 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Foster | PS_BC066 | Lower Mainland | 50.7801 | -126.0257 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 5323396 | 6000 | 520 |  | 0.47 | 246 | 173 | Single-Stage | Single-Stage | 8.6 | 6 | 42 | 1619.7032 |  |  | 1840.6991 | 78.2415 | 1918.9406 | 135.5147 | 135.5147 | 32.3941 | 32394.0642 | 1 | 0 | 1 | 1840699.162 | 306783.5754 | 112.2344 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Freda | PS_BC067 | Lower Mainland | 49.9094 | -124.2844 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Man Made | 14684773 | 6000 | 196 |  | 0.2 | 680 | 476 | Single-Stage | Single-Stage | 8.6 | 6 | 38.3 | 1853.1648 |  |  | 2106.0147 | 85.7253 | 2191.74 | 154.7796 | 154.7796 | 18.5316 | 18531.6485 | 1 | 0 | 1 | 2106014.4164 | 351002.7845 | 128.4969 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Frogpond - Powell | PS_BC068 | Lower Mainland | 50.0282 | -124.4127 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 6396034 | 6000 | 450 |  | 0.2 | 296 | 207 | Single-Stage | Single-Stage | 8.6 | 6 | 21.3 | 1345.2019 |  |  | 1528.7441 | 68.9804 | 1597.7245 | 112.8306 | 112.8306 | 13.452 | 13452.0191 | 1 | 0 | 1 | 1528743.6421 | 254790.4161 | 93.3378 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Gastineau | PS_BC069 | Lower Mainland | 50.357 | -124.7432 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2471577 | 6000 | 1120 |  | 0.35 | 114 | 80 | Multi-Stage | Multi-Stage | 8.6 | 6 | 81 | 2194.8561 |  |  | 2494.327 | 96.1537 | 2590.4808 | 182.9385 | 182.9385 | 43.8971 | 43897.1215 | 1 | 0 | 1 | 2494327.1228 | 415720.8054 | 152.3181 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Gibson | PS_BC070 | Vancouver Island | 49.2792 | -125.1987 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 2855373 | 6000 | 1008 |  | 0.2 | 132 | 93 | Multi-Stage | Multi-Stage | 8.6 | 6 | 44.1 | 1881.5528 |  |  | 2138.2759 | 86.614 | 2224.8899 | 157.1207 | 157.1207 | 18.8155 | 18815.5283 | 1 | 0 | 1 | 2138276.0807 | 356379.7285 | 130.5584 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Goat | PS_BC071 | Lower Mainland | 50.001 | -124.4905 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake | 4928451 | 6000 | 584 |  | 0.39 | 228 | 160 | Single-Stage | Single-Stage | 8.6 | 6 | 27.5 | 1764.4013 |  |  | 2005.14 | 82.9178 | 2088.0578 | 147.4577 | 147.4577 | 17.644 | 17644.013 | 1 | 0 | 1 | 2005139.7394 | 334190.5292 | 122.4271 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Goldstream - Sooke1 | PS_BC072 | Vancouver Island | 48.5207 | -123.6973 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 10504436 | 6000 | 274 |  | 0.05 | 486 | 340 | Single-Stage | Single-Stage | 8.6 | 6 | 37.2 | 1932.4389 |  |  | 2196.105 | 88.1963 | 2284.3013 | 161.3163 | 161.3163 | 19.3244 | 19324.3887 | 1 | 0 | 1 | 2196105.4289 | 366016.9989 | 133.9941 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Goldstream - Sooke2 | PS_BC073 | Vancouver Island | 48.5363 | -123.6973 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 5252218 | 3000 | 274 |  | 0.05 | 243 | 170 | Single-Stage | Single-Stage | 8.6 | 6 | 30.5 | 1341.9856 |  |  | 1525.089 | 68.8684 | 1593.9574 | 112.5645 | 225.129 | 20.1298 | 40259.5656 | 1 | 0 | 1 | 3050178.3051 | 508363.4326 | 186.2175 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Grant | PS_BC074 | Lower Mainland | 49.6228 | -124.2737 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 4464784 | 6000 | 620 |  | 0.34 | 207 | 145 | Single-Stage | Single-Stage | 8.6 | 6 | 32 | 1877.4218 |  |  | 2133.5813 | 86.4849 | 2220.0663 | 156.78 | 156.78 | 37.5484 | 37548.436 | 1 | 0 | 1 | 2133581.7051 | 355596.3782 | 130.5584 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Griffin | PS_BC075 | Lower Mainland | 50.6068 | -125.5573 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 4070832 | 6000 | 680 |  | 0.49 | 188 | 132 | Single-Stage | Single-Stage | 8.6 | 6 | 77 | 1632.4556 |  |  | 1855.1914 | 78.6589 | 1933.8503 | 136.5676 | 136.5676 | 32.6491 | 32649.1123 | 1 | 0 | 1 | 1855191.1428 | 309198.9056 | 113.3797 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Griffin - Glendale | PS_BC076 | Lower Mainland | 50.615 | -125.6219 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4853652 | 6000 | 593 |  | 0.17 | 225 | 157 | Single-Stage | Single-Stage | 8.6 | 6 | 28.9 | 1459.5605 |  |  | 1658.7062 | 72.9062 | 1731.6124 | 122.2856 | 122.2856 | 14.5956 | 14595.6052 | 1 | 0 | 1 | 1658706.4984 | 276450.5104 | 101.24 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Gun - Downton | PS_BC077 | Lower Mainland | 50.8328 | -122.8738 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 21163349 | 6000 | 136 |  | 0.05 | 980 | 686 | Single-Stage | Single-Stage | 8.6 | 6 | 27.2 | 2049.2456 |  |  | 2328.8492 | 91.7786 | 2420.6278 | 170.9436 | 170.9436 | 20.4925 | 20492.4568 | 1 | 0 | 1 | 2328848.9498 | 388142.0643 | 142.1254 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Gun-Carpenter | PS_BC078 | Lower Mainland | 50.8779 | -122.8271 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 13576488 | 6000 | 212 |  | 0.14 | 629 | 440 | Single-Stage | Single-Stage | 8.6 | 6 | 20.5 | 1624.8908 |  |  | 1846.5945 | 78.4114 | 1925.0059 | 135.943 | 135.943 | 16.2489 | 16248.9085 | 1 | 0 | 1 | 1846594.9038 | 307766.1991 | 112.6925 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Gustafson | PS_BC079 | Lower Mainland | 49.6602 | -123.6572 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 1977261 | 6000 | 1400 |  | 0.4 | 92 | 64 | Multi-Stage | Multi-Stage | 8.6 | 6 | 73 | 2078.4643 |  |  | 2362.0545 | 92.6644 | 2454.7189 | 173.3511 | 173.3511 | 41.5693 | 41569.2873 | 1 | 0 | 1 | 2362054.2992 | 393675.9074 | 144.3014 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Halfway | PS_BC080 | Lower Mainland | 49.6181 | -123.8407 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 3025318 | 6000 | 915 |  | 0.51 | 140 | 98 | Multi-Stage | Multi-Stage | 8.6 | 6 | 123 | 2297.3331 |  |  | 2610.7862 | 99.1769 | 2709.9631 | 191.3763 | 191.3763 | 45.9467 | 45946.6614 | 1 | 0 | 1 | 2610786.3482 | 435130.4854 | 159.1896 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Haliday | PS_BC081 | Lower Mainland | 50.9106 | -126.2795 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 3075740 | 6000 | 900 |  | 0.41 | 142 | 100 | Multi-Stage | Multi-Stage | 8.6 | 6 | 57 | 1980.5471 |  |  | 2250.7772 | 89.6799 | 2340.4571 | 165.282 | 165.282 | 39.6109 | 39610.9413 | 1 | 0 | 1 | 2250777.3256 | 375129.7451 | 137.4299 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Hat | PS_BC082 | Lower Mainland | 50.3949 | -124.5447 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2386350 | 6000 | 1160 |  | 0.45 | 110 | 77 | Multi-Stage | Multi-Stage | 8.6 | 6 | 93 | 2117.0569 |  |  | 2405.9127 | 93.8281 | 2499.7408 | 176.5305 | 176.5305 | 42.3411 | 42341.137 | 1 | 0 | 1 | 2405912.7549 | 400984.8865 | 146.5919 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Haynon - Chochiwa | PS_BC083 | Lower Mainland | 50.1003 | -121.8581 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4076793 | 6000 | 706 |  | 0.21 | 189 | 132 | Multi-Stage | Multi-Stage | 8.6 | 6 | 31.8 | 1334.7584 |  |  | 1516.8757 | 68.6166 | 1585.4923 | 111.9667 | 111.9667 | 13.3476 | 13347.5839 | 1 | 0 | 1 | 1516875.4267 | 252812.5711 | 92.5361 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Hays | PS_BC084 | Lower Mainland | 50.3309 | -124.95 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 3460208 | 6000 | 800 |  | 1.07 | 160 | 112 | Multi-Stage | Multi-Stage | 8.6 | 6 | 34 | 2104.8438 |  |  | 2392.0333 | 93.4606 | 2485.4939 | 175.5244 | 175.5244 | 42.0969 | 42096.876 | 1 | 0 | 1 | 2392033.4823 | 398672.6288 | 145.4466 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Heather - Cowichan | PS_BC085 | Vancouver Island | 48.924 | -124.4497 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3484522 | 6000 | 826 |  | 0.15 | 161 | 113 | Multi-Stage | Multi-Stage | 8.6 | 6 | 27 | 1931.8096 |  |  | 2195.3899 | 88.1768 | 2283.5667 | 161.2644 | 161.2644 | 19.3181 | 19318.0956 | 1 | 0 | 1 | 2195389.6483 | 365897.893 | 133.9941 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Heather - Kissinger | PS_BC086 | Vancouver Island | 48.9212 | -124.4812 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 1803393 | 3000 | 798 |  | 0.15 | 83 | 58 | Multi-Stage | Multi-Stage | 8.6 | 6 | 31.2 | 1331.0541 |  |  | 1512.666 | 68.4874 | 1581.1534 | 111.6603 | 223.3206 | 19.9658 | 39931.6213 | 1 | 0 | 1 | 3025332.1281 | 504222.2122 | 184.6141 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Henderson | PS_BC087 | Vancouver Island | 49.1081 | -125.0876 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 5482315 | 6000 | 525 |  | 0.35 | 254 | 178 | Single-Stage | Single-Stage | 8.6 | 6 | 64.8 | 1494.4195 |  |  | 1698.3213 | 74.083 | 1772.4043 | 125.1664 | 125.1664 | 14.9442 | 14944.195 | 1 | 0 | 1 | 1698321.8065 | 283054.0162 | 103.645 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | High Falls - Powell | PS_BC088 | Lower Mainland | 50.162 | -124.3575 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2692437 | 6000 | 1069 |  | 0.34 | 125 | 87 | Multi-Stage | Multi-Stage | 8.6 | 6 | 26.9 | 1528.6178 |  |  | 1737.1858 | 75.2289 | 1812.4147 | 127.9919 | 127.9919 | 15.2862 | 15286.1789 | 1 | 0 | 1 | 1737185.8313 | 289530.3993 | 106.0501 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Highland Point | PS_BC089 | Lower Mainland | 49.6898 | -123.8229 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2944858 | 6000 | 940 |  | 0.47 | 136 | 95 | Multi-Stage | Multi-Stage | 8.6 | 6 | 46 | 2062.3353 |  |  | 2343.7248 | 92.1759 | 2435.9007 | 172.0222 | 172.0222 | 41.2467 | 41246.7061 | 1 | 0 | 1 | 2343724.589 | 390620.3831 | 143.1561 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Hirsch-16 | PS_BC090 | 2L99 | 54.027 | -128.38 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 8165150 | 16000 | 940 |  | 0.31 | 142 | 99 | Multi-Stage | Multi-Stage | 22.9 | 16 | 84.8 | 1612.5467 |  |  | 1832.5661 | 78.0068 | 1910.5729 | 134.9238 | 134.9238 | 16.1123 | 16112.2791 | 1 | 0 | 1 | 1612547.2376 | 100784.2023 | 111.8908 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Hirsch-48 | PS_BC091 | 2L99 | 54.033 | -128.334 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 12247726 | 24000 | 940 |  | 0.31 | 71 | 50 | Multi‐Stage | Multi‐Stage | 68.6 | 48 | 142.6 | 2199.1959 |  |  | 2499.2589 | 96.2826 | 2595.5416 | 183.2959 | 366.5918 | 32.9502 | 65900.376 | 1 | 0 | 1 | 4398391.7666 | 91633.6629 | 305.0943 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Hkusam Mountain | PS_BC092 | Vancouver Island | 50.3797 | -125.8537 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2268989 | 6000 | 1220 |  | 0.39 | 105 | 74 | Multi-Stage | Multi-Stage | 8.6 | 6 | 45 | 1987.9586 |  |  | 2259.2 | 89.9075 | 2349.1074 | 165.8929 | 165.8929 | 39.7592 | 39759.172 | 1 | 0 | 1 | 2259199.4867 | 376533.8204 | 137.4299 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Hkusam Mountain South | PS_BC093 | Vancouver Island | 50.3612 | -125.7429 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 5033029 | 6000 | 550 |  | 0.14 | 233 | 163 | Single-Stage | Single-Stage | 8.6 | 6 | 145 | 2251.8427 |  |  | 2559.089 | 97.8403 | 2656.9293 | 187.6311 | 187.6311 | 45.0369 | 45036.8539 | 1 | 0 | 1 | 2559088.6631 | 426514.7772 | 155.7539 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Holyoak - Holland | PS_BC094 | Vancouver Island | 48.9442 | -123.8631 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 3615849 | 3000 | 398 |  | 0.07 | 167 | 117 | Single-Stage | Single-Stage | 8.6 | 6 | 38.9 | 1360.5526 |  |  | 1546.1894 | 69.5134 | 1615.7028 | 114.1002 | 228.2003 | 20.4083 | 40816.5781 | 1 | 0 | 1 | 3092378.4402 | 515396.4067 | 188.737 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Homfray | PS_BC095 | Lower Mainland | 50.2792 | -124.6239 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2661698 | 6000 | 1040 |  | 0.65 | 123 | 86 | Multi-Stage | Multi-Stage | 8.6 | 6 | 168 | 2361.4229 |  |  | 2683.6206 | 101.0456 | 2784.6662 | 196.6518 | 196.6518 | 47.2285 | 47228.4585 | 1 | 0 | 1 | 2683620.7487 | 447270.1248 | 163.7706 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Hugh-16 | PS_BC096 | 2L99 | 53.75 | -128.774 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 9137192 | 16000 | 840 |  | 0.09 | 159 | 111 | Multi-Stage | Multi-Stage | 22.9 | 16 | 73.2 | 1661.6676 |  |  | 1888.3891 | 79.611 | 1968.0002 | 138.9792 | 138.9792 | 16.5905 | 16590.5351 | 1 | 0 | 1 | 1661668.1123 | 103854.6149 | 115.212 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Hugh-48 | PS_BC097 | 2L99 | 53.697 | -128.672 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 13705788 | 24000 | 840 |  | 0.09 | 79 | 56 | Multi‐Stage | Multi‐Stage | 68.6 | 48 | 111.5 | 1693.7436 |  |  | 1924.8417 | 80.6504 | 2005.4921 | 141.6269 | 283.2538 | 25.3806 | 50761.1004 | 1 | 0 | 1 | 3387487.3473 | 70572.5338 | 235.0051 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Hulton | PS_BC098 | Lower Mainland | 50.7199 | -126.2389 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 4131591 | 6000 | 670 |  | 0.67 | 191 | 134 | Single-Stage | Single-Stage | 8.6 | 6 | 44 | 1615.4121 |  |  | 1835.8225 | 78.1008 | 1913.9233 | 135.1604 | 135.1604 | 32.3082 | 32308.2427 | 1 | 0 | 1 | 1835822.6918 | 305970.4486 | 112.2344 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Irving - Uun-named | PS_BC099 | Vancouver Island | 49.6277 | -126.3218 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4853652 | 6000 | 593 |  | 0.2 | 225 | 157 | Single-Stage | Single-Stage | 8.6 | 6 | 29.1 | 1359.5176 |  |  | 1545.0131 | 69.4775 | 1614.4906 | 114.0146 | 114.0146 | 13.5952 | 13595.1753 | 1 | 0 | 1 | 1545013.0494 | 257502.3658 | 94.254 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Isabel - Pitt | PS_BC100 | Lower Mainland | 49.4935 | -122.5712 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 5959038 | 6000 | 483 |  | 0.22 | 276 | 193 | Single-Stage | Single-Stage | 8.6 | 6 | 26 | 1455.2727 |  |  | 1653.8333 | 72.7608 | 1726.5941 | 121.9313 | 121.9313 | 14.5527 | 14552.7271 | 1 | 0 | 1 | 1653833.4639 | 275638.5289 | 100.8964 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Jesse Creek 1-16 | PS_BC101 | 2L99 | 53.929 | -128.901 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 23985129 | 16000 | 320 |  | 0.15 | 416 | 291 | Single-Stage | Single-Stage | 22.9 | 16 | 137.6 | 1859.9255 |  |  | 2113.6978 | 85.9373 | 2199.6351 | 155.3372 | 155.3372 | 18.5695 | 18569.5254 | 1 | 0 | 1 | 1859925.6022 | 116245.0638 | 128.955 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Jesse Creek 1-48 | PS_BC102 | 2L99 | 53.939 | -128.929 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 35977694 | 24000 | 320 |  | 0.15 | 208 | 146 | Single‐Stage | Single‐Stage | 68.6 | 48 | 251.8 | 2712.9777 |  |  | 3083.1422 | 111.0212 | 3194.1635 | 225.5703 | 451.1406 | 40.6435 | 81287.0253 | 1 | 0 | 1 | 5425954.9778 | 113040.6571 | 376.3288 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Jesse Creek 2 | PS_BC103 | 2L99 | 53.963 | -128.948 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 27411576 | 16000 | 280 |  | 0.11 | 476 | 333 | Single-Stage | Single-Stage | 22.9 | 16 | 200.9 | 2248.3612 |  |  | 2555.1325 | 97.7377 | 2652.8702 | 187.3444 | 187.3444 | 22.4615 | 22461.5396 | 1 | 0 | 1 | 2248360.8502 | 140522.0521 | 155.9829 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Jesse Lake-16 | PS_BC104 | 2L99 | 53.917 | -128.898 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 22574239 | 16000 | 340 |  | 0.11 | 392 | 274 | Single-Stage | Single-Stage | 22.9 | 16 | 242.1 | 1955.7344 |  |  | 2222.5791 | 88.9162 | 2311.4952 | 163.2367 | 163.2367 | 19.526 | 19526.0373 | 1 | 0 | 1 | 1955734.8429 | 122233.5708 | 135.5975 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Jesse Lake-48 | PS_BC105 | 2L99 | 53.935 | -128.934 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 33861359 | 24000 | 340 |  | 0.11 | 196 | 137 | Single‐Stage | Single‐Stage | 68.6 | 48 | 414.2 | 2794.5481 |  |  | 3175.8424 | 113.275 | 3289.1173 | 232.2759 | 464.5518 | 41.868 | 83736.0258 | 1 | 0 | 1 | 5589096.8429 | 116439.7562 | 387.6668 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Jordan River East | PS_BC106 | Vancouver Island | 48.4208 | -124.0513 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 9227220 | 6000 | 300 |  | 0.1 | 427 | 299 | Single-Stage | Single-Stage | 8.6 | 6 | 55 | 2455.9707 |  |  | 2791.0687 | 103.7728 | 2894.8415 | 204.4323 | 204.4323 | 49.1194 | 49119.4146 | 1 | 0 | 1 | 2791069.155 | 465178.3834 | 170.6421 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Jordan River South | PS_BC107 | Vancouver Island | 48.4081 | -123.9978 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 4613610 | 6000 | 600 |  | 0.13 | 214 | 150 | Single-Stage | Single-Stage | 8.6 | 6 | 75 | 2004.2801 |  |  | 2277.7484 | 90.4076 | 2368.156 | 167.2381 | 167.2381 | 40.0856 | 40085.6012 | 1 | 0 | 1 | 2277747.9395 | 379624.8475 | 138.5751 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Kaipit - Zeballos | PS_BC108 | Vancouver Island | 50.0852 | -126.7451 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 13263666 | 6000 | 217 |  | 0.04 | 614 | 430 | Single-Stage | Single-Stage | 8.6 | 6 | 38.9 | 2158.7505 |  |  | 2453.2951 | 95.0778 | 2548.3729 | 179.9649 | 179.9649 | 21.5875 | 21587.505 | 1 | 0 | 1 | 2453295.1417 | 408882.5236 | 149.684 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Keary - Carpenter | PS_BC109 | Lower Mainland | 50.8343 | -122.4712 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2645419 | 6000 | 1088 |  | 0.16 | 122 | 86 | Multi-Stage | Multi-Stage | 8.6 | 6 | 27.2 | 1796.1286 |  |  | 2041.1963 | 83.9264 | 2125.1227 | 150.0752 | 150.0752 | 17.9613 | 17961.2859 | 1 | 0 | 1 | 2041196.7589 | 340199.6507 | 124.6031 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Kenyon - Stave | PS_BC110 | Lower Mainland | 49.4025 | -122.2722 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 5005592 | 6000 | 575 |  | 0.29 | 232 | 162 | Single-Stage | Single-Stage | 8.6 | 6 | 26.4 | 1303.728 |  |  | 1481.6115 | 67.5304 | 1549.1419 | 109.3997 | 109.3997 | 13.0373 | 13037.2798 | 1 | 0 | 1 | 1481612.0648 | 246935.1533 | 90.4747 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Kitimat 1-16 | PS_BC111 | 2L99 | 54.044 | -128.12 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 10371948 | 16000 | 740 |  | 0.13 | 180 | 126 | Single-Stage | Single-Stage | 22.9 | 16 | 113.1 | 1737.4171 |  |  | 1974.474 | 82.0554 | 2056.5294 | 145.2311 | 145.2311 | 17.3491 | 17349.148 | 1 | 0 | 1 | 1737417.1716 | 108589.0743 | 120.4802 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Kitimat 1-48 | PS_BC112 | 2L99 | 54.049 | -128.032 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 15557922 | 24000 | 740 |  | 0.13 | 90 | 63 | Single‐Stage | Single‐Stage | 68.6 | 48 | 198.3 | 2540.4458 |  |  | 2887.0697 | 106.1811 | 2993.2508 | 211.382 | 422.7639 | 38.0585 | 76116.9132 | 1 | 0 | 1 | 5080891.4546 | 105851.9292 | 352.3931 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Kitimat 2-16 | PS_BC113 | 2L99 | 54.07 | -128.123 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 9840053 | 16000 | 780 |  | 0.12 | 171 | 120 | Multi-Stage | Multi-Stage | 22.9 | 16 | 114.4 | 1893.0957 |  |  | 2151.3937 | 86.9741 | 2238.3679 | 158.0725 | 158.0725 | 18.9158 | 18915.8487 | 1 | 0 | 1 | 1893095.4489 | 118317.9645 | 131.3601 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Kitimat 2-48 | PS_BC114 | 2L99 | 54.049 | -128.032 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 14760080 | 24000 | 780 |  | 0.12 | 85 | 60 | Multi‐Stage | Multi‐Stage | 68.6 | 48 | 199.6 | 2613.9026 |  |  | 2970.5491 | 108.2543 | 3078.8034 | 217.4236 | 434.8473 | 39.1593 | 78318.5399 | 1 | 0 | 1 | 5227805.1414 | 108912.0345 | 362.5858 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Knight - Fourth | PS_BC115 | Vancouver Island | 49.0699 | -124.4168 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 2705090 | 3000 | 532 |  | 0.1 | 125 | 88 | Single-Stage | Single-Stage | 8.6 | 6 | 29.5 | 1167.868 |  |  | 1327.2144 | 62.6724 | 1389.8868 | 98.1531 | 196.3063 | 17.518 | 35036.0391 | 1 | 0 | 1 | 2654428.3517 | 442405.107 | 162.0527 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Lake of the Mountains - Georgie | PS_BC116 | Vancouver Island | 50.7598 | -127.7357 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 33467622 | 6000 | 86 |  | 0.03 | 1549 | 1085 | Single-Stage | Single-Stage | 8.6 | 6 | 51.6 | 2779.1115 |  |  | 3158.2995 | 112.8501 | 3271.1496 | 231.007 | 231.007 | 27.7911 | 27791.115 | 1 | 0 | 1 | 3158298.9725 | 526382.7803 | 192.7454 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Lawrence | PS_BC117 | Lower Mainland | 50.4297 | -125.1179 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 7481530 | 6000 | 370 |  | 0.46 | 346 | 242 | Single-Stage | Single-Stage | 8.6 | 6 | 52 | 1932.1754 |  |  | 2195.8056 | 88.1881 | 2283.9938 | 161.2946 | 161.2946 | 38.6435 | 38643.5082 | 1 | 0 | 1 | 2195805.3736 | 365967.7531 | 133.9941 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lewis - Dodd | PS_BC118 | Lower Mainland | 49.9561 | -124.3168 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 12623752 | 6000 | 228 |  | 0.09 | 584 | 409 | Single-Stage | Single-Stage | 8.6 | 6 | 31.1 | 1692.4566 |  |  | 1923.3791 | 80.6088 | 2003.9879 | 141.5207 | 141.5207 | 16.9246 | 16924.5664 | 1 | 0 | 1 | 1923379.2682 | 320563.2114 | 117.388 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Lewis - Horseshoe | PS_BC119 | Lower Mainland | 49.9211 | -124.3017 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 11512862 | 6000 | 250 |  | 0.05 | 533 | 373 | Single-Stage | Single-Stage | 8.6 | 6 | 36.9 | 1971.6234 |  |  | 2240.636 | 89.4056 | 2330.0416 | 164.5464 | 164.5464 | 19.7162 | 19716.2345 | 1 | 0 | 1 | 2240636.1457 | 373439.3576 | 136.7427 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Lewis - Nanton | PS_BC120 | Lower Mainland | 49.9181 | -124.3305 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 11747818 | 6000 | 245 |  | 0.05 | 544 | 381 | Single-Stage | Single-Stage | 8.6 | 6 | 40.2 | 1910.1487 |  |  | 2170.7736 | 87.5049 | 2258.2784 | 159.4786 | 159.4786 | 19.1015 | 19101.4878 | 1 | 0 | 1 | 2170773.6663 | 361795.611 | 132.5053 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Lookout - Harrison | PS_BC121 | Lower Mainland | 49.4138 | -121.7656 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2107039 | 6000 | 1366 |  | 0.38 | 98 | 68 | Multi-Stage | Multi-Stage | 8.6 | 6 | 35.3 | 1803.1759 |  |  | 2049.2052 | 84.1497 | 2133.3549 | 150.6565 | 150.6565 | 18.0318 | 18031.7599 | 1 | 0 | 1 | 2049205.4851 | 341533.8658 | 125.0612 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Loquilts - Un-named | PS_BC122 | Lower Mainland | 50.1868 | -123.683 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 7757993 | 6000 | 371 |  | 0.08 | 359 | 251 | Single-Stage | Single-Stage | 8.6 | 6 | 38.4 | 1758.5472 |  |  | 1998.4872 | 82.7311 | 2081.2182 | 146.9746 | 146.9746 | 17.5855 | 17585.4713 | 1 | 0 | 1 | 1998486.988 | 333080.7829 | 121.969 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Loretta‐Bardon | PS_BC123 | 2L99 | 53.636 | -129.088 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 38376207 | 24000 | 300 |  | 0.03 | 222 | 155 | Single‐Stage | Single‐Stage | 68.6 | 48 | 208.8 | 2092.5065 |  |  | 2378.0126 | 93.0886 | 2471.1013 | 174.508 | 349.016 | 31.3546 | 62709.2541 | 1 | 0 | 1 | 4185013.5542 | 87187.8062 | 290.3206 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Hirsch 2-48 | PS_BC124 | 2L99 | 54.017 | -128.446 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 12513980 | 24000 | 920 |  | 0.11 | 72 | 51 | Multi‐Stage | Multi‐Stage | 68.6 | 48 | 105.8 | 2176.7212 |  |  | 2473.7177 | 95.614 | 2569.3317 | 181.445 | 362.89 | 32.6162 | 65232.4667 | 1 | 0 | 1 | 4353441.8887 | 90696.8492 | 302.0022 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Clore 1-16 | PS_BC125 | 2L99 | 54.275 | -127.94 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 10099002 | 16000 | 760 |  | 0.07 | 175 | 123 | Multi-Stage | Multi-Stage | 22.9 | 16 | 69.1 | 1935.6992 |  |  | 2199.8102 | 88.2972 | 2288.1074 | 161.5851 | 161.5851 | 19.3281 | 19328.1383 | 1 | 0 | 1 | 1935698.7116 | 120980.6684 | 134.2232 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Clore 1-48 | PS_BC126 | 2L99 | 54.184 | -127.975 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 15148503 | 24000 | 760 |  | 0.07 | 88 | 61 | Multi‐Stage | Multi‐Stage | 68.6 | 48 | 104.3 | 1765.7938 |  |  | 2006.7226 | 82.9622 | 2089.6848 | 147.5726 | 295.1451 | 26.4566 | 52913.2523 | 1 | 0 | 1 | 3531587.1573 | 73574.2314 | 244.9688 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Clore 2-16 | PS_BC127 | 2L99 | 54.295 | -127.924 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 15990086 | 16000 | 480 |  | 0.05 | 278 | 194 | Single-Stage | Single-Stage | 22.9 | 16 | 98.2 | 1889.3512 |  |  | 2147.1384 | 86.8574 | 2233.9958 | 157.7637 | 157.7637 | 18.8664 | 18866.3739 | 1 | 0 | 1 | 1889351.6299 | 118084.3337 | 131.0165 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Clore 2-48 | PS_BC128 | 2L99 | 54.341 | -127.793 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 23985129 | 24000 | 480 |  | 0.05 | 139 | 97 | Single‐Stage | Single‐Stage | 68.6 | 48 | 161.1 | 2171.1016 |  |  | 2467.3314 | 95.4465 | 2562.7779 | 180.9822 | 361.9643 | 32.5297 | 65059.3051 | 1 | 0 | 1 | 4342203.5602 | 90462.0731 | 301.2005 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Falls-16 | PS_BC129 | 2L99 | 53.735 | -128.498 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 13233175 | 16000 | 580 |  | 0.14 | 230 | 161 | Single-Stage | Single-Stage | 22.9 | 16 | 87.2 | 1624.9355 |  |  | 1846.6452 | 78.4129 | 1925.0581 | 135.9467 | 135.9467 | 16.2277 | 16227.7202 | 1 | 0 | 1 | 1624935.396 | 101558.3907 | 112.6925 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Falls-48 | PS_BC130 | 2L99 | 53.702 | -128.527 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 19849762 | 24000 | 580 |  | 0.14 | 115 | 80 | Single‐Stage | Single‐Stage | 68.6 | 48 | 152.8 | 2310.5002 |  |  | 2625.7499 | 99.5622 | 2725.312 | 192.4602 | 384.9205 | 34.62 | 69239.922 | 1 | 0 | 1 | 4621000.6859 | 96270.776 | 320.5552 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Hirsch 1-16 | PS_BC131 | 2L99 | 54.098 | -128.484 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 6852894 | 16000 | 1120 |  | 0.09 | 119 | 83 | Multi-Stage | Multi-Stage | 22.9 | 16 | 76.6 | 1876.5839 |  |  | 2132.6291 | 86.4588 | 2219.0879 | 156.7109 | 156.7109 | 18.7509 | 18750.9328 | 1 | 0 | 1 | 1876584.3941 | 117286.0952 | 130.2148 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Hirsch 1-48 | PS_BC132 | 2L99 | 54.033 | -128.334 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 10279341 | 24000 | 1120 |  | 0.09 | 59 | 42 | Multi‐Stage | Multi‐Stage | 68.6 | 48 | 114.6 | 2102.9743 |  |  | 2389.9086 | 93.4043 | 2483.3129 | 175.3704 | 350.7408 | 31.5031 | 63006.1027 | 1 | 0 | 1 | 4205948.7059 | 87624.1461 | 291.6949 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Hirsch 2-16 | PS_BC133 | 2L99 | 54.088 | -128.487 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 8342654 | 16000 | 920 |  | 0.11 | 145 | 101 | Multi-Stage | Multi-Stage | 22.9 | 16 | 66.9 | 1791.2072 |  |  | 2035.6034 | 83.7703 | 2119.3737 | 149.6692 | 149.6692 | 17.8934 | 17893.3703 | 1 | 0 | 1 | 1791207.2265 | 111950.3801 | 124.2595 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Lukes-16 | PS_BC134 | 2L99 | 54.147 | -128.733 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 9840053 | 16000 | 780 |  | 0.07 | 171 | 120 | Multi-Stage | Multi-Stage | 22.9 | 16 | 98.4 | 2129.1612 |  |  | 2419.6686 | 94.1917 | 2513.8603 | 177.5276 | 177.5276 | 21.2741 | 21274.1454 | 1 | 0 | 1 | 2129161.0439 | 133072.2074 | 147.7371 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lower Lukes-48 | PS_BC135 | 2L99 | 54.196 | -128.884 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 14760080 | 24000 | 780 |  | 0.07 | 85 | 60 | Multi‐Stage | Multi‐Stage | 68.6 | 48 | 158.2 | 2804.3447 |  |  | 3186.9756 | 113.5442 | 3300.5198 | 233.0811 | 466.1623 | 42.0164 | 84032.8743 | 1 | 0 | 1 | 5608689.7627 | 116847.4648 | 389.0411 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Lyon | PS_BC136 | Lower Mainland | 49.655 | -123.8604 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2611477 | 6000 | 1060 |  | 0.37 | 121 | 85 | Multi-Stage | Multi-Stage | 8.6 | 6 | 92 | 2156.3377 |  |  | 2450.5531 | 95.0057 | 2545.5588 | 179.7662 | 179.7662 | 43.1268 | 43126.7538 | 1 | 0 | 1 | 2450553.4156 | 408425.5693 | 150.0276 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Marshall - Carpenter | PS_BC137 | Lower Mainland | 50.8901 | -122.6054 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 6059401 | 6000 | 475 |  | 0.13 | 281 | 196 | Single-Stage | Single-Stage | 8.6 | 6 | 24.4 | 1420.4684 |  |  | 1614.2802 | 71.5757 | 1685.8559 | 119.0543 | 119.0543 | 14.2047 | 14204.6837 | 1 | 0 | 1 | 1614279.9993 | 269046.4757 | 98.4914 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | McConnel | PS_BC138 | Lower Mainland | 50.1462 | -123.8856 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 3375812 | 6000 | 820 |  | 0.39 | 156 | 109 | Multi-Stage | Multi-Stage | 8.6 | 6 | 166 | 2384.0784 |  |  | 2709.3673 | 101.7022 | 2811.0695 | 198.5164 | 198.5164 | 47.6816 | 47681.5682 | 1 | 0 | 1 | 2709367.0914 | 451561.3728 | 164.9159 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | McDonald | PS_BC139 | Lower Mainland | 50.6038 | -125.5301 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 3844675 | 6000 | 720 |  | 0.33 | 178 | 125 | Multi-Stage | Multi-Stage | 8.6 | 6 | 44 | 1565.3715 |  |  | 1778.9542 | 76.4513 | 1855.4055 | 131.0279 | 131.0279 | 31.3074 | 31307.4314 | 1 | 0 | 1 | 1778954.2075 | 296492.3679 | 108.7987 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | McNab | PS_BC140 | Lower Mainland | 49.5669 | -123.3478 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 5649319 | 6000 | 490 |  | 0.41 | 262 | 183 | Single-Stage | Single-Stage | 8.6 | 6 | 64 | 1722.2706 |  |  | 1957.261 | 81.5694 | 2038.8304 | 143.9812 | 143.9812 | 34.4454 | 34445.4125 | 1 | 0 | 1 | 1957261.4598 | 326210.4342 | 119.1059 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | McVey- Khartoum | PS_BC141 | Lower Mainland | 49.9007 | -124.0911 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3657199 | 6000 | 787 |  | 0.14 | 169 | 119 | Multi-Stage | Multi-Stage | 8.6 | 6 | 26.2 | 1790.3471 |  |  | 2034.6259 | 83.7431 | 2118.369 | 149.5982 | 149.5982 | 17.9035 | 17903.4714 | 1 | 0 | 1 | 2034626.4654 | 339104.7926 | 124.145 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Mid Point | PS_BC142 | Lower Mainland | 49.6499 | -123.7119 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2386350 | 6000 | 1160 |  | 0.41 | 110 | 77 | Multi-Stage | Multi-Stage | 8.6 | 6 | 104 | 2245.2352 |  |  | 2551.5799 | 97.6455 | 2649.2254 | 187.087 | 187.087 | 44.9047 | 44904.7036 | 1 | 0 | 1 | 2551580.4107 | 425263.02 | 155.7539 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Misery | PS_BC143 | Lower Mainland | 49.6867 | -123.5571 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 3504008 | 6000 | 790 |  | 0.3 | 162 | 114 | Multi-Stage | Multi-Stage | 8.6 | 6 | 56 | 2057.5397 |  |  | 2338.2749 | 92.0305 | 2430.3054 | 171.627 | 171.627 | 41.1508 | 41150.795 | 1 | 0 | 1 | 2338275.4943 | 389712.2006 | 143.1561 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Moh | PS_BC144 | Lower Mainland | 50.5257 | -125.0199 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2471577 | 6000 | 1120 |  | 0.43 | 114 | 80 | Multi-Stage | Multi-Stage | 8.6 | 6 | 37 | 2017.3634 |  |  | 2292.6168 | 90.8075 | 2383.4243 | 168.3163 | 168.3163 | 40.3473 | 40347.2677 | 1 | 0 | 1 | 2292616.7072 | 382103.1663 | 139.7204 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Mouat | PS_BC145 | Lower Mainland | 49.6581 | -124.3158 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 6291287 | 6000 | 440 |  | 0.29 | 291 | 204 | Single-Stage | Single-Stage | 8.6 | 6 | 74 | 1887.1612 |  |  | 2144.6496 | 86.7891 | 2231.4387 | 157.5831 | 157.5831 | 37.7432 | 37743.2245 | 1 | 0 | 1 | 2144649.3914 | 357441.3744 | 130.5584 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Mount Hallowell | PS_BC146 | Lower Mainland | 49.6942 | -123.8853 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2839145 | 6000 | 975 |  | 0.31 | 131 | 92 | Multi-Stage | Multi-Stage | 8.6 | 6 | 80 | 2177.9687 |  |  | 2475.1355 | 95.6512 | 2570.7867 | 181.5477 | 181.5477 | 43.5594 | 43559.375 | 1 | 0 | 1 | 2475135.0401 | 412522.1249 | 151.1729 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Mount Troubridge | PS_BC147 | Lower Mainland | 49.779 | -124.2 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2883506 | 6000 | 960 |  | 0.26 | 133 | 93 | Multi-Stage | Multi-Stage | 8.6 | 6 | 91 | 2296.189 |  |  | 2609.486 | 99.1434 | 2708.6294 | 191.2821 | 191.2821 | 45.9238 | 45923.7794 | 1 | 0 | 1 | 2609486.4906 | 434914.0333 | 159.1896 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Mt Collison | PS_BC148 | Vancouver Island | 50.53 | -126.7421 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2636349 | 6000 | 1050 |  | 0.38 | 122 | 85 | Multi-Stage | Multi-Stage | 8.6 | 6 | 92 | 2259.2032 |  |  | 2567.4539 | 98.0572 | 2665.511 | 188.2371 | 188.2371 | 45.1841 | 45184.0653 | 1 | 0 | 1 | 2567453.5618 | 427908.5452 | 156.8991 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Mt Collison South | PS_BC149 | Vancouver Island | 50.5144 | -126.679 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2129359 | 6000 | 1300 |  | 0.28 | 99 | 69 | Multi-Stage | Multi-Stage | 8.6 | 6 | 125 | 2415.1879 |  |  | 2744.7214 | 102.6006 | 2847.322 | 201.0765 | 201.0765 | 48.3038 | 48303.7579 | 1 | 0 | 1 | 2744720.928 | 457453.6789 | 167.2064 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Mt Palmerston | PS_BC150 | Vancouver Island | 50.4804 | -126.3474 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2636349 | 6000 | 1050 |  | 0.36 | 122 | 85 | Multi-Stage | Multi-Stage | 8.6 | 6 | 141 | 2425.5772 |  |  | 2756.5283 | 102.8998 | 2859.4281 | 201.9315 | 201.9315 | 48.5115 | 48511.5451 | 1 | 0 | 1 | 2756528.4452 | 459421.2167 | 168.3516 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Myers | PS_BC151 | Lower Mainland | 49.6843 | -123.8756 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2611477 | 6000 | 1060 |  | 0.41 | 121 | 85 | Multi-Stage | Multi-Stage | 8.6 | 6 | 180 | 2505.5592 |  |  | 2847.4231 | 105.1897 | 2952.6128 | 208.5121 | 208.5121 | 50.1112 | 50111.183 | 1 | 0 | 1 | 2847423.4224 | 474570.5704 | 174.0778 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Mystery - Harrison | PS_BC152 | Lower Mainland | 49.5283 | -121.8872 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 7800042 | 6000 | 369 |  | 0.12 | 361 | 253 | Single-Stage | Single-Stage | 8.6 | 6 | 39.9 | 1731.0438 |  |  | 1967.2311 | 81.8511 | 2049.0822 | 144.7052 | 144.7052 | 17.3104 | 17310.4375 | 1 | 0 | 1 | 1967230.8523 | 327872.1905 | 120.0221 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Nelson Island | PS_BC153 | Lower Mainland | 49.7596 | -124.1338 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 5323396 | 6000 | 520 |  | 0.87 | 246 | 173 | Single-Stage | Single-Stage | 8.6 | 6 | 42 | 1777.0814 |  |  | 2019.5503 | 83.3216 | 2102.8719 | 148.5038 | 148.5038 | 35.5416 | 35541.6288 | 1 | 0 | 1 | 2019550.4076 | 336592.1163 | 123.6869 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Nepah | PS_BC154 | Lower Mainland | 51.0082 | -126.7762 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 6437596 | 6000 | 430 |  | 0.36 | 298 | 209 | Single-Stage | Single-Stage | 8.6 | 6 | 74 | 1781.3282 |  |  | 2024.3765 | 83.4566 | 2107.8331 | 148.8542 | 148.8542 | 35.6266 | 35626.5639 | 1 | 0 | 1 | 2024376.4868 | 337396.0811 | 123.6869 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Newcastle Peak | PS_BC155 | Vancouver Island | 50.4387 | -126.0581 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2636349 | 6000 | 1050 |  | 0.27 | 122 | 85 | Multi-Stage | Multi-Stage | 8.6 | 6 | 99 | 2304.8088 |  |  | 2619.2819 | 99.3957 | 2718.6776 | 191.9917 | 191.9917 | 46.0962 | 46096.176 | 1 | 0 | 1 | 2619281.8052 | 436547.1584 | 160.3349 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Nimpkish 1 | PS_BC156 | Vancouver Island | 50.5029 | -127.0237 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3029701 | 6000 | 950 |  | 0.3 | 140 | 98 | Multi-Stage | Multi-Stage | 8.6 | 6 | 43 | 1789.0851 |  |  | 2033.1918 | 83.703 | 2116.8948 | 149.4941 | 149.4941 | 17.8909 | 17890.8519 | 1 | 0 | 1 | 2033191.4684 | 338865.4356 | 124.145 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Nimpkish 2 | PS_BC157 | Vancouver Island | 50.3547 | -126.9309 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3289389 | 6000 | 875 |  | 0.23 | 152 | 107 | Multi-Stage | Multi-Stage | 8.6 | 6 | 66.7 | 1774.1784 |  |  | 2016.2512 | 83.2292 | 2099.4804 | 148.2643 | 148.2643 | 17.7418 | 17741.784 | 1 | 0 | 1 | 2016250.9452 | 336042.3968 | 123.1143 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | North Bonanza | PS_BC158 | Vancouver Island | 50.3808 | -126.7789 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 8200044 | 6000 | 351 |  | 0.18 | 380 | 266 | Single-Stage | Single-Stage | 8.6 | 6 | 59.1 | 1583.7714 |  |  | 1799.8646 | 77.0597 | 1876.9244 | 132.5475 | 132.5475 | 15.8377 | 15837.7148 | 1 | 0 | 1 | 1799864.1637 | 299977.3606 | 109.8294 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | North Harrison | PS_BC159 | Lower Mainland | 49.7465 | -122.1169 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 1810198 | 6000 | 1590 |  | 0.33 | 84 | 59 | Multi-Stage | Multi-Stage | 8.6 | 6 | 37.4 | 1872.0629 |  |  | 2127.4912 | 86.3174 | 2213.8086 | 156.3381 | 156.3381 | 18.7206 | 18720.6284 | 1 | 0 | 1 | 2127491.2709 | 354581.6876 | 129.8712 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | North Henderson | PS_BC160 | Vancouver Island | 49.1207 | -125.0901 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 6772272 | 6000 | 425 |  | 0.24 | 314 | 219 | Single-Stage | Single-Stage | 8.6 | 6 | 25.5 | 1588.3838 |  |  | 1805.1064 | 77.2119 | 1882.3183 | 132.9284 | 132.9284 | 15.8838 | 15883.8386 | 1 | 0 | 1 | 1805105.9684 | 300851.1856 | 110.173 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | North Hirsch-16 | PS_BC161 | 2L99 | 54.063 | -128.253 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 10371948 | 16000 | 740 |  | 0.13 | 180 | 126 | Single-Stage | Single-Stage | 22.9 | 16 | 135.8 | 2073.9824 |  |  | 2356.9611 | 92.5288 | 2449.4898 | 172.9818 | 172.9818 | 20.7134 | 20713.4315 | 1 | 0 | 1 | 2073982.9472 | 129623.8626 | 143.8433 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | North Hirsch-48 | PS_BC162 | 2L99 | 54.034 | -128.327 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 15,557,922 | 24000 | 740 |  | 0.13 | 90 | 63 | Single‐Stage | Single‐Stage | 68.6 | 48 | 241.9 | 3550.3475 |  |  | 4034.7647 | 133.2478 | 4168.0125 | 294.3431 | 588.6861 | 53.1854 | 106370.727 | 1 | 0 | 1 | 7100694.9622 | 147930.6679 | 492.4571 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Oliphant - Shawnigan | PS_BC163 | Vancouver Island | 48.6001 | -123.6231 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 9499061 | 6000 | 303 |  | 0.09 | 440 | 308 | Single-Stage | Single-Stage | 8.6 | 6 | 51.1 | 2449.919 |  |  | 2784.1913 | 103.5993 | 2887.7906 | 203.9344 | 203.9344 | 24.4992 | 24499.1906 | 1 | 0 | 1 | 2784190.7895 | 464031.9891 | 169.955 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Oliver-16 | PS_BC164 | 2L99 | 54.803 | -128.193 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 12379422 | 16000 | 620 |  | 0.24 | 215 | 150 | Single-Stage | Single-Stage | 22.9 | 16 | 119.2 | 1699.6404 |  |  | 1931.543 | 80.8408 | 2012.3837 | 142.1136 | 142.1136 | 16.9698 | 16969.8416 | 1 | 0 | 1 | 1699639.9881 | 106227.5708 | 117.8461 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Oliver-48 | PS_BC165 | 2L99 | 54.82 | -128.165 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 18569132 | 24000 | 620 |  | 0.24 | 107 | 75 | Single‐Stage | Single‐Stage | 68.6 | 48 | 215.9 | 2702.0967 |  |  | 3070.7767 | 110.719 | 3181.4957 | 224.6757 | 449.3514 | 40.4827 | 80965.4394 | 1 | 0 | 1 | 5404192.9564 | 112587.1385 | 374.84 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Palisade - Seymour | PS_BC166 | Lower Mainland | 49.4454 | -122.9711 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 5420368 | 6000 | 531 |  | 0.14 | 251 | 176 | Single-Stage | Single-Stage | 8.6 | 6 | 25.5 | 1383.3808 |  |  | 1572.1323 | 70.3025 | 1642.4348 | 115.988 | 115.988 | 13.8338 | 13833.8085 | 1 | 0 | 1 | 1572132.5456 | 262021.5183 | 95.9719 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Peneplain - Coquitlam | PS_BC167 | Lower Mainland | 49.435 | -122.7589 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3531553 | 6000 | 815 |  | 0.22 | 163 | 114 | Multi-Stage | Multi-Stage | 8.6 | 6 | 27.1 | 1575.0673 |  |  | 1789.9729 | 76.7722 | 1866.7451 | 131.8287 | 131.8287 | 15.7507 | 15750.6736 | 1 | 0 | 1 | 1789972.6481 | 298329.3473 | 109.2568 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Picton | PS_BC168 | Lower Mainland | 50.4595 | -125.4162 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 15378700 | 6000 | 180 |  | 0.3 | 712 | 498 | Single-Stage | Single-Stage | 8.6 | 6 | 61 | 2533.6335 |  |  | 2879.328 | 105.9878 | 2985.3158 | 210.8216 | 210.8216 | 50.6727 | 50672.6711 | 1 | 0 | 1 | 2879327.769 | 479887.9615 | 175.2231 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Pointer - Hornet | PS_BC169 | Lower Mainland | 50.775 | -126.4348 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 7885522 | 6000 | 365 |  | 0.15 | 365 | 256 | Single-Stage | Single-Stage | 8.6 | 6 | 32 | 1518.4897 |  |  | 1725.6757 | 74.8904 | 1800.5661 | 127.1551 | 127.1551 | 15.1849 | 15184.8966 | 1 | 0 | 1 | 1725676.0788 | 287612.1072 | 105.3629 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Pointer - Loose | PS_BC170 | Lower Mainland | 50.7586 | -126.3891 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 7842549 | 6000 | 367 |  | 0.44 | 363 | 254 | Single-Stage | Single-Stage | 8.6 | 6 | 26 | 1458.6247 |  |  | 1657.6426 | 72.8745 | 1730.5171 | 122.2083 | 122.2083 | 14.5862 | 14586.2474 | 1 | 0 | 1 | 1657642.5621 | 276274.1421 | 101.1255 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Port Alberni | PS_BC171 | Vancouver Island | 49.2324 | -124.8384 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 6751625 | 6000 | 410 |  | 0.13 | 313 | 219 | Single-Stage | Single-Stage | 8.6 | 6 | 182 | 2587.5298 |  |  | 2940.578 | 107.5122 | 3048.0901 | 215.2547 | 215.2547 | 51.7506 | 51750.5955 | 1 | 0 | 1 | 2940577.976 | 490096.7111 | 179.8041 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Potato - Un-named | PS_BC172 | Lower Mainland | 50.1515 | -123.6883 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3643311 | 6000 | 790 |  | 0.16 | 169 | 118 | Multi-Stage | Multi-Stage | 8.6 | 6 | 33.4 | 1702.7454 |  |  | 1935.0717 | 80.9409 | 2016.0126 | 142.3699 | 142.3699 | 17.0275 | 17027.4533 | 1 | 0 | 1 | 1935071.1152 | 322512.4252 | 118.0752 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Powell 1 | PS_BC173 | Lower Mainland | 50.0082 | -124.5635 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3048957 | 6000 | 944 |  | 0.16 | 141 | 99 | Multi-Stage | Multi-Stage | 8.6 | 6 | 124.3 | 1767.6492 |  |  | 2008.8311 | 83.0213 | 2091.8524 | 147.7256 | 147.7256 | 17.6765 | 17676.4923 | 1 | 0 | 1 | 2008830.8769 | 334805.5279 | 122.6562 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Powell 2 | PS_BC174 | Lower Mainland | 49.998 | -124.5637 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3671193 | 6000 | 784 |  | 0.46 | 170 | 119 | Multi-Stage | Multi-Stage | 8.6 | 6 | 80.8 | 1577.1398 |  |  | 1792.3282 | 76.8407 | 1869.1689 | 131.9998 | 131.9998 | 15.7714 | 15771.398 | 1 | 0 | 1 | 1792328.4253 | 298721.0225 | 109.3713 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Powell 3 | PS_BC175 | Lower Mainland | 50.0511 | -124.533 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 4334662 | 6000 | 664 |  | 0.19 | 201 | 140 | Single-Stage | Single-Stage | 8.6 | 6 | 48 | 1527.4202 |  |  | 1735.8248 | 75.1889 | 1811.0136 | 127.8929 | 127.8929 | 15.2742 | 15274.2019 | 1 | 0 | 1 | 1735825.2755 | 289303.64 | 105.9355 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Powell 4 | PS_BC176 | Lower Mainland | 50.1091 | -124.4317 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 4283059 | 6000 | 672 |  | 0.17 | 198 | 139 | Single-Stage | Single-Stage | 8.6 | 6 | 39.8 | 1436.9793 |  |  | 1633.0439 | 72.1391 | 1705.183 | 120.4192 | 120.4192 | 14.3698 | 14369.7931 | 1 | 0 | 1 | 1633043.7589 | 272174.1507 | 99.6367 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Powell 5 | PS_BC177 | Lower Mainland | 50.01 | -124.3761 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 6586306 | 6000 | 437 |  | 0.24 | 305 | 213 | Single-Stage | Single-Stage | 8.6 | 6 | 47.4 | 1560.1784 |  |  | 1773.0526 | 76.2791 | 1849.3317 | 130.5989 | 130.5989 | 15.6018 | 15601.7844 | 1 | 0 | 1 | 1773052.7394 | 295508.599 | 108.226 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Pretty Girl - Ellen | PS_BC178 | Vancouver Island | 49.4646 | -126.2192 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 11844508 | 6000 | 243 |  | 0.06 | 548 | 384 | Single-Stage | Single-Stage | 8.6 | 6 | 36.6 | 1862.2319 |  |  | 2116.3188 | 86.0096 | 2202.3285 | 155.5274 | 155.5274 | 18.6223 | 18622.319 | 1 | 0 | 1 | 2116319.3669 | 352719.5127 | 129.1841 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Purcell | PS_BC179 | Lower Mainland | 50.7913 | -124.9116 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2944858 | 6000 | 940 |  | 0.63 | 136 | 95 | Multi-Stage | Multi-Stage | 8.6 | 6 | 68 | 2162.3903 |  |  | 2457.4316 | 95.1865 | 2552.6181 | 180.2647 | 180.2647 | 43.2478 | 43247.8066 | 1 | 0 | 1 | 2457431.7811 | 409571.9635 | 150.0276 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Quimper - Bulson | PS_BC180 | Vancouver Island | 49.3114 | -125.7229 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 3010686 | 3000 | 478 |  | 0.18 | 139 | 98 | Single-Stage | Single-Stage | 8.6 | 6 | 28.9 | 1091.0881 |  |  | 1239.9585 | 59.8467 | 1299.8052 | 91.7916 | 183.5833 | 16.3663 | 32732.6434 | 1 | 0 | 1 | 2479916.4546 | 413319.2182 | 151.4019 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Ramsay | PS_BC181 | Lower Mainland | 50.4361 | -124.9723 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2661698 | 6000 | 1040 |  | 0.42 | 123 | 86 | Multi-Stage | Multi-Stage | 8.6 | 6 | 69 | 2038.3143 |  |  | 2316.4264 | 91.4462 | 2407.8726 | 170.0428 | 170.0428 | 40.7663 | 40766.2868 | 1 | 0 | 1 | 2316426.4339 | 386071.4541 | 140.8656 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Raza | PS_BC182 | Lower Mainland | 50.2805 | -125.0129 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 3375812 | 6000 | 820 |  | 0.68 | 156 | 109 | Multi-Stage | Multi-Stage | 8.6 | 6 | 34 | 2170.7521 |  |  | 2466.9342 | 95.4361 | 2562.3703 | 180.9534 | 180.9534 | 43.415 | 43415.0416 | 1 | 0 | 1 | 2466933.912 | 411155.8429 | 150.0276 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Salsbury - Stave | PS_BC183 | Lower Mainland | 49.3594 | -122.2747 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 8294569 | 6000 | 347 |  | 0.08 | 384 | 269 | Single-Stage | Single-Stage | 8.6 | 6 | 29.6 | 1721.7374 |  |  | 1956.655 | 81.5523 | 2038.2073 | 143.9372 | 143.9372 | 17.2174 | 17217.3745 | 1 | 0 | 1 | 1956654.4778 | 326109.6523 | 119.4495 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Saumarez | PS_BC184 | Lower Mainland | 49.897 | -123.9383 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 2913859 | 6000 | 950 |  | 0.53 | 135 | 94 | Multi-Stage | Multi-Stage | 8.6 | 6 | 47 | 2051.1548 |  |  | 2331.0188 | 91.8366 | 2422.8555 | 171.1009 | 171.1009 | 41.0231 | 41023.0963 | 1 | 0 | 1 | 2331019.1966 | 388502.8177 | 142.0109 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Sechelt - Henriette | PS_BC185 | Lower Mainland | 49.6735 | -123.3392 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 8566118 | 6000 | 336 |  | 0.09 | 397 | 278 | Single-Stage | Single-Stage | 8.6 | 6 | 37.9 | 1742.9343 |  |  | 1980.744 | 82.2321 | 2062.9761 | 145.6864 | 145.6864 | 17.4293 | 17429.3429 | 1 | 0 | 1 | 1980743.6452 | 330123.75 | 120.9383 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Shamrock | PS_BC186 | Lower Mainland | 50.6437 | -125.5216 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 4464784 | 6000 | 620 |  | 0.34 | 207 | 145 | Single-Stage | Single-Stage | 8.6 | 6 | 43 | 1602.5123 |  |  | 1821.1626 | 77.6772 | 1898.8397 | 134.0952 | 134.0952 | 32.0502 | 32050.2456 | 1 | 0 | 1 | 1821162.3593 | 303527.6325 | 111.0892 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Skwim - Freda | PS_BC187 | Lower Mainland | 50.0072 | -124.1489 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4441691 | 6000 | 648 |  | 0.16 | 206 | 144 | Single-Stage | Single-Stage | 8.6 | 6 | 33 | 1414.1755 |  |  | 1607.1287 | 71.3605 | 1678.4892 | 118.5341 | 118.5341 | 14.1418 | 14141.7557 | 1 | 0 | 1 | 1607129.0645 | 267854.2715 | 98.0333 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Sleeman-16 | PS_BC188 | 2L99 | 53.671 | -128.675 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 12792069 | 16000 | 600 |  | 0.21 | 222 | 155 | Single-Stage | Single-Stage | 22.9 | 16 | 109.5 | 1522.3707 |  |  | 1730.0862 | 75.0202 | 1805.1064 | 127.4758 | 127.4758 | 15.2052 | 15205.2419 | 1 | 0 | 1 | 1522370.3314 | 95148.432 | 105.592 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Sleeman-48 | PS_BC189 | 2L99 | 53.697 | -128.672 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 19188103 | 24000 | 600 |  | 0.21 | 111 | 78 | Single‐Stage | Single‐Stage | 68.6 | 48 | 191.1 | 2127.3671 |  |  | 2417.6297 | 94.1379 | 2511.7676 | 177.3798 | 354.7597 | 31.8741 | 63748.224 | 1 | 0 | 1 | 4254734.0228 | 88639.982 | 295.1307 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Sliammon - Powell | PS_BC190 | Lower Mainland | 49.9379 | -124.5469 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 41117364 | 6000 | 70 |  | 0.05 | 1904 | 1333 | Single-Stage | Single-Stage | 8.6 | 6 | 43.5 | 2542.7242 |  |  | 2889.659 | 106.2457 | 2995.9046 | 211.5694 | 211.5694 | 25.4272 | 25427.242 | 1 | 0 | 1 | 2889659.0602 | 481609.2707 | 176.3683 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Slippery - Clowhom | PS_BC191 | Lower Mainland | 49.7432 | -123.471 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2257424 | 6000 | 1275 |  | 0.35 | 105 | 73 | Multi-Stage | Multi-Stage | 8.6 | 6 | 32.6 | 1584.4195 |  |  | 1800.6011 | 77.0811 | 1877.6822 | 132.601 | 132.601 | 15.8442 | 15844.1946 | 1 | 0 | 1 | 1800600.5588 | 300099.9023 | 109.9439 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Slollicum - Harrison | PS_BC192 | Lower Mainland | 49.4024 | -121.7595 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2308112 | 6000 | 1247 |  | 0.32 | 107 | 75 | Multi-Stage | Multi-Stage | 8.6 | 6 | 28.6 | 1715.165 |  |  | 1949.1859 | 81.341 | 2030.5268 | 143.3948 | 143.3948 | 17.1516 | 17151.6498 | 1 | 0 | 1 | 1949186.3091 | 324864.7666 | 118.9914 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Snout | PS_BC193 | Lower Mainland | 50.3992 | -124.6315 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 6291287 | 6000 | 440 |  | 0.44 | 291 | 204 | Single-Stage | Single-Stage | 8.6 | 6 | 129 | 1956.4751 |  |  | 2223.4208 | 88.939 | 2312.3598 | 163.2978 | 163.2978 | 39.1295 | 39129.5015 | 1 | 0 | 1 | 2223420.7627 | 370570.5089 | 135.1394 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Stakawus | PS_BC194 | Lower Mainland | 50.0545 | -123.7844 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 9886307 | 6000 | 280 |  | 0.47 | 458 | 320 | Single-Stage | Single-Stage | 8.6 | 6 | 51 | 2087.0492 |  |  | 2371.8108 | 92.9238 | 2464.7346 | 174.0584 | 174.0584 | 41.741 | 41740.9842 | 1 | 0 | 1 | 2371810.6754 | 395302.161 | 144.3014 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Storm | PS_BC195 | Lower Mainland | 49.6382 | -123.7783 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 4772700 | 6000 | 580 |  | 0.36 | 221 | 155 | Single-Stage | Single-Stage | 8.6 | 6 | 87 | 1770.8311 |  |  | 2012.4471 | 83.1227 | 2095.5698 | 147.9881 | 147.9881 | 35.4166 | 35416.6214 | 1 | 0 | 1 | 2012447.5733 | 335407.9289 | 122.5416 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Stukolait - Chochiwa | PS_BC196 | Lower Mainland | 50.1014 | -121.8581 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 8465340 | 6000 | 340 |  | 0.07 | 392 | 274 | Single-Stage | Single-Stage | 8.6 | 6 | 40 | 1839.2881 |  |  | 2090.2446 | 85.2893 | 2175.5339 | 153.6352 | 153.6352 | 18.3929 | 18392.881 | 1 | 0 | 1 | 2090244.3377 | 348374.438 | 127.5807 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Sue-Bardon 1-16 | PS_BC197 | 2L99 | 53.675 | -129.018 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 25584138 | 16000 | 300 |  | 0.04 | 444 | 311 | Single-Stage | Single-Stage | 22.9 | 16 | 201.7 | 2149.5015 |  |  | 2442.7842 | 94.8013 | 2537.5855 | 179.2031 | 179.2031 | 21.472 | 21472.0444 | 1 | 0 | 1 | 2149501.8114 | 134343.4337 | 149.1114 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Sue-Bardon 2-16 | PS_BC198 | 2L99 | 53.668 | -129.048 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 34887461 | 16000 | 220 |  | 0.05 | 606 | 424 | Single-Stage | Single-Stage | 22.9 | 16 | 161.6 | 2203.4673 |  |  | 2504.1132 | 96.4095 | 2600.5226 | 183.6477 | 183.6477 | 22.0163 | 22016.2667 | 1 | 0 | 1 | 2203467.0894 | 137716.192 | 152.8907 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Sue‐Bardon 1-48 | PS_BC199 | 2L99 | 53.639 | -129.1 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 38376207 | 24000 | 300 |  | 0.04 | 222 | 155 | Single‐Stage | Single‐Stage | 68.6 | 48 | 356.5 | 2437.1042 |  |  | 2769.628 | 103.2313 | 2872.8594 | 202.88 | 405.7599 | 36.5124 | 73024.7409 | 1 | 0 | 1 | 4874208.3679 | 101545.7929 | 338.0775 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Sue‐Bardon 2-48 | PS_BC200 | 2L99 | 53.639 | -129.1 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 52331191 | 24000 | 220 |  | 0.05 | 303 | 212 | Single‐Stage | Single‐Stage | 68.6 | 48 | 281.4 | 2518.979 |  |  | 2862.674 | 105.5716 | 2968.2455 | 209.6161 | 419.2322 | 37.7369 | 75473.7414 | 1 | 0 | 1 | 5037958.3602 | 104957.4897 | 349.4155 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Syren | PS_BC201 | Lower Mainland | 49.882 | -124.0329 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 11534025 | 6000 | 240 |  | 2.4 | 534 | 374 | Single-Stage | Single-Stage | 8.6 | 6 | 50 | 2469.6141 |  |  | 2806.5736 | 104.1635 | 2910.7371 | 205.5549 | 205.5549 | 49.3923 | 49392.2816 | 1 | 0 | 1 | 2806573.5359 | 467762.0651 | 171.7873 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Thornhill | PS_BC202 | Lower Mainland | 49.6598 | -123.5961 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2587071 | 6000 | 1070 |  | 0.47 | 120 | 84 | Multi-Stage | Multi-Stage | 8.6 | 6 | 103 | 2153.3698 |  |  | 2447.1802 | 94.917 | 2542.0972 | 179.5217 | 179.5217 | 43.0674 | 43067.3955 | 1 | 0 | 1 | 2447180.6573 | 407863.252 | 148.8824 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Thors | PS_BC203 | Lower Mainland | 50.059 | -124.7001 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Man Made | 3548931 | 6000 | 780 |  | 0.43 | 164 | 115 | Multi-Stage | Multi-Stage | 8.6 | 6 | 34 | 1969.5956 |  |  | 2238.3315 | 89.3432 | 2327.6747 | 164.3793 | 164.3793 | 39.3919 | 39391.9112 | 1 | 0 | 1 | 2238331.9047 | 373055.6992 | 136.2846 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Tsable - Comox | PS_BC204 | Vancouver Island | 49.568 | -125.1687 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3255900 | 6000 | 884 |  | 0.14 | 151 | 106 | Multi-Stage | Multi-Stage | 8.6 | 6 | 27.2 | 1985.2287 |  |  | 2256.0976 | 89.8237 | 2345.9213 | 165.6679 | 165.6679 | 19.8523 | 19852.2867 | 1 | 0 | 1 | 2256098.1524 | 376016.1679 | 137.6589 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Tsable - Nimnim | PS_BC205 | Vancouver Island | 49.5007 | -125.1545 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 5252218 | 6000 | 548 |  | 0.12 | 243 | 170 | Single-Stage | Single-Stage | 8.6 | 6 | 34.2 | 1505.3919 |  |  | 1710.7908 | 74.4515 | 1785.2424 | 126.073 | 126.073 | 15.0539 | 15053.919 | 1 | 0 | 1 | 1710791.2776 | 285131.4979 | 104.4467 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Tsable - Willemar | PS_BC206 | Vancouver Island | 49.5159 | -125.1762 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3964484 | 6000 | 726 |  | 0.13 | 184 | 128 | Multi-Stage | Multi-Stage | 8.6 | 6 | 29.7 | 1765.2227 |  |  | 2006.0735 | 82.944 | 2089.0175 | 147.5254 | 147.5254 | 17.6522 | 17652.2267 | 1 | 0 | 1 | 2006073.1173 | 334345.1378 | 122.4271 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Tsakonu | PS_BC207 | Lower Mainland | 50.6387 | -126.1686 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 5323396 | 6000 | 520 |  | 0.33 | 246 | 173 | Single-Stage | Single-Stage | 8.6 | 6 | 53 | 1676.4109 |  |  | 1905.1441 | 80.0896 | 1985.2337 | 140.1963 | 140.1963 | 33.5282 | 33528.2192 | 1 | 0 | 1 | 1905144.6136 | 317523.7205 | 116.8154 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Twin Lakes - Stave | PS_BC208 | Lower Mainland | 49.3588 | -122.2736 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 7177595 | 6000 | 401 |  | 0.27 | 332 | 233 | Single-Stage | Single-Stage | 8.6 | 6 | 51.4 | 1734.5853 |  |  | 1971.2559 | 81.9646 | 2053.2205 | 144.9975 | 144.9975 | 17.3459 | 17345.8531 | 1 | 0 | 1 | 1971256.4025 | 328542.1611 | 120.3657 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Tyaughton - Carpenter | PS_BC209 | Lower Mainland | 50.9068 | -122.7385 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 8591688 | 6000 | 335 |  | 0.07 | 398 | 278 | Single-Stage | Single-Stage | 8.6 | 6 | 27.8 | 1736.8527 |  |  | 1973.8326 | 82.0373 | 2055.8699 | 145.1846 | 145.1846 | 17.3685 | 17368.5268 | 1 | 0 | 1 | 1973832.0675 | 328971.6295 | 120.4802 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Effiingham | PS_BC210 | Vancouver Island | 49.166 | -125.2757 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3742803 | 6000 | 769 |  | 0.12 | 173 | 121 | Multii-Stage | Multii-Stage | 8.6 | 6 | 37.4 | 1842.6687 |  |  | 2094.0864 | 85.3956 | 2179.4821 | 153.914 | 153.914 | 18.4267 | 18426.6876 | 1 | 0 | 1 | 2094086.6481 | 349014.6322 | 127.8098 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Goat | PS_BC211 | Lower Mainland | 50.0791 | -124.2223 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2687409 | 6000 | 1071 |  | 0.2 | 124 | 87 | Multi-Stage | Multi-Stage | 8.6 | 6 | 28.7 | 1687.4663 |  |  | 1917.7079 | 80.4475 | 1998.1553 | 141.1088 | 141.1088 | 16.8747 | 16874.6633 | 1 | 0 | 1 | 1917707.9951 | 319618.3809 | 117.0444 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Hesquiat | PS_BC212 | Vancouver Island | 49.5159 | -126.3912 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 5440861 | 6000 | 529 |  | 0.11 | 252 | 176 | Single-Stage | Single-Stage | 8.6 | 6 | 29.4 | 1841.4702 |  |  | 2092.7244 | 85.3579 | 2178.0823 | 153.8151 | 153.8151 | 18.4147 | 18414.7014 | 1 | 0 | 1 | 2092724.9471 | 348787.8729 | 127.6953 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Huaskin | PS_BC213 | Lower Mainland | 50.9793 | -126.9184 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 18332583 | 6000 | 157 |  | 0.08 | 849 | 594 | Single-Stage | Single-Stage | 8.6 | 6 | 33.7 | 1973.2333 |  |  | 2242.4655 | 89.4551 | 2331.9206 | 164.6791 | 164.6791 | 19.7323 | 19732.3322 | 1 | 0 | 1 | 2242465.1083 | 373743.9938 | 136.8573 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-Named - Powell | PS_BC214 | Lower Mainland | 50.2433 | -124.3535 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4341200 | 6000 | 663 |  | 0.21 | 201 | 141 | Single-Stage | Single-Stage | 8.6 | 6 | 31.7 | 1443.4376 |  |  | 1640.3833 | 72.3589 | 1712.7422 | 120.953 | 120.953 | 14.4344 | 14434.3759 | 1 | 0 | 1 | 1640383.6597 | 273397.2766 | 100.0948 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Stafford | PS_BC215 | Lower Mainland | 50.7707 | -125.4373 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2468452 | 6000 | 1166 |  | 0.33 | 114 | 80 | Multi-Stage | Multi-Stage | 8.6 | 6 | 31.1 | 1556.4783 |  |  | 1768.8475 | 76.1563 | 1845.0039 | 130.2933 | 130.2933 | 15.5648 | 15564.7825 | 1 | 0 | 1 | 1768847.3851 | 294807.7066 | 107.997 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Tzoonie 1 | PS_BC216 | Lower Mainland | 49.8751 | -123.6214 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3418308 | 6000 | 842 |  | 0.17 | 158 | 111 | Multi-Stage | Multi-Stage | 8.6 | 6 | 34.8 | 1732.6525 |  |  | 1969.0594 | 81.9027 | 2050.9621 | 144.838 | 144.838 | 17.3265 | 17326.5248 | 1 | 0 | 1 | 1969059.815 | 328176.8267 | 120.1366 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Tzoonie 2 | PS_BC217 | Lower Mainland | 49.8763 | -123.618 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3270699 | 6000 | 880 |  | 0.28 | 151 | 106 | Multi-Stage | Multi-Stage | 8.6 | 6 | 33.3 | 1621.4495 |  |  | 1842.6836 | 78.2987 | 1920.9823 | 135.6589 | 135.6589 | 16.2145 | 16214.4949 | 1 | 0 | 1 | 1842683.8785 | 307113.4071 | 112.4635 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Uchuck | PS_BC218 | Vancouver Island | 49.036 | -125.0937 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 2741158 | 3000 | 525 |  | 0.07 | 127 | 89 | Single-Stage | Single-Stage | 8.6 | 6 | 34.4 | 1283.039 |  |  | 1458.0996 | 66.8015 | 1524.9011 | 107.6878 | 215.3756 | 19.2456 | 38491.1706 | 1 | 0 | 1 | 2916199.0605 | 486033.3676 | 177.9717 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Un-named - Zeballos | PS_BC219 | Vancouver Island | 50.0827 | -126.7279 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Lake to Lake | 3652558 | 3000 | 394 |  | 0.06 | 169 | 118 | Single-Stage | Single-Stage | 8.6 | 6 | 32.6 | 1292.5829 |  |  | 1468.9458 | 67.1382 | 1536.0839 | 108.4775 | 216.955 | 19.3887 | 38777.4875 | 1 | 0 | 1 | 2937891.2218 | 489648.9187 | 179.346 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Clore-16 | PS_BC220 | 2L99 | 54.212 | -127.933 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 11287120 | 16000 | 680 |  | 0.16 | 196 | 137 | Single-Stage | Single-Stage | 22.9 | 16 | 87.7 | 1374.2614 |  |  | 1561.7686 | 69.9878 | 1631.7564 | 115.2339 | 115.2339 | 13.721 | 13720.9992 | 1 | 0 | 1 | 1374261.0047 | 85891.3844 | 95.2847 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Upper Clore-48 | PS_BC221 | 2L99 | 54.184 | -127.975 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 16930679 | 24000 | 680 |  | 0.16 | 98 | 69 | Single‐Stage | Single‐Stage | 68.6 | 48 | 151.1 | 1599.9772 |  |  | 1818.2815 | 77.5938 | 1895.8753 | 133.8858 | 267.7716 | 23.9705 | 47941.0393 | 1 | 0 | 1 | 3199953.9691 | 66666.0894 | 221.9493 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Upper Deserted - Un-named | PS_BC222 | Lower Mainland | 50.1539 | -123.6856 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3959031 | 6000 | 727 |  | 0.23 | 183 | 128 | Multi-Stage | Multi-Stage | 8.6 | 6 | 26.9 | 1269.8635 |  |  | 1443.1264 | 66.3353 | 1509.4618 | 106.5975 | 106.5975 | 12.6986 | 12698.6343 | 1 | 0 | 1 | 1443125.9722 | 240520.6136 | 88.0696 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Eldrid - Lower Eldrid | PS_BC223 | Lower Mainland | 50.1557 | -124.1422 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3728258 | 6000 | 772 |  | 0.3 | 173 | 121 | Multi-Stage | Multi-Stage | 8.6 | 6 | 32 | 1617.1033 |  |  | 1837.7444 | 78.1563 | 1915.9007 | 135.3 | 135.3 | 16.171 | 16171.0327 | 1 | 0 | 1 | 1837744.4196 | 306291.1183 | 112.1199 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Elsie | PS_BC224 | Vancouver Island | 49.4415 | -125.1668 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 7514923 | 6000 | 383 |  | 0.12 | 348 | 244 | Single-Stage | Single-Stage | 8.6 | 6 | 49.3 | 1958.411 |  |  | 2225.6208 | 88.9987 | 2314.6195 | 163.4573 | 163.4573 | 19.5841 | 19584.1095 | 1 | 0 | 1 | 2225620.7861 | 370936.9886 | 135.8265 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Falls-16 | PS_BC225 | 2L99 | 53.7 | -128.488 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 13705788 | 16000 | 560 |  | 0.21 | 238 | 167 | Single-Stage | Single-Stage | 22.9 | 16 | 118.6 | 1696.6316 |  |  | 1928.1238 | 80.7436 | 2008.8674 | 141.8653 | 141.8653 | 16.9533 | 16953.35 | 1 | 0 | 1 | 1696631.419 | 106039.75 | 117.7316 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Upper Falls-48 | PS_BC226 | 2L99 | 53.702 | -128.527 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 20558682 | 24000 | 560 |  | 0.21 | 119 | 83 | Single‐Stage | Single‐Stage | 68.6 | 48 | 214.5 | 2659.0269 |  |  | 3021.8303 | 109.5186 | 3131.3489 | 221.1344 | 442.2688 | 39.8395 | 79679.0957 | 1 | 0 | 1 | 5318054.1982 | 110792.5333 | 368.8847 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Upper Frell | PS_BC227 | Lower Mainland | 49.8636 | -123.913 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 4464784 | 6000 | 620 |  | 0.41 | 207 | 145 | Single-Stage | Single-Stage | 8.6 | 6 | 43 | 1570.1982 |  |  | 1784.4394 | 76.6111 | 1861.0505 | 131.4265 | 131.4265 | 31.404 | 31403.9633 | 1 | 0 | 1 | 1784439.9502 | 297406.2766 | 108.7987 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Upper Great Central | PS_BC228 | Vancouver Island | 49.3776 | -125.2262 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 3575423 | 6000 | 805 |  | 0.35 | 166 | 116 | Multi-Stage | Multi-Stage | 8.6 | 6 | 43.2 | 1693.5509 |  |  | 1924.6227 | 80.6442 | 2005.2668 | 141.611 | 141.611 | 16.9355 | 16935.5093 | 1 | 0 | 1 | 1924623.0086 | 320770.5014 | 117.5025 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Lukes-16 | PS_BC229 | 2L99 | 54.132 | -128.845 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Not stated | 11287120 | 16000 | 680 |  | 0.09 | 196 | 137 | Single-Stage | Single-Stage | 22.9 | 16 | 128.5 | 2074.2738 |  |  | 2357.2922 | 92.5376 | 2449.8298 | 173.0058 | 173.0058 | 20.7134 | 20713.4315 | 1 | 0 | 1 | 2074273.8404 | 129642.1866 | 143.8433 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Upper Lukes-48 | PS_BC230 | 2L99 | 54.196 | -128.884 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 500 | 500 | 80% | Fresh | Not stated | 16930679 | 24000 | 680 |  | 0.09 | 98 | 69 | Single‐Stage | Single‐Stage | 68.6 | 48 | 223.7 | 3309.0472 |  |  | 3760.5409 | 127.0348 | 3887.5756 | 274.5388 | 549.0775 | 49.5737 | 99147.4125 | 1 | 0 | 1 | 6618095.0511 | 137876.5269 | 459.0158 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Upper Misery - Lower Misery | PS_BC231 | Lower Mainland | 49.7558 | -123.602 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4920027 | 6000 | 585 |  | 0.37 | 228 | 159 | Single-Stage | Single-Stage | 8.6 | 6 | 34.9 | 1303.5677 |  |  | 1481.4294 | 67.5247 | 1548.9541 | 109.3864 | 109.3864 | 13.0357 | 13035.6776 | 1 | 0 | 1 | 1481428.825 | 246905.3768 | 90.3601 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Misery - Un-named | PS_BC232 | Lower Mainland | 49.8098 | -123.5848 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 7159740 | 6000 | 402 |  | 0.07 | 331 | 232 | Single-Stage | Single-Stage | 8.6 | 6 | 39.1 | 1777.9231 |  |  | 2020.5068 | 83.3484 | 2103.8551 | 148.5733 | 148.5733 | 17.7792 | 17779.2303 | 1 | 0 | 1 | 2020506.6905 | 336751.306 | 123.3433 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Quinsam - Upper Campbell | PS_BC233 | Vancouver Island | 49.8679 | -125.6338 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 27943840 | 6000 | 103 |  | 0.03 | 1294 | 906 | Single-Stage | Single-Stage | 8.6 | 6 | 31.2 | 2479.5918 |  |  | 2817.9127 | 104.4489 | 2922.3616 | 206.3758 | 206.3758 | 24.7959 | 24795.9178 | 1 | 0 | 1 | 2817912.6463 | 469651.726 | 172.0164 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Tzoonie - Lower Tzoonie | PS_BC234 | Lower Mainland | 49.8819 | -123.6145 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 2945973 | 6000 | 977 |  | 0.19 | 136 | 95 | Multi-Stage | Multi-Stage | 8.6 | 6 | 33.8 | 1707.6584 |  |  | 1940.655 | 81.0993 | 2021.7543 | 142.7753 | 142.7753 | 17.0766 | 17076.5845 | 1 | 0 | 1 | 1940655.3493 | 323442.3673 | 118.4187 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Upper Vancouver - Lower Vancouver | PS_BC235 | Lower Mainland | 49.9109 | -123.7357 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 5320177 | 6000 | 541 |  | 0.39 | 246 | 172 | Single-Stage | Single-Stage | 8.6 | 6 | 31.8 | 1293.9098 |  |  | 1470.4537 | 67.1849 | 1537.6386 | 108.5873 | 108.5873 | 12.9391 | 12939.0976 | 1 | 0 | 1 | 1470453.9038 | 245075.2689 | 89.7875 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | View - Great Central | PS_BC236 | Vancouver Island | 49.3697 | -125.3618 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 13387049 | 6000 | 215 |  | 0.13 | 620 | 434 | Single-Stage | Single-Stage | 8.6 | 6 | 27.6 | 1936.8914 |  |  | 2201.1651 | 88.3341 | 2289.4992 | 161.6834 | 161.6834 | 19.3689 | 19368.9149 | 1 | 0 | 1 | 2201165.139 | 366861.0474 | 134.3377 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Walt - Khartoum | PS_BC237 | Lower Mainland | 49.8916 | -124.0993 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3434625 | 6000 | 838 |  | 0.17 | 159 | 111 | Multi-Stage | Multi-Stage | 8.6 | 6 | 27 | 1687.5849 |  |  | 1917.8427 | 80.4513 | 1998.294 | 141.1186 | 141.1186 | 16.8758 | 16875.8498 | 1 | 0 | 1 | 1917843.1345 | 319640.1407 | 117.0444 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Walter | PS_BC238 | Lower Mainland | 50.2213 | -124.7845 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 5767013 | 6000 | 480 |  | 0.32 | 267 | 187 | Single-Stage | Single-Stage | 8.6 | 6 | 31 | 1795.6059 |  |  | 2040.6023 | 83.9098 | 2124.5121 | 150.032 | 150.032 | 35.9121 | 35912.118 | 1 | 0 | 1 | 2040602.3746 | 340100.014 | 124.8321 | 6 | 9
| No Existing Project | BC Hydro | [8 empty] | Wilson - Chehalis | PS_BC239 | Lower Mainland | 49.4313 | -122.0385 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 4797026 | 6000 | 600 |  | 0.13 | 222 | 155 | Single-Stage | Single-Stage | 8.6 | 6 | 27.6 | 1521.1564 |  |  | 1728.7063 | 74.9796 | 1803.6859 | 127.3754 | 127.3754 | 15.2116 | 15211.5648 | 1 | 0 | 1 | 1728706.4077 | 288117.162 | 105.4774 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Windsor - Goat | PS_BC240 | Lower Mainland | 50.0265 | -124.292 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 19713805 | 6000 | 146 |  | 0.09 | 913 | 639 | Single-Stage | Single-Stage | 8.6 | 6 | 37 | 1875.9466 |  |  | 2131.9048 | 86.4388 | 2218.3436 | 156.6584 | 156.6584 | 18.7595 | 18759.466 | 1 | 0 | 1 | 2131905.0605 | 355316.9375 | 130.1003 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Windsor - Powell | PS_BC241 | Lower Mainland | 50.0233 | -124.3233 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 19713805 | 6000 | 146 |  | 0.04 | 913 | 639 | Single-Stage | Single-Stage | 8.6 | 6 | 36.1 | 2249.1206 |  |  | 2555.9955 | 97.7601 | 2653.7555 | 187.407 | 187.407 | 22.4912 | 22491.2061 | 1 | 0 | 1 | 2555995.3456 | 425999.4151 | 155.9829 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Woss 1 | PS_BC242 | Vancouver Island | 50.1144 | -126.5996 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Man Made | 4680025 | 6000 | 615 |  | 0.2 | 217 | 152 | Single-Stage | Single-Stage | 8.6 | 6 | 51.4 | 1548.5481 |  |  | 1759.8354 | 75.8929 | 1835.7283 | 129.6383 | 129.6383 | 15.4855 | 15485.4809 | 1 | 0 | 1 | 1759835.4207 | 293306.2852 | 107.4244 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Woss 2 | PS_BC243 | Vancouver Island | 50.1437 | -126.6183 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Fresh | Lake to Lake | 3505744 | 6000 | 821 |  | 0.14 | 162 | 114 | Multi-Stage | Multi-Stage | 8.6 | 6 | 32.2 | 1855.3035 |  |  | 2108.4452 | 85.7924 | 2194.2376 | 154.956 | 154.956 | 18.553 | 18553.0349 | 1 | 0 | 1 | 2108444.6348 | 351407.0574 | 128.726 | 5 | 8
| No Existing Project | BC Hydro | [8 empty] | Young | PS_BC244 | Lower Mainland | 50.7617 | -125.706 | British Columbia.a |  |  |  | 50 | Hydro_pump | hydro_pump | 1000 | 1000 | 80% | Salt | Lake | 2661698 | 6000 | 1040 |  | 0.37 | 123 | 86 | Multi-Stage | Multi-Stage | 8.6 | 6 | 102 | 2172.9377 |  |  | 2469.4181 | 95.5012 | 2564.9193 | 181.1334 | 181.1334 | 43.4588 | 43458.7546 | 1 | 0 | 1 | 2469417.9571 | 411569.2778 | 151.1729 | 6 | 9
Specific Notes:
Loaded Capital Cost presumed to be the equivalent of Implementation Costs, namely they include Capital Overhead and IDC
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume Hydro_daily and Hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset
Note on AZ2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note this is an added column that does not appear for other provinces

## Distribution
BC | EXISTING TRANSFORMERS
| Substation Name | Substation Code | Owner | Latitude | Longitude | Operating Region | Transformers | Primary Voltage | Secondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Other References | Notes | Count
[8 empty] | (kV) | (kV) | (MVA) | (MVA) |  | (MW) | (MW)
| AA Lambert | BC_AAL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 1
| AA Lambert | BC_AAL_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 40 | 50 | 0.9 | 36 | 45 |  |  | 721
| Abbotsford | BC_ABB_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 3
| Aberfeldie GS | BC_ABN_GSS | BC Hydro | 49.4933 | -115.3624 | British Columbia | [10 empty] | 4
| Afton Mine | BC_AFN_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 6
| Ainsworth | BC_AWL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 27
| Aiyansh | BC_AYH_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 11.25 | 12 | 0.9 | 10.125 | 10.8 |  |  | 29
| Albreda | BC_ABA_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 2
| Alouette GS | BC_ALU_GSS | BC Hydro | 49.3721 | -122.3124 | British Columbia | [10 empty] | 9
| Annacis Island | BC_ANN_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 48 | 55 | 0.9 | 43.2 | 49.5 |  |  | 14
| Annacis Island | BC_ANN_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 48 | 62 | 0.9 | 43.2 | 55.8 |  |  | 15
| Annacis Island | BC_ANN_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 12 | 48 | 55 | 0.9 | 43.2 | 49.5 |  |  | 16
| Annacis Island Wastewater Treatment Plant | BC_AWT_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 28
| Apollo Forest Products | BC_AFP_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 7
| Arawana | BC_AWA_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 10 | 12.5 | 0.9 | 9 | 11.25 |  |  | 722
| Armstrong | BC_ARM_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33 | 0.9 | 25.2 | 29.7 |  |  | 17
| Armstrong | BC_ARM_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 28 | 33 | 0.9 | 25.2 | 29.7 |  |  | 18
| Arnott | BC_ARN_DSS | BC Hydro |  |  | British Columbia | T11 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 19
| Arnott | BC_ARN_DSS | BC Hydro |  |  | British Columbia | T12 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 20
| Arrow Lakes GS | BC_ALH_GSS | FortisBC | 49.343 | -117.7688 | British Columbia | [10 empty] | 723
| AS Mawdsley TS | BC_ASM_TSS | FortisBC |  |  | British Columbia | [10 empty] | 724
| Ash River GS | BC_ASH_GSS | BC Hydro | 49.3734 | -125.1506 | British Columbia | [10 empty] | 21
| Ashcroft | BC_AFT_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 14 | 15 | 0.9 | 12.6 | 13.5 |  |  | 8
| Ashlu GS | BC_ASL_GSS | BC Hydro | 49.9143 | -123.325 | British Columbia | [10 empty] | 22
| Ashton Creek | BC_ACK_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 5
| Atchelitz | BC_ALZ_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 10
| Atchelitz | BC_ALZ_DSS | BC Hydro |  |  | British Columbia | T4 | 230 | 25 | 87 | 100 | 0.9 | 78.3 | 90 |  |  | 11
| Atchelitz | BC_ALZ_DSS | BC Hydro |  |  | British Columbia | T5 | 60 | 25 | 49 | 55 | 0.9 | 44.1 | 49.5 |  |  | 12
| Atchelitz | BC_ALZ_DSS | BC Hydro |  |  | British Columbia | T6 | 60 | 25 | 49 | 55 | 0.9 | 44.1 | 49.5 |  |  | 13
| Athalmer | BC_ATH_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 52 | 67 | 0.9 | 46.8 | 60.3 |  |  | 23
| Athalmer | BC_ATH_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 52 | 67 | 0.9 | 46.8 | 60.3 |  |  | 24
| Avola | BC_AVO_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 12 | 2 | 2.4 | 0.9 | 1.8 | 2.16 |  |  | 25
| Avola | BC_AVO_DSS | BC Hydro |  |  | British Columbia | T2 | 12 | 25 | 0.3 | 0.3 | 0.9 | 0.27 | 0.27 |  |  | 26
| Babine Lake | BC_BAB_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 16.7 | 20 | 0.9 | 15.03 | 18 |  |  | 30
| Balfour | BC_BAL_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 31
| Balfour | BC_BAL_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 32
| Barlow | BC_BLW_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 55
| Barnard | BC_BND_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 12 | 177 | 214 | 0.9 | 159.3 | 192.6 |  |  | 60
| Barnard | BC_BND_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 12 | 177 | 214 | 0.9 | 159.3 | 192.6 |  |  | 61
| Barriere | BC_BAR_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 18.8 | 23.2 | 0.9 | 16.92 | 20.88 |  |  | 33
| BC Chemical | BC_BCM_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 38
| BC Gas | BC_BCG_ISS | FortisBC |  |  | British Columbia | [10 empty] | 725
| BC Rail | BC_BCR_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 39
| Bear Creek GS | BC_BRK_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 69
| Bear Mountain | BC_BMT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 57
| Bear Mountain GS | BC_BMW_GSS | BC Hydro | 55.7041 | -120.4264 | British Columbia | [10 empty] | 58
| Beaver Cove | BC_BVC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 79
| Beaver Park | BC_BEP_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 10 | 12.5 | 0.9 | 9 | 11.25 |  |  | 726
| Beaverley | BC_BVY_DSS | BC Hydro |  |  | British Columbia | T10 | 66 | 25 | 43.7 | 55.3 | 0.9 | 39.33 | 49.77 |  |  | 80
| Beaverley | BC_BVY_DSS | BC Hydro |  |  | British Columbia | T11 | 66 | 25 | 43.7 | 55.3 | 0.9 | 39.33 | 49.77 |  |  | 81
| Bentley TS | BC_BEN_TSS | FortisBC |  |  | British Columbia | [10 empty] | 727
| Benvoulin | BC_BEV_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 728
| Big Bend | BC_BBS_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 35
| Big Bend | BC_BBS_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 36
| Big Silver GS | BC_BSV_GSS | BC Hydro | 49.693 | -121.8591 | British Columbia | [10 empty] | 75
| Big White | BC_BWS_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 38 | 47.5 | 0.9 | 34.2 | 42.75 |  |  | 729
| Bingham | BC_BMP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 56
| Black Mountain | BC_BLK_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 730
| Blackpool | BC_BLP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 53
| Blue River | BC_BLU_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 17.4 | 21.2 | 0.9 | 15.66 | 19.08 |  |  | 54
| Blue River Pumping Station | BC_BLE_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 51
| Blueberry | BC_BLB_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 10 | 12.5 | 0.9 | 9 | 11.25 |  |  | 731
| Bob Quinn | BC_BQN_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 64
| Bone Creek | BC_BET_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 42
| Bone Creek GS | BC_BNC_GSS | BC Hydro | 52.2553 | -119.1808 | British Columbia | [10 empty] | 59
| Boston Bar GS | BC_BBR_DFS | BC Hydro | 49.8113 | -121.4585 | British Columbia | T1 | 60 | 25 | 13 | 15 | 0.9 | 11.7 | 13.5 |  |  | 34
| Boulder Creek GS | BC_BDH_GSS | BC Hydro | 50.635 | -123.405 | British Columbia | [10 empty] | 40
| Box Canyon GS | BC_BOX_GSS | BC Hydro | 49.6006 | -123.4267 | British Columbia | [10 empty] | 63
| BP Noel 2 | BC_NL2_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 448
| BP Noel 3 | BC_NL3_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 449
| BP Noel 5 | BC_NL5_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 450
| Bradford | BC_BRA_DSS | FortisBC |  |  | British Columbia | [10 empty] | 732
| Bremner GS | BC_BRE_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 68
| Brenda Mines | BC_BDM_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 41
| Bridge River 1 GS | BC_BR1_DFS | BC Hydro | 50.7299 | -122.24 | British Columbia | T14 | 12.6 | 12.6 | 2 | 2.2 | 0.9 | 1.8 | 1.98 |  |  | 65
| Bridge River 1 GS | BC_BR1_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 67
| Bridge River 2 GS | BC_BR2_GSS | BC Hydro | 50.7299 | -122.24 | British Columbia | [10 empty] | 66
| Bridge River TS | BC_BRT_TSS | BC Hydro |  |  | British Columbia | [10 empty] | 74
| Brilliant Expansion GS | BC_BRX_GSS | FortisBC | 49.3231 | -117.6198 | British Columbia | [10 empty] | 734
| Brilliant GS | BC_BRD_GSS | FortisBC | 49.3249 | -117.6207 | British Columbia | [10 empty] | 735
| Brilliant SWs | BC_BSS_SWS | FortisBC |  |  | British Columbia | [10 empty] | 736
| Brilliant TS | BC_BTS_TSS | FortisBC |  |  | British Columbia | [10 empty] | 78
| Brilliant TS | BC_BTS_TSS | FortisBC |  |  | British Columbia | [10 empty] | 733
| Britannia | BC_BTA_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 34 | 5 | 6 | 0.9 | 4.5 | 5.4 |  |  | 77
| Brocklehurst | BC_BKL_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 52 | 66.3 | 0.9 | 46.8 | 59.67 |  |  | 49
| Brocklehurst | BC_BKL_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 52 | 66.3 | 0.9 | 46.8 | 59.67 |  |  | 50
| Brown Lake GS | BC_BRL_GSS | BC Hydro | 54.0273 | -129.8437 | British Columbia | [10 empty] | 70
| Brucejack Mine | BC_BJK_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 45
| Brucejack TS | BC_BJT_TSS | BC Hydro |  |  | British Columbia | [10 empty] | 46
| Buckeye | BC_BCI_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 37
| Buckley Bay | BC_BKB_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 84 | 100 | 0.9 | 75.6 | 90 |  |  | 47
| Buckley Bay | BC_BKB_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 84 | 100 | 0.9 | 75.6 | 90 |  |  | 48
| Bull River Mineral | BC_BRM_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 71
| Bullmoose | BC_BLM_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 52
| Burnett | BC_BNT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 62
| Burns Lake | BC_BRN_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33.3 | 0.9 | 25.2 | 29.97 |  |  | 72
| Burns Lake | BC_BRN_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 26.2 | 33.3 | 0.9 | 23.58 | 29.97 |  |  | 73
| Burrard GS | BC_BSY_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 76
| Cache Creek GS | BC_CCW_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 95
| Cambie | BC_CAM_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 82
| Cambie | BC_CAM_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 25 | 87 | 100 | 0.9 | 78.3 | 90 |  |  | 83
| Cambie | BC_CAM_DSS | BC Hydro |  |  | British Columbia | T4 | 230 | 25 | 87 | 100 | 0.9 | 78.3 | 90 |  |  | 84
| Camosun | BC_CSN_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 12 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 134
| Camosun | BC_CSN_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 12 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 135
| Campbell River | BC_CBL_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 77.25 | 94.5 | 0.9 | 69.525 | 85.05 |  |  | 89
| Campbell River | BC_CBL_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 77.25 | 94.5 | 0.9 | 69.525 | 85.05 |  |  | 90
| Campbell River | BC_CBL_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 81 | 99.38 | 0.9 | 72.9 | 89.442 |  |  | 91
| Canadian Auto Parts Toyota | BC_CAN_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 85
| Canadian National | BC_CNG_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 117
| Canal Flats | BC_CNL_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 3.8 | 4.5 | 0.9 | 3.42 | 4.05 |  |  | 119
| Canexus | BC_NEX_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 437
| Canexus Corporation | BC_NXC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 467
| Canfor | BC_PLT_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 496
| Canfor Rustad Division | BC_NOS_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 456
| Canoe Creek GS | BC_CNK_GSS | BC Hydro | 49.1769 | -125.3956 | British Columbia | [10 empty] | 118
| Canoe Forest Products Ltd | BC_FCO_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 192
| Canreed | BC_CRD_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 130
| Cape Scott GS | BC_CSS_GSS | BC Hydro | 50.789 | -128.0033 | British Columbia | [10 empty] | 139
| Capilano | BC_CAP_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 43.68 | 55.33 | 0.9 | 39.312 | 49.797 |  |  | 86
| Capilano | BC_CAP_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 43.68 | 55.33 | 0.9 | 39.312 | 49.797 |  |  | 87
| Capilano Pumps | BC_CPS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 126
| Cariboo Pulp GS | BC_CBP_GSS | BC Hydro | 52.997 | -122.4853 | British Columbia | [10 empty] | 94
| Carquille | BC_CRQ_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 131
| Cascade | BC_CSC_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 737
| Castlegar | BC_CAS_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 738
| Catalyst Paper Crofton GS | BC_CFT_GSS | BC Hydro | 48.8757 | -123.65 | British Columbia | [10 empty] | 97
| Cathedral Square | BC_CSQ_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 12 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 136
| Cathedral Square | BC_CSQ_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 12 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 137
| Cathedral Square | BC_CSQ_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 12 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 138
| Chappell Pumping Station | BC_CPL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 125
| Chase | BC_CHS_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 18.8 | 22.1 | 0.9 | 16.92 | 19.89 |  |  | 102
| Cheakamus GS | BC_CMS_DFS | BC Hydro | 49.9337 | -123.291 | British Columbia | T3 | 230 | 25 | 4.5 | 5.4 | 0.9 | 4.05 | 4.86 |  |  | 114
| Cheekye | BC_CKY_DSS | BC Hydro |  |  | British Columbia | T8 | 60 | 25 | 8.82 | 11.17 | 0.9 | 7.938 | 10.053 |  |  | 103
| Cheekye | BC_CKY_DSS | BC Hydro |  |  | British Columbia | T9 | 60 | 25 | 26.25 | 33.25 | 0.9 | 23.625 | 29.925 |  |  | 104
| Chetwynd | BC_CWD_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 143
| Chetwynd | BC_CWD_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 144
| Chetwynd GS | BC_LAP_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 348
| Chevron | BC_CVN_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 142
| Chief Lake | BC_CHF_DSS | BC Hydro |  |  | British Columbia | T10 | 66 | 25 | 43.7 | 55.3 | 0.9 | 39.33 | 49.77 |  |  | 98
| Chief Lake | BC_CHF_DSS | BC Hydro |  |  | British Columbia | T11 | 66 | 25 | 43.7 | 55.3 | 0.9 | 39.33 | 49.77 |  |  | 99
| Chilliwack | BC_CHK_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 44 | 56 | 0.9 | 39.6 | 50.4 |  |  | 100
| Chilliwack | BC_CHK_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 44 | 56 | 0.9 | 39.6 | 50.4 |  |  | 101
| Christina Lake | BC_CHR_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 5 | 6.25 | 0.9 | 4.5 | 5.625 |  |  | 739
| Clayburn | BC_CBN_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 92
| Clayburn | BC_CBN_DSS | BC Hydro |  |  | British Columbia | T4 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 93
| Clearwater | BC_CLW_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 30 | 0.9 | 25.2 | 27 |  |  | 111
| Clinton | BC_CLN_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 13.1 | 16 | 0.9 | 11.79 | 14.4 |  |  | 110
| Clowhom GS | BC_COM_GSS | BC Hydro | 49.7109 | -123.5321 | British Columbia | [10 empty] | 124
| Coal Mountain | BC_CMO_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 113
| Coffee Creek | BC_COF_DSS | FortisBC |  |  | British Columbia | T3 |  |  | 8.4 | 10.5 | 0.9 | 7.56 | 9.45 |  |  | 740
| Colebank | BC_CLB_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 5.6 | 6.7 | 0.9 | 5.04 | 6.03 |  |  | 105
| Colwood | BC_CLD_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 106
| Colwood | BC_CLD_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 107
| Colwood | BC_CLD_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 108
| Como Lake | BC_COK_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 120
| Como Lake | BC_COK_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 121
| Como Lake | BC_COK_DSS | BC Hydro |  |  | British Columbia | T4 | 230 | 25 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 122
| Como Lake | BC_COK_DSS | BC Hydro |  |  | British Columbia | T5 | 230 | 25 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 123
| Comox | BC_CMX_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 78.8 | 93.9 | 0.9 | 70.92 | 84.51 |  |  | 115
| Comox | BC_CMX_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 78.8 | 93.9 | 0.9 | 70.92 | 84.51 |  |  | 116
| Confor Houston Sawmill | BC_NHS_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 442
| Continental Lime Limited | BC_CLL_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 109
| Conuma Coal | BC_MNK_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 407
| Conuma Hatchery | BC_CMH_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 112
| Copper Mountain | BC_CUM_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 141
| Coquitlam | BC_CQM_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 44 | 44 | 0.9 | 39.6 | 39.6 |  |  | 127
| Coquitlam | BC_CQM_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 12 | 44 | 44 | 0.9 | 39.6 | 39.6 |  |  | 128
| Corra Linn GS | BC_COR_GSS | FortisBC | 49.4689 | -117.4686 | British Columbia | [10 empty] | 741
| Cottonwood | BC_COT_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 10 | 12.5 | 0.9 | 9 | 11.25 |  |  | 742
| Cranbrook | BC_CBK_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 88
| Crawford Bay | BC_CRA_DSS | FortisBC |  |  | British Columbia | T5 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 743
| Crestbrook | BC_CFE_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 96
| Crestbrook Canal Flats | BC_CRC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 129
| Crestbrook Skookumchuck | BC_CRS_DFS | BC Hydro | 49.5284 | -115.7578 | British Columbia | [10 empty] | 132
| Creston | BC_CRE_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 744
| Creston | BC_CRE_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 745
| Crowsnest Pass GS | BC_CRW_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 133
| Culliton Creek GS | BC_CTN_GSS | BC Hydro | 49.8772 | -123.1599 | British Columbia | [10 empty] | 140
| Cypress | BC_CYP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 145
| Dal Grauer | BC_DGR_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 153
| Dal Grauer | BC_DGR_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 154
| Dal Grauer | BC_DGR_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 155
| Dal Grauer | BC_DGR_DSS | BC Hydro |  |  | British Columbia | T4 | 60 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 156
| Darfield | BC_DFD_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 151
| Dasque Creek GS | BC_DSQ_GSS | BC Hydro | 54.3835 | -128.9149 | British Columbia | [10 empty] | 163
| Dawson Creek | BC_DAW_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 56 | 66.5 | 0.9 | 50.4 | 59.85 |  |  | 146
| Dawson Creek | BC_DAW_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 56 | 66.5 | 0.9 | 50.4 | 59.85 |  |  | 147
| Dawson Creek | BC_DAW_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 148
| Deep Cove | BC_DCV_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 49.7 | 61.85 | 0.9 | 44.73 | 55.665 |  |  | 149
| Deep Cove | BC_DCV_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 12 | 49.7 | 61.85 | 0.9 | 44.73 | 55.665 |  |  | 150
| Delta Port Terminal | BC_DPT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 162
| DG Bell | BC_DGB_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 746
| Diana Lake | BC_DIL_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 7.2 | 0.2 | 0.24 | 0.9 | 0.18 | 0.216 |  |  | 157
| Dokie | BC_DKT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 158
| Dokie GS | BC_DKW_GSS | BC Hydro | 55.8118 | -122.2474 | British Columbia | [10 empty] | 159
| Domtar Kamloops | BC_WEY_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 690
| Doran Taylor GS | BC_DTR_GSS | BC Hydro | 49.2964 | -125.2755 | British Columbia | [10 empty] | 164
| Douglas GS | BC_DGL_GSS | BC Hydro | 49.7676 | -122.151 | British Columbia | [10 empty] | 152
| Douglas Street | BC_DUG_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 80 | 87.3 | 0.9 | 72 | 78.57 |  |  | 165
| Douglas Street | BC_DUG_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 88.2 | 107.2 | 0.9 | 79.38 | 96.48 |  |  | 166
| Douglas Street | BC_DUG_DSS | BC Hydro |  |  | British Columbia | T4 | 138 | 25 | 80 | 87.3 | 0.9 | 72 | 78.57 |  |  | 167
| Duck Lake | BC_DUC_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 23 | 28.75 | 0.9 | 20.7 | 25.875 |  |  | 747
| Dunkley Lumber | BC_DKY_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 160
| Dunsmuir | BC_DMR_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 161
| East Toba River GS | BC_ETR_GSS | BC Hydro | 50.6751 | -123.9603 | British Columbia | [10 empty] | 184
| Elk Falls Mill | BC_EFM_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 173
| Elkford | BC_EFD_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 18.6 | 22.1 | 0.9 | 16.74 | 19.89 |  |  | 171
| Elkford | BC_EFD_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 12.9 | 15 | 0.9 | 11.61 | 13.5 |  |  | 172
| Elko GS | BC_ELK_GSS | BC Hydro | 49.2901 | -115.1046 | British Columbia | [10 empty] | 175
| Elkview Coal | BC_EV1_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 186
| Ellison | BC_ELL_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 748
| Ellsworth | BC_EWL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 187
| Emerald SWS | BC_ESS_SWS | FortisBC |  |  | British Columbia | [10 empty] | 749
| Encana 15-27 | BC_E15_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 169
| Encana 4-26 | BC_E42_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 170
| Encana 9-27 | BC_KIS_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 333
| Encana Tower | BC_ET3_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 183
| Endako | BC_EKO_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 174
| Enderby | BC_END_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 10.6 | 13.3 | 0.9 | 9.54 | 11.97 |  |  | 176
| Enderby | BC_END_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 |  |  | 177
| Equity Silver | BC_EQU_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 178
| Erco Worldwide | BC_ERW_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 179
| Esco Foundry | BC_ESC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 180
| Esquimalt | BC_ESQ_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 12 | 157.5 | 200 | 0.9 | 141.75 | 180 |  |  | 181
| Esquimalt | BC_ESQ_DSS | BC Hydro |  |  | British Columbia | T13 | 230 | 12 | 168 | 200 | 0.9 | 151.2 | 180 |  |  | 182
| Eurocan | BC_EUR_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 185
| FA Lee TS | BC_LEE_TSS | FortisBC |  |  | British Columbia | tert |  |  | 52.3 | 52.3 | 0.9 | 47.07 | 47.07 |  |  | 750
| Fairmont | BC_FMT_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 4 | 4.8 | 0.9 | 3.6 | 4.32 |  |  | 207
| Fairmont | BC_FMT_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 12.5 | 15 | 0.9 | 11.25 | 13.5 |  |  | 208
| Falls River GS | BC_FLS_GSS | BC Hydro | 53.9835 | -129.7342 | British Columbia | [10 empty] | 201
| Fareview Container Terminal | BC_PRT_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 506
| Fernie | BC_FNE_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 25 | 30 | 0.9 | 22.5 | 27 |  |  | 210
| Fernie | BC_FNE_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 26.2 | 33.3 | 0.9 | 23.58 | 29.97 |  |  | 211
| Fiberco | BC_FBC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 188
| Finlay Forest Industries | BC_FFI_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 193
| Finn Pumping Station | BC_FPS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 215
| Fire GS | BC_FRE_GSS | BC Hydro | 49.7834 | -122.2347 | British Columbia | [10 empty] | 217
| Fleetwood | BC_FLW_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 202
| Fleetwood | BC_FLW_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 203
| Fletcher Challenge | BC_FCC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 189
| FMC Prince George | BC_FMC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 206
| Foothills | BC_FHS_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 46.8 | 55.3 | 0.9 | 42.12 | 49.77 |  |  | 195
| Foothills | BC_FHS_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 42 | 53.2 | 0.9 | 37.8 | 47.88 |  |  | 196
| Fording Coal | BC_FRO_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 219
| Forest Kerr GS | BC_FKR_GSS | BC Hydro | 56.7172 | -130.6866 | British Columbia | [10 empty] | 200
| Forest View | BC_FVW_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 223
| Forest View | BC_FVW_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 26.25 | 33.25 | 0.9 | 23.625 | 29.925 |  |  | 224
| Fort Nelson GS | BC_FNG_GSS | BC Hydro | 58.801 | -122.7562 | British Columbia | [10 empty] | 212
| Fort St James | BC_FM2_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 13.75 | 16.6 | 0.9 | 12.375 | 14.94 |  |  | 204
| Fort St James | BC_FM2_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 28 | 33.3 | 0.9 | 25.2 | 29.97 |  |  | 205
| Fort St James Green Energy GS | BC_FGE_GSS | BC Hydro | 54.4893 | -124.2153 | British Columbia | [10 empty] | 194
| Fort St. John | BC_FJN_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 197
| Fort St. John | BC_FJN_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 56 | 66.5 | 0.9 | 50.4 | 59.85 |  |  | 198
| Fort St. John | BC_FJN_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 56 | 66.5 | 0.9 | 50.4 | 59.85 |  |  | 199
| Fort Steele | BC_FST_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 1.7 | 2.1 | 0.9 | 1.53 | 1.89 |  |  | 222
| Fox Creek | BC_FOX_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 26.3 | 33.3 | 0.9 | 23.67 | 29.97 |  |  | 213
| Fox Creek | BC_FOX_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 26.3 | 33.3 | 0.9 | 23.67 | 29.97 |  |  | 214
| Fraser Lake | BC_FSR_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 14 | 15 | 0.9 | 12.6 | 13.5 |  |  | 220
| Fraser Lake Sawmill | BC_FSS_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 221
| Fruitvale | BC_FRU_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 8 | 10 | 0.9 | 7.2 | 9 |  |  | 751
| Function Junction | BC_FCN_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 78.75 | 99.75 | 0.9 | 70.875 | 89.775 |  |  | 190
| Function Junction | BC_FCN_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 78.75 | 99.75 | 0.9 | 70.875 | 89.775 |  |  | 191
| Furry Creek | BC_FRC_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 2.67 | 3.2 | 0.9 | 2.403 | 2.88 |  |  | 216
| Furry Creek GS | BC_FRI_GSS | BC Hydro | 49.5793 | -123.202 | British Columbia | [10 empty] | 218
| Galiano | BC_GLS_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33.6 | 0.9 | 25.2 | 30.24 |  |  | 240
| Gavin Lake | BC_GVL_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 12.5 | 15 | 0.9 | 11.25 | 13.5 |  |  | 257
| George Dickie | BC_GDK_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 4 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 229
| George Dickie | BC_GDK_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 4 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 230
| George Tripp | BC_GTP_DSS | BC Hydro |  |  | British Columbia | T11 | 138 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 254
| George Tripp | BC_GTP_DSS | BC Hydro |  |  | British Columbia | T12 | 138 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 255
| George Tripp | BC_GTP_DSS | BC Hydro |  |  | British Columbia | T13 | 138 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 256
| Gibraltar Capacitor | BC_GBC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 225
| Gibraltar Mine | BC_GBR_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 226
| Gibraltar Wells | BC_GBW_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 227
| Gibsons | BC_GIB_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 233
| Gibsons | BC_GIB_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 26.25 | 33.25 | 0.9 | 23.625 | 29.925 |  |  | 234
| Glenannan | BC_GLN_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 237
| Glenmerry | BC_GLM_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 752
| Glenmore | BC_GLR_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 4 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 238
| Glenmore | BC_GLR_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 4 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 239
| Glenmore | BC_GLR_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 28 | 35 | 0.9 | 25.2 | 31.5 |  |  | 753
| Glenmore | BC_GLR_DSS | FortisBC |  |  | British Columbia | T3 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 754
| Gloucester | BC_GLT_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 25 | 30 | 0.9 | 22.5 | 27 |  |  | 241
| GM Shrum GS | BC_GMS_GSS | BC Hydro | 56.0148 | -122.1957 | British Columbia | [10 empty] | 242
| Gold River | BC_GLD_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 10.5 | 13.3 | 0.9 | 9.45 | 11.97 |  |  | 235
| Gold River | BC_GLD_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 10.5 | 13.3 | 0.9 | 9.45 | 11.97 |  |  | 236
| Gold River Pulp | BC_GRP_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 249
| Golden | BC_GDN_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 26.2 | 33.3 | 0.9 | 23.58 | 29.97 |  |  | 231
| Golden | BC_GDN_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 25 | 26.2 | 33.3 | 0.9 | 23.58 | 29.97 |  |  | 232
| Goldstream | BC_GST_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 253
| Goldstream Mine | BC_GSM_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 251
| Goward | BC_GOW_DSS | BC Hydro |  |  | British Columbia | T5 | 230 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 243
| Goward | BC_GOW_DSS | BC Hydro |  |  | British Columbia | T6 | 230 | 25 | 78.75 | 100 | 0.9 | 70.875 | 90 |  |  | 244
| Grand Forks TS | BC_GFT_TSS | FortisBC |  |  | British Columbia | T3 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 755
| Great Central | BC_GCL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 228
| Green River | BC_GRR_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 2.4 | 0.08 | 0.09 | 0.9 | 0.072 | 0.081 |  |  | 250
| Greenhills | BC_GRH_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 248
| Grief Point | BC_GPT_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 12 | 29.4 | 37.24 | 0.9 | 26.46 | 33.516 |  |  | 245
| Grief Point | BC_GPT_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 29.4 | 37.24 | 0.9 | 26.46 | 33.516 |  |  | 246
| Grief Point | BC_GPT_DSS | BC Hydro |  |  | British Columbia | T54 | 25 | 12 | 26.25 | 33.25 | 0.9 | 23.625 | 29.925 |  |  | 247
| GVRD Sapperton Pumps | BC_GSP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 252
| Haa-Ak-Suuk GS | BC_HAS_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 258
| Haney | BC_HNY_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 79 | 96 | 0.9 | 71.1 | 86.4 |  |  | 269
| Haney | BC_HNY_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 270
| Harewood | BC_HWD_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 80 | 87.3 | 0.9 | 72 | 78.57 |  |  | 291
| Harewood | BC_HWD_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 78.8 | 87.3 | 0.9 | 70.92 | 78.57 |  |  | 292
| Harewood West | BC_HWW_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 293
| Harmac Pacific | BC_HMC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 265
| Harvest Energy | BC_FNC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 209
| Harvie Road | BC_HRD_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 279
| Harvie Road | BC_HRD_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 280
| Hazelton | BC_HZN_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 18.8 | 22.1 | 0.9 | 16.92 | 19.89 |  |  | 294
| Hazelton | BC_HZN_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 28 | 33.3 | 0.9 | 25.2 | 29.97 |  |  | 295
| Hearns | BC_HER_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 1.9 | 2.375 | 0.9 | 1.71 | 2.1375 |  |  | 756
| Hedley | BC_HED_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 10 | 12.5 | 0.9 | 9 | 11.25 |  |  | 757
| Heffley | BC_HFY_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 16.9 | 20.7 | 0.9 | 15.21 | 18.63 |  |  | 262
| Heffley | BC_HFY_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 25 | 33.3 | 0.9 | 22.5 | 29.97 |  |  | 263
| Highland | BC_HLD_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 5 | 5 | 0.9 | 4.5 | 4.5 |  |  | 264
| Highland Valley Copper | BC_HVC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 290
| Hillcrest | BC_HCT_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 260
| Hillcrest | BC_HCT_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 261
| Hollywood | BC_HOL_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 758
| Hollywood | BC_HOL_DSS | FortisBC |  |  | British Columbia | T3 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 759
| Hope | BC_HOP_DSS | BC Hydro |  |  | British Columbia | T11 | 60 | 25 | 15 | 18 | 0.9 | 13.5 | 16.2 |  |  | 271
| Hope | BC_HOP_DSS | BC Hydro |  |  | British Columbia | T12 | 60 | 25 | 15 | 18 | 0.9 | 13.5 | 16.2 |  |  | 272
| Hope Pumping Station | BC_HPS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 278
| Horne Payne | BC_HPN_DSS | BC Hydro |  |  | British Columbia | T4 | 230 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 273
| Horne Payne | BC_HPN_DSS | BC Hydro |  |  | British Columbia | T5 | 230 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 274
| Horne Payne | BC_HPN_DSS | BC Hydro |  |  | British Columbia | T6 | 230 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 275
| Horne Payne | BC_HPN_DSS | BC Hydro |  |  | British Columbia | T7 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 276
| Horne Payne | BC_HPN_DSS | BC Hydro |  |  | British Columbia | T8 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 277
| Horsey | BC_HSY_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 157.5 | 200 | 0.9 | 141.75 | 180 |  |  | 284
| Horsey | BC_HSY_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 157.5 | 200 | 0.9 | 141.75 | 180 |  |  | 285
| Horsey | BC_HSY_DSS | BC Hydro |  |  | British Columbia | T11 | 230 | 12 | 157.5 | 200 | 0.9 | 141.75 | 180 |  |  | 286
| Horsey | BC_HSY_DSS | BC Hydro |  |  | British Columbia | T12 | 230 | 12 | 168 | 200 | 0.9 | 151.2 | 180 |  |  | 287
| Horsheshoe Bay | BC_HSB_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 26.25 | 33.25 | 0.9 | 23.625 | 29.925 |  |  | 281
| Horsheshoe Bay | BC_HSB_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 26.25 | 33.25 | 0.9 | 23.625 | 29.925 |  |  | 282
| Houston | BC_HUS_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 18.7 | 22.1 | 0.9 | 16.83 | 19.89 |  |  | 288
| Houston | BC_HUS_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 18.8 | 22 | 0.9 | 16.92 | 19.8 |  |  | 289
| Howe Sound Pulp | BC_HSP_ISS | BC Hydro | 49.522 | -123.4862 | British Columbia | [10 empty] | 283
| Huckleberry | BC_HML_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 268
| Hundred Mile House | BC_HMH_DSS | BC Hydro |  |  | British Columbia | T5 | 60 | 25 | 43.7 | 55.2 | 0.9 | 39.33 | 49.68 |  |  | 266
| Hundred Mile House | BC_HMH_DSS | BC Hydro |  |  | British Columbia | T6 | 60 | 25 | 43.7 | 55.2 | 0.9 | 39.33 | 49.68 |  |  | 267
| Huth Avenue | BC_HUT_DSS | FortisBC |  |  | British Columbia | T4/T5/T6/T7 |  |  | 12 | 15 | 0.9 | 10.8 | 13.5 |  |  | 760
| Huth Avenue | BC_HUT_DSS | FortisBC |  |  | British Columbia | T8 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 761
| Illecillewaet | BC_ILL_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 27.4 | 33.8 | 0.9 | 24.66 | 30.42 |  |  | 297
| Illecillewaet | BC_ILL_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 27.4 | 33.8 | 0.9 | 24.66 | 30.42 |  |  | 298
| Ingledow | BC_ING_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 299
| Invermere | BC_INV_DSS | BC Hydro |  |  | British Columbia | T4 | 60 | 25 | 13.7 | 15 | 0.9 | 12.33 | 13.5 |  |  | 300
| Ioco Esso Petroleum | BC_IOC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 301
| Island GS | BC_ICG_GSS | BC Hydro | 50.0691 | -125.2819 | British Columbia | [10 empty] | 296
| Isle Pierre | BC_IPR_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 10 | 12 | 0.9 | 9 | 10.8 |  |  | 302
| James Richardson | BC_JRI_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 313
| Jamie Creek GS | BC_JME_GSS | BC Hydro | 50.8282 | -123.0568 | British Columbia | [10 empty] | 307
| Jeune Landing | BC_JUL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 314
| Jimmie Creek GS | BC_JMC_GSS | BC Hydro | 50.604 | -124.0249 | British Columbia | [10 empty] | 306
| Jinglepot | BC_JPT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 312
| Joe Riche | BC_JRH_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 16 | 20 | 0.9 | 14.4 | 18 |  |  | 762
| John Hart GS | BC_JHT_GSS | BC Hydro | 50.044 | -125.3109 | British Columbia | [10 empty] | 303
| John Lawson | BC_JLN_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 304
| John Lawson | BC_JLN_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 46.5 | 55.33 | 0.9 | 41.85 | 49.797 |  |  | 305
| Jordan River GS | BC_JOR_DFS | BC Hydro | 48.4297 | -124.0523 | British Columbia | T1 | 138 | 25 | 26.3 | 33.3 | 0.9 | 23.67 | 29.97 |  |  | 310
| Jordan River GS | BC_JOR_DFS | BC Hydro | 48.4297 | -124.0523 | British Columbia | T2 | 138 | 25 | 26.3 | 33.3 | 0.9 | 23.67 | 29.97 |  |  | 311
| Joseph Creek | BC_JOE_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 13.7 | 17.5 | 0.9 | 12.33 | 15.75 |  |  | 308
| Joseph Creek | BC_JOE_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 13.7 | 17.5 | 0.9 | 12.33 | 15.75 |  |  | 309
| Kaledon | BC_KAL2_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 7.5 | 9.375 | 0.9 | 6.75 | 8.4375 |  |  | 763
| Kalum | BC_KAL_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 28 | 33.3 | 0.9 | 25.2 | 29.97 |  |  | 315
| Kalum | BC_KAL_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 28 | 33.3 | 0.9 | 25.2 | 29.97 |  |  | 316
| Kamwood | BC_KWD_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 345
| Kaslo | BC_KAS_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 13.3 | 16.625 | 0.9 | 11.97 | 14.9625 |  |  | 764
| Keating | BC_KTG_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 78.8 | 94.5 | 0.9 | 70.92 | 85.05 |  |  | 342
| Keating | BC_KTG_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 78.8 | 94.5 | 0.9 | 70.92 | 85.05 |  |  | 343
| Kelly Lake | BC_KLY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 337
| Kemano GS | BC_KMO_GSS | BC Hydro | 53.5632 | -127.9426 | British Columbia | [10 empty] | 339
| Kemess Mine | BC_KMI_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 338
| Kennedy | BC_KDS_DSS | BC Hydro |  |  | British Columbia | T5 | 138 | 25 | 17.4 | 22 | 0.9 | 15.66 | 19.8 |  |  | 320
| Kennedy Capacitor Station | BC_KDY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 321
| Kent | BC_KEN_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 322
| Kent | BC_KEN_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 323
| Keogh | BC_KGH_DSS | BC Hydro |  |  | British Columbia | T4 | 138 | 25 | 28 | 33.6 | 0.9 | 25.2 | 30.24 |  |  | 324
| Keremeos | BC_KER_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 20 | 25 | 0.9 | 18 | 22.5 |  |  | 765
| Kettle Valley | BC_KET_DSS | FortisBC |  |  | British Columbia | T1/T2 |  |  | 80 | 100 | 0.9 | 72 | 90 |  |  | 766
| Kicking Horse | BC_KHS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 326
| Kidd #1 | BC_KI1_DSS | BC Hydro |  |  | British Columbia | T7 | 60 | 12 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 327
| Kidd #1 | BC_KI1_DSS | BC Hydro |  |  | British Columbia | T8 | 60 | 12 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 328
| Kidd #1 | BC_KI1_DSS | BC Hydro |  |  | British Columbia | T5 | 60 | 4 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 329
| Kidd #1 | BC_KI1_DSS | BC Hydro |  |  | British Columbia | T6 | 60 | 4 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 330
| Kidd #2 | BC_KI2_DSS | BC Hydro |  |  | British Columbia | T4 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 331
| Kidd #2 | BC_KI2_DSS | BC Hydro |  |  | British Columbia | T5 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 332
| Kimberley | BC_KBY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 317
| Kitimat | BC_KIT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 334
| Kokish GS | BC_KKS_GSS | BC Hydro | 50.5199 | -126.8755 | British Columbia | [10 empty] | 335
| Kokish TS | BC_KTS_TSS | BC Hydro |  |  | British Columbia | [10 empty] | 344
| Koksilah | BC_KSH_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 78.8 | 94 | 0.9 | 70.92 | 84.6 |  |  | 340
| Koksilah | BC_KSH_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 78.8 | 94 | 0.9 | 70.92 | 84.6 |  |  | 341
| Kootenay Canal GS | BC_KCL_GSS | BC Hydro | 49.4533 | -117.5179 | British Columbia | [10 empty] | 319
| Kootenay Canal GS | BC_KCL_GSS | FortisBC | 49.4533 | -117.5179 | British Columbia | [10 empty] | 767
| Kraft GS | BC_KRA_GSS | FortisBC | 49.3361 | -117.7275 | British Columbia | [10 empty] | 768
| Kraft GS | BC_KRA_GSS | FortisBC | 49.3361 | -117.7275 | British Columbia | [10 empty] | 769
| Kruger Products | BC_SCP_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 562
| Kwalse GS | BC_KWL_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 346
| Kwoen | BC_KGP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 325
| Kwoiek Creek GS | BC_KCH_GSS | BC Hydro | 50.1051 | -121.5671 | British Columbia | [10 empty] | 318
| Ladore Falls GS | BC_LDR_GSS | BC Hydro | 50.0173 | -125.393 | British Columbia | [10 empty] | 360
| Ladysmith | BC_LDY_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 50 | 59.5 | 0.9 | 45 | 53.55 |  |  | 361
| Ladysmith | BC_LDY_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 52.75 | 65.15 | 0.9 | 47.475 | 58.635 |  |  | 362
| Lafarge #1 | BC_LF1_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 363
| Lafarge #2 | BC_LF2_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 364
| Lajoie GS | BC_LAJ_GSS | BC Hydro | 50.8397 | -122.8559 | British Columbia | T2 | 60 | 12 | 3.8 | 4.5 | 0.9 | 3.42 | 4.05 |  |  | 347
| Lake Buntzen GS | BC_LB1_GSS | BC Hydro | 49.3706 | -122.8736 | British Columbia | T3 | 60 | 2.3 | 0.8 | 1 | 0.9 | 0.72 | 0.9 |  |  | 349
| Lake Buntzen GS | BC_LB1_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 350
| Lake Cowichan | BC_LCW_DSS | BC Hydro |  |  | British Columbia | T1 | 69 | 25 | 25 | 32.8 | 0.9 | 22.5 | 29.52 |  |  | 358
| Lake Cowichan | BC_LCW_DSS | BC Hydro |  |  | British Columbia | T2 | 69 | 25 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 359
| Lamont GS | BC_LMN_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 367
| Lantic Real Property | BC_LRP_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 373
| Lantzville | BC_LTZ_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 78.8 | 100 | 0.9 | 70.92 | 90 |  |  | 374
| Lantzville | BC_LTZ_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 78.8 | 100 | 0.9 | 70.92 | 90 |  |  | 375
| Lehigh Heidelberg | BC_LNH_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 368
| Line Creek Coal | BC_LCC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 355
| Lions Bay | BC_LBY_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 12.5 | 15 | 0.9 | 11.25 | 13.5 |  |  | 353
| Lions Bay | BC_LBY_DSS | BC Hydro |  |  | British Columbia | MO8 | 60 | 12 | 15 | 15 | 0.9 | 13.5 | 13.5 |  |  | 354
| Long Beach | BC_LBH_DSS | BC Hydro |  |  | British Columbia | T11 | 60 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 351
| Long Beach | BC_LBH_DSS | BC Hydro |  |  | British Columbia | T12 | 60 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 352
| Long Lake | BC_LNT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 370
| Long Lake GS | BC_LNL_GSS | BC Hydro | 56.0623 | -130.0185 | British Columbia | [10 empty] | 369
| Longo Developments | BC_DVM_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 168
| Lornex Low Level Dam | BC_LLD_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 366
| Lougheed | BC_LOH_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 371
| Lougheed | BC_LOH_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 12 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 372
| Lower Bear GS | BC_BHL_GSS | BC Hydro | 49.748 | -123.5159 | British Columbia | [10 empty] | 43
| Lower Bonnington GS | BC_LBO_GSS | FortisBC | 49.4617 | -117.5004 | British Columbia | [10 empty] | 770
| Lower Clowhom GS | BC_LCH_GSS | BC Hydro | 49.8176 | -123.3973 | British Columbia | [10 empty] | 356
| Lumby #2 | BC_LU2_ISS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 27.2 | 33.5 | 0.9 | 24.48 | 30.15 |  |  | 376
| Lumby #2 | BC_LU2_ISS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 27.5 | 33.7 | 0.9 | 24.75 | 30.33 |  |  | 377
| Lynn Valley | BC_LYN_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 12 | 78.75 | 99.75 | 0.9 | 70.875 | 89.775 |  |  | 378
| Lynn Valley | BC_LYN_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 12 | 78.75 | 99.75 | 0.9 | 70.875 | 89.775 |  |  | 379
| Mainwaring | BC_MAN_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 381
| Mainwaring | BC_MAN_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 382
| Mainwaring | BC_MAN_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 12 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 383
| Malaspina | BC_MSA_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 419
| Mamquam GS | BC_MAM_GSS | BC Hydro | 49.7214 | -123.0919 | British Columbia | [10 empty] | 380.5
| Maple Ridge | BC_MRG_DSS | BC Hydro |  |  | British Columbia | T11 | 60 | 25 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 413
| Maple Ridge | BC_MRG_DSS | BC Hydro |  |  | British Columbia | T12 | 60 | 25 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 414
| Maple Ridge | BC_MRG_DSS | BC Hydro |  |  | British Columbia | T13 | 60 | 25 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 415
| Marble River Hatchery | BC_MRH_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 416
| Marguerite | BC_MGT_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 5 | 6 | 0.9 | 4.5 | 5.4 |  |  | 391
| Marion 3 Creek GS | BC_MRK_GSS | BC Hydro | 49.2342 | -125.3569 | British Columbia | [10 empty] | 380
| Marysville | BC_MVL_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 13.8 | 16.8 | 0.9 | 12.42 | 15.12 |  |  | 426
| Marysville | BC_MVL_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 25 | 30 | 0.9 | 22.5 | 27 |  |  | 427
| Mascot Mines | BC_MAS_ISS | FortisBC |  |  | British Columbia | [10 empty] | 771
| McCulloch Creek | BC_MCK_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 0.2 | 0.2 | 0.9 | 0.18 | 0.18 |  |  | 385
| McEwan | BC_MWN_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 12.5 | 15 | 0.9 | 11.25 | 13.5 |  |  | 428
| McLellan | BC_MLN_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 403
| McLellan | BC_MLN_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 404
| McMahon Gas Plant | BC_MGP_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 390
| McMahon GS | BC_MCM_GSS | BC Hydro | 56.1463 | -120.6711 | British Columbia | [10 empty] | 386
| Meikle GS | BC_MKL_GSS | BC Hydro | 55.2856 | -121.4691 | British Columbia | [10 empty] | 399
| Meikle SWS | BC_MKT_SWS | BC Hydro |  |  | British Columbia | [10 empty] | 400
| Meridian | BC_MDN_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 387
| Merritt | BC_MRT_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 75 | 100 | 0.9 | 67.5 | 90 |  |  | 417
| Merritt | BC_MRT_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 75 | 100 | 0.9 | 67.5 | 90 |  |  | 418
| Merritt Green GS | BC_MIG_GSS | BC Hydro | 50.0971 | -120.7957 | British Columbia | [10 empty] | 394
| Methanex | BC_MHX_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 392
| Meziadin | BC_MEZ_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 2 | 2.4 | 0.9 | 1.8 | 2.16 |  |  | 388
| Mica GS | BC_MCA_GSS | BC Hydro | 52.0759 | -118.5705 | British Columbia | T11 | 60 | 12 | 10 | 12 | 0.9 | 9 | 10.8 |  |  | 384
| Minette | BC_MIN_DSS | BC Hydro |  |  | British Columbia | T2 | 287 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 395
| Minette | BC_MIN_DSS | BC Hydro |  |  | British Columbia | T3 | 287 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 396
| Mission | BC_MIS_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 397
| Mission | BC_MIS_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 398
| Monashee | BC_MON_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 12 | 28 | 33.3 | 0.9 | 25.2 | 29.97 |  |  | 408
| Monashee | BC_MON_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 12 | 8 | 9.6 | 0.9 | 7.2 | 8.64 |  |  | 409
| Monte Lake | BC_MTE_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 12 | 2 | 2.4 | 0.9 | 1.8 | 2.16 |  |  | 421
| Montrose Creek GS | BC_MTC_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 420
| Moose Lake GS | BC_MLW_GSS | BC Hydro | 55.2856 | -121.2986 | British Columbia | [10 empty] | 405
| Morfee | BC_MFE_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 16.6 | 20 | 0.9 | 14.94 | 18 |  |  | 389
| Mount Lehman | BC_MLE_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 401
| Mount Lehman | BC_MLE_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 402
| Mount Milligan | BC_MML_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 406
| Mount Pleasant | BC_MPT_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 12 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 410
| Mount Pleasant | BC_MPT_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 12 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 411
| Mount Polley Mining | BC_MTP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 422
| Moyie | BC_MYE_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 5 | 6 | 0.9 | 4.5 | 5.4 |  |  | 429
| Murphy | BC_MHY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 393
| Murrary River Coal | BC_MRC_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 412
| Murrin | BC_MUR_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 423
| Murrin | BC_MUR_DSS | BC Hydro |  |  | British Columbia | T5 | 230 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 424
| Murrin | BC_MUR_DSS | BC Hydro |  |  | British Columbia | T7 | 230 | 12 | 88 | 112 | 0.9 | 79.2 | 100.8 |  |  | 425
| Nakusp | BC_NAK_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 12 | 3.9 | 5.5 | 0.9 | 3.51 | 4.95 |  |  | 430
| Nakusp | BC_NAK_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 12 | 3.9 | 5.5 | 0.9 | 3.51 | 4.95 |  |  | 431
| Narrows Inlet GS | BC_NIT_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 444
| Natal | BC_NTL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 458
| Nechako Lumber | BC_NLV_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 451
| Nelson | BC_NLS_DSS | FortisBC |  |  | British Columbia | [10 empty] | 772
| Nelway | BC_NLY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 452
| Nelway | BC_NLY_DSS | FortisBC |  |  | British Columbia | [10 empty] | 773
| Neptune Bulk Terminal | BC_LCS_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 357
| New Denver | BC_NDR_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 12 | 5.6 | 6.7 | 0.9 | 5.04 | 6.03 |  |  | 432
| New Denver | BC_NDR_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 12 | 4 | 4.8 | 0.9 | 3.6 | 4.32 |  |  | 433
| New Westminster | BC_NWR_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 463
| New Westminster | BC_NWR_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 53 | 67 | 0.9 | 47.7 | 60.3 |  |  | 464
| New Westminster | BC_NWR_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 12 | 53 | 67 | 0.9 | 47.7 | 60.3 |  |  | 465
| Newell | BC_NEL_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 12 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 434
| Newell | BC_NEL_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 12 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 435
| Newell | BC_NEL_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 12 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 436
| Newsteck Recycling | BC_NRG_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 457
| Nicola | BC_NIC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 443
| Nicomekl | BC_NKL_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 445
| Nicomekl | BC_NKL_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 44 | 56 | 0.9 | 39.6 | 50.4 |  |  | 446
| Nicomekl | BC_NKL_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 25 | 44 | 56 | 0.9 | 39.6 | 50.4 |  |  | 447
| Nk'Mip | BC_NKM_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 20 | 25 | 0.9 | 18 | 22.5 |  |  | 774
| North Vancouver | BC_NVR_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 459
| North Vancouver | BC_NVR_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 460
| North West Energy | BC_NWE_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 461
| Northfield | BC_NFD_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 50 | 61 | 0.9 | 45 | 54.9 |  |  | 438
| Northfield | BC_NFD_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 50 | 61 | 0.9 | 45 | 54.9 |  |  | 439
| Northfield | BC_NFD_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 50 | 61 | 0.9 | 45 | 54.9 |  |  | 440
| Northgate | BC_NOR_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 21 | 26.6 | 0.9 | 18.9 | 23.94 |  |  | 453
| Northgate | BC_NOR_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 21 | 26.6 | 0.9 | 18.9 | 23.94 |  |  | 454
| Northgate | BC_NOR_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 12 | 21 | 26.6 | 0.9 | 18.9 | 23.94 |  |  | 455
| Northwest Stave GS | BC_NWS_GSS | BC Hydro | 49.6281 | -122.4625 | British Columbia | [10 empty] | 466
| Northwood | BC_NWP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 462
| OK Falls | BC_OKF_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 775
| Okanagan Mission | BC_OKM_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 776
| Okanagan Mission | BC_OKM_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 777
| Oldfield | BC_OFD_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 12 | 28 | 33.3 | 0.9 | 25.2 | 29.97 |  |  | 468
| Oldfield | BC_OFD_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 12 | 22.4 | 26.6 | 0.9 | 20.16 | 23.94 |  |  | 469
| Oldfield | BC_OFD_DSS | BC Hydro |  |  | British Columbia | T3 | 66 | 25 | 43.6 | 55.3 | 0.9 | 39.24 | 49.77 |  |  | 470
| Oldfield | BC_OFD_DSS | BC Hydro |  |  | British Columbia | T4 | 66 | 25 | 43.6 | 55.3 | 0.9 | 39.24 | 49.77 |  |  | 471
| Oliver | BC_OLI_DSS | FortisBC |  |  | British Columbia | T3 |  |  | 16 | 20 | 0.9 | 14.4 | 18 |  |  | 778
| Ootischenia | BC_OOT_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 16 | 20 | 0.9 | 14.4 | 18 |  |  | 779
| Osoyoos | BC_OSO_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 780
| Osoyoos | BC_OSO_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 781
| Oyster River | BC_OYR_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 45.1 | 53.5 | 0.9 | 40.59 | 48.15 |  |  | 472
| Oyster River | BC_OYR_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 473
| Parkland | BC_PLD_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 495
| Parksville | BC_PVL_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 78.8 | 95.2 | 0.9 | 70.92 | 85.68 |  |  | 512
| Parksville | BC_PVL_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 80.6 | 98.33 | 0.9 | 72.54 | 88.497 |  |  | 513
| Parsnip | BC_PRS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 505
| Parsons | BC_PSN_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 3.8 | 4.5 | 0.9 | 3.42 | 4.05 |  |  | 507
| Passmore | BC_PAS_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 5.6 | 7 | 0.9 | 5.04 | 6.3 |  |  | 782
| Patricia | BC_PCA_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 12 | 46.7 | 55.3 | 0.9 | 42.03 | 49.77 |  |  | 478
| Patricia | BC_PCA_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 12 | 46.7 | 55.3 | 0.9 | 42.03 | 49.77 |  |  | 479
| Patricia | BC_PCA_DSS | BC Hydro |  |  | British Columbia | T3 | 66 | 12 | 46.7 | 55.3 | 0.9 | 42.03 | 49.77 |  |  | 480
| Pavilion | BC_PAV_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 0.4 | 0.4 | 0.9 | 0.36 | 0.36 |  |  | 476
| Peace Canyon GS | BC_PCN_GSS | BC Hydro | 55.9826 | -121.995 | British Columbia | [10 empty] | 481
| Pemberton | BC_PEM_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 18.8 | 22.5 | 0.9 | 16.92 | 20.25 |  |  | 484
| Pemberton | BC_PEM_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 18.8 | 22.5 | 0.9 | 16.92 | 20.25 |  |  | 485
| Pender Harbour | BC_PHR_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 486
| Pender Harbour | BC_PHR_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 17.43 | 22.08 | 0.9 | 15.687 | 19.872 |  |  | 487
| Pennask GS | BC_PSW_GSS | BC Hydro | 49.9256 | -120.1093 | British Columbia | [10 empty] | 508
| Petro Canada Products | BC_PCP_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 482
| PetroCan | BC_KLC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 336
| Pike Lake | BC_PIK_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 490
| Pine Street | BC_PNS_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 783
| Pine Street | BC_PNS_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 20 | 25 | 0.9 | 18 | 22.5 |  |  | 784
| Pineview | BC_PVW_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 43.8 | 52.4 | 0.9 | 39.42 | 47.16 |  |  | 516
| Pineview | BC_PVW_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 26.2 | 32.2 | 0.9 | 23.58 | 28.98 |  |  | 517
| Pingston GS | BC_PIN_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 491
| Pinnacle Pellets | BC_PBL_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 477
| Pinnacle Pellets Meadowbank | BC_PMB_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 497
| Playmore | BC_PLA_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 16 | 20 | 0.9 | 14.4 | 18 |  |  | 785
| Port Alberni | BC_PAL_DSS | BC Hydro |  |  | British Columbia | T11 | 138 | 25 | 78.8 | 99.15 | 0.9 | 70.92 | 89.235 |  |  | 474
| Port Alberni | BC_PAL_DSS | BC Hydro |  |  | British Columbia | T12 | 138 | 25 | 78.8 | 99.15 | 0.9 | 70.92 | 89.235 |  |  | 475
| Port Edward | BC_PED_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 10 | 12 | 0.9 | 9 | 10.8 |  |  | 483
| Port Hardy | BC_PHY_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 |  |  | 488
| Port Hardy | BC_PHY_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 25 | 30 | 0.9 | 22.5 | 27 |  |  | 489
| Port Kells | BC_PKL_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 492
| Port Kells | BC_PKL_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 493
| Port Kells Pumping | BC_PKP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 494
| Port McNeil | BC_PML_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 498
| Port McNeil | BC_PML_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 27 | 32.9 | 0.9 | 24.3 | 29.61 |  |  | 499
| Portage Pass | BC_PPS_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 14 | 17.7 | 0.9 | 12.6 | 15.93 |  |  | 501
| Portage Pass | BC_PPS_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 14 | 17.7 | 0.9 | 12.6 | 15.93 |  |  | 502
| Porteau Cove | BC_PTO_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 0.2 | 0.24 | 0.9 | 0.18 | 0.216 |  |  | 509
| Powell | BC_POW_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 500
| Prevost | BC_PVO_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 59 | 72.5 | 0.9 | 53.1 | 65.25 |  |  | 514
| Prevost | BC_PVO_DSS | BC Hydro |  |  | British Columbia | T4 | 138 | 25 | 59 | 72.5 | 0.9 | 53.1 | 65.25 |  |  | 515
| Prince George Pulp | BC_HCR_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 259
| Prince Rupert Grain | BC_PRG_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 503
| Princeton | BC_PRI_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 504
| Princeton | BC_PRI_DSS | FortisBC |  |  | British Columbia | T4 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 786
| Puntledge GS | BC_PUN_DFS | BC Hydro | 49.665 | -125.0939 | British Columbia | T3 | 138 | 25 | 50 | 61.1 | 0.9 | 45 | 54.99 |  |  | 510
| Puntledge GS | BC_PUN_DFS | BC Hydro | 49.665 | -125.0939 | British Columbia | T4 | 138 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 511
| Qualicum | BC_QLC_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 45.1 | 55.46 | 0.9 | 40.59 | 49.914 |  |  | 518
| Qualicum | BC_QLC_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 48.3 | 61.18 | 0.9 | 43.47 | 55.062 |  |  | 519
| Quality GS | BC_QTY_GSS | BC Hydro | 55.1846 | -120.8547 | British Columbia | [10 empty] | 525
| Quesnel | BC_QNL_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 12 | 27.5 | 33.3 | 0.9 | 24.75 | 29.97 |  |  | 520
| Quesnel | BC_QNL_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 12 | 22 | 26.6 | 0.9 | 19.8 | 23.94 |  |  | 521
| Quesnel | BC_QNL_DSS | BC Hydro |  |  | British Columbia | T3 | 66 | 12 | 22 | 26.6 | 0.9 | 19.8 | 23.94 |  |  | 522
| Quesnel River Pulp | BC_QRP_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 524
| Quintette | BC_QNT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 523
| Radium | BC_RDM_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 13.7 | 16.8 | 0.9 | 12.33 | 15.12 |  |  | 530
| Rainbow | BC_RBW_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 78.75 | 99.75 | 0.9 | 70.875 | 89.775 |  |  | 528
| Rainbow | BC_RBW_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 78.75 | 99.75 | 0.9 | 70.875 | 89.775 |  |  | 529
| Rearguard Pumping Station | BC_REG_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 531
| Recreation | BC_REC_DSS | FortisBC |  |  | British Columbia | T1/T2 |  |  | 57.6 | 72 | 0.9 | 51.84 | 64.8 |  |  | 787
| Red Bluff | BC_RBF_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 526
| Red Bluff | BC_RBF_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 527
| Revelstoke GS | BC_REV_GSS | BC Hydro | 51.0486 | -118.1939 | British Columbia | [10 empty] | 532
| RG Anderson | BC_RGA_DSS | FortisBC |  |  | British Columbia | T3 |  |  | 20 | 25 | 0.9 | 18 | 22.5 |  |  | 788
| Richmond | BC_RIM_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 87 | 100 | 0.9 | 78.3 | 90 |  |  | 533
| Richmond | BC_RIM_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 12 | 87 | 100 | 0.9 | 78.3 | 90 |  |  | 534
| Richmond Steel Recycling | BC_RSR_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 539
| Ridley Terminals Inc | BC_RTI_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 540
| Riverside | BC_RVS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 545
| Rosedale | BC_ROS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 537
| Rosemont | BC_RSM_DSS | FortisBC |  |  | British Columbia | [10 empty] | 789
| Royal 2 | BC_RO2_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 535
| Royal 2 | BC_RO2_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 536
| Ruckles | BC_RUC_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 16 | 20 | 0.9 | 14.4 | 18 |  |  | 790
| Ruckles | BC_RUC_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 10 | 12.5 | 0.9 | 9 | 11.25 |  |  | 791
| Rupert | BC_RUP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 541
| Rupert Gas | BC_RPG_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 538
| Ruskin GS | BC_RUS_GSS | BC Hydro | 49.195 | -122.4083 | British Columbia | [10 empty] | 542
| Rutherford Creek GS | BC_RUT_GSS | BC Hydro | 50.2727 | -122.867 | British Columbia | [10 empty] | 543
| Sachteen | BC_SAC_DSS | BC Hydro |  |  | British Columbia | T1 | 208 | 14.4 | 4 | 4.8 | 0.9 | 3.6 | 4.32 |  |  | 546
| Sahtlam | BC_SAT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 551
| Salmo | BC_SLM_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 13.3 | 16.625 | 0.9 | 11.97 | 14.9625 |  |  | 792
| Salmon Arm | BC_SAM_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 53 | 65.6 | 0.9 | 47.7 | 59.04 |  |  | 549
| Salmon Arm | BC_SAM_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 53 | 65.6 | 0.9 | 47.7 | 59.04 |  |  | 550
| Salmon Valley | BC_SVY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 624
| Saltery Bay | BC_SAY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 552
| Saltspring | BC_SAL_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 53.5 | 63.6 | 0.9 | 48.15 | 57.24 |  |  | 547
| Saltspring | BC_SAL_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 53.5 | 63.6 | 0.9 | 48.15 | 57.24 |  |  | 548
| Saskatchewan Wheat Pool | BC_SWP_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 627
| Saucier | BC_SAU_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 793
| Savona GS | BC_SVA_DFS | BC Hydro | 50.7488 | -120.8551 | British Columbia | T5 | 138 | 25 | 10 | 12.6 | 0.9 | 9 | 11.34 |  |  | 621
| Scott | BC_SCT_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 29 | 36 | 0.9 | 26.1 | 32.4 |  |  | 563
| Scott | BC_SCT_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 48 | 61 | 0.9 | 43.2 | 54.9 |  |  | 564
| Sea Island | BC_SEA_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 565
| Sea Island | BC_SEA_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 566
| Sechelt | BC_SEC_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 78.75 | 99.75 | 0.9 | 70.875 | 89.775 |  |  | 567
| Sechelt | BC_SEC_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 78.75 | 99.75 | 0.9 | 70.875 | 89.775 |  |  | 568
| Sechelt Creek GS | BC_SCG_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 557
| Selkirk | BC_SEL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 569
| Selkirk | BC_SEL_DSS | FortisBC |  |  | British Columbia | [10 empty] | 794
| Septimus | BC_SEP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 570
| Seton Lake GS | BC_SON_DFS | BC Hydro | 50.6727 | -121.9241 | British Columbia | T2 | 60 | 12 | 22.4 | 26.9 | 0.9 | 20.16 | 24.21 |  |  | 593
| Seton Lake GS | BC_SON_DFS | BC Hydro | 50.6727 | -121.9241 | British Columbia | T3 | 60 | 12 | 21 | 26.6 | 0.9 | 18.9 | 23.94 |  |  | 594
| Seven Mile GS | BC_SEV_GSS | BC Hydro | 49.0302 | -117.5041 | British Columbia | [10 empty] | 571
| Seventy Mile House | BC_SMH_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 8.8 | 10 | 0.9 | 7.92 | 9 |  |  | 586
| Seventy Mile House | BC_SMH_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 25 | 30 | 0.9 | 22.5 | 27 |  |  | 587
| Sexsmith | BC_SEX_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 795
| Shawnigan | BC_SHA_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 75 | 99 | 0.9 | 67.5 | 89.1 |  |  | 575
| Shawnigan | BC_SHA_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 75 | 99 | 0.9 | 67.5 | 89.1 |  |  | 576
| Shelburn | BC_SHL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 577
| Shell Groundbirch | BC_SGB_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 574
| Shell Saturn Gas Plant | BC_SRN_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 606
| Shell Sunset Prairie | BC_SST_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 613
| Sicamous | BC_SCM_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 11.3 | 13.9 | 0.9 | 10.17 | 12.51 |  |  | 559
| Sicamous | BC_SCM_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 28.3 | 33.6 | 0.9 | 25.47 | 30.24 |  |  | 560
| Silverdale | BC_SVD_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 622
| Silverdale | BC_SVD_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 623
| Similco | BC_SCO_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 561
| Simon Fraser University | BC_SFU_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 573
| Site C GS | BC_STC_GSS | BC Hydro | 56.1966 | -120.914 | British Columbia | [10 empty] | 614
| Skeena | BC_SKA_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 578
| Skeena Cellulose | BC_SKL_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 580
| Skookum Creek GS | BC_SKO_GSS | BC Hydro | 49.7205 | -122.9956 | British Columbia | [10 empty] | 581
| Skookumchuck | BC_SKU_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 5 | 6 | 0.9 | 4.5 | 5.4 |  |  | 582
| Smithers | BC_SRS_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 607
| Smithers | BC_SRS_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 28 | 33.25 | 0.9 | 25.2 | 29.925 |  |  | 608
| Smithers | BC_SRS_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 26.25 | 33.25 | 0.9 | 23.625 | 29.925 |  |  | 609
| Soda Creek | BC_SCK_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 558
| Solex Gas | BC_NGL_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 441
| Sooke | BC_SOO_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 595
| Sooke | BC_SOO_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 56 | 66.5 | 0.9 | 50.4 | 59.85 |  |  | 596
| Sorrento | BC_STO_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 52.5 | 52.5 | 0.9 | 47.25 | 47.25 |  |  | 616
| Sorrento | BC_STO_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 28.5 | 34.8 | 0.9 | 25.65 | 31.32 |  |  | 617
| South Bank | BC_SBK_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 553
| South Campus | BC_UNS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 667
| South Cranberry GS | BC_SCB_GSS | BC Hydro | 50.7716 | -118.1041 | British Columbia | [10 empty] | 556
| South Slocan GS | BC_SLC_GSS | BC Hydro | 49.4555 | -117.5197 | British Columbia | [10 empty] | 583
| South Slocan GS | BC_SLC_GSS | FortisBC | 49.4555 | -117.5197 | British Columbia | T1 |  |  | 4.5 | 7 | 0.9 | 4.05 | 6.3 |  |  | 796
| South Sutton GS | BC_SSH_GSS | BC Hydro | 49.2876 | -125.3092 | British Columbia | [10 empty] | 612
| South Wellington | BC_SWN_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 84 | 100 | 0.9 | 75.6 | 90 |  |  | 625
| South Wellington | BC_SWN_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 84 | 100 | 0.9 | 75.6 | 90 |  |  | 626
| Sparwood | BC_SPD_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 14 | 16.8 | 0.9 | 12.6 | 15.12 |  |  | 597
| Spatsum | BC_STL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 615
| Spences Bridge | BC_SBR_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 13.3 | 16 | 0.9 | 11.97 | 14.4 |  |  | 554
| Sperling | BC_SPG_DSS | BC Hydro |  |  | British Columbia | T12 | 230 | 12 | 177 | 214 | 0.9 | 159.3 | 192.6 |  |  | 598
| Sperling | BC_SPG_DSS | BC Hydro |  |  | British Columbia | T13 | 230 | 12 | 177 | 214 | 0.9 | 159.3 | 192.6 |  |  | 599
| Spillimacheen GS | BC_SPN_DFS | BC Hydro |  |  | British Columbia | T1 | 12 | 4 | 2.5 | 3 | 0.9 | 2.25 | 2.7 |  |  | 602
| Spuzzum | BC_SZM_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 0.75 | 0.9 | 0.9 | 0.675 | 0.81 |  |  | 631
| Squamish | BC_SQH_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 22 | 26 | 0.9 | 19.8 | 23.4 |  |  | 603
| Squamish | BC_SQH_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 604
| Squamish | BC_SQH_DSS | BC Hydro |  |  | British Columbia | T3 | 60 | 25 | 43.68 | 55.33 | 0.9 | 39.312 | 49.797 |  |  | 605
| St Leon Creek | BC_SLK_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 584
| Stave Falls GS | BC_SFL_GSS | BC Hydro | 49.2288 | -122.3561 | British Columbia | [10 empty] | 572
| Steeples | BC_SPL_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 44.3 | 44.3 | 0.9 | 39.87 | 39.87 |  |  | 600
| Steeples | BC_SPL_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 43.8 | 53.5 | 0.9 | 39.42 | 48.15 |  |  | 601
| Steveston | BC_STV_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 94 | 109 | 0.9 | 84.6 | 98.1 |  |  | 618
| Steveston | BC_STV_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 25 | 94 | 109 | 0.9 | 84.6 | 98.1 |  |  | 619
| Stewart | BC_STW_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 16.6 | 20 | 0.9 | 14.94 | 18 |  |  | 620
| Stokke GS | BC_SKK_GSS | BC Hydro | 49.7111 | -122.0343 | British Columbia | [10 empty] | 579
| Stoney Creek | BC_STY_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 10 | 12.5 | 0.9 | 9 | 11.25 |  |  | 797
| Strathcona GS | BC_SCA_GSS | BC Hydro | 49.9981 | -125.5856 | British Columbia | [10 empty] | 555
| Strawberry Hill | BC_SYH_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 87 | 112 | 0.9 | 78.3 | 100.8 |  |  | 628
| Strawberry Hill | BC_SYH_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 87 | 112 | 0.9 | 78.3 | 100.8 |  |  | 629
| Strawberry Hill | BC_SYH_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 25 | 87 | 112 | 0.9 | 78.3 | 100.8 |  |  | 630
| Sukinka | 0 | BC Hydro |  |  | British Columbia | [10 empty] | 590
| Sumas Way | BC_SMW_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 588
| Sumas Way | BC_SMW_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 44 | 55 | 0.9 | 39.6 | 49.5 |  |  | 589
| Summerland | BC_SUM_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 20 | 25 | 0.9 | 18 | 22.5 |  |  | 798
| Sundance Lake | BC_SLS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 585
| Surrey | BC_SRY_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 610
| Surrey | BC_SRY_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 12 | 21 | 26 | 0.9 | 18.9 | 23.4 |  |  | 611
| Sydney | BC_SNY_DSS | BC Hydro |  |  | British Columbia | T1 | 69 | 25 | 73.8 | 87.5 | 0.9 | 66.42 | 78.75 |  |  | 591
| Sydney | BC_SNY_DSS | BC Hydro |  |  | British Columbia | T2 | 69 | 25 | 73.8 | 87.5 | 0.9 | 66.42 | 78.75 |  |  | 592
| Tachick | BC_TAC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 632
| Tahsis Village | BC_TSV_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 14 | 16.6 | 0.9 | 12.6 | 14.94 |  |  | 654
| Tahsis Village | BC_TSV_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 11.81 | 14.96 | 0.9 | 10.629 | 13.464 |  |  | 655
| Takla Forest Products | BC_TFP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 638
| Tarrys | BC_TAR_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 3.5 | 3.5 | 0.9 | 3.15 | 3.15 |  |  | 799
| Tatogga | BC_TAT_DSS | BC Hydro |  |  | British Columbia | T1 | 287 | 25 | 16.6 | 16.6 | 0.9 | 14.94 | 14.94 |  |  | 633
| Taylor | BC_TAY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 634
| Taylor River Rest Area | BC_TRR_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 652
| Telkwa | BC_TKW_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 642
| Terrace | BC_TER_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 22.4 | 26.6 | 0.9 | 20.16 | 23.94 |  |  | 636
| Terrace | BC_TER_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 28 | 33 | 0.9 | 25.2 | 29.7 |  |  | 637
| Terrace Skeena Cellulose | BC_TSC_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 653
| Texaco | BC_TXB_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 660
| Timber West | BC_TWT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 658
| Timbernorth | BC_TBN_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 635
| Tipella GS | BC_TPA_GSS | BC Hydro | 49.7409 | -122.1622 | British Columbia | [10 empty] | 649
| Tisdall | BC_TIS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 641
| Tolko Armstrong GS | BC_RVG_GSS | BC Hydro | 50.3922 | -119.2259 | British Columbia | [10 empty] | 544
| Tolko Industries Heffley | BC_TOK_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 648
| Tolko Industries Lavington | BC_TIL_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 640
| Tolko Lignum | BC_LGW_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 365
| Topley | BC_TPY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 650
| Trans Mountain | BC_TMO_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 646
| TransMountain Kamloops | BC_TMT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 647
| TransMountain McMurphy | BC_TMM_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 645
| Tree Island Industries | BC_TII_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 639
| Tretheway GS | BC_TWY_GSS | BC Hydro | 49.7038 | -122.0796 | British Columbia | [10 empty] | 659
| Trio GS | BC_TRE_GSS | BC Hydro |  |  | British Columbia | [10 empty] | 651
| Trout Creek | BC_TRC_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 15 | 18.75 | 0.9 | 13.5 | 16.875 |  |  | 800
| Tsawassen | BC_TSW_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 47 | 56 | 0.9 | 42.3 | 50.4 |  |  | 656
| Tsawassen | BC_TSW_DSS | BC Hydro |  |  | British Columbia | T2 | 60 | 25 | 47 | 56 | 0.9 | 42.3 | 50.4 |  |  | 657
| Tumbler Ridge | BC_TLR_DSS | BC Hydro |  |  | British Columbia | T1 | 230 | 25 | 78.8 | 100 | 0.9 | 70.92 | 90 |  |  | 643
| Tumbler Ridge | BC_TLR_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 78.8 | 100 | 0.9 | 70.92 | 90 |  |  | 644
| Tyax Lake | BC_TXL_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 0.6 | 0.6 | 0.9 | 0.54 | 0.54 |  |  | 661
| University of BC | BC_UNY_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 668
| Upper Bear GS | BC_BHU_GSS | BC Hydro | 49.7954 | -123.5721 | British Columbia | [10 empty] | 44
| Upper Bonnington GS | BC_UBO_GSS | FortisBC | 49.4601 | -117.4842 | British Columbia | [10 empty] | 801
| Upper Bonnington SWS | BC_USS_SWS | FortisBC |  |  | British Columbia | [10 empty] | 802
| Upper Clowhom GS | BC_UCH_GSS | BC Hydro | 49.8543 | -123.4461 | British Columbia | [10 empty] | 662
| Upper Fraser | BC_UFR_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 14 | 15 | 0.9 | 12.6 | 13.5 |  |  | 663
| Upper Harrison | BC_UHT_DSS | BC Hydro |  |  | British Columbia | T1 | 208 | 14.4 | 4 | 4.8 | 0.9 | 3.6 | 4.32 |  |  | 664
| Upper Lillooet River GS | BC_ULR_GSS | BC Hydro | 50.657 | -123.4476 | British Columbia | [10 empty] | 665
| Upper Mamquam GS | BC_UMH_GSS | BC Hydro | 49.7178 | -123.0546 | British Columbia | [10 empty] | 666
| Upper Stave River GS | BC_USR_GSS | BC Hydro | 49.566 | -122.3503 | British Columbia | [10 empty] | 669
| Valemount | BC_VLM_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 16.7 | 20 | 0.9 | 15.03 | 18 |  |  | 676
| Valhalla | BC_VAL_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 8 | 10 | 0.9 | 7.2 | 9 |  |  | 803
| Valhalla | BC_VAL_DSS | FortisBC |  |  | British Columbia | T2 |  |  | 10 | 12.5 | 0.9 | 9 | 11.25 |  |  | 804
| Valleyview | BC_VVW_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 681
| Vancouver Dry Dock | BC_VDK_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 674
| Vancouver International Airport | BC_YVR_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 718
| Vancouver Island TS | BC_VIT_TSS | BC Hydro |  |  | British Columbia | [10 empty] | 675
| Vancouver Shipyards | BC_VSY _ISS | BC Hydro |  |  | British Columbia | [10 empty] | 680
| Vanderhoof | BC_VDF_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 28 | 33 | 0.9 | 25.2 | 29.7 |  |  | 672
| Vanderhoof | BC_VDF_DSS | BC Hydro |  |  | British Columbia | T3 | 66 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 673
| Vaseux Lake | BC_VAS_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 670
| Vaseux Lake | BC_VAS_DSS | FortisBC |  |  | British Columbia | [10 empty] | 805
| Vavenby | BC_VBY_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 28 | 33.6 | 0.9 | 25.2 | 30.24 |  |  | 671
| Vernon | BC_VNT_DSS | BC Hydro |  |  | British Columbia | T4 | 138 | 25 | 57.8 | 71 | 0.9 | 52.02 | 63.9 |  |  | 677
| Vernon | BC_VNT_DSS | BC Hydro |  |  | British Columbia | T5 | 138 | 25 | 57.8 | 71 | 0.9 | 52.02 | 63.9 |  |  | 678
| Vernon | BC_VNT_DSS | BC Hydro |  |  | British Columbia | T6 | 138 | 25 | 80.6 | 98.3 | 0.9 | 72.54 | 88.47 |  |  | 679
| Vernon | BC_VNT_DSS | FortisBC |  |  | British Columbia | [10 empty] | 806
| Wahleach GS | BC_WAH_DFS | BC Hydro | 49.2366 | -121.6807 | British Columbia | T3 | 60 | 25 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 682
| Wahleach GS | BC_WAH_DFS | BC Hydro | 49.2366 | -121.6807 | British Columbia | T4 | 60 | 25 | 26 | 33 | 0.9 | 23.4 | 29.7 |  |  | 683
| Wahleach Pumping Station | BC_WHP_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 695
| Walden North GS | BC_WDN_GSS | BC Hydro | 50.6605 | -121.9833 | British Columbia | [10 empty] | 689
| Walter Hardman GS | BC_WHN_GSS | BC Hydro | 50.8139 | -118.06 | British Columbia | [10 empty] | 694
| Walters | BC_WLT_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 704
| Waneta Expansion GS | BC_WAX_GSS | FortisBC | 49.0047 | -117.616 | British Columbia | [10 empty] | 807
| Waneta GS | BC_WAN_GSS | FortisBC | 49.0041 | -117.6129 | British Columbia | [10 empty] | 808
| Waneta SS | BC_WHS_TSS | FortisBC |  |  | British Columbia | [10 empty] | 809
| Warfield | BC_WTS_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 12 | 2.5 | 3 | 0.9 | 2.25 | 2.7 |  |  | 684
| Warfield | BC_WTS_DSS | FortisBC |  |  | British Columbia | [10 empty] | 810
| Waterford | BC_WAT_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 32 | 40 | 0.9 | 28.8 | 36 |  |  | 811
| Wescup | BC_WSP_DSS | BC Hydro |  |  | British Columbia | T1 | 144 | 25 | 41.7 | 50 | 0.9 | 37.53 | 45 |  |  | 713
| Wescup | BC_WSP_DSS | BC Hydro |  |  | British Columbia | T2 | 144 | 25 | 41.7 | 50 | 0.9 | 37.53 | 45 |  |  | 714
| West Bench | BC_WEB_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 8 | 10 | 0.9 | 7.2 | 9 |  |  | 812
| West Fraser Quesnel | BC_WFQ_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 691
| West Fraser Quesnel Plywood | BC_WQL_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 709
| West Fraser Williams Lake | BC_WWL_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 717
| West Kamloops | BC_WKA_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 75 | 100 | 0.9 | 67.5 | 90 |  |  | 699
| West Kamloops | BC_WKA_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 75 | 100 | 0.9 | 67.5 | 90 |  |  | 700
| West Pine | BC_WPN_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 708
| Westar | BC_WST_DSS | FortisBC |  |  | British Columbia | [10 empty] | 813
| Westbank | BC_WBK_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 25 | 56.8 | 66.5 | 0.9 | 51.12 | 59.85 |  |  | 685
| Westbank | BC_WBK_DSS | BC Hydro |  |  | British Columbia | T2 | 138 | 25 | 27.5 | 32 | 0.9 | 24.75 | 28.8 |  |  | 686
| Westbank | BC_WBK_DSS | BC Hydro |  |  | British Columbia | T3 | 138 | 25 | 55 | 55 | 0.9 | 49.5 | 49.5 |  |  | 687
| Westcoast Cellufibre | BC_WCF_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 688
| Westmin Resources | BC_WNR_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 706
| Westminster | BC_WES_DSS | FortisBC |  |  | British Columbia | T1/T2 |  |  | 30 | 37.5 | 0.9 | 27 | 33.75 |  |  | 814
| Westshore Terminals | BC_WTL_ISS | BC Hydro |  |  | British Columbia | [10 empty] | 715
| Westwold | BC_WWD_DSS | BC Hydro |  |  | British Columbia | T1 | 60 | 25 | 5.6 | 6 | 0.9 | 5.04 | 5.4 |  |  | 716
| Whalley | BC_WHY_DSS | BC Hydro |  |  | British Columbia | T2 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 696
| Whalley | BC_WHY_DSS | BC Hydro |  |  | British Columbia | T3 | 230 | 25 | 158 | 200 | 0.9 | 142.2 | 180 |  |  | 697
| Whatshan GS | BC_WGS_GSS | BC Hydro | 49.9106 | -118.0718 | British Columbia | [10 empty] | 693
| White Rock | BC_WRK_DSS | BC Hydro |  |  | British Columbia | T11 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 710
| White Rock | BC_WRK_DSS | BC Hydro |  |  | British Columbia | T12 | 60 | 25 | 79 | 100 | 0.9 | 71.1 | 90 |  |  | 711
| Whonnock | BC_WNK_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 705
| Williams Lake | BC_WLM_DSS | BC Hydro |  |  | British Columbia | T1 | 66 | 25 | 52.5 | 66.5 | 0.9 | 47.25 | 59.85 |  |  | 701
| Williams Lake | BC_WLM_DSS | BC Hydro |  |  | British Columbia | T2 | 66 | 25 | 43.7 | 55.3 | 0.9 | 39.33 | 49.77 |  |  | 702
| Williams Lake | BC_WLM_DSS | BC Hydro |  |  | British Columbia | T3 | 66 | 25 | 43.79 | 55.5 | 0.9 | 39.411 | 49.95 |  |  | 703
| Williston | BC_WSN_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 712
| Windsor | BC_WIN_DSS | BC Hydro |  |  | British Columbia | T4 | 60 | 25 | 26.4 | 33.3 | 0.9 | 23.76 | 29.97 |  |  | 698
| Woodfibre | BC_WFR_DSS | BC Hydro |  |  | British Columbia | [10 empty] | 692
| Woss | BC_WOS_DSS | BC Hydro |  |  | British Columbia | T1 | 138 | 12 | 8 | 9.6 | 0.9 | 7.2 | 8.64 |  |  | 707
| Ymir | BC_YMR_DSS | FortisBC |  |  | British Columbia | T1 |  |  | 1.5 | 1.875 | 0.9 | 1.35 | 1.6875 |  |  | 815
| Zeballos Lake GS | BC_ZBL_GSS | BC Hydro | 50.0535 | -126.7797 | British Columbia | [10 empty] | 719
| Zeballos Lake TS | BC_ZBT_TSS | BC Hydro |  |  | British Columbia | [10 empty] | 720
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## System
BC | SYSTEM CHARACTERISTICS
| Generator Type | ELCC Prior to WAEA | Winter Available Energy Adjustment (WAEA) | Capacity Adjustment (DGC or ELCC) | Capacity Factor | Other References | Notes | Reserve Requirements | Line Losses
|  |  |  | (%) | (%) |  |  | (% installed MW) | (% across system)
| Natural Gas CCGT |  |  | 94% | by facility |  | DGC varies from 88 per cent to 100 per cent of installed capacity, so 94% used as an average | 12 | 7
| Natural Gas SCGT |  |  | 94% | by facility |  | DGC varies from 88 per cent to 100 per cent of installed capacity, so 94% used as an average; BC Hydro presumes a minimum 18% capacity factor for its SCGTs
| Biogas |  |  | 95% | by facility |  | DGC
| Biomass |  |  | 97% | by facility |  | d
| MSW |  |  | 100% | by facility |  | DGC
| Hydro_run | 60% | 53.7% | 32.22% | by facility | BC Hydro 2013 IRP Appendix 3C Table1 | ELCC is the weighted average of approximately 60 per cent of the forecasted average MW of potential in the December/January period; the aggregate energy (i.e. "average MW of potential") available in December/January is 300 GWh/year (in each month) of a total annual of 6,700 GWh/year, or 4.5% (see other reference) or 53.7% of the monthly average energy; these two factors are used to calculate the ELCC for each run-of-river facility
| Hydro_daily |  |  | 100% | by facility |  | ELCC
| Hydro_monthly |  |  | 100% | by facility |  | ELCC
| Wind |  |  | 26% | by facility |  | ELCC
| Solar |  |  | 24% | by facility |  | ELCC
Specific Notes:
BC Hydro line losses are 3% for transmission and 4% for distribution.
Dependable generating capacity (DGC), which is used for non-intermittent resources and is the amount of megawatts (MW) a plant can reliably produce when required, assuming all units are in service
Effective load carrying capability (ELCC), which is used for intermittent or variable generation resources and is the maximum peak load (measured in MW) that a generating unit or system of units can reliably supply such that the loss of load expectation will be no greater than one day in 10 years

## HGWh
BC | HISTORICAL ANNUAL ENERGY | UNIT | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2013-2018
| Annual Energy Demand (after DSM) | GWh/year |  |  |  |  | 56267 | 57261 | 56663 | 56998 | 56533 | 57330
| Annual Change in Energy Demand | GWh/year |  |  |  |  | 56267 | 994 | -598 | 335 | -465 | 797 | Average
| Percentage Change in Energy Demand | % | [5 empty] | 1.767% | -1.044% | 0.5912% | -0.8158% | 1.41% | 0.375%
Notes:

## HMW
BC | HISTORICAL PEAK CAPACITY | UNIT | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
| Annual Capacity Demand (after DSM) | MW
| Annual Change in Capacity Demand | MW |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Percentage Change in Capacity Demand | % |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Notes:

## FGWh
BC | FORECAST ANNUAL ENERGY DEMAND
|  | (GWh) | F2021 | F2022 | F2023 | F2024 | F2025 | F2026 | F2027 | F2028 | F2029 | F2030 | F2031 | F2032 | F2033 | F2034 | F2035 | F2036 | F2037 | F2038 | F2039 | F2040 | F2041 | F2042 | F2043 | F2044 | F2045 | F2046 | F2047 | F2048 | F2049 | F2050 | F2051 | F2031-F2041 | Notes
|  |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2030-2040
| Existing and Committed Heritage Resources | (a) | 46898 | 46898 | 46898 | 46898 | 47264 | 50790 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184 | 52184
| Existing and Committed IPP Resources | (b) | 15451 | 15719 | 13717 | 13278 | 13059 | 12807 | 12728 | 12638 | 12210 | 10997 | 9997 | 9501 | 9323 | 9055 | 8541 | 7716 | 7350 | 7212 | 6952 | 6922 | 6736
| System Capability (before planned resources) | (c) = a + b | 62349 | 62617 | 60615 | 60176 | 60323 | 63597 | 64912 | 64822 | 64394 | 63181 | 62181 | 61685 | 61507 | 61239 | 60725 | 59900 | 59534 | 59396 | 59136 | 59106 | 58920
Demand - Integrated System Total Gross Requirements
| Dec 2020 Reference Load Forecast before DSM | (d) | -56513 | -58526 | -60140 | -61545 | -63029 | -64573 | -65696 | -66789 | -67435 | -68127 | -68811 | -69594 | -70214 | -70903 | -71612 | -72371 | -73002 | -73698 | -74379 | -75121 | -75829
Existing and Committed Demand Side Management
| F21 Energy Conservations Programs Savings |  | 72 | 105 | 117 | 117 | 118 | 112 | 112 | 112 | 109 | 104 | 71 | 60 | 47 | 47 | 43 | 17 | 12 | 12 | 12 | 11 | 10
| Codes & Standards |  | 233 | 563 | 824 | 1077 | 1316 | 1543 | 1750 | 1938 | 2118 | 2288 | 2451 | 2607 | 2756 | 2905 | 3056 | 3206 | 3357 | 3507 | 3657 | 3807 | 3870
| Energy Conservation Rate Structures |  | 63 | 138 | 177 | 210 | 239 | 268 | 296 | 325 | 354 | 383 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 333
| Sub-total | (e) | 368 | 806 | 1118 | 1404 | 1673 | 1922 | 2159 | 2375 | 2582 | 2775 | 2917 | 3063 | 3200 | 3349 | 3495 | 3619 | 3764 | 3915 | 4065 | 4215 | 4213
| Net Metering | (f) | 32 | 40 | 50 | 62 | 77 | 95 | 117 | 143 | 174 | 212 | 258 | 311 | 371 | 438 | 510 | 588 | 667 | 749 | 832 | 915 | 998
| Surplus / (Deficit) before planned resources | (g) = c + d + e + f | 6237 | 4937 | 1643 | 97 | -957 | 1042 | 1492 | 552 | -286 | -1958 | -3454 | -4535 | -5136 | -5877 | -6881 | -8264 | -9037 | -9639 | -10346 | -10886 | -11698
| Future Demand Side Management | (h) | 0 | 161 | 296 | 472 | 649 | 860 | 1029 | 1255 | 1493 | 1721 | 1979 | 2181 | 2372 | 2527 | 2680 | 2842 | 2935 | 3029 | 3098 | 3164 | 3231
| Dec 2020 Reference Load Forecast before DSM | (d) | 56513 | 58526 | 60140 | 61545 | 63029 | 64573 | 65696 | 66789 | 67435 | 68127 | 68811 | 69594 | 70214 | 70903 | 71612 | 72371 | 73002 | 73698 | 74379 | 75121 | 75829 | [10 empty] | 2030-2040 Rate | Assume extended to 2050
| Incremental annual load growth before DSM |  |  | 3.562% | 2.758% | 2.336% | 2.411% | 2.45% | 1.739% | 1.664% | 0.9672% | 1.026% | 1.004% | 1.138% | 0.8909% | 0.9813% | 1% | 1.06% | 0.8719% | 0.9534% | 0.924% | 0.9976% | 0.9425% | [10 empty] | 0.9759%
| Dec 2020 Reference Load Forecast after DSM | (i) = d - e - f - h | 56113 | 57519 | 58676 | 59607 | 60630 | 61696 | 62391 | 63016 | 63186 | 63419 | 63657 | 64039 | 64271 | 64589 | 64927 | 65322 | 65636 | 66005 | 66384 | 66827 | 67387 | 67771.8152 | 68158.8279 | 68548.0506 | 68939.4961 | 69333.1768 | 69729.1057 | 70127.2956 | 70527.7593 | 70930.5099 | 71335.5604 | 2030-2040 Rate | Assume extended to 2050
| Incremental annual load growth after DSM |  |  |  | 2.012% | 1.587% | 1.716% | 1.758% | 1.126% | 1.002% | 0.2698% | 0.3688% | 0.3753% | 0.6001% | 0.3623% | 0.4948% | 0.5233% | 0.6084% | 0.4807% | 0.5622% | 0.5742% | 0.6673% | 0.838% | 0.5711% | 0.5711% | 0.5711% | 0.5711% | 0.5711% | 0.5711% | 0.5711% | 0.5711% | 0.5711% | 0.5711% | 0.5711% | Mid-load forecast for use in COPPER
| British Columbia | GWh/y | 56113 | 57519 | 58676 | 59607 | 60630 | 61696 | 62391 | 63016 | 63186 | 63419 | 63657 | 64039 | 64271 | 64589 | 64927 | 65322 | 65636 | 66005 | 66384 | 66827 | 67387 | 67771.8152 | 68158.8279 | 68548.0506 | 68939.4961 | 69333.1768 | 69729.1057 | 70127.2956 | 70527.7593 | 70930.5099 | 71335.5604
Notes:
Operational View: The Operational View shows the forecasted operation of these same resources given market conditions, expected system conditions in the near term and average conditions in the long term. This view is relevant for forecasting revenue requirements because it mimics actual operation.
Planning View: The Planning View reflects the capability of resources based on BC Hydro’s planning criteria, including the requirement contained in subsection 6(2) of the Clean Energy Act to achieve electricity self-sufficiency under prescribed water conditions from its hydroelectric Heritage assets. The planning view is summarized in the Energy Load Resource Balances as “Surplus/Deficit as % of Net Load (planning view)” where lower than 100 per cent means that there is a system shortfall and a need for additional resources.

## FMW
BC | FORECAST ANNUAL ENERGY DEMAND
|  | (GWh) | F2021 | F2022 | F2023 | F2024 | F2025 | F2026 | F2027 | F2028 | F2029 | F2030 | F2031 | F2032 | F2033 | F2034 | F2035 | F2036 | F2037 | F2038 | F2039 | F2040 | F2041 | F2042 | F2043 | F2044 | F2045 | F2046 | F2047 | F2048 | F2049 | F2050 | F2051 | F2031-F2041 | Notes
|  |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2030-2040
| Existing and Committed Heritage Resources | (a) | 11628 | 11818 | 11818 | 11818 | 11818 | 12965 | 12965 | 12618 | 12618 | 12791 | 12791 | 12791 | 12965 | 12965 | 12965 | 12965 | 12965 | 12965 | 12965 | 12965 | 12965
| Existing and Committed IPP Resources | (b) | 1663 | 1795 | 1512 | 1495 | 1481 | 1400 | 1400 | 1391 | 1362 | 1068 | 974 | 940 | 917 | 885 | 580 | 480 | 480 | 445 | 445 | 437 | 437
| 12% Reserves | (c) | -1537 | -1574 | -1540 | -1540 | -1540 | -1674 | -1674 | -1633 | -1629 | -1615 | -1604 | -1600 | -1618 | -1617 | -1583 | -1576 | -1576 | -1576 | -1576 | -1576 | -1576
| System Capability (before planned resources) | (d) = a + b + c | 11754 | 12039 | 11790 | 11773 | 11759 | 12691 | 12691 | 12376 | 12351 | 12244 | 12161 | 12131 | 12264 | 12233 | 11962 | 11869 | 11869 | 11834 | 11834 | 11826 | 11826
Demand - Integrated System Total Gross Requirements
| Dec 2020 Reference Load Forecast before DSM | (e) | -10478 | -10862 | -11140 | -11363 | -11560 | -11753 | -11936 | -12100 | -12247 | -12399 | -12550 | -12718 | -12882 | -13052 | -13230 | -13420 | -13605 | -13788 | -13970 | -14149 | -14318
Existing and Committed Demand Side Management
| F21 Energy Conservations Programs Savings |  | 21 | 21 | 21 | 21 | 20 | 18 | 18 | 17 | 17 | 16 | 12 | 10 | 8 | 8 | 8 | 4 | 3 | 3 | 3 | 3 | 3
| Codes & Standards |  | 49 | 118 | 166 | 212 | 254 | 293 | 329 | 361 | 391 | 419 | 445 | 470 | 493 | 520 | 548 | 576 | 604 | 632 | 659 | 687 | 700
| Energy Conservation Rate Structures |  | 5 | 11 | 16 | 19 | 23 | 26 | 29 | 31 | 34 | 37 | 38 | 38 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 33
| Sub-total | (f) | 75 | 150 | 203 | 252 | 297 | 337 | 376 | 409 | 442 | 472 | 495 | 518 | 538 | 565 | 593 | 617 | 644 | 672 | 699 | 727 | 736
| Net Metering | (g) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Surplus / (Deficit) before planned resources | (h) = d + e + f + g | 1351 | 1327 | 853 | 662 | 496 | 1275 | 1131 | 685 | 546 | 317 | 106 | -69 | -80 | -254 | -675 | -934 | -1092 | -1282 | -1437 | -1596 | -1756
| Future Demand Side Management | (i) | 0 | 30 | 56 | 85 | 139 | 318 | 380 | 456 | 536 | 707 | 765 | 818 | 871 | 920 | 972 | 1023 | 1066 | 1107 | 1146 | 1182 | 1222
| Dec 2020 Reference Load Forecast before DSM | (d) | 10478 | 10862 | 11140 | 11363 | 11560 | 11753 | 11936 | 12100 | 12247 | 12399 | 12550 | 12718 | 12882 | 13052 | 13230 | 13420 | 13605 | 13788 | 13970 | 14149 | 14318 | [10 empty] | 2030-2040 Rate | Assume extended to 2050
| Incremental annual load growth before DSM |  |  | 3.665% | 2.559% | 2.002% | 1.734% | 1.67% | 1.557% | 1.374% | 1.215% | 1.241% | 1.218% | 1.339% | 1.29% | 1.32% | 1.364% | 1.436% | 1.379% | 1.345% | 1.32% | 1.281% | 1.194% | [10 empty] | 1.327%
| Dec 2020 Reference Load Forecast after DSM | (j) = e - f - g - i | 10403 | 10682 | 10881 | 11026 | 11124 | 11098 | 11180 | 11235 | 11269 | 11220 | 11290 | 11382 | 11473 | 11567 | 11665 | 11780 | 11895 | 12009 | 12125 | 12240 | 12360 | 12472.4256 | 12585.8739 | 12700.3541 | 12815.8756 | 12932.4478 | 13050.0804 | 13168.783 | 13288.5653 | 13409.4371 | 13531.4083 | 2030-2040 Rate | Assume extended to 2050
| Incremental annual load growth after DSM |  |  | 2.682% | 1.863% | 1.333% | 0.8888% | -0.2337% | 0.7389% | 0.4919% | 0.3026% | -0.4348% | 0.6239% | 0.8149% | 0.7995% | 0.8193% | 0.8472% | 0.9859% | 0.9762% | 0.9584% | 0.9659% | 0.9485% | 0.9804% | 0.9096% | 0.9096% | 0.9096% | 0.9096% | 0.9096% | 0.9096% | 0.9096% | 0.9096% | 0.9096% | 0.9096% | 0.9096% | Mid-load forecast for use in COPPER
| British Columbia | MW | 10403 | 10682 | 10881 | 11026 | 11124 | 11098 | 11180 | 11235 | 11269 | 11220 | 11290 | 11382 | 11473 | 11567 | 11665 | 11780 | 11895 | 12009 | 12125 | 12240 | 12360 | 12472.4256 | 12585.8739 | 12700.3541 | 12815.8756 | 12932.4478 | 13050.0804 | 13168.783 | 13288.5653 | 13409.4371 | 13531.4083
Notes:
Operational View: The Operational View shows the forecasted operation of these same resources given market conditions, expected system conditions in the near term and average conditions in the long term. This view is relevant for forecasting revenue requirements because it mimics actual operation.
Planning View: The Planning View reflects the capability of resources based on BC Hydro’s planning criteria, including the requirement contained in subsection 6(2) of the Clean Energy Act to achieve electricity self-sufficiency under prescribed water conditions from its hydroelectric Heritage assets. The planning view is summarized in the Energy Load Resource Balances as “Surplus/Deficit as % of Net Load (planning view)” where lower than 100 per cent means that there is a system shortfall and a need for additional resources.

## Hourly
BC | Hourly
See Hourly Data

## Inputs
BC | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance