## README
SK | LEGEND
| SK-Sources | Primary sources for the provincial data
| Generation | Characteristics of existing interconnected generators
| Storage | Characteristics of existing grid-scale storage facilities
| Transmission | Characteristics of existing system transmission
| Nodes | Characteristics of existing transmission system nodes
| BLANK | Separates included from excluded tabs in CODERS
| HydroExisting | Characteristics specific to existing interconnected hydroelectric generators with hourly or monthly storage
| HydroRenewals | Characteristics specific to potential future capacity upgrades and pumped storage additions at existing facilities
| HydroGreenfield | Characteristics specific to potential future greenfield hydroelectric projects
| HydroPS | Characteristics specific to potential future pumped storage hydroelectric projects
| Distribution | Characteristics of existing distribution substations
| System | Miscellaneous provincial system characteristics
| HGWh | Provincial historical energy demand, after DSM
| HMW | Provincial historical capacity demand, after DSM
| FGWh | Provincial mid-load energy forecast, before and after DSM
| FMW | Provincial mid-load capacity forecast, before and after DSM
| Hourly | Provincial hourly generation data
| Inputs | Inputs to the data calculations
Data not yet obtained
Data under review
Data obtained and calculated
| 27 | Calculated values (may be overlain by reference shading)
all other colours are linked to references

## SK-Sources
SK | PRIMARY SOURCES
| Source | Year | Name | Link | Publication | Region | Notes
| SaskPower | 2007 | Clean Coal Project. Proposed Change in Development/Technology at the Shand Power Station | http://www.environment.gov.sk.ca/2007-052ScreeningProjectProposal |  | Saskatchewan
| Manitoba Hydro | 2019 | Manitoba Hydro Power Sale Arrangements | https://www.hydro.mb.ca/corporate/electricity_exports/power_sale_arrangements/ |  | Saskatchewan
| Nova Scotia Power Inc. | 2020 | NS Power 2020 IRP Modeling Results Release | https://irp.nspower.ca/documents/modeling-results/ |  | Nova Scotia
| NPCC | 2017 | 2017 Québec Balancing Authority Area Comprehensive Review of Resource Adequacy | https://www.npcc.org/Library/Resource%20Adequacy/Forms/Public%20List.aspx |  | Québec
| World Resources Institute | 2019 | Global Power Plant Database | http://datasets.wri.org/dataset/globalpowerplantdatabase
| Google Maps / Google Earth | 2020
See "Other References" Column of the relevant tab
| Manitoba Hydro | 2016 | 2016/17 Resource Planning Assumptions & Analysis | https://www.hydro.mb.ca/regulatory_affairs/pdf/electric/general_rate_application_2017/07.3_appendix_7.3_mh_resource_planning_assumptions_and_analysis.pdf |  | Manitoba
| Saskpower | 2012 | Saskpower Presentation to the Lake Diefenbaker Stakeholder Group | https://www.wsask.ca/Global/Lakes%20and%20Rivers/Dams%20and%20Reservoirs/Operating%20Plans/Developing%20an%20Operating%20Plan%20for%20Lake%20Diefenbaker/LainLovelaceHydroPowerGenerationPresentation.pdf |  | Saskatchewan
| Energy and Environmental Economics | 2019 | Planning Reserve Margin and Capacity Value Study | https://irp.nspower.ca/documents/pre-irp-deliverables/ |  | Nova Scotia
| SaskPower | 2018 | 2018 Rate Application | https://www.saskratereview.ca/docs/saskpower2017/saskpower-2018-rate-application.pdf |  | Saskatchewan
| SaskPower | 2020 | System Map | https://www.saskpower.com/Our-Power-Future/Our-Electricity/Electrical-System/System-Map |  | Saskatchewan
| Environment Canada | 2019 | Historical Hydrometric Data Search | https://wateroffice.ec.gc.ca/search/historical_e.html |  | Saskatchewan
| SaskPower | 2018 | Saskatchewan Rate Review Panel Round One Interrogatory Responses [2018 Rate Application]. SRRP Q23 Reference: Export Revenues. | https://www.saskratereview.ca/secuap.php?apn=aug_015_017_sp |  | Saskatchewan
| SaskPower | 2018 | Saskatchewan Rate Review Panel Round One Interrogatory Responses [2018 Rate Application]. SRRP Q103 Reference: Load Forecasts. | https://www.saskratereview.ca/secuap.php?apn=aug_015_017_sp |  | Saskatchewan
| SaskPower | 2018 | Saskatchewan Rate Review Panel Round One Interrogatory Responses [2018 Rate Application]. SRRP Q141 Reference: Integrated Resource Plan. | https://www.saskratereview.ca/secuap.php?apn=aug_015_017_sp |  | Saskatchewan
| SaskPower | 2016 | Round One Interrogatory Responses [2016 and 2017 Rate Application] SRRP Q109 Reference: Load Forecasts. | https://www.saskratereview.ca/docs/saskpower2016/saskpower-round-one-interrogatories-srrp-website.pdf |  | Saskatchewan
| Tazi Twé Hydroelectric Project | 2014 | Tazi Twé Hydroelectric Project Environmental Impact Statement | https://www.ceaa.gc.ca/050/documents/p80031/98788E.pdf |  | Saskatchewan
| SaskPower | 2018 | Saskatchewan Rate Review Panel Round One Interrogatory Responses [2018 Rate Application]. SRRP Q107 Reference: Load Forecast. | https://www.saskratereview.ca/secuap.php?apn=aug_015_017_sp |  | Saskatchewan
| SaskPower | 2019 | Annual Report [see 2011 - 2019 Annual Reports] | https://www.saskpower.com/about-us/Our-Company/Current-Reports |  | Saskatchewan
| The Water Power Act | 2018 |  | The Water Power Rental Regulations, W-6 Reg 4 |  | Saskatchewan
| Manitoba Hydro, SaskPower | 2019 | Inter-Regional Planning Exploratory Study | https://www.oasis.oati.com/spc/index.html |  | Manitoba, Saskatchewan
| NERC | 2020 | 2020 Summer Reliability Assessment | https://www.nerc.com/pa/RAPA/ra/Reliability%20Assessments%20DL/NERC_SRA_2020.pdf |  | Manitoba
| Overbye et al. | 2017 | Power System Analysis and Design (Sixth Edition). Table 5.2
| Athari, MH and Zhifang, W. | 2017 | Interdependence of Transmission Branch Parameters on the Voltage Levels. Electrical Engineering and Systems Science. | https://arxiv.org/abs/1709.06930
| Gutman, R., Marchenko, P.P., and Dunlop, R.D. | 1979 | Analytical Development of Loadability Characteristics for EHV and UHV Transmission Lines | http://home.eng.iastate.edu/~jdm/ee552/StClairAEP.pdf
| Canada Energy Regulator | 2021 | International Power Lines Dashboard | https://www.cer-rec.gc.ca/en/data-analysis/facilities-we-regulate/international-power-lines-dashboard/index.html |  | Canada

## Generation
SK | EXISTING GENERATION | [12 empty] | DESIGN
| Project Name | Gen Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Operating Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy | # of units | Other References | Notes
[16 empty] | (MW) |  | (MW) | (%) | (GWh/year)
| Awassis | SK_AWS00_GEN | Elemental Energy | TBD | 50.4136 | -104.4685 | Saskatchewan.a | Saskatachewan | Regina South | SK_REG_DSS | 138 | 2022 | 2042 | Solar_PV | solar | 10 | 10% | 1 | 18% | 15.768
| Blue Hills | SK_BLH00_GEN | Algonquin Power | Morse | 50.3991 | -107.2231 | Saskatchewan.a | Saskatachewan | Morse | SK_MRS_DSS | 138 | 2021 | 2041 | Wind_Onshore | wind | 176 | 20% | 35.2 | 40% | 616.704
| Boundary Dam_03 | SK_BDM03_GEN | SaskPower | Estevan | 49.096 | -103.0305 | Saskatchewan.a | Saskatachewan | Boundary Dam | SK_BDM_GSS | 230 | 2014 | 2044 | Coal_CCS | coalCCS | 139 | 90% | 125.1 | 80% | 974.112 | 2
| Boundary Dam_06 | SK_BDM06_GEN | SaskPower | Estevan | 49.096 | -103.0305 | Saskatchewan.a | Saskatachewan | Boundary Dam | SK_BDM_GSS | 230 | 1959 | 2027 | Coal | coal | 284 | 90% | 255.6 | 80% | 1990.272 | 2
| Centennial | SK_CTN00_GEN | SaskPower | Swift Current | 50.1325 | -107.4928 | Saskatchewan.a | Saskatachewan | Swift Current | SK_SWC_DSS | 138 | 2006 | 2026 | Wind_Onshore | wind | 150 | 20% | 30 | 40% | 525.6
| Charlot | SK_CHL00_GEN | SaskPower | Lake Athabasca | 59.6125 | -109.1141 | Saskatchewan.a | Manitoba | Uranium City | SK_URC_DSS | 115 | 1980 | 2050 | Hydro_daily | hydro_daily | 10 | 98.1% | 9.81 | 45% | 39.42 | 1
| Chinook | SK_CHN00_GEN | SaskPower | Swift Current | 50.342 | -107.938 | Saskatchewan.a | Saskatachewan | Swift Current | SK_SWC_DSS | 230 | 2019 | 2049 | NG_CC | gasCC | 350 | 73% | 255.5 | 80% | 2452.8 | 1 |  | Units: One combustion, one steam
| Cory_01 | SK_CRY01_GEN | SaskPower/ATCO Power | Saskatoon | 52.0927 | -106.8533 | Saskatchewan.a | Saskatachewan | Cory | SK_CRY_GSS | 138 | 2003 | 2033 | NG_CG | gasCC | 83 | 73% | 60.59 | 80% | 581.664 | 3
| Cory_02 | SK_CRY02_GEN | SaskPower/ATCO Power | Saskatoon | 52.0927 | -106.8533 | Saskatchewan.a | Saskatachewan | Cory | SK_CRY_GSS | 138 | 2003 | 2033 | NG_CG | gasCC | 83 | 73% | 60.59 | 80% | 581.664 | 3
| Cory_03 | SK_CRY03_GEN | SaskPower/ATCO Power | Saskatoon | 52.0927 | -106.8533 | Saskatchewan.a | Saskatachewan | Cory | SK_CRY_GSS | 138 | 2003 | 2033 | NG_CG | gasCC | 83 | 73% | 60.59 | 80% | 581.664 | 3
| Coteau Creek_01 | SK_CCK01_GEN | SaskPower | Elbow | 51.2749 | -106.8735 | Saskatchewan.a | Saskatachewan | Coteau Creek | SK_CCK_GSS | 230 | 1969 | 2039 | Hydro_daily | hydro_daily | 62 | 98.1% | 60.822 | 45% | 244.404 | 3
| Coteau Creek_02 | SK_CCK02_GEN | SaskPower | Elbow | 51.2749 | -106.8735 | Saskatchewan.a | Saskatachewan | Coteau Creek | SK_CCK_GSS | 230 | 1969 | 2039 | Hydro_daily | hydro_daily | 62 | 98.1% | 60.822 | 45% | 244.404 | 3
| Coteau Creek_03 | SK_CCK03_GEN | SaskPower | Elbow | 51.2749 | -106.8735 | Saskatchewan.a | Saskatachewan | Coteau Creek | SK_CCK_GSS | 230 | 1969 | 2039 | Hydro_daily | hydro_daily | 62 | 98.1% | 60.822 | 45% | 244.404 | 3
| Cypress | SK_CYP00_GEN | SaskPower | Gull Lake | 50.0183 | -108.4903 | Saskatchewan.a | Saskatachewan | Bone Creek | SK_BCK_DSS | 138 | 2002 | 2022 | Wind_Onshore | wind | 11 | 20% | 2.2 | 40% | 38.544
| EB Campbell_01 | SK_EBC01_GEN | SaskPower | Nipawin | 53.689 | -103.3475 | Saskatchewan.a | Saskatachewan | EB Campbell | SK_EBC_GSS | 230 | 1963 | 2033 | Hydro_daily | hydro_daily | 36 | 98.1% | 35.316 | 45% | 141.912 | 8
| EB Campbell_02 | SK_EBC02_GEN | SaskPower | Nipawin | 53.689 | -103.3475 | Saskatchewan.a | Saskatachewan | EB Campbell | SK_EBC_GSS | 230 | 1963 | 2033 | Hydro_daily | hydro_daily | 36 | 98.1% | 35.316 | 45% | 141.912 | 8
| EB Campbell_03 | SK_EBC03_GEN | SaskPower | Nipawin | 53.689 | -103.3475 | Saskatchewan.a | Saskatachewan | EB Campbell | SK_EBC_GSS | 230 | 1963 | 2033 | Hydro_daily | hydro_daily | 36 | 98.1% | 35.316 | 45% | 141.912 | 8
| EB Campbell_04 | SK_EBC04_GEN | SaskPower | Nipawin | 53.689 | -103.3475 | Saskatchewan.a | Saskatachewan | EB Campbell | SK_EBC_GSS | 230 | 1963 | 2033 | Hydro_daily | hydro_daily | 36 | 98.1% | 35.316 | 45% | 141.912 | 8
| EB Campbell_05 | SK_EBC05_GEN | SaskPower | Nipawin | 53.689 | -103.3475 | Saskatchewan.a | Saskatachewan | EB Campbell | SK_EBC_GSS | 230 | 1963 | 2033 | Hydro_daily | hydro_daily | 36 | 98.1% | 35.316 | 45% | 141.912 | 8
| EB Campbell_06 | SK_EBC06_GEN | SaskPower | Nipawin | 53.689 | -103.3475 | Saskatchewan.a | Saskatachewan | EB Campbell | SK_EBC_GSS | 230 | 1963 | 2033 | Hydro_daily | hydro_daily | 36 | 98.1% | 35.316 | 45% | 141.912 | 8
| EB Campbell_07 | SK_EBC07_GEN | SaskPower | Nipawin | 53.689 | -103.3475 | Saskatchewan.a | Saskatachewan | EB Campbell | SK_EBC_GSS | 230 | 1966 | 2036 | Hydro_daily | hydro_daily | 36 | 98.1% | 35.316 | 45% | 141.912 | 8
| EB Campbell_08 | SK_EBC08_GEN | SaskPower | Nipawin | 53.689 | -103.3475 | Saskatchewan.a | Saskatachewan | EB Campbell | SK_EBC_GSS | 230 | 1966 | 2036 | Hydro_daily | hydro_daily | 36 | 98.1% | 35.316 | 45% | 141.912 | 8
| Ermine_01 | SK_ERM01_GEN | SaskPower | Kerrobert | 51.8578 | -109.0334 | Saskatchewan.a | Saskatachewan | Ermine | SK_ERM_GSS | 138 | 2009 | 2039 | NG_CT | gasSC | 46 | 93% | 42.78 | 20% | 80.592 | 2
| Ermine_02 | SK_ERM02_GEN | SaskPower | Kerrobert | 51.8578 | -109.0334 | Saskatchewan.a | Saskatachewan | Ermine | SK_ERM_GSS | 138 | 2009 | 2039 | NG_CT | gasSC | 46 | 93% | 42.78 | 20% | 80.592 | 2
| Foxtail Grove | SK_FXT00_GEN | Kruger Energy Saskatchewan | Regina | 50.5143 | -104.6877 | Saskatchewan.a | Saskatachewan | Condie | SK_CND_DSS | 138 | 2022 | 2042 | Solar_PV | solar | 10 | 10% | 1 | 18% | 15.768
| Golden South | SK_GST00_GEN | Potentia Renewables | Assiniboia | 49.6266 | -105.9754 | Saskatchewan.a | Saskatachewan | Assiniboia | SK_ASS_DSS | 138 | 2020 | 2040 | Wind_Onshore | wind | 200 | 20% | 40 | 40% | 700.8
| Great Plains | SK_GTP00_GEN | SaskPower | Moose Jaw | 50.3667 | -105.4883 | Saskatchewan.a | Saskatachewan | Pasqua | SK_PQA_DSS | 138 | 2025 | 2055 | NG_CC | gasCC | 350 | 73% | 255.5 | 80% | 2452.8 | 1
| Highfield | SK_HFL00_GEN | Saturn Power | Coulee | 50.1778 | -107.4685 | Saskatchewan.a | Saskatachewan | Rushlake Creek | SK_RUC_DSS | 230 | 2022 | 2042 | Solar_PV | solar | 10 | 10% | 1 | 18% | 15.768
| Island Falls_01 | SK_ISF01_GEN | SaskPower | Sandy Bay | 55.529 | -102.3569 | Saskatchewan.a | Manitoba | Island Falls | SK_ISF_GSS | 230 | 1930 | 2040 | Hydro_daily | hydro_daily | 13 | 98.1% | 12.753 | 45% | 51.246 | 7
| Island Falls_02 | SK_ISF02_GEN | SaskPower | Sandy Bay | 55.529 | -102.3569 | Saskatchewan.a | Manitoba | Island Falls | SK_ISF_GSS | 230 | 1930 | 2040 | Hydro_daily | hydro_daily | 13 | 98.1% | 12.753 | 45% | 51.246 | 7
| Island Falls_03 | SK_ISF03_GEN | SaskPower | Sandy Bay | 55.529 | -102.3569 | Saskatchewan.a | Manitoba | Island Falls | SK_ISF_GSS | 230 | 1930 | 2040 | Hydro_daily | hydro_daily | 13 | 98.1% | 12.753 | 45% | 51.246 | 7
| Island Falls_04 | SK_ISF04_GEN | SaskPower | Sandy Bay | 55.529 | -102.3569 | Saskatchewan.a | Manitoba | Island Falls | SK_ISF_GSS | 230 | 1936 | 2046 | Hydro_daily | hydro_daily | 18 | 98.1% | 17.658 | 45% | 70.956 | 7
| Island Falls_05 | SK_ISF05_GEN | SaskPower | Sandy Bay | 55.529 | -102.3569 | Saskatchewan.a | Manitoba | Island Falls | SK_ISF_GSS | 230 | 1938 | 2048 | Hydro_daily | hydro_daily | 18 | 98.1% | 17.658 | 45% | 70.956 | 7
| Island Falls_06 | SK_ISF06_GEN | SaskPower | Sandy Bay | 55.529 | -102.3569 | Saskatchewan.a | Manitoba | Island Falls | SK_ISF_GSS | 230 | 1947 | 2057 | Hydro_daily | hydro_daily | 18 | 98.1% | 17.658 | 45% | 70.956 | 7
| Island Falls_07 | SK_ISF07_GEN | SaskPower | Sandy Bay | 55.529 | -102.3569 | Saskatchewan.a | Manitoba | Island Falls | SK_ISF_GSS | 230 | 1959 | 2029 | Hydro_daily | hydro_daily | 18 | 98.1% | 17.658 | 45% | 70.956 | 7
| Landis | SK_LDS00_GEN | SaskPower | Landis | 52.2244 | -108.433 | Saskatchewan.a | Saskatachewan | Landis | SK_LDS_GSS | 138 | 1975 | 2035 | NG_CT | gasSC | 79 | 93% | 73.47 | 20% | 138.408 | 1
| Meadow Lake | SK_MDL00_GEN | SaskPower | Meadow Lake | 54.0884 | -108.4375 | Saskatchewan.a | Saskatachewan | Meadow Lake | SK_MDL_GSS | 230 | 1984 | 2044 | NG_CT | gasSC | 44 | 93% | 40.92 | 20% | 77.088 | 1
| Meridian_01 | SK_MRD01_GEN | Meridian Limited Partnership | Lloydminster | 53.2594 | -109.9514 | Saskatchewan.a | Saskatachewan | Lloydminster | SK_LDM_DSS | 230 | 1999 | 2029 | NG_CG | gasCC | 76 | 73% | 55.48 | 80% | 532.608 | 3
| Meridian_02 | SK_MRD02_GEN | Meridian Limited Partnership | Lloydminster | 53.2594 | -109.9514 | Saskatchewan.a | Saskatachewan | Lloydminster | SK_LDM_DSS | 230 | 1999 | 2029 | NG_CG | gasCC | 76 | 73% | 55.48 | 80% | 532.608 | 3
| Meridian_03 | SK_MRD03_GEN | Meridian Limited Partnership | Lloydminster | 53.2594 | -109.9514 | Saskatchewan.a | Saskatachewan | Lloydminster | SK_LDM_DSS | 230 | 1999 | 2029 | NG_CG | gasCC | 76 | 73% | 55.48 | 80% | 532.608 | 3
| Morse | SK_MRS00_GEN | SaskPower | Morse | 50.399 | -106.9574 | Saskatchewan.a | Saskatachewan | Morse | SK_MRS_GSS | 138 | 2015 | 2035 | Wind_Onshore | wind | 23 | 20% | 4.6 | 40% | 80.592
| Nipawin_01 | SK_NIP01_GEN | SaskPower | Nipawin | 53.3209 | -104.0431 | Saskatchewan.a | Saskatachewan | Nipawin | SK_NIP_GSS | 138 | 1985 | 2055 | Hydro_daily | hydro_daily | 85 | 98.1% | 83.385 | 45% | 335.07 | 3
| Nipawin_02 | SK_NIP02_GEN | SaskPower | Nipawin | 53.3209 | -104.0431 | Saskatchewan.a | Saskatachewan | Nipawin | SK_NIP_GSS | 138 | 1985 | 2055 | Hydro_daily | hydro_daily | 85 | 98.1% | 83.385 | 45% | 335.07 | 3
| Nipawin_03 | SK_NIP03_GEN | SaskPower | Nipawin | 53.3209 | -104.0431 | Saskatchewan.a | Saskatachewan | Nipawin | SK_NIP_GSS | 138 | 1985 | 2055 | Hydro_daily | hydro_daily | 85 | 98.1% | 83.385 | 45% | 335.07 | 3
| North Battleford_01 | SK_BFD01_GEN | Northland Power | North Battleford | 52.6832 | -108.1715 | Saskatchewan.a | Saskatachewan | Battleford | SK_BFD_GSS | 138 | 2013 | 2043 | NG_CT | gasSC | 176 | 93% | 163.68 | 20% | 308.352 | 2
| North Battleford_02 | SK_BFD02_GEN | Northland Power | North Battleford | 52.6832 | -108.1715 | Saskatchewan.a | Saskatachewan | Battleford | SK_BFD_GSS | 138 | 2013 | 2043 | NG_CC | gasCC | 95 | 73% | 69.35 | 80% | 665.76 | 2
| NRGreen Alameda Heat Recovery Facility | SK_NRGA00_GEN | NRGreen Power | Alameda | 49.3238 | -102.2957 | Saskatchewan.a | Saskatachewan | Shand | SK_SHD_GSS | 138 | 2008 | 2038 | Biogas | biomass | 5 | 95% | 4.75 | 95% | 41.61 | 1
| NRGreen Estlin Heat Recovery Facility | SK_NRGE00_GEN | NRGreen Power | Estlin | 50.2526 | -104.4072 | Saskatchewan.a | Saskatachewan | Regina South | SK_REG_DSS | 138 | 2008 | 2038 | Biogas | biomass | 5 | 95% | 4.75 | 95% | 41.61 | 1
| NRGreen Kerrobert Heat Recovery Facility | SK_NRGK00_GEN | NRGreen Power | Kerrobert | 51.9389 | -109.1807 | Saskatchewan.a | Saskatachewan | Ermine | SK_ERM_GSS | 138 | 2006 | 2036 | Biogas | biomass | 5 | 95% | 4.75 | 95% | 41.61 | 1
| NRGreen Loreburn Heat Recovery Facility | SK_NRGL00_GEN | NRGreen Power | Loreburn | 51.2404 | -106.6768 | Saskatchewan.a | Saskatachewan | Hawarden | SK_HWD_DSS | 138 | 2008 | 2038 | Biogas | biomass | 5 | 95% | 4.75 | 95% | 41.61 | 1
| Pesâkâstêw | SK_PSK00_GEN | Pesâkâstêw Solar Inc. | Weyburn | 49.6417 | -103.9048 | Saskatchewan.a | Saskatachewan | Weyburn | SK_WEY_DSS | 138 | 2022 | 2042 | Solar_PV | solar | 10 | 10% | 1 | 18% | 15.768
| Poplar River_01 | SK_PPR01_GEN | SaskPower | Coronach | 49.0579 | -105.4848 | Saskatchewan.a | Saskatachewan | Poplar River | SK_PPR_GSS | 230 | 1981 | 2029 | Coal | coal | 291 | 90% | 261.9 | 80% | 2039.328 | 2
| Poplar River_02 | SK_PPR02_GEN | SaskPower | Coronach | 49.0579 | -105.4848 | Saskatchewan.a | Saskatachewan | Poplar River | SK_PPR_GSS | 230 | 1981 | 2029 | Coal | coal | 291 | 90% | 261.9 | 80% | 2039.328 | 2
| PURCHASES - MB-SK (PPA_01) | PP_MBSK00_GEN | Manitoba Hydro | MB-SK Border | 54.7947 | -101.8859 | Saskatchewan.a | Manitoba | IPB Island Falls | PP_MBSK1_IPT | 115 | 2015 | 2022 | Hydro_daily | hydro_daily | 25 | 98.1% | 24.525 | 90% | 197.1
| PURCHASES - MB-SK (PPA_02) | PP_MBSK02_GEN | Manitoba Hydro | MB-SK Border | 53.7227 | -101.7696 | Saskatchewan.a | Saskatachewan | IPB EB Campbell | PP_MBSK2_IPT | 230 | 2020 | 2040 | Hydro_daily | hydro_daily | 100 | 98.1% | 98.1 | 90% | 788.4 |  |  | Assumed connection point for sales and purchases
| PURCHASES - MB-SK (PPA_03) | PP_MBSK03_GEN | Manitoba Hydro | MB-SK Border | 50.5445 | -101.4747 | Saskatchewan.a | Saskatachewan | IPB Tantallon | PP_MBSK4_IPT | 230 | 2022 | 2038 | Hydro_daily | hydro_daily | 215 | 98.1% | 210.915 | 90% | 1695.06 |  |  | Assumed connection point for sales and purchases
| Queen Elizabeth_01 | SK_QEB00_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 1959 | 2049 | NG_CC | gasCC | 61 | 73% | 44.53 | 80% | 427.488 | 12
| Queen Elizabeth_02 | SK_QEB02_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 1959 | 2049 | NG_CC | gasCC | 62 | 73% | 45.26 | 80% | 434.496 | 12
| Queen Elizabeth_03 | SK_QEB03_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 1971 | 2031 | NG_CC | gasCC | 95 | 73% | 69.35 | 80% | 665.76 | 12
| Queen Elizabeth_04 | SK_QEB04_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2002 | 2032 | NG_CC | gasCC | 25 | 73% | 18.25 | 80% | 175.2 | 12
| Queen Elizabeth_05 | SK_QEB05_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2002 | 2032 | NG_CC | gasCC | 25 | 73% | 18.25 | 80% | 175.2 | 12
| Queen Elizabeth_06 | SK_QEB06_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2002 | 2032 | NG_CC | gasCC | 25 | 73% | 18.25 | 80% | 175.2 | 12
| Queen Elizabeth_07 | SK_QEB07_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2002 | 2032 | NG_CC | gasCC | 25 | 73% | 18.25 | 80% | 175.2 | 12
| Queen Elizabeth_08 | SK_QEB08_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2002 | 2032 | NG_CC | gasCC | 25 | 73% | 18.25 | 80% | 175.2 | 12
| Queen Elizabeth_09 | SK_QEB09_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2002 | 2032 | NG_CC | gasCC | 25 | 73% | 18.25 | 80% | 175.2 | 12
| Queen Elizabeth_10 | SK_QEB10_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2010 | 2040 | NG_CC | gasCC | 36 | 73% | 26.28 | 80% | 252.288 | 12
| Queen Elizabeth_11 | SK_QEB11_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2010 | 2040 | NG_CC | gasCC | 36 | 73% | 26.28 | 80% | 252.288 | 12
| Queen Elizabeth_12 | SK_QEB12_GEN | SaskPower | Saskatoon | 52.0944 | -106.7049 | Saskatchewan.a | Saskatachewan | Queen Elizabeth | SK_QEB_GSS | 230 | 2010 | 2040 | NG_CC | gasCC | 36 | 73% | 26.28 | 80% | 252.288 | 12
| Red Lily | SK_RDL00_GEN | SaskPower | Moosomin | 50.1918 | -101.7425 | Saskatchewan.a | Saskatachewan | Kennedy | SK_KDY_DSS | 230 | 2011 | 2031 | Wind_Onshore | wind | 26 | 20% | 5.2 | 40% | 91.104
| Riverhurst | SK_RVH00_GEN | Capstone Infrastructure | Riverhurst | 50.8929 | -106.8814 | Saskatchewan.a | Saskatachewan | Riverhurst | SK_RVH_GSS | 238 | 2020 | 2040 | Wind_Onshore | wind | 10 | 20% | 2 | 40% | 35.04
| Shand | SK_SHD00_GEN | SaskPower | Estevan | 49.0883 | -102.8642 | Saskatchewan.a | Saskatachewan | Shand | SK_SHD_GSS | 230 | 1992 | 2029 | Coal | coal | 276 | 90% | 248.4 | 80% | 1934.208 | 1
| Spy Hill_01 | SK_SPH01_GEN | Northland Power | Esterhazy | 50.5989 | -101.8474 | Saskatchewan.a | Saskatachewan | Tantallon | SK_TTL_DSS | 138 | 2011 | 2041 | NG_CT | gasSC | 89 | 93% | 82.77 | 20% | 155.928 | 2
| Spy Hill_02 | SK_SPH02_GEN | Northland Power | Esterhazy | 50.5989 | -101.8474 | Saskatchewan.a | Saskatachewan | Tantallon | SK_TTL_DSS | 138 | 2011 | 2041 | NG_CT | gasSC | 89 | 93% | 82.77 | 20% | 155.928 | 2
| Sunbridge | SK_SNB00_GEN | Suncor / Enbridge | Gull Lake | 50.078 | -108.3929 | Saskatchewan.a | Saskatachewan | Bone Creek | SK_BCK_DSS | 138 | 2002 | 2022 | Wind_Onshore | wind | 11 | 20% | 2.2 | 40% | 38.544
| Waterloo | SK_WTL00_GEN | SaskPower | Lake Athabasca | 59.6323 | -109.0561 | Saskatchewan.a | Manitoba | Uranium City | SK_URC_DSS | 115 | 1961 | 2071 | Hydro_run | hydro_run | 8 | 65% | 5.2 | 35% | 24.528 | 1
| Wellington | SK_WLL00_GEN | SaskPower | Lake Athabasca | 59.6274 | -109.018 | Saskatchewan.a | Manitoba | Uranium City | SK_URC_DSS | 115 | 1939 | 2049 | Hydro_run | hydro_run | 5 | 65% | 3.25 | 35% | 15.33 | 1
| Western Lily | SK_WSL00_GEN | Gaia Power | Grenfell | 50.414 | -102.914 | Saskatchewan.a | Saskatachewan | Peebles | SK_PBL_DSS | 138 | 2019 | 2039 | Wind_Onshore | wind | 20 | 20% | 4 | 40% | 70.08
| Yellowhead_01 | SK_YLH01_GEN | SaskPower | North Battleford | 52.7232 | -108.2318 | Saskatchewan.a | Saskatachewan | Brada | SK_BRA_DSS | 230 | 2010 | 2040 | NG_CT | gasSC | 46 | 93% | 42.78 | 20% | 80.592 | 3
| Yellowhead_02 | SK_YLH02_GEN | SaskPower | North Battleford | 52.7232 | -108.2318 | Saskatchewan.a | Saskatachewan | Brada | SK_BRA_DSS | 230 | 2010 | 2040 | NG_CT | gasSC | 46 | 93% | 42.78 | 20% | 80.592 | 3
| Yellowhead_03 | SK_YLH03_GEN | SaskPower | North Battleford | 52.7232 | -108.2318 | Saskatchewan.a | Saskatachewan | Brada | SK_BRA_DSS | 230 | 2010 | 2040 | NG_CT | gasSC | 46 | 93% | 42.78 | 20% | 80.592 | 3
Notes:
SaskPower anticipates adding 100-200 MW of wind every two years to meet 50% installed renewable capacity target by 2030
Average Annual Energy for Manitoba Hydro imports estimated at 90% capacity factor
Wind and solar contracts presumed to be 20 years
General Notes:
See calculations sheets for sources of values
Start year indicates the year at which the facilitated was commissioned or refurbished to its current type
IPP contract durations presumed to be: all fossil fuel - 30 years; hydroelectric run-of-river - 40 years; wind - 20 years; solar 20 years; storage - 20 years; biomass - 30 years; biogas - 15 years; all renewals same duration as initial contract
Non-IPP project economic lives presumed to be: all fossil fuel - 30 years; nuclear - 50 years + 40 years per renewal; storage (including pumped) hydroelectric - 70 years + 40 years per renewal; hydroelectric run-of-river - 40 years; wind - 20 years; solar 20 years; storage - 20 years; biomass - 30 years; biogas - 15 years; all renewals same as initial project, unless indicated
When a substation contains two voltage levels, the generator connects at the more appropriate voltage based on generator capacity
Effective capacities estimated using the ELCC values in the "System" tab
Multi-unit hydro_run facilities treated as single-unit facilities
RH Additions, Comments and TODOs
Remote projects are not included in this list.
See calculations sheets for sources of values.
Sources

## Storage
SK | EXISTING STORAGE | [12 empty] | DESIGN
| Project Name | Storage Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Planning Region | Connecting Node Name | Connecting Node Code | Connecting Voltage | Start Year | End Year | Generation Type | Generation Type - COPPER | Storage Capacity | Storage Energy | Duration | Associated Generation | Cost | Other References | Notes
[11 empty] | kV |  |  |  |  | (MW) | (MWh) | (Hours) |  | ($M)
NONE
Specific Notes:

## Transmission
SK | EXISTING TRANSMISSION
| Circuit ID | Owner | Operating Region | Number of Circuits | Current | Line Segment Length | Line Segment Length | Line Length | Line Length | Voltage | Reactance | Smax | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Starting Node Name | Starting Node Code | Ending Node Name | Ending Node Code | Other References | Notes | Count
[5 empty] | (ad/dc) | (km) | (miles) | (km) | (miles) | (kV) | (ohm) |  | (A) | (A) | (MVA) | (MVA) |  | (MW) | (MW)
| A1P | Saskpower | Saskatchewan | 1 | ac | 110 | 67.9012 | 110 | 67.9012 | 138 | 47.6929 | 2.6257 | [5 empty] | 123.4072 | 136.5356 | Assiniboia | SK_ASS_DSS | Pasqua | SK_PQA_DSS |  |  | 1
| A1R | Saskpower | Saskatchewan | 1 | ac | 120 | 74.0741 | 120 | 74.0741 | 230 | 57.6 | 2.4793 | [5 empty] | 332.22 | 359.4918 | Assiniboia | SK_ASS_DSS | Rushlake Creek | SK_RUC_DSS |  | A1R + R1S previously referred to as A1S | 2
| B10T | Saskpower | Saskatchewan | 1 | ac | 10 | 6.1728 | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 150 | 150 | Boundary Dam | SK_BDM_GSS | INT Tioga | XX_SKUS1_INT | Saskpower reports US to SK summer capacity = winter capacity = 80 MW | Reported capacities are export capacities only | 3
| B1K | Saskpower | Saskatchewan | 1 | ac | 140 | 86.4198 | 140 | 86.4198 | 230 | 67.2 | 2.2396 | [5 empty] | 300.1058 | 324.7413 | Boundary Dam | SK_BDM_GSS | Kennedy | SK_KDY_DSS |  |  | 4
| B1L | Saskpower | Saskatchewan | 1 | ac | 150 | 92.5926 | 150 | 92.5926 | 230 | 72 | 2.14 | [5 empty] | 286.7567 | 310.2965 | Brada | SK_BRA_DSS | Lloydminster | SK_LDM_DSS |  |  | 5
| B1P | Saskpower | Saskatchewan | 1 | ac | 65 | 40.1235 | 65 | 40.1235 | 138 | 28.1821 | 3 | [5 empty] | 141 | 156 | Beatty | SK_BTY_DSS | Prince Albert | SK_PRA_DSS |  |  | 6
| B1Q | Saskpower | Saskatchewan | 1 | ac | 180 | 111.1111 | 180 | 111.1111 | 230 | 86.4 | 1.8975 | [5 empty] | 254.2691 | 275.1419 | Queen Elizabeth | SK_QEB_GSS | Beatty | SK_BTY_DSS |  |  | 7
| B1W | Saskpower | Saskatchewan | 1 | ac | 130 | 80.2469 | 130 | 80.2469 | 138 | 56.3643 | 2.3518 | [5 empty] | 110.5333 | 122.2922 | Wolverine | SK_WLV_DSS | Beatty | SK_BTY_DSS |  |  | 8
| B2N | Saskpower | Saskatchewan | 1 | ac | 5 | 3.0864 | 5 | 3.0864 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Brada | SK_BRA_DSS | Battleford | SK_BFD_GSS |  |  | 9
| B2P | Saskpower | Saskatchewan | 1 | ac | 65 | 40.1235 | 65 | 40.1235 | 138 | 28.1821 | 3 | [5 empty] | 141 | 156 | Beatty | SK_BTY_DSS | Prince Albert | SK_PRA_DSS |  |  | 10
| B2Q | Saskpower | Saskatchewan | 1 | ac | 180 | 111.1111 | 180 | 111.1111 | 230 | 86.4 | 1.8975 | [5 empty] | 254.2691 | 275.1419 | Queen Elizabeth | SK_QEB_GSS | Beatty | SK_BTY_DSS |  |  | 11
| B2R | Saskpower | Saskatchewan | 1 | ac | 210 | 129.6296 | 210 | 129.6296 | 230 | 100.8 | 1.7141 | [5 empty] | 229.69 | 248.5452 | Regina South | SK_REG_DSS | Boundary Dam | SK_BDM_GSS |  |  | 12
| B2T | Saskpower | Saskatchewan | 1 | ac | 55 | 33.9506 | 55 | 33.9506 | 138 | 23.8464 | 3 | [5 empty] | 141 | 156 | Beatty | SK_BTY_DSS | Tisdale | SK_TSD_DSS |  |  | 13
| B2W | Saskpower | Saskatchewan | 1 | ac | 95 | 58.642 | 95 | 58.642 | 138 | 41.1893 | 2.8922 | [5 empty] | 135.9346 | 150.3958 | Weyburn | SK_WEY_DSS | Boundary Dam | SK_BDM_GSS |  |  | 14
| B3P | Saskpower | Saskatchewan | 1 | ac | 130 | 80.2469 | 130 | 80.2469 | 138 | 56.3643 | 2.3518 | [5 empty] | 110.5333 | 122.2922 | Boundary Dam | SK_BDM_GSS | Peebles | SK_PBL_DSS |  |  | 15
| B3R | Saskpower | Saskatchewan | 1 | ac | 210 | 129.6296 | 210 | 129.6296 | 230 | 100.8 | 1.7141 | [5 empty] | 229.69 | 248.5452 | Regina South | SK_REG_DSS | Boundary Dam | SK_BDM_GSS |  |  | 16
| B4P | Saskpower | Saskatchewan | 1 | ac | 65 | 40.1235 | 65 | 40.1235 | 138 | 28.1821 | 3 | [5 empty] | 141 | 156 | Beatty | SK_BTY_DSS | Senator | SK_SNT_DSS |  |  | 17
| B6P | Saskpower | Saskatchewan | 1 | ac | 15 | 9.2593 | 15 | 9.2593 | 138 | 6.5036 | 3 | [5 empty] | 141 | 156 | Pasqua | SK_PQA_DSS | Belle Plain | SK_BLP_DSS |  |  | 18
| B71T | SaskPower | Saskatchewan | 1 | ac | 30 | 18.5185 | 30 | 18.5185 | 230 | 14.4 | 3 | [5 empty] | 402 | 435 | Tantallon | SK_TTL_DSS | IPT Tantallon | PP_MBSK4_IPT |  | Operational in 2021 | 73
| BR11 | Saskpower | Saskatchewan | 1 | ac | 170 | 104.9383 | 170 | 104.9383 | 230 | 81.6 | 1.9704 | [5 empty] | 264.037 | 285.7116 | Brada | SK_BRA_DSS | Meadow Lake | SK_MDL_GSS |  |  | 19
| C1B | Saskpower | Saskatchewan | 1 | ac | 90 | 55.5556 | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Beatty | SK_BTY_DSS | Codette | SK_CDT_DSS |  |  | 20
| C1E | Saskpower | Saskatchewan | 1 | ac | 200 | 123.4568 | 200 | 123.4568 | 138 | 86.7143 | 1.7702 | [5 empty] | 83.1974 | 92.0482 | Coteau Creek | SK_CCK_GSS | Ermine | SK_ERM_GSS |  |  | 21
| C1H | Saskpower | Saskatchewan | 1 | ac | 20 | 12.3457 | 20 | 12.3457 | 138 | 8.6714 | 3 | [5 empty] | 141 | 156 | Coteau Creek | SK_CCK_GSS | Hawarden | SK_HWD_DSS |  |  | 22
| C1P | Saskpower | Saskatchewan | 1 | ac | 60 | 37.037 | 160 | 98.7654 | 138 | 69.3714 | 2.0508 | [5 empty] | 96.3877 | 106.6417 | Riverhurst | SK_RVH_GSS | Coteau Creek | SK_CCK_GSS |  |  | 23
| C1P | Saskpower | Saskatchewan | 1 | ac | 100 | 61.7284 | 160 | 98.7654 | 138 | 69.3714 | 2.0508 | [5 empty] | 96.3877 | 106.6417 | Pasqua | SK_PQA_DSS | Riverhurst | SK_RVH_GSS |  |  | 23
| C1Q | Saskpower | Saskatchewan | 1 | ac | 110 | 67.9012 | 110 | 67.9012 | 138 | 47.6929 | 2.6257 | [5 empty] | 123.4072 | 136.5356 | Coteau Creek | SK_CCK_GSS | Queen Elizabeth | SK_QEB_GSS |  |  | 24
| C1S | Saskpower | Saskatchewan | 1 | ac | 140 | 86.4198 | 140 | 86.4198 | 230 | 67.2 | 2.2396 | [5 empty] | 300.1058 | 324.7413 | Swift Current | SK_SWC_DSS | Coteau Creek | SK_CCK_GSS |  |  | 25
| C1W | Saskpower | Saskatchewan | 1 | ac | 130 | 80.2469 | 130 | 80.2469 | 138 | 56.3643 | 2.3518 | [5 empty] | 110.5333 | 122.2922 | Condie | SK_CND_DSS | Wolverine | SK_WLV_DSS |  |  | 26
| C2B | Saskpower | Saskatchewan | 1 | ac | 90 | 55.5556 | 90 | 55.5556 | 230 | 43.2 | 2.9972 | [5 empty] | 401.627 | 434.5964 | Beatty | SK_BTY_DSS | Codette | SK_CDT_DSS |  |  | 27
| C2Q | Saskpower | Saskatchewan | 1 | ac | 250 | 154.321 | 250 | 154.321 | 230 | 120 | 1.5279 | [5 empty] | 204.7408 | 221.5479 | Condie | SK_CND_DSS | Queen Elizabeth | SK_QEB_GSS |  |  | 28
| C3B | Saskpower | Saskatchewan | 1 | ac | 210 | 129.6296 | 210 | 129.6296 | 230 | 100.8 | 1.7141 | [5 empty] | 229.69 | 248.5452 | Coteau Creek | SK_CCK_GSS | Brada | SK_BRA_DSS |  |  | 29
| E1L | Saskpower | Saskatchewan | 1 | ac | 70 | 43.2099 | 70 | 43.2099 | 138 | 30.35 | 3 | [5 empty] | 141 | 156 | Ermine | SK_ERM_GSS | Landis | SK_LDS_GSS |  |  | 30
| E2B | Saskpower | Saskatchewan | 1 | ac | 160 | 98.7654 | 160 | 98.7654 | 230 | 76.8 | 2.0508 | [5 empty] | 274.8076 | 297.3664 | Beatty | SK_BTY_DSS | EB Campbell | SK_EBC_GSS |  |  | 31
| E2C | Saskpower | Saskatchewan | 1 | ac | 70 | 43.2099 | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Codette | SK_CDT_DSS | EB Campbell | SK_EBC_GSS |  |  | 32
| I1K | Saskpower | Saskatchewan | 1 | ac | 350 | 216.0494 | 350 | 216.0494 | 230 | 168 | 1.2238 | [5 empty] | 163.9959 | 177.4582 | Key Lake | SK_KLK_DSS | Island Falls | SK_ISF_GSS |  |  | 33
| I2P | Saskpower | Manitoba | 1 | ac | 800 | 493.8272 | 800 | 493.8272 | 115 | 333.7143 | 0.7095 | [5 empty] | 23.2833 | 25.637 | Island Falls | SK_ISF_GSS | Uranium City | SK_URC_DSS |  |  | 34
| K1T | Saskpower | Saskatchewan | 1 | ac | 70 | 43.2099 | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Tantallon | SK_TTL_DSS | Kennedy | SK_KDY_DSS |  |  | 35
| L2E | Saskpower | Saskatchewan | 1 | ac | 190 | 117.284 | 190 | 117.284 | 138 | 82.3786 | 1.8311 | [5 empty] | 86.0599 | 95.2152 | Ermine | SK_ERM_GSS | Lloydminster | SK_LDM_DSS |  |  | 36
| N1C | Saskpower | Saskatchewan | 1 | ac | 5 | 3.0864 | 5 | 3.0864 | 138 | 2.1679 | 3 | [5 empty] | 141 | 156 | Codette | SK_CDT_DSS | Nipawin | SK_NIP_GSS |  |  | 37
| N1L | Saskpower | Saskatchewan | 1 | ac | 70 | 43.2099 | 70 | 43.2099 | 138 | 30.35 | 3 | [5 empty] | 141 | 156 | Battleford | SK_BFD_GSS | Landis | SK_LDS_GSS |  |  | 38
| N2L | Saskpower | Saskatchewan | 1 | ac | 140 | 86.4198 | 140 | 86.4198 | 138 | 60.7 | 2.2396 | [5 empty] | 105.261 | 116.459 | Battleford | SK_BFD_GSS | Lloydminster | SK_LDM_DSS |  |  | 39
| NB1 | Saskpower | Saskatchewan | 1 | ac | 170 | 104.9383 | 170 | 104.9383 | 230 | 81.6 | 1.9704 | [5 empty] | 264.037 | 285.7116 | Battleford | SK_BFD_GSS | Meadow Lake | SK_MDL_GSS |  |  | 40
| P1C | Saskpower | Saskatchewan | 1 | ac | 95 | 58.642 | 95 | 58.642 | 138 | 41.1893 | 2.8922 | [5 empty] | 135.9346 | 150.3958 | Pasqua | SK_PQA_DSS | Chaplin | SK_CHP_DSS |  |  | 56
| P1H | Saskpower | Saskatchewan | 1 | ac | 160 | 98.7654 | 160 | 98.7654 | 138 | 69.3714 | 2.0508 | [5 empty] | 96.3877 | 106.6417 | Pasqua | SK_PQA_DSS | Hawarden | SK_HWD_DSS |  |  | 41
| P1S | Saskpower | Saskatchewan | 1 | ac | 190 | 117.284 | 190 | 117.284 | 138 | 82.3786 | 1.8311 | [5 empty] | 86.0599 | 95.2152 | Swift Current | SK_SWC_DSS | Pasqua | SK_PQA_DSS |  |  | 42
| P2A | Saskpower | Saskatchewan | 1 | ac | 70 | 43.2099 | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Poplar River | SK_PPR_GSS | Assiniboia | SK_ASS_DSS |  |  | 43
| P2C | Saskpower | Saskatchewan | 1 | ac | 140 | 86.4198 | 140 | 86.4198 | 230 | 67.2 | 2.2396 | [5 empty] | 300.1058 | 324.7413 | Poplar River | SK_PPR_GSS | Condie | SK_CND_DSS |  |  | 44
| P2K | Saskpower | Saskatchewan | 1 | ac | 45 | 27.7778 | 45 | 27.7778 | 230 | 21.6 | 3 | [5 empty] | 402 | 435 | Peebles | SK_PBL_DSS | Kennedy | SK_KDY_DSS |  |  | 45
| P2P | Saskpower | Saskatchewan | 1 | ac | 140 | 86.4198 | 140 | 86.4198 | 230 | 67.2 | 2.2396 | [5 empty] | 300.1058 | 324.7413 | Poplar River | SK_PPR_GSS | Pasqua | SK_PQA_DSS |  |  | 46
| P2S | Saskpower | Saskatchewan | 1 | ac | 190 | 117.284 | 190 | 117.284 | 230 | 91.2 | 1.8311 | [5 empty] | 245.3623 | 265.504 | Swift Current | SK_SWC_DSS | Pasqua | SK_PQA_DSS |  |  | 42.5
| P3C | Saskpower | Saskatchewan | 1 | ac | 150 | 92.5926 | 150 | 92.5926 | 230 | 72 | 2.14 | [5 empty] | 286.7567 | 310.2965 | Peebles | SK_PBL_DSS | Condie | SK_CND_DSS |  |  | 47
| P52E | Saskpower | Saskatchewan | 1 | ac | 120 | 74.0741 | 120 | 74.0741 | 230 | 57.6 | 2.4793 | [5 empty] | 332.22 | 359.4918 | EB Campbell | SK_EBC_GSS | IPT EB Campbell | PP_MBSK2_IPT |  |  | 48
| PA4 | Saskpower | Saskatchewan | 1 | ac | 10 | 6.1728 | 10 | 6.1728 | 138 | 4.3357 | 3 | [5 empty] | 141 | 156 | Prince Albert | SK_PRA_DSS | Senator | SK_SNT_DSS |  |  | 49
| PQ3 | Saskpower | Saskatchewan | 1 | ac | 50 | 30.8642 | 50 | 30.8642 | 138 | 21.6786 | 3 | [5 empty] | 141 | 156 | Pasqua | SK_PQA_DSS | Lumsden | SK_LMS_DSS |  |  | 50
| Q1H | Saskpower | Saskatchewan | 1 | ac | 90 | 55.5556 | 90 | 55.5556 | 138 | 39.0214 | 2.9972 | [5 empty] | 140.8692 | 155.8552 | Queen Elizabeth | SK_QEB_GSS | Hawarden | SK_HWD_DSS |  |  | 51
| Q1N | Saskpower | Saskatchewan | 1 | ac | 140 | 86.4198 | 140 | 86.4198 | 138 | 60.7 | 2.2396 | [5 empty] | 105.261 | 116.459 | Queen Elizabeth | SK_QEB_GSS | Battleford | SK_BFD_GSS |  |  | 52
| Q1W | Saskpower | Saskatchewan | 1 | ac | 110 | 67.9012 | 110 | 67.9012 | 138 | 47.6929 | 2.6257 | [5 empty] | 123.4072 | 136.5356 | Wolverine | SK_WLV_DSS | Queen Elizabeth | SK_QEB_GSS |  |  | 53
| Q2N | Saskpower | Saskatchewan | 1 | ac | 140 | 86.4198 | 140 | 86.4198 | 138 | 60.7 | 2.2396 | [5 empty] | 105.261 | 116.459 | Queen Elizabeth | SK_QEB_GSS | Battleford | SK_BFD_GSS |  |  | 54
| Q3C | Saskpower | Saskatchewan | 1 | ac | 12 | 7.4074 | 12 | 7.4074 | 138 | 5.2029 | 3 | [5 empty] | 141 | 156 | Cory | SK_CRY_GSS | Queen Elizabeth | SK_QEB_GSS |  |  | 55
| R1P | Saskpower | Saskatchewan | 1 | ac | 65 | 40.1235 | 65 | 40.1235 | 138 | 28.1821 | 3 | [5 empty] | 141 | 156 | Pasqua | SK_PQA_DSS | Regina South | SK_REG_DSS |  |  | 56
| R1S | Saskpower | Saskatchewan | 1 | ac | 20 | 12.3457 | 20 | 12.3457 | 230 | 9.6 | 3 | [5 empty] | 402 | 435 | Rushlake Creek | SK_RUC_DSS | Swift Current | SK_SWC_DSS |  | A1R + R1S previously referred to as A1S | 57
| R25Y | Saskpower | Saskatchewan | 1 | ac | 70 | 43.2099 | 70 | 43.2099 | 230 | 33.6 | 3 | [5 empty] | 402 | 435 | Yorkton | SK_YKT_DSS | IPT Yorkton | PP_MBSK5_IPT |  |  | 58
| R2C | Saskpower | Saskatchewan | 1 | ac | 30 | 18.5185 | 30 | 18.5185 | 138 | 13.0071 | 3 | [5 empty] | 141 | 156 | Regina South | SK_REG_DSS | Condie | SK_CND_DSS |  |  | 59
| R4C | Saskpower | Saskatchewan | 1 | ac | 10 | 6.1728 | 10 | 6.1728 | 230 | 4.8 | 3 | [5 empty] | 402 | 435 | Regina South | SK_REG_DSS | Condie | SK_CND_DSS |  |  | 60
| R5B | Saskpower | Saskatchewan | 1 | ac | 45 | 27.7778 | 45 | 27.7778 | 138 | 19.5107 | 3 | [5 empty] | 141 | 156 | Regina South | SK_REG_DSS | Belle Plain | SK_BLP_DSS |  |  | 61
| R7B | Saskpower | Saskatchewan | 1 | ac | 130 | 80.2469 | 130 | 80.2469 | 230 | 62.4 | 2.3518 | [5 empty] | 315.1376 | 341.0071 | Boundary Dam | SK_BDM_GSS | IPT Boundary Dam | PP_MBSK3_IPT |  |  | 62
| S1C | Saskpower | Saskatchewan | 1 | ac | 30 | 18.5185 | 95 | 58.642 | 138 | 41.1893 | 2.8922 | [5 empty] | 135.9346 | 150.3958 | Chaplin | SK_CHP_DSS | Morse | SK_MRS_GSS |  |  | 56
| S1C | Saskpower | Saskatchewan | 1 | ac | 65 | 40.1235 | 95 | 58.642 | 138 | 41.1893 | 2.8922 | [5 empty] | 135.9346 | 150.3958 | Morse | SK_MRS_GSS | Swift Current | SK_SWC_DSS |  |  | 56
| S1M | Saskpower | Saskatchewan | 1 | ac | 170 | 104.9383 | 170 | 104.9383 | 230 | 81.6 | 1.9704 | [5 empty] | 264.037 | 285.7116 | Swift Current | SK_SWC_DSS | IPT McNeill | PP_ABSK1_IPT |  |  | 63
| S2P | Saskpower | Saskatchewan | 1 | ac | 120 | 74.0741 | 120 | 74.0741 | 230 | 57.6 | 2.4793 | [5 empty] | 332.22 | 359.4918 | Peebles | SK_PBL_DSS | Shand | SK_SHD_GSS |  |  | 64
| S3B | Saskpower | Saskatchewan | 1 | ac | 12 | 7.4074 | 12 | 7.4074 | 230 | 5.76 | 3 | [5 empty] | 402 | 435 | Boundary Dam | SK_BDM_GSS | Shand | SK_SHD_GSS |  |  | 65
| SW7 | Saskpower | Saskatchewan | 1 | ac | 30 | 18.5185 | 30 | 18.5185 | 138 | 13.0071 | 3 | [5 empty] | 141 | 156 | Swift Current | SK_SWC_DSS | Bone Creek | SK_BCK_DSS |  |  | 66
| TP7 | Saskpower | Manitoba | 1 | ac | 120 | 74.0741 | 240 | 148.1481 | 115 | 100.1143 | 1.5696 | [5 empty] | 51.5089 | 56.7161 | Island Falls | SK_ISF_GSS | IPT Island Falls | PP_MBSK1_IPT |  |  | 67
| TP7 | Saskpower | Manitoba | 1 | ac | 120 | 74.0741 | 240 | 148.1481 | 115 | 100.1143 | 1.5696 | [5 empty] | 51.5089 | 56.7161 | Island Falls | SK_ISF_GSS | IPT Island Falls | PP_MBSK1_IPT |  |  | 68
| W1R | Saskpower | Saskatchewan | 1 | ac | 110 | 67.9012 | 110 | 67.9012 | 138 | 47.6929 | 2.6257 | [5 empty] | 123.4072 | 136.5356 | Regina South | SK_REG_DSS | Weyburn | SK_WEY_DSS |  |  | 69
| W1Y | Saskpower | Saskatchewan | 1 | ac | 210 | 129.6296 | 210 | 129.6296 | 138 | 91.05 | 1.7141 | [5 empty] | 80.5629 | 89.1335 | Yorkton | SK_YKT_DSS | Wolverine | SK_WLV_DSS |  |  | 70
| Y1P | Saskpower | Saskatchewan | 1 | ac | 130 | 80.2469 | 130 | 80.2469 | 138 | 56.3643 | 2.3518 | [5 empty] | 110.5333 | 122.2922 | Peebles | SK_PBL_DSS | Yorkton | SK_YKT_DSS |  |  | 71
| Y1T | Saskpower | Saskatchewan | 1 | ac | 90 | 55.5556 | 90 | 55.5556 | 138 | 39.0214 | 2.9972 | [5 empty] | 140.8692 | 155.8552 | Tantallon | SK_TTL_DSS | Yorkton | SK_YKT_DSS |  |  | 72
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station
General Notes:
Smax = Loadability in multiples of SIL = 42.40 (Length in Miles)^(−0.6595) (this is a power function interpolation of Figure 7 in Gutman et al.)

## Nodes
SK | EXISTING SUBSTATIONS
| Node Name | Node Code | Owner | Latitude | Longitude | Operating Region | Other References | Notes
| Assiniboia | SK_ASS_DSS | Saskpower | 49.6113 | -105.9617 | Saskatachewan
| Battleford | SK_BFD_GSS | Saskpower | 52.7582 | -108.2803 | Saskatachewan
| Beatty | SK_BTY_DSS | Saskpower | 52.911 | -104.8442 | Saskatachewan
| Belle Plain | SK_BLP_DSS | Saskpower | 50.3936 | -105.1557 | Saskatachewan
| Bone Creek | SK_BCK_DSS | Saskpower | 49.9189 | -108.1173 | Saskatachewan
| Boundary Dam | SK_BDM_GSS | Saskpower | 49.0961 | -103.0305 | Saskatachewan
| Brada | SK_BRA_DSS | Saskpower | 52.7022 | -108.1727 | Saskatachewan
| Chaplin | SK_CHP_DSS | Saskpower | 50.4585 | -106.6553 | Saskatachewan
| Codette | SK_CDT_DSS | Saskpower | 53.2877 | -104.0377 | Saskatachewan
| Condie | SK_CND_DSS | Saskpower | 50.5195 | -104.7567 | Saskatachewan
| Cory | SK_CRY_GSS | Saskpower | 52.0927 | -106.8533 | Saskatachewan
| Coteau Creek | SK_CCK_GSS | Saskpower | 51.2748 | -106.8736 | Saskatachewan
| EB Campbell | SK_EBC_GSS | Saskpower | 53.689 | -103.3475 | Saskatachewan
| Ermine | SK_ERM_GSS | Saskpower | 51.873 | -109.0399 | Saskatachewan
| Hawarden | SK_HWD_DSS | Saskpower | 51.4172 | -106.6259 | Saskatachewan
| INT Tioga | XX_SKUS1_INT | SK-US Border | 48.9993 | -103.0244 | Saskatachewan
| IPT Boundary Dam | PP_MBSK3_IPT | MB-SK Border | 49.4953 | -101.3931 | Saskatachewan
| IPT EB Campbell | PP_MBSK2_IPT | MB-SK Border | 53.7227 | -101.7696 | Saskatachewan
| IPT Island Falls | PP_MBSK1_IPT | MB-SK Border | 54.7947 | -101.8859 | Manitoba
| IPT McNeill | PP_ABSK1_IPT | AB-SK Border | 50.5894 | -110.004 | Saskatachewan
| IPT Tantallon | PP_MBSK4_IPT | MB-SK Border | 50.5445 | -101.4747 | Saskatachewan
| IPT Yorkton | PP_MBSK5_IPT | MB-SK Border | 51.2025 | -101.5389 | Saskatachewan
| Island Falls | SK_ISF_GSS | Saskpower | 55.5284 | -102.3561 | Manitoba
| Kennedy | SK_KDY_DSS | Saskpower | 50.0446 | -102.422 | Saskatachewan
| Key Lake | SK_KLK_DSS | Saskpower | 57.2244 | -105.645 | Saskatachewan
| Landis | SK_LDS_GSS | Saskpower | 52.1988 | -108.4509 | Saskatachewan
| Lloydminster | SK_LDM_DSS | Saskpower | 53.247 | -109.9743 | Saskatachewan
| Lumsden | SK_LMS_DSS | Saskpower | 50.6469 | -104.8671 | Saskatachewan
| Meadow Lake | SK_MDL_GSS | Saskpower | 54.0884 | -108.4375 | Saskatachewan
| Morse | SK_MRS_GSS | Saskpower | 50.3991 | -107.2231 | Saskatachewan
| Nipawin | SK_NIP_GSS | Saskpower | 53.321 | -104.0431 | Saskatachewan
| Pasqua | SK_PQA_DSS | Saskpower | 50.3783 | -105.3913 | Saskatachewan
| Peebles | SK_PBL_DSS | Saskpower | 50.159 | -102.9476 | Saskatachewan
| Poplar River | SK_PPR_GSS | Saskpower | 49.0579 | -105.4851 | Saskatachewan
| Prince Albert | SK_PRA_DSS | Saskpower | 53.155 | -105.7356 | Saskatachewan
| Queen Elizabeth | SK_QEB_GSS | Saskpower | 52.0944 | -106.705 | Saskatachewan
| Regina South | SK_REG_DSS | Saskpower | 50.4311 | -104.5494 | Saskatachewan
| Riverhurst | SK_RVH_GSS | Saskpower | 50.8929 | -106.8814 | Saskatachewan
| Rushlake Creek | SK_RUC_DSS | Saskpower | 50.3425 | -107.4016 | Saskatachewan
| Senator | SK_SNT_DSS | Saskpower | 53.0654 | -105.7325 | Saskatachewan
| Shand | SK_SHD_GSS | Saskpower | 49.0751 | -102.8641 | Saskatachewan
| Swift Current | SK_SWC_DSS | Saskpower | 50.2983 | -107.9262 | Saskatachewan
| Tantallon | SK_TTL_DSS | Saskpower | 50.5961 | -101.8554 | Saskatachewan
| Tisdale | SK_TSD_DSS | Saskpower | 52.8787 | -104.0373 | Saskatachewan
| Uranium City | SK_URC_DSS | Saskpower | 59.569 | -108.6097 | Manitoba
| Weyburn | SK_WEY_DSS | Saskpower | 49.6434 | -103.9017 | Saskatachewan
| Wolverine | SK_WLV_DSS | Saskpower | 51.8787 | -105.3123 | Saskatachewan
| Yorkton | SK_YKT_DSS | Saskpower | 51.1867 | -102.4527 | Saskatachewan
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## HydroExisting
SK | EXISTING HYDROELECTRIC
| Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | # of units | Renewal Year | Dam Type | Penstock | Rated Head | Maximum Head | Minimum Head | Average Flow (Facility) | Rated Discharge (Unit) | Rated Discharge (Facility) | Upstream Reservoir Area | Upstream Reservoir Storage | Turbine Type | Station Flow | Upper Storage | Upper Storage Level | Lower Storage | Lower Storage Level | Upper Storage Name | Minimum Level | Maximum Level | Initial Level | Low Reference Level | High Reference Level | Low Volume | High Volume | Live Storage | M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10 | M11 | M12 | Notes
|  |  | (MW) |  | (MW) |  | (GWh/year) |  |  |  | (m) | (m) | (m) | (m) | (m3/s) | (m3/s) | (m3/s) | (km2) | (hours) |  | (WSC#) |  | (WSC#) |  | (WSC#) |  | (m) | (m) | (m) | (m) | (m) | (m3) | (m3) | (m3) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m3/s)
| Coteau Creek | Hydro-daily | 186 | 98.1% | 182.466 | 45% | 733.212 | 3 | [13 empty] | Diefenbaker Lake | 05HF003 |  |  | Diefenbaker Lake
| E.B. Campbell | Hydro-daily | 288 | 98.1% | 282.528 | 45% | 1135.296 | 8 | 2025 | [11 empty] | 05KD003 | Tobin Lake | 05KD004 |  |  | Tobin Lake
| Island Falls | Hydro-daily | 111 | 98.1% | 108.891 | 45% | 437.562 | 7 | [12 empty] | 06EA002 | Island Falls Headpond |  | Churchill River |  | Island Falls Headpond
| Nipawin | Hydro-daily | 255 | 98.1% | 250.155 | 45% | 1005.21 | 3 | [13 empty] | Codette Reservoir | 05KD006 | Tobin Lake | 05KD004 | Codette Reservoir
Specific Notes:
Hydroelectric generation type has been estimated based on available information concerning operations, reservoir size and operations, facility location and design flows.
The WSC# refers to the Water Survey of Canada Hydrometric station

## HydroRenewals
SK | HYDROELECTRIC RENEWAL | [7 empty] | EXISTING DESIGN |  |  |  |  | RENEWAL | [5 empty] | COSTS | 1.77% | 1.06
| Existing Project Name | Owner | Location | Merra Grid Location | Substation Name | Bus Voltage | Start Year | Turbine Renewal Year | Type | Installed Capacity | Dependable Capacity | Annual Average Energy (WECC) | Existing #units | Renewal Project Name | Project Short Name | Distance to Grid | Additional Installed Capacity | Additional Dependable Capacity | Additional Annual Energy | Direct Capital Cost | Capital Overhead | Interest During Construction | Implentation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Fixed O&M | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
[10 empty] | (MW) | (MW) | (GWh/year) |  |  |  | (km) | (MW) | (MW) | (GWh/year) | ($2018M) | ($M) | ($M) | ($M) | ($M) | ($M) | ($M/year) | ($M/year) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
NONE
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroGreenfield
SK | HYDROELECTRIC GREENFIELD | [10 empty] | DESIGN | [6 empty] | COSTS |  | 1.77% | 1.06 |  |  | 7% | 70
| Project Name | Short Name | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Distance to Grid | Connecting Node Name | Connecting Node Code | Substation Voltage | Generation Type | Generation Type - COPPER | Installed Capacity | Effective Capacity | Average Annual Energy | Capacity Factor | # of units | Direct Capital Cost | Direct Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Capacity Cost | Unit Energy Cost | Construction Time | Development Time | Notes
[8 empty] | (km) |  |  | (kV) |  |  | (MW) | (MW) | (GWh/year) | (%) |  | ($2014M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW-year) | ($/MWh) | (years) | (years)
| Tazi Twe | GF_TAZ | Saskpower | Black Lake First Nation | 59.1279 | -105.5298 | Saskatchewan.a | 25 |  |  |  | hydro_daily | hydro_daily | 50 | 50 | 400 | 91.32% | 2 | 500 | 532.7476 | 9.4296 | 86.3543 | 628.5316 | 75.4897 | 704.0213 | 49.7177 | 994.353 | 55975.117 | 3.1448 | 5.7 | 8.8448 |  |  | 4 | 6 | Environmental Assessment already complete
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## HydroPS
SK | HYDROELECTRIC PUIMPED STORAGE | [15 empty] | Existing Design | [8 empty] | Reservoir Design | [13 empty] | Costs | 1.77% | 1.06 |  |  | 7% | 70
| Pumped Storage Project | Project Code | Owner | Location | Latitude | Longitude | COPPER Balancing Area | Connecting Node Name | Connecting Node Code | Connecting Voltage | Distance to Market Grid | Generation Type | Generation Type - COPPER | Additional Installed Capacity | Additional Dependable Capacity | Estimated Round Trip Efficiency | Existing Project Name | Generation Type | Installed Capacity | Capacity Adjustment | Effective Capacity | Capacity Factor | Annual Average Energy - Plant | Existing #units | Start Year | Salt/Fresh | Reservoir Types | Reservoir Storage | Storage Requirement | Gross Head | Penstock | H/L Ratio | Design Flow (Generation) | Design Flow (Pumping) | Turbine Type | Pump Type | Generation Duration at Peak Output | Efficient Pumping Capacity Duration | Total Footprint | Total Capital Cost | Capital Overhead | Interest During Construction | Implementation Costs | Project Definition Costs | Total Project Cost | Annualized Project Cost | Annualized Project Cost per kW | Fixed O&M | Variable Cost | Water Rentals | Variable O&M | Unit Cost of Capacity | Unit Cost of Stored Energy | Levelized Cost | Construction Time | Development Time | Notes
[5 empty] | dd.dddd | dd.dddd |  |  |  | (kV) | (km) |  |  | (MW) | (MW) |  |  |  | (MW) | (%) | (MW) | (%) | (GWh/year) |  |  |  |  | (m3) | (MWh) | (m) | (m) | (%) | (m3/s) | (m3/s) |  |  | (h) | (h) | (ha) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($2018M) | ($M/year) | ($/kW-year) | ($/MW-year) | ($/MWh) | ($/MWh) | ($/MWh) | ($2018/MW) | ($2018/MWh) | ($2018/kW-year) | (years) | (years)
General Notes:
Unless already included in total capital costs, a distance of 25 km is added to distance to market grid to account for potential grid interconnection costs
Assume installed capacity of hydroelectric renewals is all dependable capacity, though this should be verified with new studies.
Assume hydro_daily and hydro_monthly generation has dependable capacity equal to installed capacity
Total Capital Costs include contingency and project management costs, but exclude IDC, corporate overhead, future inflation and transmission costs
Assume a Capital Overhead rate of 1.77% of total capital costs (inclusive of contingencies, as they are above) based on BC Hydro rate
Assume IDC rate of 5% each year
Assume Project Definition costs using regression curve found in the CA-Inventory dataset
Assume hydroelectric, greenfield and pumped storage facilities have an economic life of 70 years
Assume a discount rate of 7% each year
Fixed O&M and variable costs estimated using regression curves found in the CA-Inventory dataset

## Distribution
SK | EXISTING TRANSFORMERS
| Node Name | Node Code | Owner | Latitude | Longitude | Planning Region | Transformers | Primary Voltage | Secondary Voltage | Summer Rating | Winter Rating | Power Factor | Summer Capacity | Winter Capacity | Other References | Notes
[8 empty] | (kV) | (kV) | (MVA) | (MVA) |  | (MW) | (MW)
| Assiniboia | SK_ASS_SUB | Saskpower | 49.6113 | -105.9617 | Saskatchewan |  | 138
| Battleford | SK_BFD_SUB | Saskpower | 52.7582 | -108.2803 | Saskatchewan |  | 138
| Beatty | SK_BTY_SUB | Saskpower | 52.911 | -104.8442 | Saskatchewan |  | 138
| Belle Plain | SK_BLP_SUB | Saskpower | 50.3936 | -105.1557 | Saskatchewan |  | 138
| Bone Creek | SK_BCK_SUB | Saskpower | 49.9189 | -108.1173 | Saskatchewan |  | 138
| Boundary Dam | SK_BDM_SUB | Saskpower | 49.0961 | -103.0305 | Saskatchewan |  | 230
| Brada | SK_BRA_SUB | Saskpower | 52.7022 | -108.1727 | Saskatchewan |  | 230
| Chaplin | SK_CHP_SUB | Saskpower | 50.4585 | -106.6553 | Saskatchewan |  | 138
| Codette | SK_CDT_SUB | Saskpower | 53.2877 | -104.0377 | Saskatchewan |  | 138
| Condie | SK_CND_SUB | Saskpower | 50.5195 | -104.7567 | Saskatchewan |  | 138
| Cory | SK_CRY_SUB | Saskpower | 52.0927 | -106.8533 | Saskatchewan |  | 138
| Coteau Creek | SK_CCK_SUB | Saskpower | 51.2748 | -106.8736 | Saskatchewan |  | 138
| EB Campbell | SK_EBC_SUB | Saskpower | 53.689 | -103.3475 | Saskatchewan |  | 230
| Ermine | SK_ERM_SUB | Saskpower | 51.873 | -109.0399 | Saskatchewan |  | 138
| Hawarden | SK_HWD_SUB | Saskpower | 51.4172 | -106.6259 | Saskatchewan |  | 138
| Island Falls | SK_ISF_SUB | Saskpower | 55.5284 | -102.3561 | Manitoba |  | 115
| Kennedy | SK_KDY_SUB | Saskpower | 50.0446 | -102.422 | Saskatchewan |  | 230
| Key Lake | SK_KLK_SUB | Saskpower | 57.2244 | -105.645 | Saskatchewan |  | 230
| Landis | SK_LDS_SUB | Saskpower | 52.1988 | -108.4509 | Saskatchewan |  | 138
| Lloydminster | SK_LDM_SUB | Saskpower | 53.247 | -109.9743 | Saskatchewan |  | 138
| Lumsden | SK_LMS_SUB | Saskpower | 50.6469 | -104.8671 | Saskatchewan |  | 138
| Meadow Lake | SK_MDL_SUB | Saskpower | 54.0884 | -108.4375 | Saskatchewan |  | 230
| Morse | SK_MRS_SUB | Saskpower | 50.3991 | -107.2231 | Saskatchewan |  | 138
| Nipawin | SK_NIP_SUB | Saskpower | 53.321 | -104.0431 | Saskatchewan |  | 138
| Pasqua | SK_PQA_SUB | Saskpower | 50.3783 | -105.3913 | Saskatchewan |  | 138
| Peebles | SK_PBL_SUB | Saskpower | 50.159 | -102.9476 | Saskatchewan |  | 230
| Poplar River | SK_PPR_SUB | Saskpower | 49.0579 | -105.4851 | Saskatchewan |  | 230
| Prince Albert | SK_PRA_SUB | Saskpower | 53.155 | -105.7356 | Saskatchewan |  | 138
| Queen Elizabeth | SK_QEB_SUB | Saskpower | 52.0944 | -106.705 | Saskatchewan |  | 230
| Regina South | SK_REG_SUB | Saskpower | 50.4311 | -104.5494 | Saskatchewan |  | 230
| Riverhurst | SK_RVH_SUB | Saskpower | 50.8929 | -106.8814 | Saskatchewan |  | 138
| Rushlake Creek | SK_RUC_SUB | Saskpower | 50.3425 | -107.4016 | Saskatchewan |  | 230
| Senator | SK_SNT_SUB | Saskpower | 53.0654 | -105.7325 | Saskatchewan |  | 138
| Shand | SK_SHD_SUB | Saskpower | 49.0751 | -102.8641 | Saskatchewan |  | 230
| Swift Current | SK_SWC_SUB | Saskpower | 50.2983 | -107.9262 | Saskatchewan |  | 230
| Tantallon | SK_TTL_SUB | Saskpower | 50.5961 | -101.8554 | Saskatchewan |  | 230
| Tisdale | SK_TSD_SUB | Saskpower | 52.8787 | -104.0373 | Saskatchewan |  | 138
| Uranium City | SK_URC_SUB | Saskpower | 59.569 | -108.6097 | Manitoba |  | 115
| Weyburn | SK_WEY_SUB | Saskpower | 49.6434 | -103.9017 | Saskatchewan |  | 138
| Wolverine | SK_WLV_SUB | Saskpower | 51.8787 | -105.3123 | Saskatchewan |  | 138
| Yorkton | SK_YKT_SUB | Saskpower | 51.1867 | -102.4527 | Saskatchewan |  | 138
Legend:
CSS = AC/DC Converter Station
DFS = Dual Function Distribution and Generation Substation
DSS = Distribution Substation
GEN = Generating Unit
GSS = Generating Substation
INT = International Intertie
IPT = Interprovincial Intertie
ISS = Industrial Customer Substation
JCT = Junction
MTS = Municipal Transformer Station
SWS = Switching Station
TS = Transformer Station
TSS = Terminal Station

## System
SK | SYSTEM CHARACTERISTICS | [9 empty] | SYSTEM CHARACTERISTICS
| Generator Type | Capacity Adjustment (Winter) | Capacity Adjustment (Summer) | Capacity Adjustment (Average) | Capacity (2017) | Capacity (2017) | Generation (2017) | Generation (2017) | Capacity Factor | Other References | Reserve Requirements | Line Losses
|  | (%) | (%) | (%) | (%) | (MW) | (%) |  | (%) |  | (% installed MW) | (% across system)
| Coal | 90% | 90% | 90% | 34% | 1526.94 | 44% | 10724.56 | 80% | Capacity factors extrapolated from available data | 13 | 8
| Natural Gas CT | 93% | 93% | 93% | 16% | 718.56 | 5% | 1218.7 | 20% | Capacity factors extrapolated from available data
| Natural Gas CC/CG | 73% | 73% | 73% | 24% | 1077.84 | 31% | 7555.94 | 80% | Capacity factors extrapolated from available data
| Biogas/Biomass | 95% | 95% | 95% | 1.5% | 67.365 | 2.5% | 609.35 | 95% | Capacity factors extrapolated from available data
| Hydro_run | 65% | 65% | 65% |  |  |  |  | 35% | Capacity factors extrapolated from available data
| Hydro_daily | 98.1% | 98.1% | 98.1% | 20% | 898.2 | 14% | 3412.36 | 45% | Capacity factors extrapolated from available data
| Hydro_monthly | 98.1% | 98.1% | 98.1%
| Wind |  | 23.2% | 20% | 4.65% | 208.8315 | 3% | 731.22 | 40% | Capacity factors extrapolated from available data
| Solar | 5% | 15% | 10% |  |  |  |  | 20% | https://www.cer-rec.gc.ca/nrg/sttstc/lctrct/rprt/cnmcsfslrpwr/rslts-eng.html
| TOTAL |  |  |  |  | 4491 |  | 24374 | 61.96%
Notes:
ELCC is a dynamic value that changes as the wind penetration level changes, and is unique to each electricity system depending upon the capabilities of the other system generating units and the load shape.
A wind ELCC specific to Saskatachewan has not yet been located, so the average value determined in the PCWIS (Figure 1-23) has been used.

## HGWh
SK | HISTORICAL ANNUAL ENERGY | UNIT | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2010-2018
| Annual Energy Demand (after DSM) | GWh/year | 20759 | 21611 | 22129 | 23155 | 23424 | 23756 | 24374 | 25317 | 25777
| Annual Change in Energy Demand | GWh/year |  | 852 | 518 | 1026 | 269 | 332 | 618 | 943 | 460 | Average
| Percentage Change in Energy Demand | % |  | 4.104% | 2.397% | 4.636% | 1.162% | 1.417% | 2.601% | 3.869% | 1.817% | 2.743%
Notes:

## HMW
SK | HISTORICAL PEAK CAPACITY | UNIT | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2010-2018
| Annual Capacity Demand (after DSM) | MW | 3162 | 3195 | 3314 | 3543 | 3561 | 3640 | 3747 | 3792 | 3723
| Annual Change in Capacity Demand | MW |  | 33 | 119 | 229 | 18 | 79 | 107 | 45 | -69 | Average
| Percentage Change in Capacity Demand | % |  | 1.044% | 3.725% | 6.91% | 0.508% | 2.218% | 2.94% | 1.201% | -1.82% | 2.063%
Notes:

## FGWh
SK | FORECAST ANNUAL ENERGY DEMAND
|  | UNITS | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2026-2036 | Notes
| Mid-load (before DSM) | GWh/y | 25616 | 25955 | 26217 | 26568 | 26885 | 27092 | 27383 | 27633 | 28027 | 28428 | 28792 | 29223 | 29599 | 30029 | 30369 | 30695 | 31105
| Mid-load (after DSM) | GWh/y | 25422 | 25710 | 25920 | 26219 | 26482 | 26632 | 26869 | 27067 | 27411 | 27767 | 28088 | 28479 | 28819 | 29213 | 29524 | 29825 | 30214 | 30570.5954 | 30931.3994 | 31296.4618 | 31665.8327 | 32039.5631 | 32417.7044 | 32800.3086 | 33187.4284 | 33579.1172 | 33975.4288 | 34376.4178 | 34782.1394 | 35192.6494 | 35608.0044 | 2026-2036 Rate | Assume extended to 2050
|  |  |  | 1.133% | 0.8168% | 1.154% | 1.003% | 0.5664% | 0.8899% | 0.7369% | 1.271% | 1.299% | 1.156% | 1.392% | 1.194% | 1.367% | 1.065% | 1.02% | 1.304% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | 1.18% | Mid-load for use in COPPER
| Saskatachewan | GWh/y | 25422 | 25710 | 25920 | 26219 | 26482 | 26632 | 26869 | 27067 | 27411 | 27767 | 28088 | 28479 | 28819 | 29213 | 29524 | 29825 | 30214 | 30570.5954 | 30931.3994 | 31296.4618 | 31665.8327 | 32039.5631 | 32417.7044 | 32800.3086 | 33187.4284 | 33579.1172 | 33975.4288 | 34376.4178 | 34782.1394 | 35192.6494 | 35608.0044
Notes:

## FMW
SK | FORECAST PEAK DEMAND
|  | UNITS | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2026-2036 | Notes
| Mid-load (before DSM) | MW | 4088 | 4130 | 4176 | 4229 | 4283 | 4311 | 4370 | 4403 | 4455 | 4520 | 4583 | 4651 | 4696 | 4767 | 4831 | 4881 | 4934
| Mid-load (after DSM) | MW | 4050 | 4082 | 4119 | 4162 | 4207 | 4225 | 4275 | 4299 | 4343 | 4401 | 4457 | 4518 | 4557 | 4624 | 4684 | 4730 | 4780 | 4833.6709 | 4887.9443 | 4942.8272 | 4998.3263 | 5054.4486 | 5111.201 | 5168.5907 | 5226.6247 | 5285.3104 | 5344.655 | 5404.6659 | 5465.3506 | 5526.7168 | 5588.7719 | 2026-2036 Rate | Assume extended to 2050
|  |  |  | 0.7901% | 0.9064% | 1.044% | 1.081% | 0.4279% | 1.183% | 0.5614% | 1.023% | 1.335% | 1.272% | 1.369% | 0.8632% | 1.47% | 1.298% | 0.9821% | 1.057% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | 1.123% | Mid-load for use in COPPER
| Saskatachewan | MW | 4050 | 4082 | 4119 | 4162 | 4207 | 4225 | 4275 | 4299 | 4343 | 4401 | 4457 | 4518 | 4557 | 4624 | 4684 | 4730 | 4780 | 4833.6709 | 4887.9443 | 4942.8272 | 4998.3263 | 5054.4486 | 5111.201 | 5168.5907 | 5226.6247 | 5285.3104 | 5344.655 | 5404.6659 | 5465.3506 | 5526.7168 | 5588.7719
Notes:

## Hourly
SK | Hourly
See the Hourly folder

## Inputs
SK | INPUT DATA AND ASSUMPTIONS
| Reactance as function of voltage |  |  | Surge Impedance Loading | [5 empty] | Transmission line flow ratings | [8 empty] | Conversions |  |  | CPI - Canada (all items)
| Voltage | Voltage | Reactance | Voltage | Voltage | Zc (High) | Zc (Low) | SIL (Low) | SIL (High) | Voltage | Summer Ampacity | Winter Ampacity | Summer Rating | Winter Rating | MH Values | Summer Capacity | Winter Capacity | Notes | Winter/Summer Tranmission Flow Conversion | Winter/Summer Transformer Flow Conversion | Power Factor | Year | Index | Year | Index | Year | Index | Year | Index
| (V) | (kV) | (ohm/km) | (V) | (kV) | (ohms) | (ohms) | (MW) | (MW) | (kV) | (A) | (A) | (MVA) | (MVA) | (MVA) | (MW) | (MW)
| 63000 | 63 | 0.38 | 63000 | 63 | 400 | 366 | 9.9225 | 10.8443 | 69 | 500 | 650 | 59.7558 | 77.6825 |  | 53.7802 | 69.9142 | Same values used for 63-72 kV | 1.3 | 1.2 | 0.9 | 1980 | 44.0333 | 1990 | 78.3583 | 2000 | 95.375 | 2010 | 116.4667
| 66000 | 66 | 0.38214 | 66000 | 66 | 400 | 366 | 10.89 | 11.9016 | 115 | 600 | 780 | 119.5115 | 155.365 | 125 | 107.5604 | 139.8285 |  |  |  |  | 1981 | 49.525 | 1991 | 82.7667 | 2001 | 97.7833 | 2011 | 119.8583
| 69000 | 69 | 0.38429 | 69000 | 69 | 400 | 366 | 12 | 13 | 120 | 610 | 793 | 126.7861 | 164.822 |  | 114.1075 | 148.3398 |  |  |  |  | 1982 | 54.8583 | 1992 | 84 | 2002 | 99.9917 | 2012 | 121.675
| 72000 | 72 | 0.38643 | 72000 | 72 | 400 | 366 | 12.96 | 14.1639 | 138 | 650 | 845 | 155.365 | 201.9744 | 150 | 139.8285 | 181.777 |  |  |  |  | 1983 | 58.075 | 1993 | 85.5667 | 2003 | 102.75 | 2013 | 122.8167
| 115000 | 115 | 0.41714 | 115000 | 115 | 403 | 366 | 32.8164 | 36.1339 | 161 | 700 | 910 | 195.2021 | 253.7628 |  | 175.6819 | 228.3865 |  |  |  |  | 1984 | 60.575 | 1994 | 85.7083 | 2004 | 104.6583 | 2014 | 125.1583
| 120000 | 120 | 0.42071 | 120000 | 120 | 403 | 366 | 35.732 | 39.3443 | 230 | 1000 | 1300 | 398.3717 | 517.8832 | 400 | 358.5345 | 466.0949 |  |  |  |  | 1985 | 62.975 | 1995 | 87.55 | 2005 | 106.975 | 2015 | 126.6
| 138000 | 138 | 0.43357 | 138000 | 138 | 405 | 366 | 47 | 52 | 240 | 1025 | 1332.5 | 426.0845 | 553.9098 |  | 383.476 | 498.5189 |  |  |  |  | 1986 | 65.6167 | 1996 | 88.925 | 2006 | 109.1167 | 2016 | 128.375
| 144000 | 144 | 0.43786 | 144000 | 144 | 405 | 366 | 51.2 | 56.6557 | 315 | 1150 | 1495 | 627.4354 | 815.666 |  | 564.6919 | 734.0994 |  |  |  |  | 1987 | 68.475 | 1997 | 90.3667 | 2007 | 111.45 | 2017 | 130.425
| 161000 | 161 | 0.45 | 161000 | 161 | 403 | 366 | 64.3201 | 70.8224 | 345 | 1300 | 1690 | 776.8248 | 1009.8722 | 800 | 699.1423 | 908.885 |  |  |  |  | 1988 | 71.2333 | 1998 | 91.2667 | 2008 | 114.0917 | 2018 | 133.3833
| 230000 | 230 | 0.48 | 230000 | 230 | 395 | 365 | 134 | 145 | 500 | 1800 | 2340 | 1558.8457 | 2026.4994 | 1600 | 1402.9612 | 1823.8495 |  |  |  |  | 1989 | 74.7833 | 1999 | 92.85 | 2009 | 114.4333 | 2019 | 136
| 240000 | 240 | 0.47685 | 240000 | 240 | 394 | 363 | 146.1929 | 158.6777 | 735 | 2500 | 3250 | 3182.6434 | 4137.4364 | 3200 | 2864.379 | 3723.6927
| 287000 | 287 | 0.46206 | 287000 | 287 | 385 | 340 | 213.9455 | 242.2618 | 765 | 2600 | 3380 | 3445.0491 | 4478.5638 |  | 3100.5442 | 4030.7074 |  |  |  |  | Notes:
| 315000 | 315 | 0.45324 | 315000 | 315 | 375 | 310 | 264.6 | 320.0806 | [12 empty] | Statistics Canada – TABLE 18-10-0005-01, annual average, not seasonally adjusted
| 345000 | 345 | 0.4438 | 345000 | 345 | 366 | 280 | 325 | 425 | (kV): Specific Notes:
| 360000 | 360 | 0.43907 | 360000 | 360 | 360 | 275 | 360 | 471.2727 | (kV): Ampacity estimates made from known ratings on existing lines
| 500000 | 500 | 0.395 | 500000 | 500 | 294 | 233 | 850 | 1075 | (kV): MH estimates provided by David Jacobson in an email of July 30, 2019
| 735000 | 735 | 0.38 | 735000 | 735 | 270 | 250 | 2000.8333 | 2160.9
| 765000 | 765 | 0.37809 | 765000 | 765 | 266 | 254 | 2200 | 2300
Notes:
SIL (Low) assumed for summer and SIL (High) for winter
Values estimated between known values
Surge impedance loading (SIL) is the power delivered by a lossless line to a load resistance equal to the surge impedance Zc = (L/C)^0.5
L = inductance
C = capacitance