## site independent
technology assumptions | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | [9 empty] | references colour coded
[8 empty] | estimated start up times (notice to full load) |  |  |  | cycling costs |  |  | research these value and add it here
non-vre sources | levelized capital cost | fixed o&m cost | variable o&m cost (inc. fuel) | transmission investment | total system LCOE | efficiency | GHG emissions | hot start | warm start | cold start | spin ramp rate | hot start | warm start | cold start | spinning cost | minimum up time | minimum down time | shut down cost | negative change in power for spinning unit | shut down ramp limit | Operating reserve coeff. | Max capacity value | Total overnight cost in 2014
| 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh |  | kg CO2e/MWh | hours |  |  | %/min | $/MW cap. |  |  | [$ per hour committed] | [hours] | [hours] |  |  |  | [Fraction of installed capacity] | [Fraction of installed capacity] | $/kW
coal | 60 | 4.2 | 30.3 | 1.2 | 95.6 | 0.32623 | 820 | 3 | 6.5 | 10 | 2 | 59 | 65 | 105 | 10000 | 3 | 3 | 0 |  |  | 0.53 | 1 | 2917 | "Levelized cost and levelized avoided cost of new generation resources in the Annual Energy Outlook 2014" US Energy Information Administration
Natural gas | [14 empty] | 10000 | 4 | 3 | 0 |  |  |  | 1 |  | "FAQ: What is the efficiency of different types of power plants?" US Energy Information Administration
NG_CC | 14.3 | 1.7 | 49.1 | 1.2 | 66.3 | 0.55 | 490 | 1 | 2 | 4 | 5 | 35 | 55 | 79 | 10000 | 4 | 3 | 0 |  |  | 0.53 | 1 | 671 |  | Table 8.1. Average Operating Heat Rate for Selected Energy Sources, 2003-2013. US Energy Information Administration
NG_CT | 40.2 | 2.8 | 82 | 3.4 | 128.4 | 0.35 | 530 | 0.5 | 0.5 | 0.5 | 8 | 32 | 126 | 103 | 10000 | 4 | 3 | 0 |  |  | 1 | 1 | 968 |  | Annual Energy Review 2010. Appendix F: Alternatives for Estimating Energy Consumption. Table F1. Conversion Efficiencies of noncombustible Renewable Energy Sources. US Energy Information Administration.
NG_CG | 40.2 | 2.8 | 82 | 3.4 | 128.4 | 0.35 | 530 | 0.5 | 0.5 | 0.5 | 8 | 32 | 126 | 103 | 10000 | 4 | 3 | 0 |  |  | 1 | 1 | 968
diesel | 8 | 2 | 288 |  |  | 0.31849 | 733 | [6 empty] | 10000000 | 10000 |  |  | 0 |  |  | 0.86 | 1
fuel oil | 8 | 2 | 172.8 |  |  | 0.31849 | 733 | [6 empty] | 10000000 | 10000 |  |  | 0 |  |  | 0.86 | 1
nuclear | 71.4 | 11.8 | 11.8 | 1.1 | 96.1 | 0.32654 | 12 | 1 |  | 13 | 5 |  |  | 500 | 10000 | 10 | 3 | 0 |  |  | 0.2 | 1 | 5366 | "Biomass Energy Economics" Pacific Energy Systems, Inc.
hydro | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651 | Climate Change 2014: Mitigation of Climate Change. Contribution of Working Group III to the Fifth Assessment Report of the Intergovernmental Panel on Climate Change. Annex III: Technology-specific cost and performance parameters. Table A.III.2 Emissions of selected electricity supply technologies
hydro_hourly | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
hydro_daily | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
hydro_monthly | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
geothermal | 34.2 | 12.2 | 0 | 1.4 | 47.9 | 0.16 | 38 | [7 empty] | 10000 | [5 empty] | 0.32 | 1 | 2448 | "Technical Assessment of the Operation of Coal and Gas Fired Plants" Report to the DECC
biomass | 47.4 | 14.5 | 39.5 | 1.2 | 102.6 | 0.23 | 230 | [7 empty] | 10000 | [5 empty] | 0.53 | 1 | 3659 | "the westinghouse pressurized water reactor nuclear power plant" Table 16-1 Estimated Startup Time in Hours Required by NSSS
biogas | 47.4 | 14.5 | 39.5 | 1.2 | 102.6 | 0.23 | 230 | [7 empty] | 10000 | [5 empty] | 0.53 | 1 | 3659 | http://www.powerauthority.on.ca/current-electricity-contracts/sc-cc
variable renewable energy sources | levelized capital cost | fixed o&m cost | variable o&m cost (inc. fuel) | transmission investment | total system LCOE | efficiency | [17 empty] | "Cost and Performance Data for Power Generation Technologies" Prepared for the National Renewable Energy Laboratory
| 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | given by power curves | [17 empty] | "Power Plant Cycling Costs" Prepared for the National Renewable Energy Laboratory
wind | 64.1 | 13 | 0 | 3.2 | 80.3 | [5 empty] | TRUE | [10 empty] | 20% | 19.8
wind - offshore | 175.4 | 22.8 | 0 | 5.8 | 204.1 | [17 empty] | 6154 | *(likely conservative) estimate based on the fact that simple cycle is less efficient
solar PV | 114.5 | 11.4 | 0 | 4.1 | 130 | [16 empty] | 60% | 3279 | Trends in GHG Emissions in the Alberta Electricity Market
solar thermal | 195 | 42.1 | 0 | 6 | 243.1 | [17 empty] | 4052
diesel costs: Lazard LCOE version 8.0
balancing technologies | [23 empty] | assumed fuel oil costs are ~60% of diesel costs based on http://asian-power.com/regulation/commentary/reducing-diesel-power-plant-hfo-bill
"Comparison of Lifecycle Greenhouse Gas Emissions of Various Electricity Generation Sources" WNA
storage | capital cost power | capital cost capacity | annual operating costs | efficiency | applicable grid system size (MW) |  | storage capacity (kWh) |  | charge rate | discharge rate
| (avg) $/kW | (avg) $/kWh | $/kWyr | (max) | min | max | min | max | kW | kW | [13 empty] | "Electricity Storage and Renewables for Island Power" IRENA 2012
PHS | 2500 | 175 | 5 | 0.85 | 200 | 5000 |  |  | 2002500 | 2002500 | [10 empty] | 1 | 50% | 1000 | Kousksou et al. "Energy storage: Applications and challenges" Solar Energy Materials & Solar Cells 2014
CAES | 900 | 100 | 5 | 0.6 | 3 | 400 |  |  | 175000 | 300000 | [10 empty] | 1 | 50% | 650 | "Energy Technology Perspectives" IEA 2014
FES | 3000 | 2250 | 15 | 0.95 | 0.1 | 200 | 1 | 25 | 200 | 200 | [13 empty] | Nils's Paper (Submitted to Energy Economics)
batteries | [20 empty] | 1 | 50% | 1500 | EIA AEO2015 Table 8.2" Cost and Performance characteristics of new central station electricity generating technologies
Pb-acid | 550 | 325 | 30 | 0.9 | 0 | 10 | 0.5 | 10 | 0.8 | 1.25 | [13 empty] | My storage paper with Nils (YSSP report)
Ni-Cd | 1000 | 1150 |  | 0.65 | 0 | 40
Na-S | 1500 | 187.5 | 15 | 0.9 | 0.05 | 8 |  |  | 50 | 50
Li-ion | 700 | 1000 | 25 | 0.95 | 0 | 10 | 0.5 | 10 | 1.1 | 5.25
vanadium | 2500 | 575 |  | 0.85 | 0.05 | 10 | 20 | 50
hydrogen | 1000 | 15 |  | 0.5 | 0.1 | 10 |  |  | 2.505
flow battery | 1600 | 575 | 30 | 0.85 | 0.025 | 10 | 20 | 50 | 12.5 | 15
capacitors | 400 | 1000 |  | 0.65 | 0 | 0.05
supercapacitors | 300 | 2000 |  | 0.95 | 0 | 0.3
SMES | 300 | 10000 |  | 0.95 | 0.1 | 10
thermal | 250 | 26.5 |  | 0.6 | 0 | 300
sector integration - transportation
EV |  |  |  | 0.9 | [16 empty] | 1 | 50%
demand response - shifting
[5 empty] | shreddability (%) | controllability (%) | acceptability (%) | S*P | [15 empty] | "Grid Integration of Aggregated Demand Response, Part 1: Load Availability Profiles and Constraints for the Western Interconnection." NREL
assume x% flexibility - user input |  |  | commercial
assume different flexibilities during different hours |  |  | - cooling |  | 41-49 | 15-25 | 3-77 | 0.45*0.20=0.09 | summer = 9% | cooling peaks from 12-8pm
|  |  | - heating |  | 46-51 | 10-25 | 0-77 | g | winter = 8.6 % | heating peaks from 7-9 am
DR capacity = load * participation rate * sheddability |  |  | residential
participation = min (controllability, acceptability) |  |  | - cooling |  | 20-70 | 2-52 | 13-39 | 0.45*0.26=0.117 | summer = 8.35%
|  |  | - heating |  | 20-30 | 2-48 | 0-1.5 | 0.25*0.01=0.0025 | winter = 2.5%
lighting and ventilation are not easily shiftable! |  |  | - water heating |  | 25 | 13-26 | 13-39 | 0.25*0.20=0.05 |  | peaks 7am, 6pm
** would need demand data by sector |  |  | industrial |  | sheddability (%) | participation (%) | S*P | average |  | ind/mun fairly flat over day
divide year into heating/cooling, keep others year round |  |  | - agricultural water pumping |  | 100 | 10 | 10% | 6%
for multiple end uses, take average of shed * participation? |  |  | - data centres |  | 3 | 100 | 3%
for zeros, use a small non-zero number… |  |  | - regrigerated warehouses |  | 5 | 100 | 5%
for ranges, take midpoint? |  |  | municipal
|  |  | - fresh water pumping |  | 5 | 25 | 1.25%
|  |  | - waste water pumping |  | 5 | 25 | 1.25%
transmission
$ / kWh
- using existing lines | 0.009 | [22 empty] | AEO 2015 table 8
assumptions: aluminum conductor steel reinforced (ACSR), Tubular (230 kV)/Lattice (345 kV - 600 kV), >10 miles
- building new lines | $ / km | source gives in $/mile. 1 mile = 1.60934 km
-- 115 kV single circuit | 596331.4154 | [22 empty] | "Capital Costs for Transmission and Substations" prepared for the Western Electricity Coordinating Council
-- 115 kV double circuit | 954677.0726
-- 230 kV single circuit | 596331.4154
-- 230 kV double circuit | 954677.0726
-- 500 kV single circuit | 1192693.8994
-- 500 kV double circuit | 1908701.7038
-- 500 kV HVDC Bi-pole | 954677.0726
-- 600 kV HVDC Bi-pole | 1002398.4988
backup generation | depends on sources data
curtailment | output - last resort
sector integration - transportation
-- electric vehicles | base msrp | est. tax credit (US) | body type | seats | EPA range (miles conv to km) | batt size [kWh] | charge rate [kW] | [16 empty] | http://www.plugincars.com/cars
bmw i3 | 43300 | 7500 | sedan | 4 | 130.3565 | 22 | 6.6
chevrolet spark | 26000 | 7500 | coupe | 4 | 131.9659 | 19 | 3.3
fiat 500 e | 32600 | 7500 | sedan | 4 | 140.0126 | 24 | 6.6
ford focus electric | 30000 | 7500 | sedan | 5 | 122.3098 | 23 | 6.6
kia soul ev | 34500 | 7500 | sedan | 5 | 149.6686 | 27 | 6.6
mercedes B-class electric | 42400 | 7500 | sedan | 5 | 136.7939 | 28 | 10
mitsubishi i-MiEV | 23800 | 7500 | sedan | 4 | 99.7791 | 16 | 3.3
nissan LEAF | 29800 | 7500 | sedan | 5 | 135.1846 | 24 | 6.6
smart electric drive | 25700 | 7500 | coupe | 2 | 109.4351 | 17 | 3.3
tesla model s | 71000 | 7500 | sedan | 5 | 426.4751 | 85 | 10
volkswagen E-golf | 36300 | 7500 | sedan | 5 | 133.5752 | 24 | 7.2
tesla model X | 80000 | 7500 | SUV | 7 | 370.1482 | 85 | 10
-- comparison with gas vehicles | base msrp | no tax credits | body type | seats | fuel consumption (city/hwy/combined) [L/100km] | ghg emissions
smart | 14930 |  | coupe | 2 | 6.9/5.7/6.3 | 130g/km | [17 empty] | http://www.thesmart.ca/ca/en/index.html
fiat 500 | 16745 |  | sedan | 4 | 8.7/6.9 | [18 empty] | http://www.fiatcanada.com/en/2015/500/
ford focus | 17170 |  | sedan | 5 | 9.3/6.7/8.1 | [18 empty] | http://www.ford.ca/cars/focus/specifications/
ford explorer | 30700 |  | suv | 7 | 13.7/9.7 | [18 empty] | http://www.thesmart.ca/ca/en/index.html
[7 empty] | vehicle class | required battery size [kWh] | [15 empty] | "Impacts Assessment of PHEV on Electric Utilities and Regional US Power Grids Part 1: Technical Analysis" PNNL
--plug-in hybrid | assume average vehicle travels about 50 km/day - battery could easily displace fuel for such distance | [5 empty] | compact sedan | 8.6
[7 empty] | mid-size sedan | 9.9
[7 empty] | mid-size SUV | 12.5
[7 empty] | full-size SUV | 15.2
| costs |  | HEV cost premium avg $4000 | [20 empty] | Sovacool, B. and Hirsh, R. "Beyond batteries: an examination of the benefits and barriers to PHEVs and a V2G transition"
annual revenue for V2G ancillary services (grid regulation) $4000/vehicle
** cost savings dependent on electricity pricing - current avg 110 c/L for gas, 8.0 c/kWh off peak (CAD)
| ghg emission reductions |  | assuming 50% penetration, reduces GHG emissions by 27%
| petroleum displacement |  | up to 6.5 million boe/day
| benefits to grid |  | cars can serve as distributed generators
storage support - particularly for wind when generation at night corresponds with typical charge time
| base msrp | est. tax credit | body type | seats | epa range (elec only) | battery size | charge rate | [16 empty] | http://www.plugincars.com/cars
cadillac ELR | 76000 | 7500 | coupe | 4 | 59.5456 | 17 | 3.3
chevy volt | 35200 | 7500 | sedan | 4 | 61.1549 | 17 | 3.3
ford c-max energi | 32600 | 3700 | wagon | 5 | 32.1868 | 8 | 3.3
ford fusion energi | 35600 | 3700 | sedan | 5 | 32.1868 | 7 | 3.3
honda accord PH | 40700 | 3700 | sedan | 2 | 20.9214 | 7 | 6.6
porsche cayenne s e-hybrid | 78000 | 5300 | SUV | 5 | 22.5308 | 11 | 3.6
porsche panamera s e-hybrid | 100000 | 4700 | SUV | 4 | 24.1401 | 9 | 3
toyota prius PH | 30800 | 2500 | sedan | 5 | 17.7027 | 4 | 3.3
-- hybrid buses | cost premium avg 200 000 (~500 000 compared to 300 000) - mostly offset by govt | [22 empty] | "Hybrid Buses Costs and Benefits" EESI
30% ghg reduction
37% improvement in fuel economy
88% improvement in fuel efficiency
O&M (inc. fuel) costs 15% lower
| orion VII can carry average 51 passengers at peak times - vehicle displacement? | [22 empty] | https://www.ttc.ca/Routes/General_Information/General_Information.jsp

## modeled attributes
Non-vre technology assumptions
| Cost - related Technology Characteristics |  | Operating Characteristics |  | Ramping Characteristics
col. | start up cost | shut down cost | min up time | min down time | ramp rate max | ramp rate min | start up ramp limit | shut down ramp limit
| [$ / MWcap] | [$ / MWcap] | [hours] | [hours] | [MW/hr p MWcap] | [MW/hr p MWcap] | [MW/hr p MWcap] | [MW/hr p MWcap]
coal | 54 |  | 24 | 12 | 0.1 | -0.1
Natural gas
NG_CC | 66 |  | 8 | 4 | 0.25 | -0.25
NG_CT | 26 |  | 1 | 1 | 1 | -1
NG_CG | 26 |  | 1 | 1 | 1 | -1
diesel |  |  | 1 | 1 | 0.25 | -0.25
fuel oil |  |  | 1 | 1 | 0.25 | -0.25
nuclear | 55 |  | 168 | 24 | 0.01 | -0.01
hydro |  |  |  |  | 1 | -1
hydro_hourly |  |  |  |  | 1 | -1
hydro_daily |  |  |  |  | 1 | -1
hydro_monthly |  |  |  |  | 1 | -1
geothermal
biomass | 54 |  | 8 | 6 | 0.05 | -0.05
biogas | 54 |  | 8 | 6 | 0.05 | -0.05
wind
solar
PHS | 0 | 0 | 1 | 1 | 1 | -1
CAES
battery
EV
importexport
Imports
Col number | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Notes: | cost curve equation | combination of variable cost (P^1) and spinning cost (P^0)
| start up cost | cost to commit the unit ($)
shut down cost
| min up time | minimum time for which a unit must be on (status =1) after it is committed [hours]
| min down time | minimum time for which a unit must be off (status = 0) after it is de-commited [hours]
| ramp rate max | positive change in real power over 1 hour (MW/hr) for a spinning unit (with status = 1)
| ramp rate min | negative change in real power over 1 hou (MW/hr) for a spinning unit (with status =1)
| start up ramp limit | maximum positive change in real power over the first hour after startup (MW/hr)
| shut down ramp limit | maximum negative change in real power over the last hor before shutdown (MW/hr)
MW At Marginal Cost

## scenario analysis
Scenario analysis inputs
|  | Installed Capacity Metric | Flexibility Factor Metric | Investment Cost |  | Transmission network capacity metric |  |  |  |  | VRE Resrouce Metric
col. | Installed capacity by type | Max capacity value | Operating reserve coeff. | Total overnight cost in 2014 | Cost | bus number | total installed capacity on bus | fraction of load on bus | total transmission capacity to/from bus | transmission line cost | bus number | Proposed wind capacity | Proposed multi c-Si solar capacity | Proposed mono c-Si solar capacity | Proposed thin film solar capacity
| [MW] | [fraction of installed capacity] | [fraction on installed capacity] | [$/kW installed] | [$] |  | [MW] | [percentage] | [MW] |  |  | [MW] | [MW] | [MW] | [MW]
coal | 5066 | 1 | 0.53 | 2917 | 14777522000
Natural gas | 0 | 1 | 0 | 0 | 0
NG_CC | 0 | 1 | 0.53 | 671 | 0
NG_CT | 0 | 1 | 1 | 968 | 0
NG_CG | 0 | 1 | 1 | 968 | 0
diesel | 0 | 1 | 0.86 | 0 | 0
fuel oil | 0 | 1 | 0.86 | 0 | 0
nuclear | 0 | 1 | 0.2 | 5366 | 0
hydro | 0 | 1 | 0.66 | 2651 | 0
hydro_hourly | 101.7 | 1 | 0.66 | 2651 | 269606700
hydro_daily | 284 | 1 | 0.66 | 2651 | 752884000
hydro_monthly | 0 | 1 | 0.66 | 2651 | 0
geothermal | 0 | 1 | 0.32 | 2448 | 0
biomass | 0 | 1
biogas | 0 | 1
Imports | 0 | #N/A
wind | 0 | 0.2 | 0 | 19.8
solar PV | 0 | 0.6 | 0 | 3279
PHS | 0 | 0.5 | 1 | 1000
batteries | 0 | 0.5 | 1 | 1500
EV | 0 | 0.5 | 1 | 0
Col number |  | 1 | 2
Notes:

## vre plants
plant ID | name | kind | latitude | longitude | [MW] | bus-old | bus | technology type | unit capacity [kW] | latitude_MERRA | longitude_MERRA
Solar | Solar_1 | Solar_PV | 50.5833 | -111.8808 | 19 | Brooks 121S | NEWELL2075S89S | FS395 | 2 | 281 | 102
Wind | Wind_1 | wind_onshore | 49.5519 | -111.077 | 685 | Whitla 251S | NEWELL2075S89S | V_112-3.0 | 3075 | 279 | 103
Wind | Wind_13 | wind_onshore | 51.8723 | -113.3181 | 295 | Ghost Pine 114S | BENALTO17S | V_112-3.12 | 3075 | 284 | 100
Wind | Wind_17 | wind_onshore | 49.3859 | -112.9488 | 110 | Magrath 225S | NEWELL2075S89S | V_112-3.16 | 3075 | 279 | 101
Wind | Wind_26 | wind_onshore | 49.1897 | -113.6806 | 782 | Pincher Creek 396S | BENNETT520S | V_112-3.25 | 3075 | 278 | 99

## non-vre plants
plant ID | name | kind | cost curve equation | pmin | [MW] | bus | initial status | hours in status | storage content | initial power | initial status | hours in status | storage content | cascade group name | number | min storage | max storage | min water discharge | max water discharge | h factor | efficiency
Biomass_1 | Biomass_1 | biomass | 100P | 2 | 16.9 | HEARTLAKE898S
Biomass_2 | Biomass_2 | biomass | 100P | 2 | 15 | LITTLESMOKY813S
Biomass_3 | Biomass_3 | biomass | 100P | 2 | 23 | SAGITAWAH77S
Biomass_4 | Biomass_4 | biomass | 100P | 5 | 50 | BICKERDIKE39S
Biomass_5 | Biomass_5 | biomass | 100P | 0 | 4 | MITSUE732S
Biomass_6 | Biomass_6 | biomass | 100P | 0 | 1 | WHITEFISHLAKE825S
Biomass_7 | Biomass_7 | biomass | 100P | 1 | 12 | BENALTO17S
Biomass_8 | Biomass_8 | biomass | 100P | 1 | 9 | MITSUE732S
Biomass_9 | Biomass_9 | biomass | 100P | 7 | 68 | SAGITAWAH77S
Biomass_12 | Biomass_12 | biomass | 100P | 3 | 32 | LITTLESMOKY813S
Biomass_14 | Biomass_14 | biomass | 100P | 3 | 25.1 | WESLEYCREEK834S
Biomass_15 | Biomass_15 | biomass | 100P | 4 | 36 | NEWELL2075S89S
Biomass_16 | Biomass_16 | biomass | 100P | 13 | 131 | HEARTLAKE898S
Coal_1 | Coal_1 | coal | 104P | 0 | 555 | BENALTO17S
Coal_3 | Coal_3 | coal | 104P | 0 | 1371 | KEEPHILLS320P
Coal_6 | Coal_6 | coal | 104P | 0 | 151 | LITTLESMOKY813S
Coal_7 | Coal_7 | coal | 104P | 0 | 1366 | KEEPHILLS320P
Coal_10 | Coal_10 | coal | 104P | 0 | 816 | NEWELL2075S89S
Coal_12 | Coal_12 | coal | 104P | 0 | 807 | SUNDANCE310P
hydro_daily_1 | hydro_daily_1 | hydro_daily | 3.3P | 0 | 156 | SARCEE42S
hydro_daily_2 | hydro_daily_2 | hydro_daily | 3.3P | 0 | 32 | BENNETT520S
hydro_daily_3 | hydro_daily_3 | hydro_daily | 3.3P | 0 | 96 | SARCEE42S
hydro_hourly_1 | hydro_hourly_1 | hydro_hourly | 3.3P | 0 | 11.2 | SARCEE42S
hydro_hourly_2 | hydro_hourly_2 | hydro_hourly | 3.3P | 0 | 14.7 | BENNETT520S
hydro_hourly_3 | hydro_hourly_3 | hydro_hourly | 3.3P | 0 | 16.8 | BENALTO17S
hydro_hourly_4 | hydro_hourly_4 | hydro_hourly | 3.3P | 0 | 16 | RUTHLAKE848S
hydro_hourly_5 | hydro_hourly_5 | hydro_hourly | 3.3P | 0 | 5 | SARCEE42S
hydro_hourly_6 | hydro_hourly_6 | hydro_hourly | 3.3P | 0 | 7 | BENNETT520S
hydro_hourly_7 | hydro_hourly_7 | hydro_hourly | 3.3P | 0 | 31 | SARCEE42S
hydro_hourly_8 | hydro_hourly_8 | hydro_hourly | 3.3P | 0 | 34 | BENNETT520S
hydro_hourly_9 | hydro_hourly_9 | hydro_hourly | 3.3P | 0 | 3 | SARCEE42S
hydro_hourly_10 | hydro_hourly_10 | hydro_hourly | 3.3P | 0 | 2.7 | BENNETT520S
NG_CT_1 | NG_CT_1 | NG_CT | 136.5P | 18 | 90 | LITTLESMOKY813S
NG_CT_3 | NG_CT_3 | NG_CT | 136.5P | 5 | 27 | BENNETT520S
NG_CT_5 | NG_CT_5 | NG_CT | 136.5P | 4 | 20 | WESLEYCREEK834S
NG_CT_6 | NG_CT_6 | NG_CT | 136.5P | 13 | 63 | SAGITAWAH77S
NG_CT_7 | NG_CT_7 | NG_CT | 136.5P | 2 | 10 | LAMOUREUX71S
NG_CT_8 | NG_CT_8 | NG_CT | 136.5P | 9 | 45 | WESLEYCREEK834S
NG_CT_9 | NG_CT_9 | NG_CT | 136.5P | 14 | 68 | NEWELL2075S89S
NG_CT_11 | NG_CT_11 | NG_CT | 136.5P | 21 | 105 | LITTLESMOKY813S
NG_CT_13 | NG_CT_13 | NG_CT | 136.5P | 7 | 35 | NEWELL2075S89S
NG_CT_18 | NG_CT_18 | NG_CT | 136.5P | 1 | 6 | MITSUE732S
NG_CT_19 | NG_CT_19 | NG_CT | 136.5P | 2 | 9 | LITTLESMOKY813S
NG_CT_20 | NG_CT_20 | NG_CT | 136.5P | 3 | 15 | LOUISECREEK809S
NG_CT_21 | NG_CT_21 | NG_CT | 136.5P | 1 | 5 | BENALTO17S
NG_CT_22 | NG_CT_22 | NG_CT | 136.5P | 29 | 144 | SARCEE42S
NG_CT_25 | NG_CT_25 | NG_CT | 136.5P | 2 | 11 | LITTLESMOKY813S
NG_CT_27 | NG_CT_27 | NG_CT | 136.5P | 50 | 250 | CLOVERBAR987S
NG_CT_30 | NG_CT_30 | NG_CT | 136.5P | 3 | 15 | SAGITAWAH77S
NG_CT_31 | NG_CT_31 | NG_CT | 136.5P | 1 | 6 | BENALTO17S
NG_CG_1 | NG_CG_1 | NG_CG | 136.5P | 184 | 920 | BENALTO17S
NG_CG_4 | NG_CG_4 | NG_CG | 136.5P | 4 | 18 | BICKERDIKE39S
NG_CG_5 | NG_CG_5 | NG_CG | 136.5P | 89 | 445 | SALTCREEK977S
NG_CG_10 | NG_CG_10 | NG_CG | 136.5P | 281 | 1405 | RUTHLAKE848S
NG_CG_11 | NG_CG_11 | NG_CG | 136.5P | 108 | 542 | WHITEFISHLAKE825S
NG_CG_14 | NG_CG_14 | NG_CG | 136.5P | 37 | 183 | DOVER888S
NG_CG_17 | NG_CG_17 | NG_CG | 136.5P | 20 | 100 | LITTLESMOKY813S
NG_CG_23 | NG_CG_23 | NG_CG | 136.5P | 41 | 207 | DOVER888S
NG_CG_26 | NG_CG_26 | NG_CG | 136.5P | 36 | 179 | LEISMER72S
NG_CG_32 | NG_CG_32 | NG_CG | 136.5P | 37 | 183 | KINOSIS856S
NG_CG_38 | NG_CG_38 | NG_CG | 136.5P | 9 | 47 | WESLEYCREEK834S
NG_CG_39 | NG_CG_39 | NG_CG | 136.5P | 9 | 46 | LAMOUREUX71S
NG_CG_40 | NG_CG_40 | NG_CG | 136.5P | 2 | 10 | LITTLESMOKY813S
NG_CG_41 | NG_CG_41 | NG_CG | 136.5P | 39 | 195 | JOSEPHBURG410S
NG_CG_44 | NG_CG_44 | NG_CG | 136.5P | 8 | 42 | JASPER805S
NG_CG_46 | NG_CG_46 | NG_CG | 136.5P | 3 | 15 | SARCEE42S
NG_CG_47 | NG_CG_47 | NG_CG | 136.5P | 2 | 10 | ELLERSLIE89S
NG_CG_48 | NG_CG_48 | NG_CG | 136.5P | 16 | 80 | BENNETT520S
NG_CG_50 | NG_CG_50 | NG_CG | 136.5P | 21 | 105 | LEISMER72S
NG_CC_1 | NG_CC_1 | NG_CC | 75.5P | 198 | 990 | LANGDON102S | 1 |  |  | 990
NG_CC_2 | NG_CC_2 | NG_CC | 75.5P | 84 | 420 | BENALTO17S | 1 |  |  | 420
NG_CC_5 | NG_CC_5 | NG_CC | 75.5P | 62 | 310 | RUTHLAKE848S | 1 |  |  | 310
NG_CC_6 | NG_CC_6 | NG_CC | 75.5P | 16 | 80 | WESLEYCREEK834S | 1 |  |  | 80
NG_CC_8 | NG_CC_8 | NG_CC | 75.5P | 51 | 255 | NEWELL2075S89S | 1 |  |  | 255

## storage
plant ID | name | kind | pmin | [MW] | storagecapacitymax | pumprampmax | resevoir level | bus | cost curve equation | initial power | initial status | hours in status | storage content

## EV_aggregator
plant ID | name | kind | [MW] | storagecapacitymax | pumprampmax | unpluggedhours | tripenergy | bus | initial power | initial status | hours in status | storage content | cost curve equation | pmin

## demand response
index | 1 | 2
| initial status | hours in status
initial values | 0 | 0
constraint:
| over-production | under-production
maximum hourly dr limit (% of schedule) | 130% | 70%
| maximum | minimum
absolute hourly dr limit (MW) | 0 | 0
maximum
maximum daily dr (MW) | 0
| increasing_shed | decreasing_shed
ramping limiatations (MW) | 1000 | -1000
| uptime | downtime
minimum up/down times (hours) | 1 | 1

## demand centres
city | frac pop | bus | dr_potential | region
Load_1 | 0.11 | AMELIA108S | 0.1921% | Division No. 13
Load_2 | 0.11 | BANNERMAN681S | 0.1921% | Division No. 13
Load_3 | 0.2 | BENALTO17S | 0.1026% | Division No. 9
Load_4 | 0.2 | BENNETT520S | 9.213% | Division No. 6
Load_5 | 0.2 | BICKERDIKE39S | 0.144% | Division No. 14
Load_6 | 0.2 | BIRCHWOODCREEK960S | 0.3638% | Division No. 16
Load_7 | 0.09 | BIRCHWOODCREEK960S | 0.1363% | Division No. 17
Load_8 | 0.08 | BLACKFLY934S | 0.1455% | Division No. 16
Load_9 | 0.09 | BLACKFLY934S | 0.1363% | Division No. 17
Load_10 | 0.09 | BRINTNELL876S | 0.1363% | Division No. 17
Load_11 | 0.08 | CASTLEDOWNS | 2.687% | Division No. 11
Load_12 | 0.2 | CHERHILL338S | 0.144% | Division No. 14
Load_13 | 0.08 | CLOVERBAR987S | 2.687% | Division No. 11
Load_14 | 0.33 | CROSSINGS511S | 0.452% | Division No. 5
Load_15 | 0.2 | CROSSINGS511S | 9.213% | Division No. 6
Load_16 | 0.08 | DAWES2011S | 0.1455% | Division No. 16
Load_17 | 0.09 | DAWES2011S | 0.1363% | Division No. 17
Load_18 | 0.08 | DEERLAND13S | 2.687% | Division No. 11
Load_19 | 0.08 | DOME | 2.687% | Division No. 11
Load_20 | 0.08 | DOVER888S | 0.1455% | Division No. 16
Load_21 | 0.09 | DOVER888S | 0.1363% | Division No. 17
Load_22 | 0.2 | EASTCALGARY5S | 9.213% | Division No. 6
Load_23 | 0.08 | EASTEDMONTON38S | 2.687% | Division No. 11
Load_24 | 1 | ELLERSLIE89S | 1.022% | Division No. 7
Load_25 | 0.5 | ELLERSLIE89S | 2.574% | Division No. 8
Load_26 | 0.5 | ELLERSLIE89S | 1.198% | Division No. 10
Load_27 | 0.2 | GENESEE330 | 0.1026% | Division No. 9
Load_28 | 0.5 | GENESEE330 | 0.4745% | Division No. 15
Load_29 | 0.25 | HEARTLAKE898S | 0.4126% | Division No. 12
Load_30 | 0.08 | HEARTLAKE898S | 0.1455% | Division No. 16
Load_31 | 0.25 | HEARTLAND12S | 0.4126% | Division No. 12
Load_32 | 0.11 | HEARTLAND12S | 0.1921% | Division No. 13
Load_33 | 0.08 | HEATHFIELD2029S | 2.687% | Division No. 11
Load_34 | 0.11 | HEATHFIELD2029S | 0.1921% | Division No. 13
Load_35 | 0.08 | JASPER805S | 2.687% | Division No. 11
Load_36 | 0.5 | JOSEPHBURG410S | 1.198% | Division No. 10
Load_37 | 0.08 | JOSEPHBURG410S | 2.687% | Division No. 11
Load_38 | 0.2 | KEEPHILLS320P | 0.144% | Division No. 14
Load_39 | 0.08 | KETTLERIVER2049S | 0.1455% | Division No. 16
Load_40 | 0.08 | KINOSIS856S | 0.1455% | Division No. 16
Load_41 | 0.08 | LAMOUREUX71S | 2.687% | Division No. 11
Load_42 | 1 | LANGDON102S | 0.9578% | Division No. 3
Load_43 | 0.2 | LANGDON102S | 9.213% | Division No. 6
Load_44 | 0.5 | LANGDON102S | 2.574% | Division No. 8
Load_45 | 0.2 | LANGDON102S | 0.1026% | Division No. 9
Load_46 | 0.5 | LANGDON102S | 0.4745% | Division No. 15
Load_47 | 0.08 | LEISMER72S | 0.1455% | Division No. 16
Load_48 | 0.25 | LITTLESMOKY813S | 0.08905% | Division No. 18
Load_49 | 1 | LITTLESMOKY813S | 2.96% | Division No. 19
Load_50 | 0.09 | LIVOCK939S | 0.1363% | Division No. 17
Load_51 | 0.11 | LOUISECREEK809S | 0.1921% | Division No. 13
Load_52 | 0.25 | LOUISECREEK809S | 0.08905% | Division No. 18
Load_53 | 0.08 | MCMILLAN885S | 0.1455% | Division No. 16
Load_54 | 0.09 | MCMILLAN885S | 0.1363% | Division No. 17
Load_55 | 0.11 | MITSUE732S | 0.1921% | Division No. 13
Load_56 | 1 | NEWELL2075S89S | 2.032% | Division No. 1
Load_57 | 1 | NEWELL2075S89S | 4.173% | Division No. 2
Load_58 | 1 | NEWELL2075S89S | 0.2354% | Division No. 4
Load_59 | 0.33 | NEWELL2075S89S | 0.452% | Division No. 5
Load_60 | 0.09 | NORTHBARRHEAD69S | 0.1363% | Division No. 17
Load_61 | 0.25 | NORTHBARRHEAD69S | 0.08905% | Division No. 18
Load_62 | 0.08 | NORTHCALDER37S | 2.687% | Division No. 11
Load_63 | 0.11 | NORTHCALDER37S | 0.1921% | Division No. 13
Load_64 | 0.2 | PETROLIA | 0.1026% | Division No. 9
Load_65 | 0.08 | PETROLIA | 2.687% | Division No. 11
Load_66 | 0.08 | POUNDMAKER | 2.687% | Division No. 11
Load_67 | 0.25 | ROUNDHILL852S | 0.4126% | Division No. 12
Load_68 | 0.08 | ROUNDHILL852S | 0.1455% | Division No. 16
Load_69 | 0.08 | RUTHLAKE848S | 0.1455% | Division No. 16
Load_70 | 0.25 | SAGITAWAH77S | 0.08905% | Division No. 18
Load_71 | 0.08 | SALTCREEK977S | 0.1455% | Division No. 16
Load_72 | 0.33 | SARCEE42S | 0.452% | Division No. 5
Load_73 | 0.2 | SARCEE42S | 9.213% | Division No. 6
Load_74 | 0.1 | SUNDANCE310P | 0.1921% | Division No. 13
Load_75 | 0.2 | SUNDANCE310P | 0.144% | Division No. 14
Load_76 | 0.2 | SUNNYBROOK510S | 0.1026% | Division No. 9
Load_77 | 0.09 | THICKWOODHILLS951S | 0.1363% | Division No. 17
Load_78 | 0.11 | WABAMUN19S | 0.1921% | Division No. 13
Load_79 | 0.2 | WABAMUN19S | 0.144% | Division No. 14
Load_80 | 0.09 | WABASCA720S | 0.1363% | Division No. 17
Load_81 | 0.09 | WESLEYCREEK834S | 0.1363% | Division No. 17
Load_82 | 0.25 | WHITEFISHLAKE825S | 0.4126% | Division No. 12

## existing transmission
name | from bus | to bus | voltage | circuits | length | pmax | reactance | line cost
L_1 | BRINTNELL876S | WESLEYCREEK834S | 240 |  | 152.2908 |  | 0.060916
L_2 | BRINTNELL876S | WABASCA720S | 240 |  | 22.5855 |  | 0.0090342
L_3 | MITSUE732S | WABASCA720S | 240 |  | 70.983 |  | 0.028393
L_4 | LOUISECREEK809S | LITTLESMOKY813S | 240 |  | 79.3719 |  | 0.031749
L_5 | LOUISECREEK809S | LITTLESMOKY813S | 240 |  | 79.3719 |  | 0.031749
L_6 | WESLEYCREEK834S | LITTLESMOKY813S | 240 |  | 103.248 |  | 0.041299
L_7 | MITSUE732S | LOUISECREEK809S | 240 |  | 67.1112 |  | 0.026844
L_8 | MITSUE732S | NORTHBARRHEAD69S | 240 |  | 131.6412 |  | 0.052656
L_9 | CHERHILL338S | NORTHBARRHEAD69S | 240 |  | 83.889 |  | 0.033556
L_10 | CHERHILL338S | WABAMUN19S | 240 |  | 49.6881 |  | 0.019875
L_11 | SUNDANCE310P | WABAMUN19S | 240 |  | 9.6795 |  | 0.0038718
L_12 | SUNDANCE310P | WABAMUN19S | 240 |  | 9.6795 |  | 0.0038718
L_13 | SUNDANCE310P | BICKERDIKE39S | 240 |  | 167.778 |  | 0.067111
L_14 | SUNDANCE310P | BICKERDIKE39S | 240 |  | 167.778 |  | 0.067111
L_15 | SUNDANCE310P | SAGITAWAH77S | 240 |  | 154.872 |  | 0.061949
L_16 | SUNDANCE310P | SAGITAWAH77S | 240 |  | 154.872 |  | 0.061949
L_17 | LOUISECREEK809S | SAGITAWAH77S | 240 |  | 32.9103 |  | 0.013164
L_18 | LOUISECREEK809S | SAGITAWAH77S | 240 |  | 32.9103 |  | 0.013164
L_19 | SALTCREEK977S | BLACKFLY934S | 240 |  | 58.077 |  | 0.023231
L_20 | SALTCREEK977S | KINOSIS856S | 240 |  | 32.9103 |  | 0.013164
L_21 | KETTLERIVER2049S | KINOSIS856S | 240 |  | 33.5556 |  | 0.013422
L_22 | KETTLERIVER2049S | LEISMER72S | 240 |  | 25.812 |  | 0.010325
L_23 | HEARTLAKE898S | LEISMER72S | 240 |  | 54.8505 |  | 0.02194
L_24 | HEARTLAKE898S | WHITEFISHLAKE825S | 240 |  | 54.2052 |  | 0.021682
L_24 | HEARTLAKE898S | WHITEFISHLAKE825S | 240 |  | 54.2052 |  | 0.021682
L_26 | DEERLAND13S | WHITEFISHLAKE825S | 240 |  | 100.0215 |  | 0.040009
L_27 | DEERLAND13S | WHITEFISHLAKE825S | 240 |  | 100.0215 |  | 0.040009
L_28 | DEERLAND13S | HEARTLAND12S | 240 |  | 19.359 |  | 0.0077436
L_29 | DEERLAND13S | AMELIA108S | 240 |  | 12.906 |  | 0.0051624
L_30 | HEARTLAND12S | BANNERMAN681S | 240 |  | 5.1624 |  | 0.002065
L_31 | AMELIA108S | JOSEPHBURG410S | 240 |  | 3.8718 |  | 0.0015487
L_32 | LAMOUREUX71S | JOSEPHBURG410S | 240 |  | 3.2265 |  | 0.0012906
L_33 | LAMOUREUX71S | BANNERMAN681S | 240 |  | 4.5171 |  | 0.0018068
L_34 | LAMOUREUX71S | CASTLEDOWNS | 240 |  | 100.0215 |  | 0.040009
L_35 | LAMOUREUX71S | CLOVERBAR987S | 240 |  | 80.6625 |  | 0.032265
L_36 | HEARTLAKE898S | ROUNDHILL852S | 240 |  | 42.5898 |  | 0.017036
L_37 | MCMILLAN885S | ROUNDHILL852S | 240 |  | 41.2992 |  | 0.01652
L_38 | MCMILLAN885S | DAWES2011S | 240 |  | 54.2052 |  | 0.021682
L_39 | DAWES2011S | THICKWOODHILLS951S | 240 |  | 40.6539 |  | 0.016262
L_40 | RUTHLAKE848S | THICKWOODHILLS951S | 240 |  | 23.2308 |  | 0.0092923
L_41 | DOVER888S | THICKWOODHILLS951S | 240 |  | 23.2308 |  | 0.0092923
L_42 | DOVER888S | THICKWOODHILLS951S | 240 |  | 23.2308 |  | 0.0092923
L_43 | DOVER888S | RUTHLAKE848S | 240 |  | 29.6838 |  | 0.011874
L_44 | DOVER888S | BIRCHWOODCREEK960S | 240 |  | 29.0385 |  | 0.011615
L_45 | LIVOCK939S | BIRCHWOODCREEK960S | 240 |  | 51.624 |  | 0.02065
L_46 | LIVOCK939S | BRINTNELL876S | 240 |  | 32.265 |  | 0.012906
L_47 | RUTHLAKE848S | SALTCREEK977S | 240 |  | 41.9445 |  | 0.016778
L_48 | THICKWOODHILLS951S | LIVOCK939S | 500 |  | 70.983 |  | 0.021295
L_49 | SUNNYBROOK510S | LIVOCK939S | 500 |  | 467.8425 |  | 0.14035
L_50 | HEARTLAND12S | HEATHFIELD2029S | 500 |  | 9.6795 |  | 0.0029038
L_51 | HEARTLAND12S | HEATHFIELD2029S | 500 |  | 9.6795 |  | 0.0029038
L_52 | NEWELL2075S89S | HEATHFIELD2029S | 500 |  | 354.915 |  | 0.10647
L_53 | ELLERSLIE89S | HEARTLAND12S | 500 |  | 109.701 |  | 0.03291
L_54 | ELLERSLIE89S | HEARTLAND12S | 500 |  | 109.701 |  | 0.03291
L_55 | NORTHCALDER37S | WABAMUN19S | 240 |  | 122.607 |  | 0.049043
L_56 | NORTHCALDER37S | CASTLEDOWNS | 240 |  | 20.6496 |  | 0.0082598
L_57 | CLOVERBAR987S | EASTEDMONTON38S | 240 |  | 12.906 |  | 0.0051624
L_58 | CLOVERBAR987S | EASTEDMONTON38S | 240 |  | 12.906 |  | 0.0051624
L_59 | ELLERSLIE89S | EASTEDMONTON38S | 240 |  | 38.718 |  | 0.015487
L_60 | PETROLIA | ELLERSLIE89S | 240 |  | 16.1325 |  | 0.006453
L_61 | DOME | ELLERSLIE89S | 240 |  | 9.6795 |  | 0.0038718
L_62 | DOME | SUNDANCE310P | 240 |  | 132.2865 |  | 0.052915
L_63 | PETROLIA | JASPER805S | 240 |  | 32.265 |  | 0.012906
L_64 | POUNDMAKER | JASPER805S | 240 |  | 9.6795 |  | 0.0038718
L_65 | POUNDMAKER | NORTHCALDER37S | 240 |  | 35.4915 |  | 0.014197
L_66 | JASPER805S | SUNDANCE310P | 240 |  | 148.419 |  | 0.059368
L_67 | KEEPHILLS320P | BENALTO17S | 240 |  | 125.8335 |  | 0.050333
L_68 | KEEPHILLS320P | BENALTO17S | 240 |  | 125.8335 |  | 0.050333
L_69 | SUNDANCE310P | BENALTO17S | 240 |  | 135.513 |  | 0.054205
L_70 | SUNDANCE310P | BENALTO17S | 240 |  | 135.513 |  | 0.054205
L_71 | ELLERSLIE89S | GENESEE330 | 500 |  | 125.8335 |  | 0.03775
L_72 | SUNNYBROOK510S | GENESEE330 | 500 |  | 4.5171 |  | 0.0013551
L_73 | SUNNYBROOK510S | GENESEE330 | 500 |  | 4.5171 |  | 0.0013551
L_74 | SUNNYBROOK510S | KEEPHILLS320P | 500 |  | 38.718 |  | 0.011615
L_75 | ELLERSLIE89S | KEEPHILLS320P | 500 |  | 132.2865 |  | 0.039686
L_76 | SUNNYBROOK510S | CROSSINGS511S | 500 |  | 277.479 |  | 0.083244
L_77 | BENALTO17S | SARCEE42S | 240 |  | 206.496 |  | 0.082598
L_78 | BENALTO17S | SARCEE42S | 240 |  | 206.496 |  | 0.082598
L_79 | EASTCALGARY5S | LANGDON102S | 240 |  | 46.4616 |  | 0.018585
L_80 | EASTCALGARY5S | LANGDON102S | 240 |  | 46.4616 |  | 0.018585
L_81 | EASTCALGARY5S | SARCEE42S | 240 |  | 35.4915 |  | 0.014197
L_82 | CROSSINGS511S | LANGDON102S | 500 |  | 3.8718 |  | 0.0011615
L_83 | BENNETT520S | LANGDON102S | 500 |  | 4.5171 |  | 0.0013551

## excel input instructions
*create dropdown list with these options
| Generating Plant IDs |  | Storage Plant IDs
| wind |  | PHS
| wind offshore |  | CAES
| solar PV multi c-Si |  | FES
| solar PV mono c-Si |  | Pb-acid
| solar PV thin film |  | Ni-Cd
| solar thermal |  | Na-S
| coal |  | Li-ion
| NG combined |  | vanadium
| NG simple |  | hydrogen
| diesel |  | flow battery
| fuel oil |  | capacitor
| nuclear |  | supercapacitor
| hydro |  | SMES
| geothermal |  | thermal
biomass
| Trina TSM-PDG5-255 | multi c-Si | TO DO: need to change 'vre plants' sheet so that the area [m^2] and # modules gets updated according to these values, given the module type
| nominal pwr at STC [Wp] | 255
| area | 1.688
| Canadian Solar CS6V-225MM | mono c-Si
| nominal pwr at STC [Wp] | 225
| area | 1.353
| First Solar FS395 | CdTe
| nominal pwr at STC [Wp] | 95
| area [m^2] | 0.72
Each unique node must be listed at least once in the 'existing transmission' sheet under the 'from bus' category
On the demand centres sheet, the dr_potential column needs to add to one. Also the dr_potential value for each city needs to be pro-rated by the percentage of load that that city consumes. The fomula in powersystems.py (Load constraints) for the second OPF is scheduled_load(time) - power(time) >= dr_3 (UC dr) *dr_potential for each city. As such if the dr_3*dr_potenail is greater than the scheduled_load value for that city in that hour, then the OPF would have to have a negative power value, which is obviously impossible, and so it fails.

## lists
USER: do not alter this sheet
VRE generation types | Wind | Solar
| wind_onshore | multi_c_Si
| wind_offshore | thin_film
mono_c_Si
Technologies | wind_onshore | wind_offshore | multi_c_Si | thin_film | mono_c_Si
| V_112-3.0 | V_112-3.0 | TSM-PDG5-255 | FS395 | CS6V-225MM
|  |  | CHSM_6610P_250 | FS935
|  |  | CS6X_320P | FS4122_2