## site independent
technology assumptions | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | [9 empty] | references colour coded
[8 empty] | estimated start up times (notice to full load) |  |  |  | cycling costs |  |  | research these value and add it here
non-vre sources | levelized capital cost | fixed o&m cost | variable o&m cost (inc. fuel) | transmission investment | total system LCOE | efficiency | GHG emissions | hot start | warm start | cold start | spin ramp rate | hot start | warm start | cold start | spinning cost | minimum up time | minimum down time | shut down cost | negative change in power for spinning unit | shut down ramp limit | Operating reserve coeff. | Max capacity value | Total overnight cost in 2014
| 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh |  | kg CO2e/MWh | hours |  |  | %/min | $/MW cap. |  |  | [$ per hour committed] | [hours] | [hours] |  |  |  | [Fraction of installed capacity] | [Fraction of installed capacity] | $/kW
coal | 60 | 4.2 | 30.3 | 1.2 | 95.6 | 0.32623 | 820 | 3 | 6.5 | 10 | 2 | 59 | 65 | 105 | 10000 | 3 | 3 | 0 |  |  | 0.53 | 1 | 2917 | "Levelized cost and levelized avoided cost of new generation resources in the Annual Energy Outlook 2014" US Energy Information Administration
Natural gas | [14 empty] | 10000 | 4 | 3 | 0 |  |  |  | 1 |  | "FAQ: What is the efficiency of different types of power plants?" US Energy Information Administration
NG_CC | 14.3 | 1.7 | 49.1 | 1.2 | 66.3 | 0.55 | 490 | 1 | 2 | 4 | 5 | 35 | 55 | 79 | 10000 | 4 | 3 | 0 |  |  | 0.53 | 1 | 671 |  | Table 8.1. Average Operating Heat Rate for Selected Energy Sources, 2003-2013. US Energy Information Administration
NG_CT | 40.2 | 2.8 | 82 | 3.4 | 128.4 | 0.35 | 530 | 0.5 | 0.5 | 0.5 | 8 | 32 | 126 | 103 | 10000 | 4 | 3 | 0 |  |  | 1 | 1 | 968 |  | Annual Energy Review 2010. Appendix F: Alternatives for Estimating Energy Consumption. Table F1. Conversion Efficiencies of noncombustible Renewable Energy Sources. US Energy Information Administration.
NG_CG | 40.2 | 2.8 | 82 | 3.4 | 128.4 | 0.35 | 530 | 0.5 | 0.5 | 0.5 | 8 | 32 | 126 | 103 | 10000 | 4 | 3 | 0 |  |  | 1 | 1 | 968
diesel | 8 | 2 | 288 |  |  | 0.31849 | 733 | [6 empty] | 10000000 | 10000 |  |  | 0 |  |  | 0.86 | 1
fuel oil | 8 | 2 | 172.8 |  |  | 0.31849 | 733 | [6 empty] | 10000000 | 10000 |  |  | 0 |  |  | 0.86 | 1
nuclear | 71.4 | 11.8 | 11.8 | 1.1 | 96.1 | 0.32654 | 12 | 1 |  | 13 | 5 |  |  | 500 | 10000 | 10 | 3 | 0 |  |  | 0.2 | 1 | 5366 | "Biomass Energy Economics" Pacific Energy Systems, Inc.
hydro | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651 | Climate Change 2014: Mitigation of Climate Change. Contribution of Working Group III to the Fifth Assessment Report of the Intergovernmental Panel on Climate Change. Annex III: Technology-specific cost and performance parameters. Table A.III.2 Emissions of selected electricity supply technologies
hydro_hourly | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
hydro_daily | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
hydro_monthly | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
geothermal | 34.2 | 12.2 | 0 | 1.4 | 47.9 | 0.16 | 38 | [7 empty] | 10000 | [5 empty] | 0.32 | 1 | 2448 | "Technical Assessment of the Operation of Coal and Gas Fired Plants" Report to the DECC
biomass | 47.4 | 14.5 | 39.5 | 1.2 | 102.6 | 0.23 | 230 | [7 empty] | 10000 | [5 empty] | 0.53 | 1 | 3659 | "the westinghouse pressurized water reactor nuclear power plant" Table 16-1 Estimated Startup Time in Hours Required by NSSS
biogas | 47.4 | 14.5 | 39.5 | 1.2 | 102.6 | 0.23 | 230 | [7 empty] | 10000 | [5 empty] | 0.53 | 1 | 3659 | http://www.powerauthority.on.ca/current-electricity-contracts/sc-cc
variable renewable energy sources | levelized capital cost | fixed o&m cost | variable o&m cost (inc. fuel) | transmission investment | total system LCOE | efficiency | [17 empty] | "Cost and Performance Data for Power Generation Technologies" Prepared for the National Renewable Energy Laboratory
| 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | given by power curves | [17 empty] | "Power Plant Cycling Costs" Prepared for the National Renewable Energy Laboratory
wind | 64.1 | 13 | 0 | 3.2 | 80.3 | [5 empty] | TRUE | [10 empty] | 20% | 19.8
wind - offshore | 175.4 | 22.8 | 0 | 5.8 | 204.1 | [17 empty] | 6154 | *(likely conservative) estimate based on the fact that simple cycle is less efficient
solar PV | 114.5 | 11.4 | 0 | 4.1 | 130 | [16 empty] | 60% | 3279 | Trends in GHG Emissions in the Alberta Electricity Market
solar thermal | 195 | 42.1 | 0 | 6 | 243.1 | [17 empty] | 4052
diesel costs: Lazard LCOE version 8.0
balancing technologies | [23 empty] | assumed fuel oil costs are ~60% of diesel costs based on http://asian-power.com/regulation/commentary/reducing-diesel-power-plant-hfo-bill
"Comparison of Lifecycle Greenhouse Gas Emissions of Various Electricity Generation Sources" WNA
storage | capital cost power | capital cost capacity | annual operating costs | efficiency | applicable grid system size (MW) |  | storage capacity (kWh) |  | charge rate | discharge rate
| (avg) $/kW | (avg) $/kWh | $/kWyr | (max) | min | max | min | max | kW | kW | [13 empty] | "Electricity Storage and Renewables for Island Power" IRENA 2012
PHS | 2500 | 175 | 5 | 0.85 | 200 | 5000 |  |  | 2002500 | 2002500 | [10 empty] | 1 | 50% | 1000 | Kousksou et al. "Energy storage: Applications and challenges" Solar Energy Materials & Solar Cells 2014
CAES | 900 | 100 | 5 | 0.6 | 3 | 400 |  |  | 175000 | 300000 | [10 empty] | 1 | 50% | 650 | "Energy Technology Perspectives" IEA 2014
FES | 3000 | 2250 | 15 | 0.95 | 0.1 | 200 | 1 | 25 | 200 | 200 | [13 empty] | Nils's Paper (Submitted to Energy Economics)
batteries | [20 empty] | 1 | 50% | 1500 | EIA AEO2015 Table 8.2" Cost and Performance characteristics of new central station electricity generating technologies
Pb-acid | 550 | 325 | 30 | 0.9 | 0 | 10 | 0.5 | 10 | 0.8 | 1.25 | [13 empty] | My storage paper with Nils (YSSP report)
Ni-Cd | 1000 | 1150 |  | 0.65 | 0 | 40
Na-S | 1500 | 187.5 | 15 | 0.9 | 0.05 | 8 |  |  | 50 | 50
Li-ion | 700 | 1000 | 25 | 0.95 | 0 | 10 | 0.5 | 10 | 1.1 | 5.25
vanadium | 2500 | 575 |  | 0.85 | 0.05 | 10 | 20 | 50
hydrogen | 1000 | 15 |  | 0.5 | 0.1 | 10 |  |  | 2.505
flow battery | 1600 | 575 | 30 | 0.85 | 0.025 | 10 | 20 | 50 | 12.5 | 15
capacitors | 400 | 1000 |  | 0.65 | 0 | 0.05
supercapacitors | 300 | 2000 |  | 0.95 | 0 | 0.3
SMES | 300 | 10000 |  | 0.95 | 0.1 | 10
thermal | 250 | 26.5 |  | 0.6 | 0 | 300
sector integration - transportation
EV |  |  |  | 0.9 | [16 empty] | 1 | 50%
demand response - shifting
[5 empty] | shreddability (%) | controllability (%) | acceptability (%) | S*P | [15 empty] | "Grid Integration of Aggregated Demand Response, Part 1: Load Availability Profiles and Constraints for the Western Interconnection." NREL
assume x% flexibility - user input |  |  | commercial
assume different flexibilities during different hours |  |  | - cooling |  | 41-49 | 15-25 | 3-77 | 0.45*0.20=0.09 | summer = 9% | cooling peaks from 12-8pm
|  |  | - heating |  | 46-51 | 10-25 | 0-77 | g | winter = 8.6 % | heating peaks from 7-9 am
DR capacity = load * participation rate * sheddability |  |  | residential
participation = min (controllability, acceptability) |  |  | - cooling |  | 20-70 | 2-52 | 13-39 | 0.45*0.26=0.117 | summer = 8.35%
|  |  | - heating |  | 20-30 | 2-48 | 0-1.5 | 0.25*0.01=0.0025 | winter = 2.5%
lighting and ventilation are not easily shiftable! |  |  | - water heating |  | 25 | 13-26 | 13-39 | 0.25*0.20=0.05 |  | peaks 7am, 6pm
** would need demand data by sector |  |  | industrial |  | sheddability (%) | participation (%) | S*P | average |  | ind/mun fairly flat over day
divide year into heating/cooling, keep others year round |  |  | - agricultural water pumping |  | 100 | 10 | 10% | 6%
for multiple end uses, take average of shed * participation? |  |  | - data centres |  | 3 | 100 | 3%
for zeros, use a small non-zero number… |  |  | - regrigerated warehouses |  | 5 | 100 | 5%
for ranges, take midpoint? |  |  | municipal
|  |  | - fresh water pumping |  | 5 | 25 | 1.25%
|  |  | - waste water pumping |  | 5 | 25 | 1.25%
transmission
$ / kWh
- using existing lines | 0.009 | [22 empty] | AEO 2015 table 8
assumptions: aluminum conductor steel reinforced (ACSR), Tubular (230 kV)/Lattice (345 kV - 600 kV), >10 miles
- building new lines | $ / km | source gives in $/mile. 1 mile = 1.60934 km
-- 115 kV single circuit | 596331.4154 | [22 empty] | "Capital Costs for Transmission and Substations" prepared for the Western Electricity Coordinating Council
-- 115 kV double circuit | 954677.0726
-- 230 kV single circuit | 596331.4154
-- 230 kV double circuit | 954677.0726
-- 500 kV single circuit | 1192693.8994
-- 500 kV double circuit | 1908701.7038
-- 500 kV HVDC Bi-pole | 954677.0726
-- 600 kV HVDC Bi-pole | 1002398.4988
backup generation | depends on sources data
curtailment | output - last resort
sector integration - transportation
-- electric vehicles | base msrp | est. tax credit (US) | body type | seats | EPA range (miles conv to km) | batt size [kWh] | charge rate [kW] | [16 empty] | http://www.plugincars.com/cars
bmw i3 | 43300 | 7500 | sedan | 4 | 130.3565 | 22 | 6.6
chevrolet spark | 26000 | 7500 | coupe | 4 | 131.9659 | 19 | 3.3
fiat 500 e | 32600 | 7500 | sedan | 4 | 140.0126 | 24 | 6.6
ford focus electric | 30000 | 7500 | sedan | 5 | 122.3098 | 23 | 6.6
kia soul ev | 34500 | 7500 | sedan | 5 | 149.6686 | 27 | 6.6
mercedes B-class electric | 42400 | 7500 | sedan | 5 | 136.7939 | 28 | 10
mitsubishi i-MiEV | 23800 | 7500 | sedan | 4 | 99.7791 | 16 | 3.3
nissan LEAF | 29800 | 7500 | sedan | 5 | 135.1846 | 24 | 6.6
smart electric drive | 25700 | 7500 | coupe | 2 | 109.4351 | 17 | 3.3
tesla model s | 71000 | 7500 | sedan | 5 | 426.4751 | 85 | 10
volkswagen E-golf | 36300 | 7500 | sedan | 5 | 133.5752 | 24 | 7.2
tesla model X | 80000 | 7500 | SUV | 7 | 370.1482 | 85 | 10
-- comparison with gas vehicles | base msrp | no tax credits | body type | seats | fuel consumption (city/hwy/combined) [L/100km] | ghg emissions
smart | 14930 |  | coupe | 2 | 6.9/5.7/6.3 | 130g/km | [17 empty] | http://www.thesmart.ca/ca/en/index.html
fiat 500 | 16745 |  | sedan | 4 | 8.7/6.9 | [18 empty] | http://www.fiatcanada.com/en/2015/500/
ford focus | 17170 |  | sedan | 5 | 9.3/6.7/8.1 | [18 empty] | http://www.ford.ca/cars/focus/specifications/
ford explorer | 30700 |  | suv | 7 | 13.7/9.7 | [18 empty] | http://www.thesmart.ca/ca/en/index.html
[7 empty] | vehicle class | required battery size [kWh] | [15 empty] | "Impacts Assessment of PHEV on Electric Utilities and Regional US Power Grids Part 1: Technical Analysis" PNNL
--plug-in hybrid | assume average vehicle travels about 50 km/day - battery could easily displace fuel for such distance | [5 empty] | compact sedan | 8.6
[7 empty] | mid-size sedan | 9.9
[7 empty] | mid-size SUV | 12.5
[7 empty] | full-size SUV | 15.2
| costs |  | HEV cost premium avg $4000 | [20 empty] | Sovacool, B. and Hirsh, R. "Beyond batteries: an examination of the benefits and barriers to PHEVs and a V2G transition"
annual revenue for V2G ancillary services (grid regulation) $4000/vehicle
** cost savings dependent on electricity pricing - current avg 110 c/L for gas, 8.0 c/kWh off peak (CAD)
| ghg emission reductions |  | assuming 50% penetration, reduces GHG emissions by 27%
| petroleum displacement |  | up to 6.5 million boe/day
| benefits to grid |  | cars can serve as distributed generators
storage support - particularly for wind when generation at night corresponds with typical charge time
| base msrp | est. tax credit | body type | seats | epa range (elec only) | battery size | charge rate | [16 empty] | http://www.plugincars.com/cars
cadillac ELR | 76000 | 7500 | coupe | 4 | 59.5456 | 17 | 3.3
chevy volt | 35200 | 7500 | sedan | 4 | 61.1549 | 17 | 3.3
ford c-max energi | 32600 | 3700 | wagon | 5 | 32.1868 | 8 | 3.3
ford fusion energi | 35600 | 3700 | sedan | 5 | 32.1868 | 7 | 3.3
honda accord PH | 40700 | 3700 | sedan | 2 | 20.9214 | 7 | 6.6
porsche cayenne s e-hybrid | 78000 | 5300 | SUV | 5 | 22.5308 | 11 | 3.6
porsche panamera s e-hybrid | 100000 | 4700 | SUV | 4 | 24.1401 | 9 | 3
toyota prius PH | 30800 | 2500 | sedan | 5 | 17.7027 | 4 | 3.3
-- hybrid buses | cost premium avg 200 000 (~500 000 compared to 300 000) - mostly offset by govt | [22 empty] | "Hybrid Buses Costs and Benefits" EESI
30% ghg reduction
37% improvement in fuel economy
88% improvement in fuel efficiency
O&M (inc. fuel) costs 15% lower
| orion VII can carry average 51 passengers at peak times - vehicle displacement? | [22 empty] | https://www.ttc.ca/Routes/General_Information/General_Information.jsp
Note on V4: Madeleine: Note: the operating reserve coefficient is a fraction of generation in Nils' paper
Note on B74: Madeleine: Need to get real values here

## modeled attributes
Non-vre technology assumptions
| Cost - related Technology Characteristics |  | Operating Characteristics |  | Ramping Characteristics
col. | start up cost | shut down cost | min up time | min down time | ramp rate max | ramp rate min | start up ramp limit | shut down ramp limit
| [$ / MWcap] | [$ / MWcap] | [hours] | [hours] | [MW/hr p MWcap] | [MW/hr p MWcap] | [MW/hr p MWcap] | [MW/hr p MWcap]
coal | 0 |  | 24 | 12 | 0.1 | -0.1
Natural gas
NG_CC | 0 |  | 8 | 4 | 0.25 | -0.25
NG_CT | 0 |  | 1 | 1 | 1 | -1
NG_CG | 0 |  | 1 | 1 | 1 | -1
diesel |  |  | 1 | 1 | 0.25 | -0.25
fuel oil |  |  | 1 | 1 | 0.25 | -0.25
nuclear | 0 |  | 168 | 24 | 0.01 | -0.01
hydro |  |  |  |  | 1 | -1
hydro_hourly |  |  |  |  | 1 | -1
hydro_daily |  |  |  |  | 1 | -1
hydro_monthly |  |  |  |  | 1 | -1
geothermal
biomass | 0 |  | 8 | 6 | 0.05 | -0.05
biogas | 0 |  | 8 | 6 | 0.05 | -0.05
wind
solar
batteries | 0 | 0 | 1 | 1 | 1 | -1
PHS | 0 | 0 | 1 | 1 | 1 | -1
CAES
battery
EV
importexport
Imports
Col number | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Notes: | cost curve equation | combination of variable cost (P^1) and spinning cost (P^0)
| start up cost | cost to commit the unit ($)
shut down cost
| min up time | minimum time for which a unit must be on (status =1) after it is committed [hours]
| min down time | minimum time for which a unit must be off (status = 0) after it is de-commited [hours]
| ramp rate max | positive change in real power over 1 hour (MW/hr) for a spinning unit (with status = 1)
| ramp rate min | negative change in real power over 1 hou (MW/hr) for a spinning unit (with status =1)
| start up ramp limit | maximum positive change in real power over the first hour after startup (MW/hr)
| shut down ramp limit | maximum negative change in real power over the last hor before shutdown (MW/hr)
MW At Marginal Cost

## scenario analysis
Scenario analysis inputs
|  | Installed Capacity Metric | Flexibility Factor Metric | Investment Cost |  | Transmission network capacity metric |  |  |  |  | VRE Resrouce Metric
col. | Installed capacity by type | Max capacity value | Operating reserve coeff. | Total overnight cost in 2014 | Cost | bus number | total installed capacity on bus | fraction of load on bus | total transmission capacity to/from bus | transmission line cost | bus number | Proposed wind capacity | Proposed multi c-Si solar capacity | Proposed mono c-Si solar capacity | Proposed thin film solar capacity
| [MW] | [fraction of installed capacity] | [fraction on installed capacity] | [$/kW installed] | [$] |  | [MW] | [percentage] | [MW] |  |  | [MW] | [MW] | [MW] | [MW]
coal | 466 | 1 | 0.53 | 2917 | 1359322000 | NW_falls_g | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
Natural gas | 0 | 1 | 0 | 0 | 0 |  | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
NG_CC | 388 | 1 | 0.53 | 671 | 260348000 |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
NG_CT | 0 | 1 | 1 | 968 | 0 |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
NG_CG | 28 | 1 | 1 | 968 | 27104000 |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
diesel | 500 | 1 | 0.86 | 0 | 0 |  | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
fuel oil | 0 | 1 | 0.86 | 0 | 0 |  | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
nuclear | 0 | 1 | 0.2 | 5366 | 0 |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
hydro | 0 | 1 | 0.66 | 2651 | 0 |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
hydro_hourly | 0 | 1 | 0.66 | 2651 | 0 |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
hydro_daily
hydro_monthly
geothermal
biomass
biomass
Imports | 0 | [5 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
wind | 377.09 | 0.2 | 0 | 19.8 | 7466382 |  | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
solar PV | 0 | 0.6 | 0 | 3279 | 0 |  | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
PHS | 0 | 0.5 | 1 | 1000 | 0 |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
batteries | 0 | 0.5 | 1 | 1500 | 0 |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
EV | 0 | #N/A | #N/A | #N/A | #N/A |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
Col number |  | 1 | 2 |  |  |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
Notes: | [6 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
|  | #N/A | #N/A |  |  |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
|  | 24470 | 16022.5421 |  |  |  | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
|  | #N/A | #N/A |  |  |  | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | #REF! | #REF! |  | 0 | 0 | 0 | 0
Note on L4: Madeleine:

## EV_aggregator
plant ID | name | kind | [MW] | storagecapacitymax | pumprampmax | unpluggedhours | tripenergy | bus | initial power | initial status | hours in status | storage content | cost curve equation | pmin

## demand response
index | 1 | 2
| initial status | hours in status
initial values | 0 | 0
constraint:
| over-production | under-production
maximum hourly dr limit (% of schedule) | 130% | 70%
| maximum | minimum
absolute hourly dr limit (MW) | 6000 | 2
maximum
maximum daily dr (MW) | 144000
| increasing_shed | decreasing_shed
ramping limiatations (MW) | 1000 | -1000
| uptime | downtime
minimum up/down times (hours) | 1 | 1

## demand centres
city | frac pop | bus | dr_potential | region
Load_1 | 1 | AB.a | 0% | AB.a
Load_2 | 1 | BC.a | 0% | BC.a
Load_3 | 1 | MB.a | 0% | MB.a
Load_4 | 1 | NB.a | 0% | NB.a
Load_5 | 1 | NL.a | 0% | NL.a
Load_6 | 1 | NL.b | 0% | NL.b
Load_7 | 1 | NS.a | 0% | NS.a
Load_8 | 1 | ON.a | 0% | ON.a
Load_9 | 1 | ON.b | 0% | ON.b
Load_10 | 1 | PE.a | 0% | PE.a
Load_11 | 1 | QC.a | 0% | QC.a
Load_12 | 1 | QC.b | 0% | QC.b
Load_13 | 1 | SK.a | 0% | SK.a

## lists
USER: do not alter this sheet
VRE generation types | Wind | Solar
| wind_onshore | multi_c_Si
| wind_offshore | thin_film
mono_c_Si
Technologies | wind_onshore | wind_offshore | multi_c_Si | thin_film | mono_c_Si
| V_112-3.0 | V_112-3.0 | TSM-PDG5-255 | FS395 | CS6V-225MM
|  |  | CHSM_6610P_250 | FS935
|  |  | CS6X_320P | FS4122_2

## non-vre plants
plant ID | name | kind | cost curve equation | pmin | [MW] | bus | initial power | initial status | hours in status | storage content | cascade group name | number | min storage | max storage | min water discharge | max water discharge | h factor | efficiency
diesel_NS.a | diesel_NS.a | diesel | 0 | 0 | 5.6843e-14 | NS.a
nuclear_ON.a | nuclear_ON.a | nuclear | 12.P | 9765 | 13020 | ON.a
nuclear_NB.a | nuclear_NB.a | nuclear | 12.P | 472 | 630 | NB.a
biomass_BC.a | biomass_BC.a | biomass | 100P | 1051 | 10506.1886 | BC.a
biomass_AB.a | biomass_AB.a | biomass | 100P | 1290 | 12897.1734 | AB.a
biomass_SK.a | biomass_SK.a | biomass | 100P | 2 | 20 | SK.a
biomass_ON.a | biomass_ON.a | biomass | 100P | 619 | 6185.3562 | ON.a
biomass_ON.b | biomass_ON.b | biomass | 100P | 15 | 147.9 | ON.b
biomass_QC.a | biomass_QC.a | biomass | 100P | 3089 | 30886.1257 | QC.a
biomass_QC.b | biomass_QC.b | biomass | 100P | 21 | 212.1 | QC.b
biomass_NB.a | biomass_NB.a | biomass | 100P | 451 | 4513.3907 | NB.a
biomass_NS.a | biomass_NS.a | biomass | 100P | 231 | 2308.8032 | NS.a
biomass_PE.a | biomass_PE.a | biomass | 100P | 24 | 244.2961 | PE.a
hydro_daily_BC1 | hydro_daily_BC1 | hydro_daily | 3.3P | 0 | 24 | BC.a
hydro_daily_BC2 | hydro_daily_BC2 | hydro_daily | 3.3P | 0 | 9 | BC.a
hydro_daily_BC3 | hydro_daily_BC3 | hydro_daily | 3.3P | 0 | 28 | BC.a
hydro_daily_BC4 | hydro_daily_BC4 | hydro_daily | 3.3P | 0 | 206 | BC.a
hydro_daily_BC5 | hydro_daily_BC5 | hydro_daily | 3.3P | 0 | 274 | BC.a
hydro_daily_BC6 | hydro_daily_BC6 | hydro_daily | 3.3P | 0 | 150 | BC.a
hydro_daily_BC7 | hydro_daily_BC7 | hydro_daily | 3.3P | 0 | 180 | BC.a
hydro_daily_BC8 | hydro_daily_BC8 | hydro_daily | 3.3P | 0 | 45 | BC.a
hydro_daily_BC9 | hydro_daily_BC9 | hydro_daily | 3.3P | 0 | 51 | BC.a
hydro_daily_BC10 | hydro_daily_BC10 | hydro_daily | 3.3P | 0 | 12 | BC.a
hydro_daily_BC11 | hydro_daily_BC11 | hydro_daily | 3.3P | 0 | 7 | BC.a
hydro_daily_BC12 | hydro_daily_BC12 | hydro_daily | 3.3P | 0 | 138 | BC.a
hydro_daily_BC13 | hydro_daily_BC13 | hydro_daily | 3.3P | 0 | 170 | BC.a
hydro_daily_BC14 | hydro_daily_BC14 | hydro_daily | 3.3P | 0 | 591 | BC.a
hydro_daily_BC15 | hydro_daily_BC15 | hydro_daily | 3.3P | 0 | 47 | BC.a
hydro_daily_BC16 | hydro_daily_BC16 | hydro_daily | 3.3P | 0 | 25 | BC.a
hydro_daily_BC17 | hydro_daily_BC17 | hydro_daily | 3.3P | 0 | 55 | BC.a
hydro_daily_BC18 | hydro_daily_BC18 | hydro_daily | 3.3P | 0 | 31 | BC.a
hydro_daily_BC19 | hydro_daily_BC19 | hydro_daily | 3.3P | 0 | 46 | BC.a
hydro_daily_BC20 | hydro_daily_BC20 | hydro_daily | 3.3P | 0 | 24 | BC.a
hydro_daily_BC21 | hydro_daily_BC21 | hydro_daily | 3.3P | 0 | 8 | BC.a
hydro_daily_BC22 | hydro_daily_BC22 | hydro_daily | 3.3P | 0 | 114.99 | BC.a
hydro_daily_BC23 | hydro_daily_BC23 | hydro_daily | 3.3P | 0 | 48 | BC.a
hydro_daily_BC24 | hydro_daily_BC24 | hydro_daily | 3.3P | 0 | 805 | BC.a
hydro_daily_BC25 | hydro_daily_BC25 | hydro_daily | 3.3P | 0 | 6 | BC.a
hydro_daily_BC26 | hydro_daily_BC26 | hydro_daily | 3.3P | 0 | 57 | BC.a
hydro_daily_BC27 | hydro_daily_BC27 | hydro_daily | 3.3P | 0 | 91 | BC.a
hydro_daily_BC28 | hydro_daily_BC28 | hydro_daily | 3.3P | 0 | 65 | BC.a
hydro_daily_BC29 | hydro_daily_BC29 | hydro_daily | 3.3P | 0 | 63 | BC.a
hydro_daily_BC30 | hydro_daily_BC30 | hydro_daily | 3.3P | 0 | 65 | BC.a
hydro_daily_BC31 | hydro_daily_BC31 | hydro_daily | 3.3P | 0 | 8 | BC.a
hydro_daily_BC32 | hydro_daily_BC32 | hydro_daily | 3.3P | 0 | 480 | BC.a
hydro_daily_BC33 | hydro_daily_BC33 | hydro_daily | 3.3P | 0 | 335 | BC.a
hydro_daily_BC34 | hydro_daily_BC34 | hydro_daily | 3.3P | 0 | 54 | BC.a
hydro_daily_BC35 | hydro_daily_BC35 | hydro_daily | 3.3P | 0 | 48 | BC.a
hydro_daily_BC36 | hydro_daily_BC36 | hydro_daily | 3.3P | 0 | 14 | BC.a
hydro_hourly_BC1 | hydro_hourly_BC1 | hydro_hourly | 3.3P | 0 | 4 | BC.a
hydro_hourly_BC2 | hydro_hourly_BC2 | hydro_hourly | 3.3P | 0 | 40.6 | BC.a
hydro_hourly_BC3 | hydro_hourly_BC3 | hydro_hourly | 3.3P | 0 | 20 | BC.a
hydro_hourly_BC4 | hydro_hourly_BC4 | hydro_hourly | 3.3P | 0 | 16.2 | BC.a
hydro_hourly_BC5 | hydro_hourly_BC5 | hydro_hourly | 3.3P | 0 | 25 | BC.a
hydro_hourly_BC6 | hydro_hourly_BC6 | hydro_hourly | 3.3P | 0 | 14.7 | BC.a
hydro_hourly_BC7 | hydro_hourly_BC7 | hydro_hourly | 3.3P | 0 | 6 | BC.a
hydro_hourly_BC8 | hydro_hourly_BC8 | hydro_hourly | 3.3P | 0 | 15 | BC.a
hydro_hourly_BC9 | hydro_hourly_BC9 | hydro_hourly | 3.3P | 0 | 20 | BC.a
hydro_hourly_BC10 | hydro_hourly_BC10 | hydro_hourly | 3.3P | 0 | 211.5 | BC.a
hydro_hourly_BC11 | hydro_hourly_BC11 | hydro_hourly | 3.3P | 0 | 6 | BC.a
hydro_hourly_BC12 | hydro_hourly_BC12 | hydro_hourly | 3.3P | 0 | 11 | BC.a
hydro_hourly_BC13 | hydro_hourly_BC13 | hydro_hourly | 3.3P | 0 | 21.34 | BC.a
hydro_hourly_BC14 | hydro_hourly_BC14 | hydro_hourly | 3.3P | 0 | 66.2 | BC.a
hydro_hourly_BC15 | hydro_hourly_BC15 | hydro_hourly | 3.3P | 0 | 45 | BC.a
hydro_hourly_BC16 | hydro_hourly_BC16 | hydro_hourly | 3.3P | 0 | 50 | BC.a
hydro_hourly_BC17 | hydro_hourly_BC17 | hydro_hourly | 3.3P | 0 | 37 | BC.a
hydro_hourly_BC18 | hydro_hourly_BC18 | hydro_hourly | 3.3P | 0 | 3.2 | BC.a
hydro_hourly_BC19 | hydro_hourly_BC19 | hydro_hourly | 3.3P | 0 | 10 | BC.a
hydro_hourly_BC20 | hydro_hourly_BC20 | hydro_hourly | 3.3P | 0 | 66 | BC.a
hydro_hourly_BC21 | hydro_hourly_BC21 | hydro_hourly | 3.3P | 0 | 33 | BC.a
hydro_hourly_BC22 | hydro_hourly_BC22 | hydro_hourly | 3.3P | 0 | 17.5 | BC.a
hydro_hourly_BC23 | hydro_hourly_BC23 | hydro_hourly | 3.3P | 0 | 38 | BC.a
hydro_hourly_BC24 | hydro_hourly_BC24 | hydro_hourly | 3.3P | 0 | 6 | BC.a
hydro_hourly_BC25 | hydro_hourly_BC25 | hydro_hourly | 3.3P | 0 | 16.6 | BC.a
hydro_hourly_BC26 | hydro_hourly_BC26 | hydro_hourly | 3.3P | 0 | 29.2 | BC.a
hydro_hourly_BC27 | hydro_hourly_BC27 | hydro_hourly | 3.3P | 0 | 4.8 | BC.a
hydro_hourly_BC28 | hydro_hourly_BC28 | hydro_hourly | 3.3P | 0 | 21.18 | BC.a
hydro_hourly_BC29 | hydro_hourly_BC29 | hydro_hourly | 3.3P | 0 | 13.75 | BC.a
hydro_hourly_BC30 | hydro_hourly_BC30 | hydro_hourly | 3.3P | 0 | 10 | BC.a
hydro_hourly_BC31 | hydro_hourly_BC31 | hydro_hourly | 3.3P | 0 | 74 | BC.a
hydro_hourly_BC32 | hydro_hourly_BC32 | hydro_hourly | 3.3P | 0 | 17.8 | BC.a
hydro_hourly_BC33 | hydro_hourly_BC33 | hydro_hourly | 3.3P | 0 | 4 | BC.a
hydro_monthly_BC1 | hydro_monthly_BC1 | hydro_monthly | 3.3P | 0 | 3050 | BC.a
hydro_monthly_BC2 | hydro_monthly_BC2 | hydro_monthly | 3.3P | 0 | 2971 | BC.a
hydro_monthly_BC3 | hydro_monthly_BC3 | hydro_monthly | 3.3P | 0 | 700 | BC.a
hydro_monthly_BC4 | hydro_monthly_BC4 | hydro_monthly | 3.3P | 0 | 2500 | BC.a
hydro_monthly_BC5 | hydro_monthly_BC5 | hydro_monthly | 3.3P | 0 | 1132 | BC.a
hydro_daily_MB1 | hydro_daily_MB1 | hydro_daily | 3.3P | 0 | 480 | MB.a
hydro_daily_MB2 | hydro_daily_MB2 | hydro_daily | 3.3P | 0 | 129 | MB.a
hydro_daily_MB3 | hydro_daily_MB3 | hydro_daily | 3.3P | 0 | 693 | MB.a
hydro_daily_MB4 | hydro_daily_MB4 | hydro_daily | 3.3P | 0 | 56 | MB.a
hydro_daily_MB5 | hydro_daily_MB5 | hydro_daily | 3.3P | 0 | 84 | MB.a
hydro_daily_MB6 | hydro_daily_MB6 | hydro_daily | 3.3P | 0 | 33 | MB.a
hydro_daily_MB7 | hydro_daily_MB7 | hydro_daily | 3.3P | 0 | 165 | MB.a
hydro_daily_MB8 | hydro_daily_MB8 | hydro_daily | 3.3P | 0 | 68 | MB.a
hydro_daily_MB9 | hydro_daily_MB9 | hydro_daily | 3.3P | 0 | 210 | MB.a
hydro_hourly_MB1 | hydro_hourly_MB1 | hydro_hourly | 3.3P | 0 | 5 | MB.a
hydro_hourly_MB2 | hydro_hourly_MB2 | hydro_hourly | 3.3P | 0 | 5 | MB.a
hydro_monthly_MB1 | hydro_monthly_MB1 | hydro_monthly | 3.3P | 0 | 114 | MB.a
hydro_monthly_MB2 | hydro_monthly_MB2 | hydro_monthly | 3.3P | 0 | 287 | MB.a
hydro_monthly_MB3 | hydro_monthly_MB3 | hydro_monthly | 3.3P | 0 | 1224 | MB.a
hydro_monthly_MB4 | hydro_monthly_MB4 | hydro_monthly | 3.3P | 0 | 1350 | MB.a
hydro_monthly_MB5 | hydro_monthly_MB5 | hydro_monthly | 3.3P | 0 | 980 | MB.a
hydro_daily_NB1 | hydro_daily_NB1 | hydro_daily | 3.3P | 0 | 113 | NB.a
hydro_daily_NB2 | hydro_daily_NB2 | hydro_daily | 3.3P | 0 | 64 | NB.a
hydro_daily_NB3 | hydro_daily_NB3 | hydro_daily | 3.3P | 0 | 666 | NB.a
hydro_daily_NB4 | hydro_daily_NB4 | hydro_daily | 3.3P | 0 | 20 | NB.a
hydro_daily_NB5 | hydro_daily_NB5 | hydro_daily | 3.3P | 0 | 100 | NB.a
hydro_hourly_NB1 | hydro_hourly_NB1 | hydro_hourly | 3.3P | 0 | 3.8 | NB.a
hydro_hourly_NB2 | hydro_hourly_NB2 | hydro_hourly | 3.3P | 0 | 4 | NB.a
hydro_hourly_NB3 | hydro_hourly_NB3 | hydro_hourly | 3.3P | 0 | 11 | NB.a
hydro_hourly_NB4 | hydro_hourly_NB4 | hydro_hourly | 3.3P | 0 | 3 | NB.a
hydro_hourly_NB5 | hydro_hourly_NB5 | hydro_hourly | 3.3P | 0 | 9 | NB.a
hydro_hourly_NB6 | hydro_hourly_NB6 | hydro_hourly | 3.3P | 0 | 15 | NB.a
hydro_hourly_NB7 | hydro_hourly_NB7 | hydro_hourly | 3.3P | 0 | 35 | NB.a
hydro_daily_NL1 | hydro_daily_NL1 | hydro_daily | 3.3P | 0 | 22 | NL.a
hydro_daily_NL2 | hydro_daily_NL2 | hydro_daily | 3.3P | 0 | 137 | NL.a
hydro_daily_NL3 | hydro_daily_NL3 | hydro_daily | 3.3P | 0 | 125.5 | NL.a
hydro_daily_NL4 | hydro_daily_NL4 | hydro_daily | 3.3P | 0 | 75 | NL.a
hydro_daily_NL5 | hydro_daily_NL5 | hydro_daily | 3.3P | 0 | 75 | NL.a
hydro_daily_NL6 | hydro_daily_NL6 | hydro_daily | 3.3P | 0 | 8 | NL.a
hydro_daily_NL7 | hydro_daily_NL7 | hydro_daily | 3.3P | 0 | 18 | NL.a
hydro_daily_NL8 | hydro_daily_NL8 | hydro_daily | 3.3P | 0 | 9 | NL.a
hydro_hourly_NL1 | hydro_hourly_NL1 | hydro_hourly | 3.3P | 0 | 2 | NL.a
hydro_hourly_NL2 | hydro_hourly_NL2 | hydro_hourly | 3.3P | 0 | 6.26 | NL.a
hydro_hourly_NL3 | hydro_hourly_NL3 | hydro_hourly | 3.3P | 0 | 2.37 | NL.a
hydro_hourly_NL4 | hydro_hourly_NL4 | hydro_hourly | 3.3P | 0 | 8.3 | NL.a
hydro_hourly_NL5 | hydro_hourly_NL5 | hydro_hourly | 3.3P | 0 | 3.38 | NL.a
hydro_hourly_NL6 | hydro_hourly_NL6 | hydro_hourly | 3.3P | 0 | 6.15 | NL.a
hydro_hourly_NL7 | hydro_hourly_NL7 | hydro_hourly | 3.3P | 0 | 11.97 | NL.a
hydro_hourly_NL8 | hydro_hourly_NL8 | hydro_hourly | 3.3P | 0 | 1.14 | NL.a
hydro_hourly_NL9 | hydro_hourly_NL9 | hydro_hourly | 3.3P | 0 | 3.7 | NL.a
hydro_hourly_NL10 | hydro_hourly_NL10 | hydro_hourly | 3.3P | 0 | 5.31 | NL.a
hydro_hourly_NL11 | hydro_hourly_NL11 | hydro_hourly | 3.3P | 0 | 4.3 | NL.a
hydro_hourly_NL12 | hydro_hourly_NL12 | hydro_hourly | 3.3P | 0 | 11.1 | NL.a
hydro_hourly_NL13 | hydro_hourly_NL13 | hydro_hourly | 3.3P | 0 | 3.25 | NL.a
hydro_hourly_NL14 | hydro_hourly_NL14 | hydro_hourly | 3.3P | 0 | 5.96 | NL.a
hydro_hourly_NL15 | hydro_hourly_NL15 | hydro_hourly | 3.3P | 0 | 5.53 | NL.a
hydro_hourly_NL16 | hydro_hourly_NL16 | hydro_hourly | 3.3P | 0 | 3.5 | NL.a
hydro_hourly_NL17 | hydro_hourly_NL17 | hydro_hourly | 3.3P | 0 | 2.55 | NL.a
hydro_hourly_NL18 | hydro_hourly_NL18 | hydro_hourly | 3.3P | 0 | 6.5 | NL.a
hydro_monthly_NL1 | hydro_monthly_NL1 | hydro_monthly | 3.3P | 0 | 613.4 | NL.a
hydro_monthly_NL2 | hydro_monthly_NL2 | hydro_monthly | 3.3P | 0 | -170 | NL.a
hydro_monthly_NL3 | hydro_monthly_NL3 | hydro_monthly | 3.3P | 0 | 5427.95 | NL.b
hydro_monthly_NL4 | hydro_monthly_NL4 | hydro_monthly | 3.3P | 0 | 40 | NL.a
hydro_monthly_NL5 | hydro_monthly_NL5 | hydro_monthly | 3.3P | 0 | 824 | NL.b
hydro_monthly_NL6 | hydro_monthly_NL6 | hydro_monthly | 3.3P | 0 | 84 | NL.a
hydro_daily_NS1 | hydro_daily_NS1 | hydro_daily | 3.3P | 0 | 6.75 | NS.a
hydro_daily_NS2 | hydro_daily_NS2 | hydro_daily | 3.3P | 0 | 3.1 | NS.a
hydro_daily_NS3 | hydro_daily_NS3 | hydro_daily | 3.3P | 0 | 4.1 | NS.a
hydro_daily_NS4 | hydro_daily_NS4 | hydro_daily | 3.3P | 0 | 6.2 | NS.a
hydro_daily_NS5 | hydro_daily_NS5 | hydro_daily | 3.3P | 0 | 3.5 | NS.a
hydro_daily_NS6 | hydro_daily_NS6 | hydro_daily | 3.3P | 0 | 5.5 | NS.a
hydro_daily_NS7 | hydro_daily_NS7 | hydro_daily | 3.3P | 0 | 2.9 | NS.a
hydro_daily_NS8 | hydro_daily_NS8 | hydro_daily | 3.3P | 0 | 7.2 | NS.a
hydro_daily_NS9 | hydro_daily_NS9 | hydro_daily | 3.3P | 0 | 3.4 | NS.a
hydro_daily_NS10 | hydro_daily_NS10 | hydro_daily | 3.3P | 0 | 3.8 | NS.a
hydro_daily_NS11 | hydro_daily_NS11 | hydro_daily | 3.3P | 0 | 11.2 | NS.a
hydro_daily_NS12 | hydro_daily_NS12 | hydro_daily | 3.3P | 0 | 3 | NS.a
hydro_daily_NS13 | hydro_daily_NS13 | hydro_daily | 3.3P | 0 | 7.2 | NS.a
hydro_daily_NS14 | hydro_daily_NS14 | hydro_daily | 3.3P | 0 | 9 | NS.a
hydro_daily_NS15 | hydro_daily_NS15 | hydro_daily | 3.3P | 0 | 4.5 | NS.a
hydro_daily_NS16 | hydro_daily_NS16 | hydro_daily | 3.3P | 0 | 9 | NS.a
hydro_daily_NS17 | hydro_daily_NS17 | hydro_daily | 3.3P | 0 | 5.4 | NS.a
hydro_daily_NS18 | hydro_daily_NS18 | hydro_daily | 3.3P | 0 | 7.4 | NS.a
hydro_daily_NS19 | hydro_daily_NS19 | hydro_daily | 3.3P | 0 | 8.3 | NS.a
hydro_daily_NS20 | hydro_daily_NS20 | hydro_daily | 3.3P | 0 | 4.7 | NS.a
hydro_daily_NS21 | hydro_daily_NS21 | hydro_daily | 3.3P | 0 | 7.4 | NS.a
hydro_daily_NS22 | hydro_daily_NS22 | hydro_daily | 3.3P | 0 | 3.4 | NS.a
hydro_daily_NS23 | hydro_daily_NS23 | hydro_daily | 3.3P | 0 | 19 | NS.a
hydro_daily_NS24 | hydro_daily_NS24 | hydro_daily | 3.3P | 0 | 5 | NS.a
hydro_daily_NS25 | hydro_daily_NS25 | hydro_daily | 3.3P | 0 | 4.6 | NS.a
hydro_daily_NS26 | hydro_daily_NS26 | hydro_daily | 3.3P | 0 | 2.6 | NS.a
hydro_daily_NS27 | hydro_daily_NS27 | hydro_daily | 3.3P | 0 | 3.6 | NS.a
hydro_daily_NS28 | hydro_daily_NS28 | hydro_daily | 3.3P | 0 | 2.4 | NS.a
hydro_daily_NS29 | hydro_daily_NS29 | hydro_daily | 3.3P | 0 | 2 | NS.a
hydro_daily_NS30 | hydro_daily_NS30 | hydro_daily | 3.3P | 0 | 109.5 | NS.a
hydro_daily_NS31 | hydro_daily_NS31 | hydro_daily | 3.3P | 0 | 106 | NS.a
hydro_hourly_NS1 | hydro_hourly_NS1 | hydro_hourly | 3.3P | 0 | 19 | NS.a
hydro_monthly_NS1 | hydro_monthly_NS1 | hydro_monthly | 3.3P | 0 | 153 | NS.a
hydro_daily_ON1 | hydro_daily_ON1 | hydro_daily | 3.3P | 0 | 355 | ON.b
hydro_daily_ON2 | hydro_daily_ON2 | hydro_daily | 3.3P | 0 | 52 | ON.b
hydro_daily_ON3 | hydro_daily_ON3 | hydro_daily | 3.3P | 0 | 82 | ON.b
hydro_daily_ON4 | hydro_daily_ON4 | hydro_daily | 3.3P | 0 | 200 | ON.b
hydro_daily_ON5 | hydro_daily_ON5 | hydro_daily | 3.3P | 0 | 158 | ON.b
hydro_daily_ON6 | hydro_daily_ON6 | hydro_daily | 3.3P | 0 | 144 | ON.a
hydro_daily_ON7 | hydro_daily_ON7 | hydro_daily | 3.3P | 0 | 475 | ON.b
hydro_daily_ON8 | hydro_daily_ON8 | hydro_daily | 3.3P | 0 | 234 | ON.b
hydro_daily_ON9 | hydro_daily_ON9 | hydro_daily | 3.3P | 0 | 245 | ON.b
hydro_daily_ON10 | hydro_daily_ON10 | hydro_daily | 3.3P | 0 | 219 | ON.b
hydro_daily_ON11 | hydro_daily_ON11 | hydro_daily | 3.3P | 0 | 274 | ON.b
hydro_daily_ON12 | hydro_daily_ON12 | hydro_daily | 3.3P | 0 | 173 | ON.b
hydro_daily_ON13 | hydro_daily_ON13 | hydro_daily | 3.3P | 0 | 189 | ON.b
hydro_daily_ON14 | hydro_daily_ON14 | hydro_daily | 3.3P | 0 | 265 | ON.b
hydro_daily_ON15 | hydro_daily_ON15 | hydro_daily | 3.3P | 0 | 151 | ON.b
hydro_daily_ON16 | hydro_daily_ON16 | hydro_daily | 3.3P | 0 | 264 | ON.b
hydro_daily_ON17 | hydro_daily_ON17 | hydro_daily | 3.3P | 0 | 186 | ON.b
hydro_hourly_ON1 | hydro_hourly_ON1 | hydro_hourly | 3.3P | 0 | 65 | ON.b
hydro_hourly_ON2 | hydro_hourly_ON2 | hydro_hourly | 3.3P | 0 | 2 | ON.a
hydro_hourly_ON3 | hydro_hourly_ON3 | hydro_hourly | 3.3P | 0 | 179 | ON.b
hydro_hourly_ON4 | hydro_hourly_ON4 | hydro_hourly | 3.3P | 0 | 5 | ON.a
hydro_hourly_ON5 | hydro_hourly_ON5 | hydro_hourly | 3.3P | 0 | 573 | ON.a
hydro_hourly_ON6 | hydro_hourly_ON6 | hydro_hourly | 3.3P | 0 | 1504 | ON.a
hydro_hourly_ON7 | hydro_hourly_ON7 | hydro_hourly | 3.3P | 0 | 5.5 | ON.b
hydro_hourly_ON8 | hydro_hourly_ON8 | hydro_hourly | 3.3P | 0 | 10 | ON.b
hydro_hourly_ON9 | hydro_hourly_ON9 | hydro_hourly | 3.3P | 0 | 8 | ON.b
hydro_hourly_ON10 | hydro_hourly_ON10 | hydro_hourly | 3.3P | 0 | 27.6 | ON.b
hydro_hourly_ON11 | hydro_hourly_ON11 | hydro_hourly | 3.3P | 0 | 1 | ON.b
hydro_hourly_ON12 | hydro_hourly_ON12 | hydro_hourly | 3.3P | 0 | 5 | ON.b
hydro_hourly_ON13 | hydro_hourly_ON13 | hydro_hourly | 3.3P | 0 | 4.2 | ON.b
hydro_hourly_ON14 | hydro_hourly_ON14 | hydro_hourly | 3.3P | 0 | 108 | ON.b
hydro_hourly_ON15 | hydro_hourly_ON15 | hydro_hourly | 3.3P | 0 | 5.5 | ON.b
hydro_hourly_ON16 | hydro_hourly_ON16 | hydro_hourly | 3.3P | 0 | 91 | ON.b
hydro_hourly_ON17 | hydro_hourly_ON17 | hydro_hourly | 3.3P | 0 | 20 | ON.b
hydro_hourly_ON18 | hydro_hourly_ON18 | hydro_hourly | 3.3P | 0 | 3 | ON.b
hydro_hourly_ON19 | hydro_hourly_ON19 | hydro_hourly | 3.3P | 0 | 4 | ON.b
hydro_hourly_ON20 | hydro_hourly_ON20 | hydro_hourly | 3.3P | 0 | 2 | ON.a
hydro_hourly_ON21 | hydro_hourly_ON21 | hydro_hourly | 3.3P | 0 | 8 | ON.b
hydro_hourly_ON22 | hydro_hourly_ON22 | hydro_hourly | 3.3P | 0 | 23 | ON.a
hydro_hourly_ON23 | hydro_hourly_ON23 | hydro_hourly | 3.3P | 0 | 1.8 | ON.b
hydro_hourly_ON24 | hydro_hourly_ON24 | hydro_hourly | 3.3P | 0 | 17 | ON.b
hydro_hourly_ON25 | hydro_hourly_ON25 | hydro_hourly | 3.3P | 0 | 9.2 | ON.b
hydro_hourly_ON26 | hydro_hourly_ON26 | hydro_hourly | 3.3P | 0 | 2 | ON.b
hydro_hourly_ON27 | hydro_hourly_ON27 | hydro_hourly | 3.3P | 0 | 1 | ON.a
hydro_hourly_ON28 | hydro_hourly_ON28 | hydro_hourly | 3.3P | 0 | 6 | ON.a
hydro_hourly_ON29 | hydro_hourly_ON29 | hydro_hourly | 3.3P | 0 | 3 | ON.a
hydro_hourly_ON30 | hydro_hourly_ON30 | hydro_hourly | 3.3P | 0 | 12 | ON.b
hydro_hourly_ON31 | hydro_hourly_ON31 | hydro_hourly | 3.3P | 0 | 10 | ON.b
hydro_hourly_ON32 | hydro_hourly_ON32 | hydro_hourly | 3.3P | 0 | 1.2 | ON.b
hydro_hourly_ON33 | hydro_hourly_ON33 | hydro_hourly | 3.3P | 0 | 4 | ON.a
hydro_hourly_ON34 | hydro_hourly_ON34 | hydro_hourly | 3.3P | 0 | 1 | ON.b
hydro_hourly_ON35 | hydro_hourly_ON35 | hydro_hourly | 3.3P | 0 | 18 | ON.a
hydro_hourly_ON36 | hydro_hourly_ON36 | hydro_hourly | 3.3P | 0 | 5.4 | ON.b
hydro_hourly_ON37 | hydro_hourly_ON37 | hydro_hourly | 3.3P | 0 | 3 | ON.b
hydro_hourly_ON38 | hydro_hourly_ON38 | hydro_hourly | 3.3P | 0 | 6 | ON.b
hydro_hourly_ON39 | hydro_hourly_ON39 | hydro_hourly | 3.3P | 0 | 9 | ON.b
hydro_hourly_ON40 | hydro_hourly_ON40 | hydro_hourly | 3.3P | 0 | 27 | ON.b
hydro_hourly_ON41 | hydro_hourly_ON41 | hydro_hourly | 3.3P | 0 | 25 | ON.b
hydro_hourly_ON42 | hydro_hourly_ON42 | hydro_hourly | 3.3P | 0 | 2.8 | ON.b
hydro_hourly_ON43 | hydro_hourly_ON43 | hydro_hourly | 3.3P | 0 | 12 | ON.b
hydro_hourly_ON44 | hydro_hourly_ON44 | hydro_hourly | 3.3P | 0 | 2 | ON.a
hydro_hourly_ON45 | hydro_hourly_ON45 | hydro_hourly | 3.3P | 0 | 20 | ON.b
hydro_hourly_ON46 | hydro_hourly_ON46 | hydro_hourly | 3.3P | 0 | 14 | ON.b
hydro_hourly_ON47 | hydro_hourly_ON47 | hydro_hourly | 3.3P | 0 | 88 | ON.b
hydro_hourly_ON48 | hydro_hourly_ON48 | hydro_hourly | 3.3P | 0 | 10 | ON.b
hydro_hourly_ON49 | hydro_hourly_ON49 | hydro_hourly | 3.3P | 0 | 1.1 | ON.b
hydro_hourly_ON50 | hydro_hourly_ON50 | hydro_hourly | 3.3P | 0 | 3 | ON.b
hydro_hourly_ON51 | hydro_hourly_ON51 | hydro_hourly | 3.3P | 0 | 2 | ON.b
hydro_hourly_ON52 | hydro_hourly_ON52 | hydro_hourly | 3.3P | 0 | 5 | ON.a
hydro_hourly_ON53 | hydro_hourly_ON53 | hydro_hourly | 3.3P | 0 | 18 | ON.b
hydro_hourly_ON54 | hydro_hourly_ON54 | hydro_hourly | 3.3P | 0 | 4.5 | ON.b
hydro_hourly_ON55 | hydro_hourly_ON55 | hydro_hourly | 3.3P | 0 | 10 | ON.b
hydro_hourly_ON56 | hydro_hourly_ON56 | hydro_hourly | 3.3P | 0 | 2 | ON.b
hydro_hourly_ON57 | hydro_hourly_ON57 | hydro_hourly | 3.3P | 0 | 5 | ON.b
hydro_hourly_ON58 | hydro_hourly_ON58 | hydro_hourly | 3.3P | 0 | 10 | ON.b
hydro_hourly_ON59 | hydro_hourly_ON59 | hydro_hourly | 3.3P | 0 | 5.5 | ON.b
hydro_hourly_ON60 | hydro_hourly_ON60 | hydro_hourly | 3.3P | 0 | 82 | ON.b
hydro_hourly_ON61 | hydro_hourly_ON61 | hydro_hourly | 3.3P | 0 | 8 | ON.b
hydro_hourly_ON62 | hydro_hourly_ON62 | hydro_hourly | 3.3P | 0 | 10 | ON.a
hydro_hourly_ON63 | hydro_hourly_ON63 | hydro_hourly | 3.3P | 0 | 6 | ON.b
hydro_hourly_ON64 | hydro_hourly_ON64 | hydro_hourly | 3.3P | 0 | 1086 | ON.b
hydro_hourly_ON65 | hydro_hourly_ON65 | hydro_hourly | 3.3P | 0 | 7.2 | ON.b
hydro_hourly_ON66 | hydro_hourly_ON66 | hydro_hourly | 3.3P | 0 | 6 | ON.a
hydro_hourly_ON67 | hydro_hourly_ON67 | hydro_hourly | 3.3P | 0 | 4 | ON.a
hydro_hourly_ON68 | hydro_hourly_ON68 | hydro_hourly | 3.3P | 0 | 2 | ON.a
hydro_hourly_ON69 | hydro_hourly_ON69 | hydro_hourly | 3.3P | 0 | 49 | ON.b
hydro_hourly_ON70 | hydro_hourly_ON70 | hydro_hourly | 3.3P | 0 | 6 | ON.b
hydro_hourly_ON71 | hydro_hourly_ON71 | hydro_hourly | 3.3P | 0 | 5 | ON.b
hydro_hourly_ON72 | hydro_hourly_ON72 | hydro_hourly | 3.3P | 0 | 2 | ON.b
hydro_hourly_ON73 | hydro_hourly_ON73 | hydro_hourly | 3.3P | 0 | 5 | ON.b
hydro_hourly_ON74 | hydro_hourly_ON74 | hydro_hourly | 3.3P | 0 | 10 | ON.b
hydro_hourly_ON75 | hydro_hourly_ON75 | hydro_hourly | 3.3P | 0 | 3.4 | ON.b
hydro_hourly_ON76 | hydro_hourly_ON76 | hydro_hourly | 3.3P | 0 | 1.1 | ON.b
hydro_hourly_ON77 | hydro_hourly_ON77 | hydro_hourly | 3.3P | 0 | 1.6 | ON.b
hydro_hourly_ON78 | hydro_hourly_ON78 | hydro_hourly | 3.3P | 0 | 15 | ON.b
hydro_hourly_ON79 | hydro_hourly_ON79 | hydro_hourly | 3.3P | 0 | 13.5 | ON.b
hydro_hourly_ON80 | hydro_hourly_ON80 | hydro_hourly | 3.3P | 0 | 5.5 | ON.b
hydro_hourly_ON81 | hydro_hourly_ON81 | hydro_hourly | 3.3P | 0 | 73 | ON.b
hydro_hourly_ON82 | hydro_hourly_ON82 | hydro_hourly | 3.3P | 0 | 16 | ON.b
hydro_daily_QC1 | hydro_daily_QC1 | hydro_daily | 3.3P | 0 | 270 | QC.a
hydro_daily_QC2 | hydro_daily_QC2 | hydro_daily | 3.3P | 0 | 845 | QC.b
hydro_daily_QC3 | hydro_daily_QC3 | hydro_daily | 3.3P | 0 | 833 | QC.b
hydro_daily_QC4 | hydro_daily_QC4 | hydro_daily | 3.3P | 0 | 224 | QC.b
hydro_daily_QC5 | hydro_daily_QC5 | hydro_daily | 3.3P | 0 | 222 | QC.b
hydro_daily_QC6 | hydro_daily_QC6 | hydro_daily | 3.3P | 0 | 245 | QC.b
hydro_daily_QC7 | hydro_daily_QC7 | hydro_daily | 3.3P | 0 | 63 | QC.b
hydro_daily_QC8 | hydro_daily_QC8 | hydro_daily | 3.3P | 0 | 448 | QC.b
hydro_daily_QC9 | hydro_daily_QC9 | hydro_daily | 3.3P | 0 | 1436 | QC.b
hydro_daily_QC10 | hydro_daily_QC10 | hydro_daily | 3.3P | 0 | 319 | QC.b
hydro_daily_QC11 | hydro_daily_QC11 | hydro_daily | 3.3P | 0 | 184 | QC.b
hydro_daily_QC12 | hydro_daily_QC12 | hydro_daily | 3.3P | 0 | 1229 | QC.b
hydro_daily_QC13 | hydro_daily_QC13 | hydro_daily | 3.3P | 0 | 1326 | QC.b
hydro_daily_QC14 | hydro_daily_QC14 | hydro_daily | 3.3P | 0 | 235 | QC.b
hydro_daily_QC15 | hydro_daily_QC15 | hydro_daily | 3.3P | 0 | 55 | QC.b
hydro_daily_QC16 | hydro_daily_QC16 | hydro_daily | 3.3P | 0 | 523 | QC.b
hydro_daily_QC17 | hydro_daily_QC17 | hydro_daily | 3.3P | 0 | 1026 | QC.b
hydro_daily_QC18 | hydro_daily_QC18 | hydro_daily | 3.3P | 0 | 226 | QC.a
hydro_daily_QC19 | hydro_daily_QC19 | hydro_daily | 3.3P | 0 | 131 | QC.a
hydro_daily_QC20 | hydro_daily_QC20 | hydro_daily | 3.3P | 0 | 109 | QC.a
hydro_daily_QC21 | hydro_daily_QC21 | hydro_daily | 3.3P | 0 | 176 | QC.a
hydro_daily_QC22 | hydro_daily_QC22 | hydro_daily | 3.3P | 0 | 270 | QC.b
hydro_daily_QC23 | hydro_daily_QC23 | hydro_daily | 3.3P | 0 | 24 | QC.b
hydro_daily_QC24 | hydro_daily_QC24 | hydro_daily | 3.3P | 0 | 150 | QC.b
hydro_daily_QC25 | hydro_daily_QC25 | hydro_daily | 3.3P | 0 | 200 | QC.a
hydro_daily_QC26 | hydro_daily_QC26 | hydro_daily | 3.3P | 0 | 194 | QC.a
hydro_daily_QC27 | hydro_daily_QC27 | hydro_daily | 3.3P | 0 | 947 | QC.b
hydro_daily_QC28 | hydro_daily_QC28 | hydro_daily | 3.3P | 0 | 302 | QC.b
hydro_hourly_QC1 | hydro_hourly_QC1 | hydro_hourly | 3.3P | 0 | 2.1 | QC.a
hydro_hourly_QC2 | hydro_hourly_QC2 | hydro_hourly | 3.3P | 0 | 7 | QC.b
hydro_hourly_QC3 | hydro_hourly_QC3 | hydro_hourly | 3.3P | 0 | 3.4 | QC.a
hydro_hourly_QC4 | hydro_hourly_QC4 | hydro_hourly | 3.3P | 0 | 1 | QC.a
hydro_hourly_QC5 | hydro_hourly_QC5 | hydro_hourly | 3.3P | 0 | 1900 | QC.a
hydro_hourly_QC6 | hydro_hourly_QC6 | hydro_hourly | 3.3P | 0 | 1.6 | QC.a
hydro_hourly_QC7 | hydro_hourly_QC7 | hydro_hourly | 3.3P | 0 | 1 | QC.b
hydro_hourly_QC8 | hydro_hourly_QC8 | hydro_hourly | 3.3P | 0 | 3.3 | QC.a
hydro_hourly_QC9 | hydro_hourly_QC9 | hydro_hourly | 3.3P | 0 | 5 | QC.a
hydro_hourly_QC10 | hydro_hourly_QC10 | hydro_hourly | 3.3P | 0 | 56 | QC.a
hydro_hourly_QC11 | hydro_hourly_QC11 | hydro_hourly | 3.3P | 0 | 20 | QC.a
hydro_hourly_QC12 | hydro_hourly_QC12 | hydro_hourly | 3.3P | 0 | 18 | QC.b
hydro_hourly_QC13 | hydro_hourly_QC13 | hydro_hourly | 3.3P | 0 | 753 | QC.a
hydro_hourly_QC14 | hydro_hourly_QC14 | hydro_hourly | 3.3P | 0 | 152 | QC.a
hydro_hourly_QC15 | hydro_hourly_QC15 | hydro_hourly | 3.3P | 0 | 8 | QC.b
hydro_hourly_QC16 | hydro_hourly_QC16 | hydro_hourly | 3.3P | 0 | 10 | QC.a
hydro_hourly_QC17 | hydro_hourly_QC17 | hydro_hourly | 3.3P | 0 | 1.2 | QC.b
hydro_hourly_QC18 | hydro_hourly_QC18 | hydro_hourly | 3.3P | 0 | 5.9 | QC.b
hydro_hourly_QC19 | hydro_hourly_QC19 | hydro_hourly | 3.3P | 0 | 5.5 | QC.b
hydro_hourly_QC20 | hydro_hourly_QC20 | hydro_hourly | 3.3P | 0 | 13.2 | QC.b
hydro_hourly_QC21 | hydro_hourly_QC21 | hydro_hourly | 3.3P | 0 | 7.7 | QC.a
hydro_hourly_QC22 | hydro_hourly_QC22 | hydro_hourly | 3.3P | 0 | 62 | QC.b
hydro_hourly_QC23 | hydro_hourly_QC23 | hydro_hourly | 3.3P | 0 | 10 | QC.a
hydro_hourly_QC24 | hydro_hourly_QC24 | hydro_hourly | 3.3P | 0 | 1.6 | QC.a
hydro_hourly_QC25 | hydro_hourly_QC25 | hydro_hourly | 3.3P | 0 | 29 | QC.a
hydro_hourly_QC26 | hydro_hourly_QC26 | hydro_hourly | 3.3P | 0 | 13.6 | QC.b
hydro_hourly_QC27 | hydro_hourly_QC27 | hydro_hourly | 3.3P | 0 | 92 | QC.a
hydro_hourly_QC28 | hydro_hourly_QC28 | hydro_hourly | 3.3P | 0 | 23 | QC.a
hydro_hourly_QC29 | hydro_hourly_QC29 | hydro_hourly | 3.3P | 0 | 10.8 | QC.a
hydro_hourly_QC30 | hydro_hourly_QC30 | hydro_hourly | 3.3P | 0 | 25 | QC.b
hydro_hourly_QC31 | hydro_hourly_QC31 | hydro_hourly | 3.3P | 0 | 11.7 | QC.a
hydro_hourly_QC32 | hydro_hourly_QC32 | hydro_hourly | 3.3P | 0 | 4.2 | QC.a
hydro_hourly_QC33 | hydro_hourly_QC33 | hydro_hourly | 3.3P | 0 | 16 | QC.a
hydro_hourly_QC34 | hydro_hourly_QC34 | hydro_hourly | 3.3P | 0 | 40.6 | QC.a
hydro_hourly_QC35 | hydro_hourly_QC35 | hydro_hourly | 3.3P | 0 | 2.2 | QC.a
hydro_hourly_QC36 | hydro_hourly_QC36 | hydro_hourly | 3.3P | 0 | 12 | QC.b
hydro_hourly_QC37 | hydro_hourly_QC37 | hydro_hourly | 3.3P | 0 | 9.9 | QC.b
hydro_hourly_QC38 | hydro_hourly_QC38 | hydro_hourly | 3.3P | 0 | 2.2 | QC.a
hydro_hourly_QC39 | hydro_hourly_QC39 | hydro_hourly | 3.3P | 0 | 4.5 | QC.a
hydro_hourly_QC40 | hydro_hourly_QC40 | hydro_hourly | 3.3P | 0 | 67 | QC.a
hydro_hourly_QC41 | hydro_hourly_QC41 | hydro_hourly | 3.3P | 0 | 1.7 | QC.a
hydro_hourly_QC42 | hydro_hourly_QC42 | hydro_hourly | 3.3P | 0 | 109 | QC.a
hydro_hourly_QC43 | hydro_hourly_QC43 | hydro_hourly | 3.3P | 0 | 2.55 | QC.a
hydro_hourly_QC44 | hydro_hourly_QC44 | hydro_hourly | 3.3P | 0 | 23.2 | QC.a
hydro_hourly_QC45 | hydro_hourly_QC45 | hydro_hourly | 3.3P | 0 | 2.25 | QC.b
hydro_hourly_QC46 | hydro_hourly_QC46 | hydro_hourly | 3.3P | 0 | 5.5 | QC.a
hydro_hourly_QC47 | hydro_hourly_QC47 | hydro_hourly | 3.3P | 0 | 17 | QC.a
hydro_hourly_QC48 | hydro_hourly_QC48 | hydro_hourly | 3.3P | 0 | 4.5 | QC.b
hydro_hourly_QC49 | hydro_hourly_QC49 | hydro_hourly | 3.3P | 0 | 4.5 | QC.b
hydro_hourly_QC50 | hydro_hourly_QC50 | hydro_hourly | 3.3P | 0 | 131 | QC.a
hydro_hourly_QC51 | hydro_hourly_QC51 | hydro_hourly | 3.3P | 0 | 1.1 | QC.b
hydro_hourly_QC52 | hydro_hourly_QC52 | hydro_hourly | 3.3P | 0 | 294 | QC.a
hydro_hourly_QC53 | hydro_hourly_QC53 | hydro_hourly | 3.3P | 0 | 10 | QC.a
hydro_hourly_QC54 | hydro_hourly_QC54 | hydro_hourly | 3.3P | 0 | 1 | QC.b
hydro_hourly_QC55 | hydro_hourly_QC55 | hydro_hourly | 3.3P | 0 | 7.9 | QC.a
hydro_hourly_QC56 | hydro_hourly_QC56 | hydro_hourly | 3.3P | 0 | 113 | QC.a
hydro_hourly_QC57 | hydro_hourly_QC57 | hydro_hourly | 3.3P | 0 | 42 | QC.b
hydro_hourly_QC58 | hydro_hourly_QC58 | hydro_hourly | 3.3P | 0 | 22 | QC.a
hydro_hourly_QC59 | hydro_hourly_QC59 | hydro_hourly | 3.3P | 0 | 1.1 | QC.b
hydro_hourly_QC60 | hydro_hourly_QC60 | hydro_hourly | 3.3P | 0 | 119.4 | QC.a
hydro_hourly_QC61 | hydro_hourly_QC61 | hydro_hourly | 3.3P | 0 | 8.5 | QC.a
hydro_hourly_QC62 | hydro_hourly_QC62 | hydro_hourly | 3.3P | 0 | 1.8 | QC.a
hydro_hourly_QC63 | hydro_hourly_QC63 | hydro_hourly | 3.3P | 0 | 10 | QC.b
hydro_hourly_QC64 | hydro_hourly_QC64 | hydro_hourly | 3.3P | 0 | 18.3 | QC.b
hydro_hourly_QC65 | hydro_hourly_QC65 | hydro_hourly | 3.3P | 0 | 6 | QC.b
hydro_hourly_QC66 | hydro_hourly_QC66 | hydro_hourly | 3.3P | 0 | 4 | QC.b
hydro_hourly_QC67 | hydro_hourly_QC67 | hydro_hourly | 3.3P | 0 | 2.4 | QC.a
hydro_hourly_QC68 | hydro_hourly_QC68 | hydro_hourly | 3.3P | 0 | 2.1 | QC.a
hydro_hourly_QC69 | hydro_hourly_QC69 | hydro_hourly | 3.3P | 0 | 1.6 | QC.a
hydro_hourly_QC70 | hydro_hourly_QC70 | hydro_hourly | 3.3P | 0 | 1.7 | QC.b
hydro_hourly_QC71 | hydro_hourly_QC71 | hydro_hourly | 3.3P | 0 | 4.1 | QC.b
hydro_hourly_QC72 | hydro_hourly_QC72 | hydro_hourly | 3.3P | 0 | 9.1 | QC.b
hydro_hourly_QC73 | hydro_hourly_QC73 | hydro_hourly | 3.3P | 0 | 7.6 | QC.b
hydro_hourly_QC74 | hydro_hourly_QC74 | hydro_hourly | 3.3P | 0 | 9.9 | QC.b
hydro_hourly_QC75 | hydro_hourly_QC75 | hydro_hourly | 3.3P | 0 | 8.7 | QC.b
hydro_hourly_QC76 | hydro_hourly_QC76 | hydro_hourly | 3.3P | 0 | 385 | QC.b
hydro_hourly_QC77 | hydro_hourly_QC77 | hydro_hourly | 3.3P | 0 | 67 | QC.b
hydro_hourly_QC78 | hydro_hourly_QC78 | hydro_hourly | 3.3P | 0 | 76 | QC.b
hydro_hourly_QC79 | hydro_hourly_QC79 | hydro_hourly | 3.3P | 0 | 104 | QC.a
hydro_hourly_QC80 | hydro_hourly_QC80 | hydro_hourly | 3.3P | 0 | 9 | QC.a
hydro_hourly_QC81 | hydro_hourly_QC81 | hydro_hourly | 3.3P | 0 | 2.4 | QC.a
hydro_hourly_QC82 | hydro_hourly_QC82 | hydro_hourly | 3.3P | 0 | 3.7 | QC.b
hydro_hourly_QC83 | hydro_hourly_QC83 | hydro_hourly | 3.3P | 0 | 54 | QC.a
hydro_hourly_QC84 | hydro_hourly_QC84 | hydro_hourly | 3.3P | 0 | 2.65 | QC.b
hydro_hourly_QC85 | hydro_hourly_QC85 | hydro_hourly | 3.3P | 0 | 230 | QC.a
hydro_hourly_QC86 | hydro_hourly_QC86 | hydro_hourly | 3.3P | 0 | 2.9 | QC.a
hydro_hourly_QC87 | hydro_hourly_QC87 | hydro_hourly | 3.3P | 0 | 38 | QC.b
hydro_hourly_QC88 | hydro_hourly_QC88 | hydro_hourly | 3.3P | 0 | 5.7 | QC.a
hydro_hourly_QC89 | hydro_hourly_QC89 | hydro_hourly | 3.3P | 0 | 15 | QC.a
hydro_hourly_QC90 | hydro_hourly_QC90 | hydro_hourly | 3.3P | 0 | 28.9 | QC.b
hydro_hourly_QC91 | hydro_hourly_QC91 | hydro_hourly | 3.3P | 0 | 22 | QC.a
hydro_hourly_QC92 | hydro_hourly_QC92 | hydro_hourly | 3.3P | 0 | 8.2 | QC.a
hydro_hourly_QC93 | hydro_hourly_QC93 | hydro_hourly | 3.3P | 0 | 5.8 | QC.a
hydro_hourly_QC94 | hydro_hourly_QC94 | hydro_hourly | 3.3P | 0 | 4.05 | QC.a
hydro_hourly_QC95 | hydro_hourly_QC95 | hydro_hourly | 3.3P | 0 | 3.5 | QC.a
hydro_hourly_QC96 | hydro_hourly_QC96 | hydro_hourly | 3.3P | 0 | 2.3 | QC.a
hydro_hourly_QC97 | hydro_hourly_QC97 | hydro_hourly | 3.3P | 0 | 4.9 | QC.a
hydro_hourly_QC98 | hydro_hourly_QC98 | hydro_hourly | 3.3P | 0 | 17.6 | QC.b
hydro_hourly_QC99 | hydro_hourly_QC99 | hydro_hourly | 3.3P | 0 | 11.7 | QC.a
hydro_hourly_QC100 | hydro_hourly_QC100 | hydro_hourly | 3.3P | 0 | 4.5 | QC.a
hydro_hourly_QC101 | hydro_hourly_QC101 | hydro_hourly | 3.3P | 0 | 4.3 | QC.a
hydro_hourly_QC102 | hydro_hourly_QC102 | hydro_hourly | 3.3P | 0 | 2.5 | QC.b
hydro_monthly_QC1 | hydro_monthly_QC1 | hydro_monthly | 3.3P | 0 | 1178 | QC.b
hydro_monthly_QC2 | hydro_monthly_QC2 | hydro_monthly | 3.3P | 0 | 469 | QC.b
hydro_monthly_QC3 | hydro_monthly_QC3 | hydro_monthly | 3.3P | 0 | 480 | QC.b
hydro_monthly_QC4 | hydro_monthly_QC4 | hydro_monthly | 3.3P | 0 | 768 | QC.b
hydro_monthly_QC5 | hydro_monthly_QC5 | hydro_monthly | 3.3P | 0 | 51 | QC.b
hydro_monthly_QC6 | hydro_monthly_QC6 | hydro_monthly | 3.3P | 0 | 5616 | QC.b
hydro_monthly_QC7 | hydro_monthly_QC7 | hydro_monthly | 3.3P | 0 | 2106 | QC.b
hydro_monthly_QC8 | hydro_monthly_QC8 | hydro_monthly | 3.3P | 0 | 2417 | QC.b
hydro_monthly_QC9 | hydro_monthly_QC9 | hydro_monthly | 3.3P | 0 | 2779 | QC.b
hydro_monthly_QC10 | hydro_monthly_QC10 | hydro_monthly | 3.3P | 0 | 878 | QC.b
hydro_monthly_QC11 | hydro_monthly_QC11 | hydro_monthly | 3.3P | 0 | 1596 | QC.b
hydro_monthly_QC12 | hydro_monthly_QC12 | hydro_monthly | 3.3P | 0 | 1064 | QC.b
hydro_monthly_QC13 | hydro_monthly_QC13 | hydro_monthly | 3.3P | 0 | 55 | QC.a
hydro_monthly_QC14 | hydro_monthly_QC14 | hydro_monthly | 3.3P | 0 | 785 | QC.b
hydro_monthly_QC15 | hydro_monthly_QC15 | hydro_monthly | 3.3P | 0 | 67 | QC.b
hydro_monthly_QC16 | hydro_monthly_QC16 | hydro_monthly | 3.3P | 0 | 204 | QC.b
hydro_monthly_QC17 | hydro_monthly_QC17 | hydro_monthly | 3.3P | 0 | 640 | QC.b
hydro_monthly_QC18 | hydro_monthly_QC18 | hydro_monthly | 3.3P | 0 | 395 | QC.b
hydro_monthly_QC19 | hydro_monthly_QC19 | hydro_monthly | 3.3P | 0 | 245 | QC.b
hydro_monthly_QC20 | hydro_monthly_QC20 | hydro_monthly | 3.3P | 0 | 882 | QC.b
hydro_monthly_QC21 | hydro_monthly_QC21 | hydro_monthly | 3.3P | 0 | 526 | QC.b
hydro_daily_SK1 | hydro_daily_SK1 | hydro_daily | 3.3P | 0 | 10 | SK.a
hydro_daily_SK2 | hydro_daily_SK2 | hydro_daily | 3.3P | 0 | 186 | SK.a
hydro_daily_SK3 | hydro_daily_SK3 | hydro_daily | 3.3P | 0 | 288 | SK.a
hydro_daily_SK4 | hydro_daily_SK4 | hydro_daily | 3.3P | 0 | 111 | SK.a
hydro_daily_SK5 | hydro_daily_SK5 | hydro_daily | 3.3P | 0 | 255 | SK.a
hydro_hourly_SK1 | hydro_hourly_SK1 | hydro_hourly | 3.3P | 0 | 8 | SK.a
hydro_hourly_SK2 | hydro_hourly_SK2 | hydro_hourly | 3.3P | 0 | 5 | SK.a

## vre plants
plant ID | name | kind | latitude | longitude | [MW] | bus | technology type | unit capacity [kW] | latitude_MERRA | longitude_MERRA
Solar | Solar_1 | solar | 51 | -116 | 15956.5113 | BC.a | FS395 | 95 | 282 | 96
Solar | Solar_2 | solar | 52 | -114 | 17 | AB.a | FS395 | 95 | 284 | 99
Solar | Solar_3 | solar | 51 | -112.6667 | 2 | AB.a | FS395 | 95 | 282 | 101
Solar | Solar_4 | solar | 50.5 | -112 | 17 | AB.a | FS395 | 95 | 281 | 102
Solar | Solar_5 | solar | 50 | -112 | 47 | AB.a | FS395 | 95 | 280 | 102
Solar | Solar_6 | solar | 44 | -80.6667 | 50 | ON.a | FS395 | 95 | 268 | 149
Solar | Solar_7 | solar | 45.5 | -76 | 13 | QC.a | FS395 | 95 | 271 | 156
Solar | Solar_8 | solar | 45.5 | -74.6667 | 5335.2919 | ON.b | FS395 | 95 | 271 | 158
Solar | Solar_9 | solar | 46 | -73.3333 | 7496.5159 | QC.a | FS395 | 95 | 272 | 160
Solar | Solar_10 | solar | 46 | -72.6667 | 7496.5159 | QC.a | FS395 | 95 | 272 | 161
Solar | Solar_11 | solar | 47.5 | -68 | 43.4066 | NB.a | FS395 | 95 | 275 | 168
Solar | Solar_12 | solar | 45 | -64 | 2288.8746 | NS.a | FS395 | 95 | 270 | 174
Solar | Solar_13 | solar | 46 | -64 | 1282.7793 | NS.a | FS395 | 95 | 272 | 174
Solar | Solar_14 | solar | 49.5 | -58 | 4.039 | NL.a | FS395 | 95 | 279 | 183
Solar | Solar_15 | solar | 48.5 | -58 | 136.4311 | NL.a | FS395 | 95 | 277 | 183
Solar | Solar_16 | solar | 49.5 | -57.3333 | 4.039 | NL.a | FS395 | 95 | 279 | 184
Solar | Solar_17 | solar | 50 | -57.3333 | 1842.2191 | NL.a | FS395 | 95 | 280 | 184
Solar | Solar_18 | solar | 48.5 | -57.3333 | 136.4311 | NL.a | FS395 | 95 | 277 | 184
Solar | Solar_19 | solar | 48.5 | -56.6667 | 136.4311 | NL.a | FS395 | 95 | 277 | 185
Solar | Solar_20 | solar | 48 | -56 | 129.9489 | NL.a | FS395 | 95 | 276 | 186
Solar | Solar_21 | solar | 48 | -55.3333 | 129.9489 | NL.a | FS395 | 95 | 276 | 187
Solar | Solar_22 | solar | 48 | -54.6667 | 129.9489 | NL.a | FS395 | 95 | 276 | 188
Wind | Wind_1 | wind | 54 | -132 | 4041.1261 | BC.a | V_112-3.0 | 3075 | 288 | 72
Wind | Wind_2 | wind | 55.5 | -117.3333 | 1183.134 | AB.a | V_112-3.0 | 3075 | 291 | 94
Wind | Wind_3 | wind | 54 | -114.6667 | 96.8133 | AB.a | V_112-3.0 | 3075 | 288 | 98
Wind | Wind_4 | wind | 53.5 | -114 | 177.7415 | AB.a | V_112-3.0 | 3075 | 287 | 99
Wind | Wind_5 | wind | 53 | -114 | 1470.2691 | AB.a | V_112-3.0 | 3075 | 286 | 99
Wind | Wind_6 | wind | 52.5 | -114 | 128.7374 | AB.a | V_112-3.0 | 3075 | 285 | 99
Wind | Wind_7 | wind | 49.5 | -113.3333 | 2661.2738 | AB.a | V_112-3.0 | 3075 | 279 | 100
Wind | Wind_8 | wind | 52.5 | -113.3333 | 1195.7001 | AB.a | V_112-3.0 | 3075 | 285 | 100
Wind | Wind_9 | wind | 51.5 | -113.3333 | 1001.6837 | AB.a | V_112-3.0 | 3075 | 283 | 100
Wind | Wind_10 | wind | 50.5 | -113.3333 | 964.295 | AB.a | V_112-3.0 | 3075 | 281 | 100
Wind | Wind_11 | wind | 52 | -113.3333 | 82 | AB.a | V_112-3.0 | 3075 | 284 | 100
Wind | Wind_12 | wind | 53 | -113.3333 | 4931.8989 | AB.a | V_112-3.0 | 3075 | 286 | 100
Wind | Wind_13 | wind | 50 | -113.3333 | 786.8089 | AB.a | V_112-3.0 | 3075 | 280 | 100
Wind | Wind_14 | wind | 49.5 | -112.6667 | 1381.9362 | AB.a | V_112-3.0 | 3075 | 279 | 101
Wind | Wind_15 | wind | 52.5 | -112.6667 | 363.3793 | AB.a | V_112-3.0 | 3075 | 285 | 101
Wind | Wind_16 | wind | 53 | -112.6667 | 2470.7944 | AB.a | V_112-3.0 | 3075 | 286 | 101
Wind | Wind_17 | wind | 53.5 | -112.6667 | 3227.1249 | AB.a | V_112-3.0 | 3075 | 287 | 101
Wind | Wind_18 | wind | 52 | -112.6667 | 652.5283 | AB.a | V_112-3.0 | 3075 | 284 | 101
Wind | Wind_19 | wind | 51.5 | -112.6667 | 78.0198 | AB.a | V_112-3.0 | 3075 | 283 | 101
Wind | Wind_20 | wind | 50.5 | -112.6667 | 645.491 | AB.a | V_112-3.0 | 3075 | 281 | 101
Wind | Wind_21 | wind | 50.5 | -112 | 1047.0572 | AB.a | V_112-3.0 | 3075 | 281 | 102
Wind | Wind_22 | wind | 49.5 | -112 | 3992.2636 | AB.a | V_112-3.0 | 3075 | 279 | 102
Wind | Wind_23 | wind | 52 | -112 | 1444.7108 | AB.a | V_112-3.0 | 3075 | 284 | 102
Wind | Wind_24 | wind | 50 | -112 | 893.5877 | AB.a | V_112-3.0 | 3075 | 280 | 102
Wind | Wind_25 | wind | 53.5 | -112 | 551.4534 | AB.a | V_112-3.0 | 3075 | 287 | 102
Wind | Wind_26 | wind | 51 | -112 | 384.06 | AB.a | V_112-3.0 | 3075 | 282 | 102
Wind | Wind_27 | wind | 51.5 | -111.3333 | 1371.3621 | AB.a | V_112-3.0 | 3075 | 283 | 103
Wind | Wind_28 | wind | 49.5 | -111.3333 | 1183.2137 | AB.a | V_112-3.0 | 3075 | 279 | 103
Wind | Wind_29 | wind | 50 | -111.3333 | 3805.7501 | AB.a | V_112-3.0 | 3075 | 280 | 103
Wind | Wind_30 | wind | 51 | -111.3333 | 586.2588 | AB.a | V_112-3.0 | 3075 | 282 | 103
Wind | Wind_31 | wind | 53 | -111.3333 | 556.836 | AB.a | V_112-3.0 | 3075 | 286 | 103
Wind | Wind_32 | wind | 52 | -110.6667 | 1652.7352 | AB.a | V_112-3.0 | 3075 | 284 | 104
Wind | Wind_33 | wind | 49.5 | -110.6667 | 2302.7838 | AB.a | V_112-3.0 | 3075 | 279 | 104
Wind | Wind_34 | wind | 54 | -110.6667 | 404.434 | AB.a | V_112-3.0 | 3075 | 288 | 104
Wind | Wind_35 | wind | 52.5 | -110.6667 | 2509.2429 | AB.a | V_112-3.0 | 3075 | 285 | 104
Wind | Wind_36 | wind | 50.5 | -110.6667 | 1634.5798 | AB.a | V_112-3.0 | 3075 | 281 | 104
Wind | Wind_37 | wind | 51.5 | -110.6667 | 850.1899 | AB.a | V_112-3.0 | 3075 | 283 | 104
Wind | Wind_38 | wind | 50 | -110.6667 | 471.9206 | AB.a | V_112-3.0 | 3075 | 280 | 104
Wind | Wind_39 | wind | 53.5 | -110.6667 | 851.9307 | AB.a | V_112-3.0 | 3075 | 287 | 104
Wind | Wind_40 | wind | 53 | -109.3333 | 47.7983 | SK.a | V_112-3.0 | 3075 | 286 | 106
Wind | Wind_41 | wind | 49.5 | -109.3333 | 21.6835 | SK.a | V_112-3.0 | 3075 | 279 | 106
Wind | Wind_42 | wind | 52 | -109.3333 | 214.732 | SK.a | V_112-3.0 | 3075 | 284 | 106
Wind | Wind_43 | wind | 51.5 | -109.3333 | 30.9931 | SK.a | V_112-3.0 | 3075 | 283 | 106
Wind | Wind_44 | wind | 52 | -108.6667 | 265.6592 | SK.a | V_112-3.0 | 3075 | 284 | 107
Wind | Wind_45 | wind | 51.5 | -108.6667 | 267.7339 | SK.a | V_112-3.0 | 3075 | 283 | 107
Wind | Wind_46 | wind | 50 | -108.6667 | 393.5756 | SK.a | V_112-3.0 | 3075 | 280 | 107
Wind | Wind_47 | wind | 50.5 | -108.6667 | 670.613 | SK.a | V_112-3.0 | 3075 | 281 | 107
Wind | Wind_48 | wind | 51.5 | -108 | 290.4047 | SK.a | V_112-3.0 | 3075 | 283 | 108
Wind | Wind_49 | wind | 49.5 | -107.3333 | 254.4931 | SK.a | V_112-3.0 | 3075 | 279 | 109
Wind | Wind_50 | wind | 50.5 | -107.3333 | 128.3272 | SK.a | V_112-3.0 | 3075 | 281 | 109
Wind | Wind_51 | wind | 52 | -107.3333 | 730.5043 | SK.a | V_112-3.0 | 3075 | 284 | 109
Wind | Wind_52 | wind | 50 | -107.3333 | 175.2097 | SK.a | V_112-3.0 | 3075 | 280 | 109
Wind | Wind_53 | wind | 51 | -106.6667 | 566.8269 | SK.a | V_112-3.0 | 3075 | 282 | 110
Wind | Wind_54 | wind | 51 | -106 | 971.5345 | SK.a | V_112-3.0 | 3075 | 282 | 111
Wind | Wind_55 | wind | 50 | -106 | 411.6209 | SK.a | V_112-3.0 | 3075 | 280 | 111
Wind | Wind_56 | wind | 50.5 | -106 | 294.317 | SK.a | V_112-3.0 | 3075 | 281 | 111
Wind | Wind_57 | wind | 49.5 | -106 | 908.7815 | SK.a | V_112-3.0 | 3075 | 279 | 111
Wind | Wind_58 | wind | 50 | -105.3333 | 378.1484 | SK.a | V_112-3.0 | 3075 | 280 | 112
Wind | Wind_59 | wind | 51 | -105.3333 | 465.171 | SK.a | V_112-3.0 | 3075 | 282 | 112
Wind | Wind_60 | wind | 49.5 | -105.3333 | 47.8086 | SK.a | V_112-3.0 | 3075 | 279 | 112
Wind | Wind_61 | wind | 50.5 | -105.3333 | 852.9513 | SK.a | V_112-3.0 | 3075 | 281 | 112
Wind | Wind_62 | wind | 52 | -105.3333 | 224.7409 | SK.a | V_112-3.0 | 3075 | 284 | 112
Wind | Wind_63 | wind | 51 | -104.6667 | 316.151 | SK.a | V_112-3.0 | 3075 | 282 | 113
Wind | Wind_64 | wind | 49.5 | -104.6667 | 80.5977 | SK.a | V_112-3.0 | 3075 | 279 | 113
Wind | Wind_65 | wind | 51.5 | -104 | 879.5285 | SK.a | V_112-3.0 | 3075 | 283 | 114
Wind | Wind_66 | wind | 51 | -104 | 142.5268 | SK.a | V_112-3.0 | 3075 | 282 | 114
Wind | Wind_67 | wind | 52 | -104 | 713.9753 | SK.a | V_112-3.0 | 3075 | 284 | 114
Wind | Wind_68 | wind | 50 | -104 | 720.1788 | SK.a | V_112-3.0 | 3075 | 280 | 114
Wind | Wind_69 | wind | 51.5 | -103.3333 | 1434.509 | SK.a | V_112-3.0 | 3075 | 283 | 115
Wind | Wind_70 | wind | 50.5 | -103.3333 | 323.1009 | SK.a | V_112-3.0 | 3075 | 281 | 115
Wind | Wind_71 | wind | 49.5 | -103.3333 | 945.8495 | SK.a | V_112-3.0 | 3075 | 279 | 115
Wind | Wind_72 | wind | 50 | -103.3333 | 265.1577 | SK.a | V_112-3.0 | 3075 | 280 | 115
Wind | Wind_73 | wind | 51 | -103.3333 | 1010.7843 | SK.a | V_112-3.0 | 3075 | 282 | 115
Wind | Wind_74 | wind | 50.5 | -102.6667 | 648.45 | SK.a | V_112-3.0 | 3075 | 281 | 116
Wind | Wind_75 | wind | 50 | -102.6667 | 427.7972 | SK.a | V_112-3.0 | 3075 | 280 | 116
Wind | Wind_76 | wind | 51 | -102.6667 | 707.6032 | SK.a | V_112-3.0 | 3075 | 282 | 116
Wind | Wind_77 | wind | 51.5 | -102.6667 | 373.6284 | SK.a | V_112-3.0 | 3075 | 283 | 116
Wind | Wind_78 | wind | 49.5 | -102 | 749.4308 | SK.a | V_112-3.0 | 3075 | 279 | 117
Wind | Wind_79 | wind | 51 | -102 | 544.1378 | SK.a | V_112-3.0 | 3075 | 282 | 117
Wind | Wind_80 | wind | 51.5 | -102 | 318.9117 | SK.a | V_112-3.0 | 3075 | 283 | 117
Wind | Wind_81 | wind | 50.5 | -102 | 505.3908 | SK.a | V_112-3.0 | 3075 | 281 | 117
Wind | Wind_82 | wind | 50 | -102 | 526.1951 | SK.a | V_112-3.0 | 3075 | 280 | 117
Wind | Wind_83 | wind | 49.5 | -101.3333 | 1009.6871 | MB.a | V_112-3.0 | 3075 | 279 | 118
Wind | Wind_84 | wind | 51 | -101.3333 | 577.8411 | MB.a | V_112-3.0 | 3075 | 282 | 118
Wind | Wind_85 | wind | 50.5 | -100.6667 | 195.5785 | MB.a | V_112-3.0 | 3075 | 281 | 119
Wind | Wind_86 | wind | 50 | -100.6667 | 2054.6024 | MB.a | V_112-3.0 | 3075 | 280 | 119
Wind | Wind_87 | wind | 50 | -100 | 157.7394 | MB.a | V_112-3.0 | 3075 | 280 | 120
Wind | Wind_88 | wind | 51 | -99.3333 | 57.7332 | MB.a | V_112-3.0 | 3075 | 282 | 121
Wind | Wind_89 | wind | 49.5 | -98.6667 | 2883.836 | MB.a | V_112-3.0 | 3075 | 279 | 122
Wind | Wind_90 | wind | 51.5 | -98.6667 | 1287.2036 | MB.a | V_112-3.0 | 3075 | 283 | 122
Wind | Wind_91 | wind | 51 | -98.6667 | 125.0358 | MB.a | V_112-3.0 | 3075 | 282 | 122
Wind | Wind_92 | wind | 50.5 | -98 | 2400.6616 | MB.a | V_112-3.0 | 3075 | 281 | 123
Wind | Wind_93 | wind | 50.5 | -97.3333 | 595.5367 | MB.a | V_112-3.0 | 3075 | 281 | 124
Wind | Wind_94 | wind | 51 | -97.3333 | 259.7822 | MB.a | V_112-3.0 | 3075 | 282 | 124
Wind | Wind_95 | wind | 58 | -95.3333 | 145.5013 | MB.a | V_112-3.0 | 3075 | 296 | 127
Wind | Wind_96 | wind | 57.5 | -92.6667 | 981.3048 | MB.a | V_112-3.0 | 3075 | 295 | 131
Wind | Wind_97 | wind | 56 | -89.3333 | 130.6507 | ON.b | V_112-3.0 | 3075 | 292 | 136
Wind | Wind_98 | wind | 56.5 | -88.6667 | 1171.4841 | ON.b | V_112-3.0 | 3075 | 293 | 137
Wind | Wind_99 | wind | 55.5 | -86.6667 | 637.921 | ON.b | V_112-3.0 | 3075 | 291 | 140
Wind | Wind_100 | wind | 55.5 | -86 | 1890.289 | ON.b | V_112-3.0 | 3075 | 291 | 141
Wind | Wind_101 | wind | 55 | -85.3333 | 547.8023 | ON.b | V_112-3.0 | 3075 | 290 | 142
Wind | Wind_102 | wind | 55 | -84.6667 | 1151.4192 | ON.b | V_112-3.0 | 3075 | 290 | 143
Wind | Wind_103 | wind | 47 | -84.6667 | 132 | ON.b | V_112-3.0 | 3075 | 274 | 143
Wind | Wind_104 | wind | 55 | -83.3333 | 379.6835 | ON.b | V_112-3.0 | 3075 | 290 | 145
Wind | Wind_105 | wind | 55 | -82.6667 | 403.7952 | ON.b | V_112-3.0 | 3075 | 290 | 146
Wind | Wind_106 | wind | 42.5 | -82 | 3974.3062 | ON.a | V_112-3.0 | 3075 | 265 | 147
Wind | Wind_107 | wind | 43.5 | -81.3333 | 780.0568 | ON.a | V_112-3.0 | 3075 | 267 | 148
Wind | Wind_108 | wind | 45 | -81.3333 | 5 | ON.b | V_112-3.0 | 3075 | 270 | 148
Wind | Wind_109 | wind | 44.5 | -81.3333 | 4146.1503 | ON.a | V_112-3.0 | 3075 | 269 | 148
Wind | Wind_110 | wind | 44 | -81.3333 | 2528.4214 | ON.a | V_112-3.0 | 3075 | 268 | 148
Wind | Wind_111 | wind | 43.5 | -80.6667 | 5954.3366 | ON.a | V_112-3.0 | 3075 | 267 | 149
Wind | Wind_112 | wind | 44 | -80.6667 | 5753.3683 | ON.a | V_112-3.0 | 3075 | 268 | 149
Wind | Wind_113 | wind | 44.5 | -80.6667 | 5853.9503 | ON.a | V_112-3.0 | 3075 | 269 | 149
Wind | Wind_114 | wind | 43 | -80.6667 | 6003.8514 | ON.a | V_112-3.0 | 3075 | 266 | 149
Wind | Wind_115 | wind | 43.5 | -80 | 4214.8672 | ON.a | V_112-3.0 | 3075 | 267 | 150
Wind | Wind_116 | wind | 43 | -80 | 138.0355 | ON.a | V_112-3.0 | 3075 | 266 | 150
Wind | Wind_117 | wind | 44 | -80 | 2060.2897 | ON.a | V_112-3.0 | 3075 | 268 | 150
Wind | Wind_118 | wind | 44.5 | -80 | 29 | ON.a | V_112-3.0 | 3075 | 269 | 150
Wind | Wind_119 | wind | 44.5 | -79.3333 | 896.3367 | ON.a | V_112-3.0 | 3075 | 269 | 151
Wind | Wind_120 | wind | 47.5 | -79.3333 | 1121.4782 | QC.a | V_112-3.0 | 3075 | 275 | 151
Wind | Wind_121 | wind | 44 | -79.3333 | 5904.3683 | ON.a | V_112-3.0 | 3075 | 268 | 151
Wind | Wind_122 | wind | 43 | -79.3333 | 873.1879 | ON.a | V_112-3.0 | 3075 | 266 | 151
Wind | Wind_123 | wind | 44 | -78.6667 | 5904.3683 | ON.a | V_112-3.0 | 3075 | 268 | 152
Wind | Wind_124 | wind | 44 | -78 | 5376.8798 | ON.a | V_112-3.0 | 3075 | 268 | 153
Wind | Wind_125 | wind | 44 | -77.3333 | 5904.3683 | ON.a | V_112-3.0 | 3075 | 268 | 154
Wind | Wind_126 | wind | 44.5 | -76.6667 | 261 | ON.a | V_112-3.0 | 3075 | 269 | 155
Wind | Wind_127 | wind | 53.5 | -75.3333 | 4874.0757 | QC.b | V_112-3.0 | 3075 | 287 | 157
Wind | Wind_128 | wind | 46.5 | -74 | 801.1602 | QC.a | V_112-3.0 | 3075 | 273 | 159
Wind | Wind_129 | wind | 45.5 | -73.3333 | 574.5148 | QC.a | V_112-3.0 | 3075 | 271 | 160
Wind | Wind_130 | wind | 46 | -73.3333 | 5700.0372 | QC.a | V_112-3.0 | 3075 | 272 | 160
Wind | Wind_131 | wind | 46 | -72.6667 | 1033.8774 | QC.a | V_112-3.0 | 3075 | 272 | 161
Wind | Wind_132 | wind | 46.5 | -71.3333 | 1126.6975 | QC.a | V_112-3.0 | 3075 | 273 | 163
Wind | Wind_133 | wind | 46 | -71.3333 | 11 | QC.a | V_112-3.0 | 3075 | 272 | 163
Wind | Wind_134 | wind | 55.5 | -67.3333 | 377.8023 | QC.b | V_112-3.0 | 3075 | 291 | 169
Wind | Wind_135 | wind | 44 | -66 | 12.6558 | NS.a | V_112-3.0 | 3075 | 268 | 171
Wind | Wind_136 | wind | 54.5 | -65.3333 | 445.9397 | NL.b | V_112-3.0 | 3075 | 289 | 172
Wind | Wind_137 | wind | 45.5 | -64.6667 | 72.2514 | NS.a | V_112-3.0 | 3075 | 271 | 173
Wind | Wind_138 | wind | 47 | -64 | 436.2309 | PE.a | V_112-3.0 | 3075 | 274 | 174
Wind | Wind_139 | wind | 46.5 | -64 | 691.3808 | PE.a | V_112-3.0 | 3075 | 273 | 174
Wind | Wind_140 | wind | 46 | -62.6667 | 30 | PE.a | V_112-3.0 | 3075 | 272 | 176
Wind | Wind_141 | wind | 45.5 | -61.3333 | 1670.9049 | NS.a | V_112-3.0 | 3075 | 271 | 178
Wind | Wind_142 | wind | 46 | -61.3333 | 337.7951 | NS.a | V_112-3.0 | 3075 | 272 | 178
Wind | Wind_143 | wind | 48 | -58.6667 | 307.366 | NL.a | V_112-3.0 | 3075 | 276 | 182
Wind | Wind_144 | wind | 49.5 | -58 | 2372.5501 | NL.a | V_112-3.0 | 3075 | 279 | 183
Wind | Wind_145 | wind | 48 | -58 | 630.5365 | NL.a | V_112-3.0 | 3075 | 276 | 183
Wind | Wind_146 | wind | 50.5 | -57.3333 | 1077.1331 | NL.a | V_112-3.0 | 3075 | 281 | 184
Wind | Wind_147 | wind | 50 | -56 | 588.5089 | NL.a | V_112-3.0 | 3075 | 280 | 186
Wind | Wind_148 | wind | 47 | -55.3333 | 140.1969 | NL.a | V_112-3.0 | 3075 | 274 | 187
Wind | Wind_149 | wind | 47 | -54 | 35.5922 | NL.a | V_112-3.0 | 3075 | 274 | 189
Wind | Wind_150 | wind | 47 | -53.3333 | 27 | NL.a | V_112-3.0 | 3075 | 274 | 190
Wind | Wind_151 | wind | 48.5 | -53.3333 | 439.1657 | NL.a | V_112-3.0 | 3075 | 277 | 190

## storage
plant ID | name | kind | pmin | [MW] | storagecapacitymax | pumprampmax | resevoir level | bus | cost curve equation | initial power | initial status | hours in status | storage content
LB_PE.a | LB_PE.a | batteries |  | 309.7207 |  |  |  | PE.a
LB_ON.a | LB_ON.a | batteries |  | 11161.3484 |  |  |  | ON.a
LB_AB.a | LB_AB.a | batteries |  | 7135.5061 |  |  |  | AB.a
LB_QC.a | LB_QC.a | batteries |  | 7721.2692 |  |  |  | QC.a
PHS_NS.a | PHS_NS.a | PHS |  | 106.93 |  |  |  | NS.a
PHS_AB.a | PHS_AB.a | PHS |  | 156.2 |  |  |  | AB.a
PHS_SK.a | PHS_SK.a | PHS |  | 233 |  |  |  | SK.a
PHS_MB.a | PHS_MB.a | PHS |  | 1061.6 |  |  |  | MB.a
PHS_ON.b | PHS_ON.b | PHS |  | 704.4 |  |  |  | ON.b
PHS_ON.a | PHS_ON.a | PHS |  | 28.8 |  |  |  | ON.a
PHS_NB.a | PHS_NB.a | PHS |  | 172.6 |  |  |  | NB.a
PHS_NL.a | PHS_NL.a | PHS |  | 207.38 |  |  |  | NL.a
PHS_QC.a | PHS_QC.a | PHS |  | 295.2 |  |  |  | QC.a
PHS_BC.a | PHS_BC.a | PHS |  | 955.0238 |  |  |  | BC.a
LB_SK.a | LB_SK.a | batteries |  | 1625.3444 |  |  |  | SK.a
LB_MB.a | LB_MB.a | batteries |  | 1602.5618 |  |  |  | MB.a
LB_ON.b | LB_ON.b | batteries |  | 700.942 |  |  |  | ON.b
LB_NB.a | LB_NB.a | batteries |  | 43.638 |  |  |  | NB.a
LB_NL.a | LB_NL.a | batteries |  | 1138.8856 |  |  |  | NL.a
LB_NS.a | LB_NS.a | batteries |  | 1924.2828 |  |  |  | NS.a

## existing transmission
name | from bus | to bus | Voltage | length | pmax | reactance
Line_1 | AB.a | BC.a | 230 | 147 | 2200 | 0.01
Line_2 | AB.a | SK.a | 230 | 145 | 306 | 0.01
Line_3 | MB.a | ON.b | 230 | 64.2 | 200 | 0.1
Line_4 | MB.a | SK.a | 230 | 12.8 | 540 | 0.1
Line_5 | NB.a | NS.a | 230 | 10 | 650 | 0.1
Line_6 | NB.a | PE.a | 230 | 3.7 | 444 | 0.1
Line_7 | NB.a | QC.a | 345 | 225 | 1814 | 0.01
Line_8 | NL.a | NL.b | 345 | 160 | 1800 | 0.1
Line_9 | NL.a | NS.a | 345 | 141 | 847 | 0.1
Line_10 | NL.b | QC.b | 345 | 141 | 10400 | 0.01
Line_13 | ON.a | QC.a | 345 | 141 | 4725 | 0.01
Line_11 | ON.b | ON.a | 345 | 141 | 3600 | 0.1
Line_12 | ON.b | QC.b | 345 | 141 | 195 | 0.1
Line_14 | QC.b | QC.a | 345 | 141 | 59500 | 0.01