## site independent
technology assumptions | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | [9 empty] | references colour coded
[8 empty] | estimated start up times (notice to full load) |  |  |  | cycling costs |  |  | research these value and add it here
non-vre sources | levelized capital cost | fixed o&m cost | variable o&m cost (inc. fuel) | transmission investment | total system LCOE | efficiency | GHG emissions | hot start | warm start | cold start | spin ramp rate | hot start | warm start | cold start | spinning cost | minimum up time | minimum down time | shut down cost | negative change in power for spinning unit | shut down ramp limit | Operating reserve coeff. | Max capacity value | Total overnight cost in 2014
| 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh |  | kg CO2e/MWh | hours |  |  | %/min | $/MW cap. |  |  | [$ per hour committed] | [hours] | [hours] |  |  |  | [Fraction of installed capacity] | [Fraction of installed capacity] | $/kW
coal | 60 | 4.2 | 30.3 | 1.2 | 95.6 | 0.32623 | 820 | 3 | 6.5 | 10 | 2 | 59 | 65 | 105 | 10000 | 3 | 3 | 0 |  |  | 0.53 | 1 | 2917 | "Levelized cost and levelized avoided cost of new generation resources in the Annual Energy Outlook 2014" US Energy Information Administration
Natural gas | [14 empty] | 10000 | 4 | 3 | 0 |  |  |  | 1 |  | "FAQ: What is the efficiency of different types of power plants?" US Energy Information Administration
NG_CC | 14.3 | 1.7 | 49.1 | 1.2 | 66.3 | 0.55 | 490 | 1 | 2 | 4 | 5 | 35 | 55 | 79 | 10000 | 4 | 3 | 0 |  |  | 0.53 | 1 | 671 |  | Table 8.1. Average Operating Heat Rate for Selected Energy Sources, 2003-2013. US Energy Information Administration
NG_CT | 40.2 | 2.8 | 82 | 3.4 | 128.4 | 0.35 | 530 | 0.5 | 0.5 | 0.5 | 8 | 32 | 126 | 103 | 10000 | 4 | 3 | 0 |  |  | 1 | 1 | 968 |  | Annual Energy Review 2010. Appendix F: Alternatives for Estimating Energy Consumption. Table F1. Conversion Efficiencies of noncombustible Renewable Energy Sources. US Energy Information Administration.
NG_CG | 40.2 | 2.8 | 82 | 3.4 | 128.4 | 0.35 | 530 | 0.5 | 0.5 | 0.5 | 8 | 32 | 126 | 103 | 10000 | 4 | 3 | 0 |  |  | 1 | 1 | 968
diesel | 8 | 2 | 288 |  |  | 0.31849 | 733 | [6 empty] | 10000000 | 10000 |  |  | 0 |  |  | 0.86 | 1
fuel oil | 8 | 2 | 172.8 |  |  | 0.31849 | 733 | [6 empty] | 10000000 | 10000 |  |  | 0 |  |  | 0.86 | 1
nuclear | 71.4 | 11.8 | 11.8 | 1.1 | 96.1 | 0.32654 | 12 | 1 |  | 13 | 5 |  |  | 500 | 10000 | 10 | 3 | 0 |  |  | 0.2 | 1 | 5366 | "Biomass Energy Economics" Pacific Energy Systems, Inc.
hydro | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651 | Climate Change 2014: Mitigation of Climate Change. Contribution of Working Group III to the Fifth Assessment Report of the Intergovernmental Panel on Climate Change. Annex III: Technology-specific cost and performance parameters. Table A.III.2 Emissions of selected electricity supply technologies
hydro_hourly | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
hydro_daily | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
hydro_monthly | 72 | 4.1 | 6.4 | 2 | 84.5 | 0.9 | 24 | [7 empty] | 10000 | [5 empty] | 0.66 | 1 | 2651
geothermal | 34.2 | 12.2 | 0 | 1.4 | 47.9 | 0.16 | 38 | [7 empty] | 10000 | [5 empty] | 0.32 | 1 | 2448 | "Technical Assessment of the Operation of Coal and Gas Fired Plants" Report to the DECC
biomass | 47.4 | 14.5 | 39.5 | 1.2 | 102.6 | 0.23 | 230 | [7 empty] | 10000 | [5 empty] | 0.53 | 1 | 3659 | "the westinghouse pressurized water reactor nuclear power plant" Table 16-1 Estimated Startup Time in Hours Required by NSSS
biogas | 47.4 | 14.5 | 39.5 | 1.2 | 102.6 | 0.23 | 230 | [7 empty] | 10000 | [5 empty] | 0.53 | 1 | 3659 | http://www.powerauthority.on.ca/current-electricity-contracts/sc-cc
variable renewable energy sources | levelized capital cost | fixed o&m cost | variable o&m cost (inc. fuel) | transmission investment | total system LCOE | efficiency | [17 empty] | "Cost and Performance Data for Power Generation Technologies" Prepared for the National Renewable Energy Laboratory
| 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | 2012 $/MWh | given by power curves | [17 empty] | "Power Plant Cycling Costs" Prepared for the National Renewable Energy Laboratory
wind | 64.1 | 13 | 0 | 3.2 | 80.3 | [5 empty] | TRUE | [10 empty] | 20% | 19.8
wind - offshore | 175.4 | 22.8 | 0 | 5.8 | 204.1 | [17 empty] | 6154 | *(likely conservative) estimate based on the fact that simple cycle is less efficient
solar PV | 114.5 | 11.4 | 0 | 4.1 | 130 | [16 empty] | 60% | 3279 | Trends in GHG Emissions in the Alberta Electricity Market
solar thermal | 195 | 42.1 | 0 | 6 | 243.1 | [17 empty] | 4052
diesel costs: Lazard LCOE version 8.0
balancing technologies | [23 empty] | assumed fuel oil costs are ~60% of diesel costs based on http://asian-power.com/regulation/commentary/reducing-diesel-power-plant-hfo-bill
"Comparison of Lifecycle Greenhouse Gas Emissions of Various Electricity Generation Sources" WNA
storage | capital cost power | capital cost capacity | annual operating costs | efficiency | applicable grid system size (MW) |  | storage capacity (kWh) |  | charge rate | discharge rate
| (avg) $/kW | (avg) $/kWh | $/kWyr | (max) | min | max | min | max | kW | kW | [13 empty] | "Electricity Storage and Renewables for Island Power" IRENA 2012
PHS | 2500 | 175 | 5 | 0.85 | 200 | 5000 |  |  | 2002500 | 2002500 | [10 empty] | 1 | 50% | 1000 | Kousksou et al. "Energy storage: Applications and challenges" Solar Energy Materials & Solar Cells 2014
CAES | 900 | 100 | 5 | 0.6 | 3 | 400 |  |  | 175000 | 300000 | [10 empty] | 1 | 50% | 650 | "Energy Technology Perspectives" IEA 2014
FES | 3000 | 2250 | 15 | 0.95 | 0.1 | 200 | 1 | 25 | 200 | 200 | [13 empty] | Nils's Paper (Submitted to Energy Economics)
batteries | [20 empty] | 1 | 50% | 1500 | EIA AEO2015 Table 8.2" Cost and Performance characteristics of new central station electricity generating technologies
Pb-acid | 550 | 325 | 30 | 0.9 | 0 | 10 | 0.5 | 10 | 0.8 | 1.25 | [13 empty] | My storage paper with Nils (YSSP report)
Ni-Cd | 1000 | 1150 |  | 0.65 | 0 | 40
Na-S | 1500 | 187.5 | 15 | 0.9 | 0.05 | 8 |  |  | 50 | 50
Li-ion | 700 | 1000 | 25 | 0.95 | 0 | 10 | 0.5 | 10 | 1.1 | 5.25
vanadium | 2500 | 575 |  | 0.85 | 0.05 | 10 | 20 | 50
hydrogen | 1000 | 15 |  | 0.5 | 0.1 | 10 |  |  | 2.505
flow battery | 1600 | 575 | 30 | 0.85 | 0.025 | 10 | 20 | 50 | 12.5 | 15
capacitors | 400 | 1000 |  | 0.65 | 0 | 0.05
supercapacitors | 300 | 2000 |  | 0.95 | 0 | 0.3
SMES | 300 | 10000 |  | 0.95 | 0.1 | 10
thermal | 250 | 26.5 |  | 0.6 | 0 | 300
sector integration - transportation
EV |  |  |  | 0.9 | [16 empty] | 1 | 50%
demand response - shifting
[5 empty] | shreddability (%) | controllability (%) | acceptability (%) | S*P | [15 empty] | "Grid Integration of Aggregated Demand Response, Part 1: Load Availability Profiles and Constraints for the Western Interconnection." NREL
assume x% flexibility - user input |  |  | commercial
assume different flexibilities during different hours |  |  | - cooling |  | 41-49 | 15-25 | 3-77 | 0.45*0.20=0.09 | summer = 9% | cooling peaks from 12-8pm
|  |  | - heating |  | 46-51 | 10-25 | 0-77 | g | winter = 8.6 % | heating peaks from 7-9 am
DR capacity = load * participation rate * sheddability |  |  | residential
participation = min (controllability, acceptability) |  |  | - cooling |  | 20-70 | 2-52 | 13-39 | 0.45*0.26=0.117 | summer = 8.35%
|  |  | - heating |  | 20-30 | 2-48 | 0-1.5 | 0.25*0.01=0.0025 | winter = 2.5%
lighting and ventilation are not easily shiftable! |  |  | - water heating |  | 25 | 13-26 | 13-39 | 0.25*0.20=0.05 |  | peaks 7am, 6pm
** would need demand data by sector |  |  | industrial |  | sheddability (%) | participation (%) | S*P | average |  | ind/mun fairly flat over day
divide year into heating/cooling, keep others year round |  |  | - agricultural water pumping |  | 100 | 10 | 10% | 6%
for multiple end uses, take average of shed * participation? |  |  | - data centres |  | 3 | 100 | 3%
for zeros, use a small non-zero number… |  |  | - regrigerated warehouses |  | 5 | 100 | 5%
for ranges, take midpoint? |  |  | municipal
|  |  | - fresh water pumping |  | 5 | 25 | 1.25%
|  |  | - waste water pumping |  | 5 | 25 | 1.25%
transmission
$ / kWh
- using existing lines | 0.009 | [22 empty] | AEO 2015 table 8
assumptions: aluminum conductor steel reinforced (ACSR), Tubular (230 kV)/Lattice (345 kV - 600 kV), >10 miles
- building new lines | $ / km | source gives in $/mile. 1 mile = 1.60934 km
-- 115 kV single circuit | 596331.4154 | [22 empty] | "Capital Costs for Transmission and Substations" prepared for the Western Electricity Coordinating Council
-- 115 kV double circuit | 954677.0726
-- 230 kV single circuit | 596331.4154
-- 230 kV double circuit | 954677.0726
-- 500 kV single circuit | 1192693.8994
-- 500 kV double circuit | 1908701.7038
-- 500 kV HVDC Bi-pole | 954677.0726
-- 600 kV HVDC Bi-pole | 1002398.4988
backup generation | depends on sources data
curtailment | output - last resort
sector integration - transportation
-- electric vehicles | base msrp | est. tax credit (US) | body type | seats | EPA range (miles conv to km) | batt size [kWh] | charge rate [kW] | [16 empty] | http://www.plugincars.com/cars
bmw i3 | 43300 | 7500 | sedan | 4 | 130.3565 | 22 | 6.6
chevrolet spark | 26000 | 7500 | coupe | 4 | 131.9659 | 19 | 3.3
fiat 500 e | 32600 | 7500 | sedan | 4 | 140.0126 | 24 | 6.6
ford focus electric | 30000 | 7500 | sedan | 5 | 122.3098 | 23 | 6.6
kia soul ev | 34500 | 7500 | sedan | 5 | 149.6686 | 27 | 6.6
mercedes B-class electric | 42400 | 7500 | sedan | 5 | 136.7939 | 28 | 10
mitsubishi i-MiEV | 23800 | 7500 | sedan | 4 | 99.7791 | 16 | 3.3
nissan LEAF | 29800 | 7500 | sedan | 5 | 135.1846 | 24 | 6.6
smart electric drive | 25700 | 7500 | coupe | 2 | 109.4351 | 17 | 3.3
tesla model s | 71000 | 7500 | sedan | 5 | 426.4751 | 85 | 10
volkswagen E-golf | 36300 | 7500 | sedan | 5 | 133.5752 | 24 | 7.2
tesla model X | 80000 | 7500 | SUV | 7 | 370.1482 | 85 | 10
-- comparison with gas vehicles | base msrp | no tax credits | body type | seats | fuel consumption (city/hwy/combined) [L/100km] | ghg emissions
smart | 14930 |  | coupe | 2 | 6.9/5.7/6.3 | 130g/km | [17 empty] | http://www.thesmart.ca/ca/en/index.html
fiat 500 | 16745 |  | sedan | 4 | 8.7/6.9 | [18 empty] | http://www.fiatcanada.com/en/2015/500/
ford focus | 17170 |  | sedan | 5 | 9.3/6.7/8.1 | [18 empty] | http://www.ford.ca/cars/focus/specifications/
ford explorer | 30700 |  | suv | 7 | 13.7/9.7 | [18 empty] | http://www.thesmart.ca/ca/en/index.html
[7 empty] | vehicle class | required battery size [kWh] | [15 empty] | "Impacts Assessment of PHEV on Electric Utilities and Regional US Power Grids Part 1: Technical Analysis" PNNL
--plug-in hybrid | assume average vehicle travels about 50 km/day - battery could easily displace fuel for such distance | [5 empty] | compact sedan | 8.6
[7 empty] | mid-size sedan | 9.9
[7 empty] | mid-size SUV | 12.5
[7 empty] | full-size SUV | 15.2
| costs |  | HEV cost premium avg $4000 | [20 empty] | Sovacool, B. and Hirsh, R. "Beyond batteries: an examination of the benefits and barriers to PHEVs and a V2G transition"
annual revenue for V2G ancillary services (grid regulation) $4000/vehicle
** cost savings dependent on electricity pricing - current avg 110 c/L for gas, 8.0 c/kWh off peak (CAD)
| ghg emission reductions |  | assuming 50% penetration, reduces GHG emissions by 27%
| petroleum displacement |  | up to 6.5 million boe/day
| benefits to grid |  | cars can serve as distributed generators
storage support - particularly for wind when generation at night corresponds with typical charge time
| base msrp | est. tax credit | body type | seats | epa range (elec only) | battery size | charge rate | [16 empty] | http://www.plugincars.com/cars
cadillac ELR | 76000 | 7500 | coupe | 4 | 59.5456 | 17 | 3.3
chevy volt | 35200 | 7500 | sedan | 4 | 61.1549 | 17 | 3.3
ford c-max energi | 32600 | 3700 | wagon | 5 | 32.1868 | 8 | 3.3
ford fusion energi | 35600 | 3700 | sedan | 5 | 32.1868 | 7 | 3.3
honda accord PH | 40700 | 3700 | sedan | 2 | 20.9214 | 7 | 6.6
porsche cayenne s e-hybrid | 78000 | 5300 | SUV | 5 | 22.5308 | 11 | 3.6
porsche panamera s e-hybrid | 100000 | 4700 | SUV | 4 | 24.1401 | 9 | 3
toyota prius PH | 30800 | 2500 | sedan | 5 | 17.7027 | 4 | 3.3
-- hybrid buses | cost premium avg 200 000 (~500 000 compared to 300 000) - mostly offset by govt | [22 empty] | "Hybrid Buses Costs and Benefits" EESI
30% ghg reduction
37% improvement in fuel economy
88% improvement in fuel efficiency
O&M (inc. fuel) costs 15% lower
| orion VII can carry average 51 passengers at peak times - vehicle displacement? | [22 empty] | https://www.ttc.ca/Routes/General_Information/General_Information.jsp
Note on V4: Madeleine: Note: the operating reserve coefficient is a fraction of generation in Nils' paper
Note on B74: Madeleine: Need to get real values here

## modeled attributes
Non-vre technology assumptions
| Cost - related Technology Characteristics |  | Operating Characteristics |  | Ramping Characteristics
col. | start up cost | shut down cost | min up time | min down time | ramp rate max | ramp rate min | start up ramp limit | shut down ramp limit
| [$ / MWcap] | [$ / MWcap] | [hours] | [hours] | [MW/hr p MWcap] | [MW/hr p MWcap] | [MW/hr p MWcap] | [MW/hr p MWcap]
coal | 54 |  | 24 | 12 | 0.1 | -0.1
Natural gas
NG_CC | 66 |  | 8 | 4 | 0.25 | -0.25
NG_CT | 26 |  | 1 | 1 | 1 | -1
NG_CG | 26 |  | 1 | 1 | 1 | -1
diesel |  |  | 1 | 1 | 0.25 | -0.25
fuel oil |  |  | 1 | 1 | 0.25 | -0.25
nuclear | 55 |  | 168 | 24 | 0.01 | -0.01
hydro |  |  |  |  | 1 | -1
hydro_hourly |  |  |  |  | 1 | -1
hydro_daily |  |  |  |  | 1 | -1
hydro_monthly |  |  |  |  | 1 | -1
geothermal
biomass | 54 |  | 8 | 6 | 0.05 | -0.05
biogas | 54 |  | 8 | 6 | 0.05 | -0.05
wind
solar
PHS | 0 | 0 | 1 | 1 | 1 | -1
CAES
battery
EV
importexport
Imports
Col number | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Notes: | cost curve equation | combination of variable cost (P^1) and spinning cost (P^0)
| start up cost | cost to commit the unit ($)
shut down cost
| min up time | minimum time for which a unit must be on (status =1) after it is committed [hours]
| min down time | minimum time for which a unit must be off (status = 0) after it is de-commited [hours]
| ramp rate max | positive change in real power over 1 hour (MW/hr) for a spinning unit (with status = 1)
| ramp rate min | negative change in real power over 1 hou (MW/hr) for a spinning unit (with status =1)
| start up ramp limit | maximum positive change in real power over the first hour after startup (MW/hr)
| shut down ramp limit | maximum negative change in real power over the last hor before shutdown (MW/hr)
MW At Marginal Cost

## scenario analysis
Scenario analysis inputs
|  | Installed Capacity Metric | Flexibility Factor Metric | Investment Cost |  | Transmission network capacity metric |  |  |  |  | VRE Resrouce Metric
col. | Installed capacity by type | Max capacity value | Operating reserve coeff. | Total overnight cost in 2014 | Cost | bus number | total installed capacity on bus | fraction of load on bus | total transmission capacity to/from bus | transmission line cost | bus number | Proposed wind capacity | Proposed multi c-Si solar capacity | Proposed mono c-Si solar capacity | Proposed thin film solar capacity
| [MW] | [fraction of installed capacity] | [fraction on installed capacity] | [$/kW installed] | [$] |  | [MW] | [percentage] | [MW] |  |  | [MW] | [MW] | [MW] | [MW]
coal | 1928 | 1 | 0.53 | 2917 | 5623976000 | NW_falls_g | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Natural gas | 0 | 1 | 0 | 0 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
NG_CC | 921 | 1 | 0.53 | 671 | 617991000 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
NG_CT | 707 | 1 | 1 | 968 | 684376000 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
NG_CG | 477 | 1 | 1 | 968 | 461736000
diesel | 0 | 1 | 0.86 | 0 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
fuel oil | 0 | 1 | 0.86 | 0 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
nuclear | 0 | 1 | 0.2 | 5366 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
hydro | 0 | 1 | 0.66 | 2651 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
hydro_hourly | 0 | 1 | 0.66 | 2651 | 0
hydro_daily | 1190 | 1 | 0.66 | 2651 | 3154690000
hydro_monthly | 0 | 1 | 0.66 | 2651 | 0
geothermal | 0 | 1 | 0.32 | 2448 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
biomass | 0 | 1 | 0.53 | 3659 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
biogas | 20 | 1 | 0.53 | 3659 | 73180000
Imports | 0 | [5 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
wind | 618 | 0.2 | 0 | 19.8 | 12236400 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
solar PV | 40 | 0.6 | 0 | 3279 | 131160000 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
PHS | 0 | 0.5 | 1 | 1000 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
batteries | 0 | 0.5 | 1 | 1500 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
EV | 0 | 0.5 | 1 | 0 | 0 |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Col number |  | 1 | 2 |  |  |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Notes: | [6 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 5390.6 | 3489.97 |  |  |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 24470 | 16022.5421 |  |  |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0.22029 | 0.21782 |  |  |  | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[7 empty] | #REF! | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Note on L4: Madeleine:

## vre plants
plant ID | name | kind | latitude | longitude | [MW] | bus | bus-old | technology type | unit capacity [kW] | latitude_MERRA | longitude_MERRA
Wind | Wind_1 | Wind_Onshore | 50.0195 | -108.4936 | 11 | Swift Current | Bone Creek | V_112-3.0 | 3075 | 280 | 107
Wind | Wind_2 | Wind_Onshore | 50.3991 | -107.2231 | 177 | Swift Current | Swift Current_138 | V_112-3.0 | 3075 | 281 | 109
Wind | Wind_3 | Wind_Onshore | 50.414 | -102.914 | 20 | Peebles | Peebles_138 | V_112-3.0 | 3075 | 281 | 116
Wind | Wind_4 | Wind_Onshore | 50.0781 | -108.393 | 11 | Swift Current | Bone Creek | V_112-3.0 | 3075 | 280 | 107
Wind | Wind_5 | Wind_Onshore | 50.1919 | -101.7433 | 26 | Kennedy | Kennedy | V_112-3.0 | 3075 | 280 | 117
Wind | Wind_6 | Wind_Onshore | 50.3989 | -106.9585 | 23 | Swift Current | Swift Current_138 | V_112-3.0 | 3075 | 281 | 110
Wind | Wind_7 | Wind_Onshore | 49.6266 | -105.9754 | 200 | Assiniboia | Assiniboia_138 | V_112-3.0 | 3075 | 279 | 111
Wind | Wind_8 | Wind_Onshore | 50.1621 | -107.4579 | 150 | Swift Current | Swift Current_138 | V_112-3.0 | 3075 | 280 | 109
Solar | Solar_1 | multi_c_Si | 50.1621 | -107.4579 | 10 | Swift Current | Swift Current_139 | FS395 | 95 | 280 | 109
Solar | Solar_2 | multi_c_Si | 50.1621 | -107.4579 | 10 | Swift Current | Swift Current_140 | FS395 | 95 | 280 | 109
Solar | Solar_3 | multi_c_Si | 50.1621 | -107.4579 | 10 | Swift Current | Swift Current_141 | FS395 | 95 | 280 | 109
Solar | Solar_4 | multi_c_Si | 50.1621 | -107.4579 | 10 | Swift Current | Swift Current_142 | FS395 | 95 | 280 | 109

## non-vre plants
plant ID | name | kind | cost curve equation | pmin | [MW] | bus | initial power | initial status | hours in status | storage content | initial power | initial status | hours in status | storage content | cascade group name | number | min storage | max storage | min water discharge | max water discharge | h factor | efficiency
hydro_daily_1 | hydro_daily_1 | hydro_daily | 3.3P | 0 | 1190 | Coteau Creek
NG_CC_1 | NG_CC_1 | NG_CC | 75.5P | 12.2 | 61 | Queen Elizabeth
NG_CC_2 | NG_CC_2 | NG_CC | 75.5P | 12.4 | 62 | Queen Elizabeth
NG_CC_3 | NG_CC_3 | NG_CC | 75.5P | 19 | 95 | Queen Elizabeth
NG_CC_4 | NG_CC_4 | NG_CC | 75.5P | 5 | 25 | Queen Elizabeth
NG_CC_5 | NG_CC_5 | NG_CC | 75.5P | 5 | 25 | Queen Elizabeth
NG_CC_6 | NG_CC_6 | NG_CC | 75.5P | 5 | 25 | Queen Elizabeth
NG_CC_7 | NG_CC_7 | NG_CC | 75.5P | 5 | 25 | Queen Elizabeth
NG_CC_8 | NG_CC_8 | NG_CC | 75.5P | 5 | 25 | Queen Elizabeth
NG_CC_9 | NG_CC_9 | NG_CC | 75.5P | 5 | 25 | Queen Elizabeth
NG_CC_10 | NG_CC_10 | NG_CC | 75.5P | 7.2 | 36 | Queen Elizabeth
NG_CC_11 | NG_CC_11 | NG_CC | 75.5P | 7.2 | 36 | Queen Elizabeth
NG_CC_12 | NG_CC_12 | NG_CC | 75.5P | 7.2 | 36 | Queen Elizabeth
NG_CC_13 | NG_CC_13 | NG_CC | 75.5P | 19 | 95 | Battleford
NG_CC_14 | NG_CC_14 | NG_CC | 75.5P | 70 | 350 | Swift Current
NG_CG_1 | NG_CG_1 | NG_CG | 136.5P | 16.6 | 83 | Queen Elizabeth
NG_CG_2 | NG_CG_2 | NG_CG | 136.5P | 16.6 | 83 | Queen Elizabeth
NG_CG_3 | NG_CG_3 | NG_CG | 136.5P | 16.6 | 83 | Queen Elizabeth
NG_CG_4 | NG_CG_4 | NG_CG | 136.5P | 15.2 | 76 | Lloydminster
NG_CG_5 | NG_CG_5 | NG_CG | 136.5P | 15.2 | 76 | Lloydminster
NG_CG_6 | NG_CG_6 | NG_CG | 136.5P | 15.2 | 76 | Lloydminster
Coal_1 | Coal_1 | coal | 104P | 0 | 672 | Boundary Dam
Coal_2 | Coal_2 | coal | 104P | 0 | 120 | Boundary Dam
Coal_3 | Coal_3 | coal | 104P | 0 | 139 | Boundary Dam
Coal_4 | Coal_4 | coal | 104P | 0 | 139 | Boundary Dam
Coal_5 | Coal_5 | coal | 104P | 0 | 291 | Poplar River
Coal_6 | Coal_6 | coal | 104P | 0 | 291 | Poplar River
Coal_7 | Coal_7 | coal | 104P | 0 | 276 | Shand
Biogas_1 | Biogas_1 | biogas | 100P | 1 | 5 | Shand
Biogas_2 | Biogas_2 | biogas | 100P | 1 | 5 | Regina
Biogas_3 | Biogas_3 | biogas | 100P | 1 | 5 | Battleford
Biogas_4 | Biogas_4 | biogas | 100P | 1 | 5 | Queen Elizabeth
NG_CT_1 | NG_CT_1 | NG_CT | 136.5P | 9 | 46 | Battleford
NG_CT_2 | NG_CT_2 | NG_CT | 136.5P | 9 | 46 | Battleford
NG_CT_3 | NG_CT_3 | NG_CT | 136.5P | 18 | 89 | Tantallon
NG_CT_4 | NG_CT_4 | NG_CT | 136.5P | 18 | 89 | Tantallon
NG_CT_5 | NG_CT_5 | NG_CT | 136.5P | 9 | 46 | Brada
NG_CT_6 | NG_CT_6 | NG_CT | 136.5P | 9 | 46 | Brada
NG_CT_7 | NG_CT_7 | NG_CT | 136.5P | 9 | 46 | Brada
NG_CT_8 | NG_CT_8 | NG_CT | 136.5P | 35 | 176 | Battleford
NG_CT_9 | NG_CT_9 | NG_CT | 136.5P | 16 | 79 | Battleford
NG_CT_10 | NG_CT_10 | NG_CT | 136.5P | 9 | 44 | Meadow Lake
importexport_1 | importexport_1 | importexport | 0P | 0 | 1 | Queen Elizabeth

## storage
plant ID | name | kind | pmin | [MW] | storagecapacitymax | pumprampmax | resevoir level | bus | cost curve equation | initial power | initial status | hours in status | storage content

## EV_aggregator
plant ID | name | kind | [MW] | storagecapacitymax | pumprampmax | unpluggedhours | tripenergy | bus | initial power | initial status | hours in status | storage content | cost curve equation | pmin

## demand response
index | 1 | 2
| initial status | hours in status
initial values | 0 | 0
constraint:
| over-production | under-production
maximum hourly dr limit (% of schedule) | 130% | 70%
| maximum | minimum
absolute hourly dr limit (MW) | 6000 | 2
maximum
maximum daily dr (MW) | 144000
| increasing_shed | decreasing_shed
ramping limiatations (MW) | 1000 | -1000
| uptime | downtime
minimum up/down times (hours) | 1 | 1

## demand centres
city | frac pop | bus | dr_potential | region
Load_1 | 33% | Assiniboia | 0.0068577 | Weyburn
Load_2 | 33% | Assiniboia | 0.0037887 | Assiniboia
Load_3 | 50% | Battleford | 0.017298 | North Battleford
Load_4 | 25% | Battleford | 0.010903 | Lloydminster
Load_5 | 50% | Beatty | 0.016432 | Melfort
Load_6 | 50% | Beatty | 0.039108 | Prince Albert
Load_7 | 33% | Boundary Dam | 0.0095443 | Estevan
Load_8 | 33% | Boundary Dam | 0.0068577 | Weyburn
Load_9 | 25% | Brada | 0.010903 | Lloydminster
Load_10 | 33% | Codette | 0.0072065 | Battleford
Load_11 | 100% | Codette | 0.021144 | Kindersley
Load_12 | 33% | Condie | 0.078969 | Regina
Load_13 | 50% | Condie | 0.00754 | Wynyard
Load_14 | 100% | Coteau Creek | 0.042969 | Moose Jaw
Load_15 | 50% | Coteau Creek | 0.13813 | Saskatoon
Load_16 | 33% | Coteau Creek | 0.0072065 | Battleford
Load_17 | 50% | EB Campbell | 0.016432 | Melfort
Load_18 | 50% | EB Campbell | 0.016872 | La Loche
Load_19 | 33% | Kennedy | 0.0095443 | Estevan
Load_20 | 25% | Lloydminster | 0.010903 | Lloydminster
Load_21 | 25% | Meadow Lake | 0.010903 | Lloydminster
Load_22 | 50% | Meadow Lake | 0.016872 | La Loche
Load_23 | 33% | Pasqua | 0.0037887 | Assiniboia
Load_24 | 50% | Peebles | 0.014453 | Melville
Load_25 | 33% | Peebles | 0.078969 | Regina
Load_26 | 50% | Peebles | 0.00754 | Wynyard
Load_27 | 33% | Poplar River | 0.0068577 | Weyburn
Load_28 | 33% | Poplar River | 0.0037887 | Assiniboia
Load_29 | 50% | Queen Elizabeth | 0.13813 | Saskatoon
Load_30 | 33% | Queen Elizabeth | 0.0072065 | Battleford
Load_31 | 50% | Queen Elizabeth | 0.039108 | Prince Albert
Load_32 | 50% | Queen Elizabeth | 0.017298 | North Battleford
Load_33 | 33% | Regina | 0.078969 | Regina
Load_34 | 50% | Rushlake Creek | 0.004941 | Maple Creek
Load_35 | 100% | Rushlake Creek | 0.027967 | Swift Current
Load_36 | 33% | Shand | 0.0095443 | Estevan
Load_37 | 50% | Swift Current | 0.004941 | Maple Creek
Load_38 | 50% | Tantallon | 0.014453 | Melville
Load_39 | 100% | Tantallon | 0.032443 | Yorkton

## existing transmission
name | from bus | to bus | voltage | circuits | length | pmax | reactance-old | reactance | line type | line cost
Line_1 | Poplar River | Assiniboia | 230 |  | 70 |  | 28 | 0.028
Line_2 | Queen Elizabeth | Beatty | 230 |  | 180 |  | 72 | 0.072
Line_3 | Queen Elizabeth | Beatty | 230 |  | 180 |  | 72 | 0.072
Line_4 | Regina | Boundary Dam | 230 |  | 210 |  | 84 | 0.084
Line_5 | Regina | Boundary Dam | 230 |  | 210 |  | 84 | 0.084
Line_6 | Coteau Creek | Brada | 230 |  | 210 |  | 84 | 0.084
Line_7 | Beatty | Codette | 230 |  | 90 |  | 36 | 0.036
Line_8 | Beatty | Codette | 230 |  | 90 |  | 36 | 0.036
Line_9 | Peebles | Condie | 230 |  | 150 |  | 60 | 0.06
Line_10 | Poplar River | Condie | 230 |  | 140 |  | 56 | 0.056
Line_11 | Regina | Condie | 230 |  | 10 |  | 4 | 0.004
Line_12 | Swift Current | Coteau Creek | 230 |  | 140 |  | 56 | 0.056
Line_13 | Beatty | EB Campbell | 230 |  | 160 |  | 64 | 0.064
Line_14 | Codette | EB Campbell | 230 |  | 70 |  | 28 | 0.028
Line_16 | Boundary Dam | Kennedy | 230 |  | 140 |  | 56 | 0.056
Line_17 | Peebles | Kennedy | 230 |  | 45 |  | 18 | 0.018
Line_18 | Tantallon | Kennedy | 230 |  | 70 |  | 28 | 0.028
Line_19 | Brada | Lloydminster | 230 |  | 150 |  | 60 | 0.06
Line_20 | Battleford | Meadow Lake | 230 |  | 170 |  | 68 | 0.068
Line_21 | Brada | Meadow Lake | 230 |  | 170 |  | 68 | 0.068
Line_22 | Poplar River | Pasqua | 230 |  | 140 |  | 56 | 0.056
Line_23 | Condie | Queen Elizabeth | 230 |  | 250 |  | 100 | 0.1
Line_24 | Assiniboia | Rushlake Creek | 230 |  | 120 |  | 48 | 0.048
Line_25 | Boundary Dam | Shand | 230 |  | 12 |  | 4.8 | 0.0048
Line_26 | Peebles | Shand | 230 |  | 120 |  | 48 | 0.048
Line_27 | Rushlake Creek | Swift Current | 230 |  | 20 |  | 8 | 0.008

## modeled attributes _original
Non-vre technology assumptions
| Cost - related Technology Characteristics |  |  | Operating Characteristics |  | Ramping Characteristics
col. | cost curve equation | start up cost | shut down cost | min up time | min down time | ramp rate max | ramp rate min | start up ramp | shut down ramp
| [$/ MBTU] | [$ / MWcap] | [$ / MWcap] | [hours] | [hours] | [MW/hr p MWcap] | [MW/hr p MWcap] | [MW/hr p MWcap] | [MW/hr p MWcap]
coal | 0.00888P + 10000 | 105 | 0 | 3 | 3 | 120 | -120 | 0.1 | -0.1
Natural gas | 0P + 10000 |  | 0 | 4 | 3
NG_CC | 0.01439P + 10000 | 79 | 0 | 4 | 3 | 300 | -300 | 0.25 | -0.25
NG_CT | 0.02403P + 10000 | 103 | 0 | 4 | 3 | 480 | -480 | 2 | -2
diesel | 0.08441P + 10000 | 10000000 | 0
fuel oil | 0.05064P + 10000 | 10000000 | 0
nuclear | 0.00346P + 10000 | 500 | 0 | 10 | 3 | 300 | -300 | 0.076923 | -0.076923
hydro | 0.00188P + 10000
geothermal | 0P + 10000
biomass | 0.01158P + 10000
wind | 0P
solar | 0P
PHS | 0P + 0 | 0 | 0
CAES | 0P + 0 | 0 | 0
battery | 0P + 0 | 0 | 0
EV | 0P + 0 | 0 | 0
Col number | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Notes: | cost curve equation | combination of variable cost (P^1) and spinning cost (P^0)
| start up cost | cost to commit the unit ($)
shut down cost
| min up time | minimum time for which a unit must be on (status =1) after it is committed [hours]
| min down time | minimum time for which a unit must be off (status = 0) after it is de-commited [hours]
| ramp rate max | positive change in real power over 1 hour (MW/hr) for a spinning unit (with status = 1)
| ramp rate min | negative change in real power over 1 hou (MW/hr) for a spinning unit (with status =1)
| start up ramp limit | maximum positive change in real power over the first hour after startup (MW/hr)
| shut down ramp limit | maximum negative change in real power over the last hor before shutdown (MW/hr)

## excel input instructions
*create dropdown list with these options
| Generating Plant IDs |  | Storage Plant IDs
| wind |  | PHS
| wind offshore |  | CAES
| solar PV multi c-Si |  | FES
| solar PV mono c-Si |  | Pb-acid
| solar PV thin film |  | Ni-Cd
| solar thermal |  | Na-S
| coal |  | Li-ion
| NG combined |  | vanadium
| NG simple |  | hydrogen
| diesel |  | flow battery
| fuel oil |  | capacitor
| nuclear |  | supercapacitor
| hydro |  | SMES
| geothermal |  | thermal
biomass
| Trina TSM-PDG5-255 | multi c-Si | TO DO: need to change 'vre plants' sheet so that the area [m^2] and # modules gets updated according to these values, given the module type
| nominal pwr at STC [Wp] | 255
| area | 1.688
| Canadian Solar CS6V-225MM | mono c-Si
| nominal pwr at STC [Wp] | 225
| area | 1.353
| First Solar FS395 | CdTe
| nominal pwr at STC [Wp] | 95
| area [m^2] | 0.72
Each unique node must be listed at least once in the 'existing transmission' sheet under the 'from bus' category
On the demand centres sheet, the dr_potential column needs to add to one. Also the dr_potential value for each city needs to be pro-rated by the percentage of load that that city consumes. The fomula in powersystems.py (Load constraints) for the second OPF is scheduled_load(time) - power(time) >= dr_3 (UC dr) *dr_potential for each city. As such if the dr_3*dr_potenail is greater than the scheduled_load value for that city in that hour, then the OPF would have to have a negative power value, which is obviously impossible, and so it fails.

## lists
USER: do not alter this sheet
VRE generation types | Wind | Solar
| wind_onshore | multi_c_Si
| wind_offshore | thin_film
mono_c_Si
Technologies | wind_onshore | wind_offshore | multi_c_Si | thin_film | mono_c_Si
| V_112-3.0 | V_112-3.0 | TSM-PDG5-255 | FS395 | CS6V-225MM
|  |  | CHSM_6610P_250 | FS935
|  |  | CS6X_320P | FS4122_2